| 05SY - Systemwide | Cxxx-NCR-000030 | NCR | Corroded PRD Cover Plate Fixings |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2015-10-28 | 2015-10-29 11:46 | 1 | 2015-07-13 16:37 | Track - Track Bed | 500 |  | Material | Reject | 4 (0.5-3k) | Complete | Material/Preservation Problems - Not Defined | Completed |  | Connaught Tunnel – Eastbound - Particularly A3 The fixings installed to hold the PRD covers are corroding and leaving staining down the stainless steel covers (see attached pictures). The hammer screws and washers are Zinc plated as specified on the drawing.
| 05SY - Systemwide | Cxxx-NCR-000031 | NCR | Defective RF 196M Baseplate for Connaught |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2015-10-14 | 2015-10-13 12:47 | -1 | 2015-07-15 11:40 | Track - Rails and Sleepers | 1000 |  | Manufacturing Defect | Reject | 4 (0.5-3k) | Complete | Subcontractor Problems - Other | Completed |  | RF 196 M baseplate for Connaught ID number: 15022187 The surface of the baseplate where the serrated washer is to be fixed is flat. Pictures attached.
| 05SY - Systemwide | Cxxx-NCR-000032 | NCR | Galvanisation Issue of T-Head Screws Associated with Baseplates for Connaught Tunnel |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-05-31 | 2016-03-14 16:03 | -78 | 2015-07-15 14:07 | Track - Rails and Sleepers | 6000 |  | Manufacturing Defect | Reject | 3 (3-6k) | Complete | Material/Preservation Problems - Other | Completed |  | It has been reported that when the nut is fitted onto the T-head screws it is sometimes difficult to screws the nut (need a lot of force), also the thread seem to be stripped of its galvanisation after tightening and the it is difficult to tighten the clips correctly to the required torque.
| 05SY - Systemwide | Cxxx-NCR-000033 | NCR | Commencing works at VDP and CHS without an accepted ITP |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2015-09-15 | 2015-08-28 12:14 | -18 | 2015-07-17 14:57 | Track - Track General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Works has commenced on the Switches and Crossings at Victoria Dock Portal and Custom House without first obtaining a Code 1 acceptance from the Supervisor (and Code 1 design drawings).
| 05SY - Systemwide | Cxxx-NCR-000034 | NCR | Non-compliant baseplate undersides |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2015-10-18 | 2015-10-16 13:42 | -2 | 2015-07-20 11:03 | Track - Track Bed | 2500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Connaught EB CH18371 – CH 18402 (Cages 149-154) The inspection of baseplate undersides undertaken in cage 150 as per the ITP revealed non-compliant surfaces; 2 No baseplates were initially inspected and as a result of these 2 failing, 4 more were checked. As these 4 failed as well, all baseplates cast on the same date as cage 150 (14/05/2015) were inspected. Pictures available, full assessment will follow.
| 05SY - Systemwide | Cxxx-NCR-000035 | NCR | Longitudinal PRD Installation |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2015-08-29 | 2015-08-11 08:03 | -18 | 2015-07-30 11:41 | Track - Track Bed | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Victoria Dock Portal Site Ch 16688EB to 16708EB Drawings state tolerances for longitudinal PRD strip installation are: 1250mm +/- 40mm from edge of slab. Design drawing: Cxxx-__-R4-DDL-CR144_Z-10550 Longitudinal PRD strip installed at some points 1290 to 1370mm from edge of slab.
| 05SY - Systemwide | Cxxx-NCR-000036 | NCR | Timber cast on track slab wall |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2015-09-28 | 2015-09-16 13:20 | -12 | 2015-07-30 11:59 | Track - Track Bed | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | A strip of 18mm ply wood has been found to be cast in the slab at CH17+870 on the EB 6ft side. No inclusion of foreign materials shall be allowed in the concrete slab.
| 05SY - Systemwide | Cxxx-NCR-000037 | NCR | Water ingress through trackslab at WB CH18269 |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-04-30 | 2016-03-21 11:39 | -40 | 2015-08-03 16:50 | Track - Track Bed | 10000 |  | System Defect | Repair | 2 (6-60k) | Complete | External Phenomenon - Other | Completed |  | Connaught Tunnel WB Cage 514 – approx. CH18294 Concrete poured in this section on 20 July 2015. During the concrete pour, water ingress started to occur through the wet concrete. The following observations were made on the 21 July 2015: Concrete around the place where the water emerged from the top of the Stage 2 concrete had not properly hardened Concrete round about approx. 0.5m radius was hardened as expected. Small flow of water through the Stage 2 concrete, emerging on the top surface, still present Small flow of surface water also visible in the outer drainage channel Water flowing through the Stage 2 concrete is being conducted to the central drainage channel through an additional surface groove formed in the top surface of the Stage 2 concrete. The water emerging from the Stage 2 concrete appears to be clear. Nearest visible transverse pressure relief drains are at: Ch 18273 (uphill) Ch 18267 (downhill) There is no sign of water in the nearby (+/- 1.5m) spindle holes left in the Stage 2 concrete Please see photos below and also attached Site Observation TRK CT /0041.
| 05SY - Systemwide | Cxxx-NCR-000038 | NCR | Crossing Nose Vertical Alignment Defect |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-05-31 | 2016-05-31 14:38 | 0 | 2015-08-14 09:47 | Track - Turnouts | 2000 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | On the 05/08/2015 at VDP & CHS, C11 & C12 Crossover (and C13 & C14 Crossover). The Cast Manganese Crossings are 4 mm higher than the rest of the turnout alignment. However, rails on both sides of the crossings (sharing the same bearer) are in the correct position according to survey. It appears that there is an issue between the design distance of top of rail (crossing) to top of bearer and the actual measurement on site. C11 has been concreted on the 06/08/2015 following the assessment that this could be corrected afterwards.
| 05SY - Systemwide | Cxxx-NCR-000039 | NCR | Baseplate underside failure cage 575 |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2015-11-12 | 2015-11-11 15:15 | -1 | 2015-08-14 10:05 | Track - Track Bed | 1000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Connaught tunnel WB CH 18582, 3rd baseplate on the RH side rail of cage 575 (from low to high chainage) 2 voids present greater in width than 30-40 mm and spaced less than 15 mm
| 05SY - Systemwide | Cxxx-NCR-000040 | NCR | Cracks appearing in S&C concrete slab at Victoria Dock Portal site |  | Contr | SKC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-04-14 | 2016-04-11 11:15 | -3 | 2015-09-04 14:58 | Track - Track Bed | 5000 |  | Design | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | Track concrete slab is cracked in the proximity of Pressure Relief Drainage transversal strips and first stage concrete construction joints at Victoria Dock Portal turnouts. Installation of all materials and components has been carried out in conformance with the accepted design (Cxxx-__-R4-LRG-CRG03-50004) and approved method statement (Cxxx-__-R4-GMS-CRG03-50009).
| 05SY - Systemwide | Cxxx-NCR-000042 | NCR | Water Ingress In High Attentuation Slepers & S312 Twin Booted Sleepers |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2015-11-18 | 2015-10-12 11:42 | -37 | 2015-09-09 10:51 | Track - Rails and Sleepers | 1000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper handling of material | Completed |  | Prior to the concrete pouring of the test track at Plumstead it was noted that the HAS and S312 Twin Booted sleepers were not properly sealed. There was water present in the boot of the sleepers. The weather conditions had been adverse due to heavy rain. On inspection of the sleeper gaskets it was found that the cause of the water ingress was due to ineffective sealing.
| 05SY - Systemwide | Cxxx-NCR-000043 | NCR | S312 Twin Booted Sleepers |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-01-29 | 2016-01-29 15:43 | 0 | 2015-09-10 10:58 | Track - Rails and Sleepers | 4000 |  | Manufacturing Defect | Reject | 3 (3-6k) | Complete | Verification Problems - Inspection points not adequate | Completed |  | Some of the sleepers being delivered on site were found to be defective. This was pointed out to the supplier/manufacturer at the time. As a result NCR000026 was also raised. In spite of several discussions and constant reminders the situation is far from satisfactory. The latest delivery of S312 Twin Booted sleepers have found to be cracked around the tie bar. Approximately 40 have been identified so far.
| 05SY - Systemwide | Cxxx-NCR-000044 | NCR | Broken Baseplate - Old Oak Common - Demonstartion Track |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2015-11-25 | 2015-11-25 13:38 | 0 | 2015-09-15 10:00 | Track - Rails and Sleepers | 2000 |  | Manufacturing Defect | Reject | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Whilst tightening the nut on the 'T' bolt within the baseplate assembly, one of the two brackets housing this bolt snapped. These brackets are part of the baseplate casting.
| 05SY - Systemwide | Cxxx-NCR-000045 | NCR | Concrete Poured Without Flow Table Test |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2015-10-28 | 2015-10-29 12:08 | 1 | 2015-09-15 09:59 | Track - Track Bed | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Supervision - Other | Completed |  | Due to lack of equipment and concrete technician on site, a concrete load of 7.6 cubic meters from the ready mix truck on the evening of 4th September,2015 was poured without carrying out a flow table test on the Westbound Road at Victoria Dock Portal (between CH16922 and CH16930). Initially 3 cubic meters of concrete had been poured from the first lorry load. The second lorry load was rejected and the batching plant advised that further deliveries were unlikely. As a result the concrete technicians were demobilised for the day. The carpenters were instructed to install an 'emergency stop end'. This was found to be not possible because of the high workability of the concrete. Whilst this was taking place another a concrete truck arrived on site at approximately 18.30 hours without prior notice. The load was poured since it resembled the characteristics of the previous compliant loads. Moreover the previous 28 day compressive strength of the cubes in the area had been found to be sufficient. However 4 cubes of concrete were filled using a non UKAS person. These cubes have now been sent for a 28 day test.
| 05SY - Systemwide | Cxxx-NCR-000046 | NCR | Missing Incline Wedge on Standard Bearer |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-01-15 | 2016-01-15 14:18 | 0 | 2015-09-18 10:51 | Track - Rails and Sleepers | 2000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | RH side of the 7th Bearer towards high chainage from C12 hollow bearer (CH ˜16865, WB, VDP) 1:20 inclined wedge missing on the left hand side of a standard bearer at CH ˜16865 between C12 and C13 (WB track, VDP)
| 05SY - Systemwide | Cxxx-NCR-000047 | NCR | Sleeper out of square |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2015-12-17 | 2015-12-08 10:14 | -9 | 2015-09-18 11:09 | Track - Rails and Sleepers | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Last sleeper (approximately CH 16818) before C12 from low chainage , WB VDP is out of tolerance for spacing and squareness with the rail. Sleeper spacing to bearer and previous sleeper is 650 mm +/-15 Sleeper not squared with the rail. As a result the spacing between this sleeper and the previous bearer is beyond the allowed tolerance and so is the spacing with the next sleeper. Sketch and pictures attached.
| 05SY - Systemwide | Cxxx-NCR-000048 | NCR | Qualification of tolerance for survey controls |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2015-11-10 | 2015-10-29 14:05 | -12 | 2015-09-21 13:13 | Surveying - GIS Engineering & Land Surveying | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | There is a requirement to qualify the minimum constraints, acceptable degrees of freedom and optimal limits.
| 05SY - Systemwide | Cxxx-NCR-000049 | NCR | Omission of identification of changes to documents as required by ISO9001 |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2015-11-09 | 2015-10-30 14:38 | -10 | 2015-09-21 13:23 | Surveying - GIS Engineering & Land Surveying | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Not Defined | Completed |  | Revision changes to Cxxx-__-R-RGN-CRG03-50002 not identified as required by ISO 9001:2008 clause 4.2.3c
| 05SY - Systemwide | Cxxx-NCR-000050 | NCR | Tunnel Ventilation Attenuators – non conforming product |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-03-02 | 2016-02-10 16:17 | -21 | 2015-09-25 08:10 | Systems - Ventilation and Pressure Relief | 5000 |  | Design | Use As-Is | 3 (3-6k) | Complete | Verification Problems - Other | Completed |  | Works Information, Vol 2C Tunnel Ventilation Equipment Specification, Cxxx-MMD-O8-RSP-CR001-00003 v 5.0, clause 9.1 requires the attenuators to be of splitter type, with removable splitters installed in a free standing fabricated housing. The product under supply from the Contractors supplier (__) contains modular units with fixed splitters within the modules, the splitters are not removable from the modules as stipulated in the above specification reference. Affect of non compliance: This non compliance is causing complications surrounding the access and maintenance of the attenuators and the maintenance spatial access routes within certain stations and shafts.
| 05SY - Systemwide | Cxxx-NCR-000051 | NCR | Turnouts C12 & C13 stock rails/fronts alignment |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-11-02 | 2016-09-26 07:27 | -37 | 2015-09-30 10:42 | Track - Turnouts | 10000 |  | Manufacturing Defect | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Other | Completed |  | Incorrect curvature of stock rails / fronts (reverse curve) resulting in incorrect alignment and track gauge which can only be maintained with additional lateral support. Main line is L/H curve R=950m Turnout C12 – Right hand curved stock rail (6ft side) - reverse curve R=254m Turnout C13 – Left hand curved stock rail (6ft side) - reverse curve R=245m
| 05SY - Systemwide | Cxxx-NCR-000052 | NCR | C15 bearers spacing |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2015-11-30 | 2015-10-29 11:42 | -32 | 2015-09-30 12:31 | Track - Turnouts | 1000 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper handling of material | Completed |  | Custom House, C15 Turnout Bearer have been laid as per manufacturer’s markings (from pre-assembly) Spacing: - 667mm btw 1515 and 1516 bearers - 625mm btw 1516 and 1517 bearers This is contradictory to Drawing Cxxx-__-R4-DDA-CR146_1-00401 Bearer spacing through switch area should be 650mm (± 10mm)
| 05SY - Systemwide | Cxxx-NCR-000053 | NCR | Infill Drainage – Exposed Aggregates – Connaught |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2015-12-29 | 2015-11-06 08:22 | -53 | 2015-09-30 15:34 | Track - Track General | 2000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Not Defined | Completed |  | Connaught Tunnel Heavy rain washed away superficial fine mix leaving aggregate exposed at various channel locations of infill drainage
| 05SY - Systemwide | Cxxx-NCR-000054 | NCR | Defective design of stay wire fixing |  | Contr | SKC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2015-11-24 | 2015-11-27 16:28 | 3 | 2015-10-27 16:49 | Electrical - OHLE | 1500 |  | Design | Reject | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Insufficient distance designed between edge of bolt hole and stay wire connection plate to accommodate both the washer and the fillet weld (rev P02, attached).
| 05SY - Systemwide | Cxxx-NCR-000055 | NCR | Drop tube galvanising found damaged on delivery |  | Contr | SKC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-04-28 | 2016-04-27 15:45 | -1 | 2015-10-27 16:56 | Electrical - OHLE | 2000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper handling of material | Completed |  | When checked at delivery, the galvanising treatment to several OHLE drop tubes was found to be damaged.
| 05SY - Systemwide | Cxxx-NCR-000056 | NCR | OHLE packaging damaged on receipt |  | Contr | SKC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-04-28 | 2016-04-27 15:46 | -1 | 2015-10-27 16:58 | Electrical - OHLE | 2000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper handling of material | Completed |  | Several instances of damaged packaging were observed during receiving inspections of OHLE components. The related goods were damaged.
| 05SY - Systemwide | Cxxx-NCR-000057 | NCR | Manufacture of Rigid Overhead Conductor began before acceptance of ITP |  | Contr | SKC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-03-02 | 2016-03-02 10:01 | 0 | 2015-10-27 16:59 | Electrical - OHLE | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Manufacture of Rigid Overhead Conductor began before CRL acceptance of ITP
| 05SY - Systemwide | Cxxx-NCR-000058 | NCR | Documentation associated to Concrete Train works not accepted by Crossrail as identified during a planned Crossrail surveillance. |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2015-11-04 | 2015-11-06 08:26 | 2 | 2015-10-21 10:04 | Civil - Track | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | During a Crossrail planned surveillance undertaken on 20th October 2015 which was scheduled as a follow up to surveillance Cxxx-XRL-O4-RGN-CR001-50015, it was identified that the following documentation had still not been accepted by Crossrail, 12 days after the Concrete Train works had commenced. -Technical Specification - Construction of Concrete Train for STS - Cxxx-__-R4-RSP-CRG03-50047 (Rev 2) which is the specification that defines requirements for the concrete mix constituents and end product performance. -Component Product Specification – Concrete Mix Design for the STS – Cxxx-__-R4-RSP-CRG03-50057 (Rev 1) which defines concrete compliance to the Technical Specification. -__ ITP – Still internal between __ and __, no eB number produced. This controls the production of pre-blended aggregates for use in the approved concrete mix design. Furthermore, as the Technical Specification had been updated, the changes should be reviewed to highlight the impact on other documentation relating to the Concrete Train works, such as Method Statements and Inspection and Test Plans. Works Information Vol 2B Part 20.4 states “The Contractor shall not start any activity on any part of the works for which the Contract Quality Plan, applicable QSPs or ITPs, are not accepted by the Project Manager”. Furthermore Part 20.8 states “The Contractor and his subcontractors and suppliers of any tier engaged in supplying, manufacturing, construction, installation, commissioning and testing or any other service connected with the works, shall maintain ITPs appropriate for the services they provide that are accepted by the Supervisor ….”
| 05SY - Systemwide | Cxxx-NCR-000059 | NCR | Tensile Splitting testing not undertaken on the Concrete Train concrete mix as required by the Technical Specification |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2015-12-04 | 2015-11-25 13:26 | -9 | 2015-10-21 10:07 | Civil - Track | 500 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | During a Crossrail planned surveillance undertaken on 20th October 2015 which was scheduled as a follow up to surveillance Cxxx-XRL-O4-RGN-CR001-50015, it was identified that Tensile Splitting testing had not been undertaken during the pre-construction trials and during production on the concrete being used as part of the Concrete Train. Technical Specification - Construction of Concrete Train for STS - Cxxx-__-R4-RSP-CRG03-50047 Rev 1 and Rev 2 states a requirement for tensile splitting testing to be undertaken with a performance value of 2.1N/mm2 to be achieved. Following requests during the surveillance, it was stated that none had been carried out.
| 05SY - Systemwide | Cxxx-NCR-000060 | NCR | STS Concrete Compressive Strength Failure at 16h |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2015-11-18 | 2015-11-23 08:52 | 5 | 2015-10-21 11:10 | Track - Track Bed | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | Thames Tunnel EB - CH22+360 - 22+390 Concrete compressive strength at 16h measured at 1.5MPa.
| 05SY - Systemwide | Cxxx-NCR-000061 | NCR | Calibration of Concrete Train weighing mechanisms not undertaken by a UKAS accredited company and in accordance with documented procedures |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-01-18 | 2016-01-15 14:57 | -3 | 2015-10-21 16:32 | Civil - Track | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | During a Crossrail planned surveillance undertaken on 20th October 2015 which was scheduled as a follow up to surveillance Cxxx-XRL-O4-RGN-CR001-50015, calibration reports were made available for the concrete train weighing mechanisms (aggregate, cement, admixtures and water), report certificate number 17890. Following post surveillance review of the reports the following was identified: 1 – __ who undertook the calibration of the weighing mechanisms are not UKAS accredited to undertake calibration activities. The reports detail a UKAS symbol, however following clarification with UKAS this symbol represents that __ have been certified by a UKAS accredited organisation for their Quality Management System, in this instance __ and in fact do not hold UKAS accreditation for calibration services. “The Contractor shall maintain a schedule of all inspection, measuring and test equipment used for the works that includes records of the calibration of such equipment to nationally recognised standards”. 2 – Quality Scheme Ready Mix Concrete (QSRMC) regulations state under clause 7.6 (2.2) ‘Calibration’ that scale increments shale not exceed 10kg for cement and additions, and 50kg for aggregates. On review of the report, the calibration for the aggregates and cement had been undertaken in 100kg increments. 3 - Quality Scheme Ready Mix Concrete (QSRMC) regulations state under clause 7.6 (2.3.1) ‘Calibration’ that all weighing equipment should be calibrated and tested over its full working range by a specialist. The calibration had only been undertaken up to 500kg for both the aggregate and cement, with the working range 4500kg and 1000kg respectively. 4 – On review of the calibration reports it was further identified that no mention had been made to the load cell serial numbers to provide traceability of the issued reports to the load cells calibrated. ISO 9001 states under clause 7.6 ‘Control of Monitoring and Measuring Equipment’ that “Where necessary to ensure valid results, measuring equipment shall … a) be calibrated or verified, or both, at specified intervals, or prior to use, against measurement standards traceable to international or national measurement standards”.
| 05SY - Systemwide | Cxxx-NCR-000062 | NCR | Concrete cubes manufactured for concrete train works not being stored as defined by the British Standard |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2015-12-02 | 2015-11-11 10:22 | -21 | 2015-10-26 13:44 | Civil - Track | 1000 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper storage of material | Completed |  | During a Crossrail planned surveillance undertaken on 22nd October 2015 (night shift) which involved a site visit to witness concrete train activities, it was identified that the concrete train still did not have any facility in place to allow for the manufactured concrete cubes to be stored free from shock and vibration, and within the required environmental conditions. This has resulted in cubes being stored on the walkway curing in non standard ambient temperatures, which can potentially lead to reduced strengths and inconsistent results. BS EN 12390-2:2009 Part 2: Making and curing specimens for strength tests states under clause 5.5 ‘curing of test specimens’; “leave the test specimens in the mould for at least 16 hours, but not longer than 3 days, protected against shock, vibration and dehydration at a temperature of (20+-5)oC”. This NCR was raised resulting from the surveillance as the cubes to date have not been stored as required by the standard.
| 05SY - Systemwide | Cxxx-NCR-000063 | NCR | Flow consistency testing for concrete train works not undertaken in accordance with the British Standard requirements. |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2015-11-30 | 2015-11-11 14:40 | -19 | 2015-10-26 13:47 | Civil - Track | 500 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Verification Problems - Not Defined | Completed |  | During a Crossrail planned surveillance undertaken on 22nd October 2015 (night shift) which involved a site visit to witness concrete train activities, the concrete consistency flow testing was witnessed being undertaken by the __ materials technician. On review, the test was being undertaken on the walkway, which due to the size of the flow table caused it to over hang of the edge. When the technician undertook the 15 drop cycle as defined in BS EN 12350-5:2009 it was noted that the table ‘double bounced’ after each drop due to the table over hanging off the walkway. Although the consistency was within the defined limits, the location of the test caused a big double bounce reaction resulting in more drops than the defined 15 within the standard. BS EN 12350-5:2009 clause 6 states “Place the flow table on a flat and horizontal surface free from external vibration or shock…..Support the table in such a way that when the top of the table falls to the lower stop, there is minimal tendency for the top to bounce”.
| 05SY - Systemwide | Cxxx-NCR-000064 | NCR | Crack in C14 Slab Track above Construction Joint |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-04-30 | 2016-03-02 13:00 | -59 | 2015-11-02 11:09 | Track - Track Bed | 5000 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Not Defined | Completed |  | Cracks appear on the track slab around construction joint of foundation concrete at ch. 16880 EB. The boot of a bearer (just above the construction joint of foundation concrete) has moved following the concrete opening. And it’s now ungluing to the bearer. The cracks are now opened around 10mm. The cracks are transversal (entire track slab). Survey of top rail carry-out on 23/10 does not report any vertical movement.
| 05SY - Systemwide | Cxxx-NCR-000065 | NCR | Bending Tests on Flash Butt Welds Non-Compliant with BS EN 14587-2 2009 Requirements |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-02-12 | 2016-02-15 13:56 | 3 | 2015-11-03 16:33 | Track - Welding | 4000 |  | Documentation and Records | Rework | 3 (3-6k) | Complete | Verification Problems - Inspection points not adequate | Completed |  | First two samples sent to the laboratory showed the following results after bend testing: - Minimum load achieved without destruction of the sample - Minimum deflection not achieved To date 58 flash butt welds have been produced in the Thames Tunnel WB: ch19540-22960
| 05SY - Systemwide | Cxxx-NCR-000066 | NCR | Concrete train manual batching outputs non compliant with allowable standard variation requirements |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2015-11-30 | 2015-12-03 14:58 | 3 | 2015-11-02 12:52 | Civil - Track | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | During a Crossrail planned surveillance undertaken on 22nd October 2015 which involved a site visit to witness concrete train batching, it was identified that the manual batch outputs varied against the automatic batch outputs. A post surveillance request was made for the Contractor to provide a copy of the excel batch logs for 20th – 22nd October. Following receipt of the excel spreadsheets for the aforementioned periods, based on the inputs it was identified that from a total of twenty five 1.5m3 loads batched manually, eleven non conformed on the quantity of aggregate batched, with percentage variations to the theoretical (2745kg detailed in the CPS – note this does not include water contained within aggregates) ranging from 3.1% to 6.8%. It was also noticed that manual batching was not just being undertaken at the start of shift as defined, but at periods throughout the shift. BS EN 206:2013 Concrete – Specification, Performance, Production and Conformity states under clause 9.7 ‘Batching of Constituents’ (2) “For quantities of concrete of 1m3 or more, the tolerance of batching constituents shall not exceed the values given in Table 27 except where other tolerances are given in provisions valid in the place of use”. Table 27 ‘Tolerances for the batching process of constituents’ states “Total Aggregates - ±3% of required quantity”. This NCR was raised as the aggregates had not been batched within the allowable variation from the theoretical mix design causing potential issues with the associated placed concretes long term durability and performance. Furthermore, this NCR only covers a defined period time, an assessment should be undertaken to determine the full extent for periods outside that looked at during the surveillance.
| 05SY - Systemwide | Cxxx-NCR-000067 | NCR | Damaged UTX Ducts |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2015-12-04 | 2015-11-13 09:54 | -21 | 2015-11-02 15:38 | Civil - Track | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During a series of inspections for the construction of the STS, damage to the previously installed UTX ducts has been identified. Cxxx drawing for UTX installation states that 287mm of exposed ducting (dwg Cxxx-OVE-C4-DDD-CR001_Z-73101). The exposed ducts at various locations within the eastbound section from Plumstead portal at rings 105, 242 and 424 were observed as being cracked or broken off. With the damage encountered there is a potential risk of blockages to these UTX's.
| 05SY - Systemwide | Cxxx-NCR-000068 | NCR | Incorrect Offsets on Survey Targets |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2015-12-09 | 2015-12-03 14:28 | -6 | 2015-11-09 16:27 | Surveying - Surveying General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | On the 05/11/2015 while doing the final track adjustment in Thames Tunnels EB between rings 700 to 816 the TMD/VMS operator noticed some discrepancies of around 40mm between the survey target offset labels and his instruments.
| 05SY - Systemwide | Cxxx-NCR-000069 | NCR | __ Walkway Bracket - Quality of steel prep, welding and galvanisation |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2015-12-11 | 2015-12-10 10:20 | -1 | 2015-11-11 14:03 | Systems - Systems Engineering General | 2500 |  | Manufacturing Defect | Reject | 4 (0.5-3k) | Complete | Material/Preservation Problems - Not Defined | Completed |  | Upon receipt of brackets from __ Ltd, the Walkway subcontractor, on site at Plumstead Rail head set down it was noticed during a quality inspection of materials (on the 10th Nov 2015) that; 1. The welding 'splatter' had not been cleaned off the steel before galvanization process. 2. There were rough edge from cutting the steel prior to galv that had not been dealt with. 3. Condition of the galv finish unsatisfactory due to apparent localized flaking back to unfinished steel. 4. 'Veining' through the finish possibly due to galv process. 5. Steel appears not to have been blasted properly before galvanization.
| 05SY - Systemwide | Cxxx-NCR-000070 | NCR | Crack in Concrete Slab above 1st stage Construction Joint on EB at CH17330 |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-05-11 | 2016-03-07 12:05 | -65 | 2015-11-13 11:37 | Track - Track Bed | 3000 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | A crack has appeared on the track slab above a 1st stage construction joint on the EB at CH17330. A sleeper is located on top of the 1st stage construction joint and a crack inducer was installed in the next sleeper bay as per proposed answer to Cxxx-NCR-000040.
| 05SY - Systemwide | Cxxx-NCR-000071 | NCR | Concrete Level Around Catchpit ring 756 EB Thames Tunnel |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-03-31 | 2016-03-07 11:58 | -24 | 2015-11-16 14:12 | Track - Track General | 1000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The concrete level around catchpit and the catchpit at ring 756 (CH 21345) on the EB are not following the required finish level. See attached pictures.
| 05SY - Systemwide | Cxxx-NCR-000072 | NCR | Low 28 days concrete compressive strength result |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-02-16 | 2016-02-17 10:57 | 1 | 2015-11-18 14:29 | Track - Track Bed | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | Concrete compressive strength results for 2nd stage concrete (Thames tunnel EB Ring 10) at 28days are 38.7 and 39.4MPa for a 40MPa requirement.
| 05SY - Systemwide | Cxxx-NCR-000073 | NCR | Incorrect slope of the central drainage channel at Custom House on the WB between Ch 16991 - 17003 |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-02-15 | 2016-01-22 15:13 | -24 | 2015-11-17 23:20 | Track - Track General | 3000 |  | Design | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Custom House, Plain Line, WB, CH 16991-17003 Slope of the central drainage channel is not allowing water to run to the nearest catchpit and water is stagnating at the end of the channel and running over the top of the slab.
| 05SY - Systemwide | Cxxx-NCR-000074 | NCR | Section of track poured outside authorised area |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-01-22 | 2015-12-16 16:33 | -37 | 2015-11-23 12:18 | Track - Track General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Thames tunnel EB track CH 20646 to CH 20651. The concrete pour of the EB STS track was authorised from CH 20744 to CH 20651 (ring 1030). It was however poured up to CH 20646 (ring 1033), exceeding by approximately 5 meters the authorised section as recorded on the Authorisation for Concreting QCR 6ST dated 16/11/2015 record number 22.
| 05SY - Systemwide | Cxxx-NCR-000075 | NCR | Hole on track slab concrete surface |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-01-27 | 2016-01-27 09:23 | 0 | 2015-11-27 12:04 | Track - Track Bed | 1000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | After uncovering previously poured concrete at Custom House Station, Plain Line, Westbound, CH17255, a hole on track slab concrete surface was noticed.
| 05SY - Systemwide | Cxxx-NCR-000076 | NCR | Maximum Drying Shrinkage – Concrete Mix Design for Concrete Train |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-01-26 | 2016-01-25 11:28 | -1 | 2015-11-27 12:23 | Track - Track Bed | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Results of the maximum drying shrinkage of the concrete mix design for the concrete train at 28 days are 0.049%, outside the specifications. Please see attached report. • __’s Technical Specification: 0.045% • KF10: 0.03%
| 05SY - Systemwide | Cxxx-NCR-000077 | NCR | Method Statements not submitted to Crossrail prior to commencement of works. |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-01-28 | 2016-03-03 11:59 | 35 | 2015-11-30 09:58 | Mechanical - Mechanical Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | A planned Crossrail surveillance was undertaken on 27th November 2015 which looked at documentation associated to the tunnel drilling machine prior to commencement of drilling in the tunnel linings. During the surveillance the following Method Statements were reviewed; Cxxx-__-O1-GMS-CRG03-50069 (Unloading of Drilling Machine), Cxxx-__-O1-GMS-CRG03-50049 (Assembly/ Dis-assembly of Walkways) and Cxxx-__-O1-GMS-CRG03-50051 (Standard Operation for Drilling Machine). Following review, it was identified that although the documents existed within the __ management system Aconex, the documents had not been submitted to Crossrail and existed as only a ‘Placeholder’ within the eB structure. As the first drilling machine had been unloaded on the 26th November 2015, the activity had commenced without the document submitted to Crossrail; additionally it was stated that the works were due to commence on 7th December 2015, as such the Method Statements are not being submitted to Crossrail to allow for the Contractual Period of Reply. Works Information Vol 2B Part 19.5.2 states: “Within four weeks of the starting date, the Contractor shall submit to the Project Manager for acceptance a preliminary Method Statements schedule …. Up to and for the first three months following the commencement of the works of the works the Contractor shall submit Method Statements for review and acceptance by the Project Manager a minimum of four weeks prior to the activity commencing.” Furthermore, it was identified that the ‘Method Statement Schedule’ created by __ to control which Method Statement documents require submitting for ‘Acceptance’ or ‘Information’ through interface with Crossrail is not being made visible to the Crossrail Delivery Team, as such the process is not being fulfilled as defined in Works Information Vol 2B Part 19.5.2: “The Contractor shall provide further submissions of the schedule when additional Method Statements are identified or the schedule of Method Statements change. The Project Manager shall specify the Method Statements requiring review and acceptance based on the potential health, safety or environments risks of the relevant work activities and their impact on others.”
| 05SY - Systemwide | Cxxx-NCR-000078 | NCR | Technical Specification for Tunnel Drilling Machine not accepted by Crossrail prior to commencement of Factory Acceptance Testing. |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-01-28 | 2016-01-29 15:55 | 1 | 2015-11-30 10:00 | Mechanical - Mechanical Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | A planned Crossrail surveillance was undertaken on 27th November 2015 which looked at documentation associated to the tunnel drilling machine prior to commencement of drilling in the tunnel linings. On review, it was identified that the Technical Specification (Cxxx-__-Y-RSP-CRG03-50008) produced by __ detailing the design requirements for the output from the drilling machine, had not been submitted to Crossrail for acceptance with the specification (Rev 4) existing on Aconex since January 2015 and being a ‘Placeholder’ on eB. Works Information Vol 2B Part 28.2.2.1 states: “Factory Acceptance Tests (FATs) shall be satisfactorily completed by the Contractor before shipment to the Site and/or Working Areas of any item of Plant and Materials in order to verify that it and its components are fit for its or their intended use and otherwise comply with the Works Information. The Factory Acceptance Tests are carried out by the Contractor, and in accordance with the Contractors accepted Method Statement, Quality Plan and Test Procedures.” As the document has not been accepted by Crossrail, the FAT which has been undertaken against the Technical Specification defined requirements may not be correct as the Technical Specification may contain comments for action following Crossrail review.
| 05SY - Systemwide | Cxxx-NCR-000079 | NCR | Contract Requirements Contract Clause Z11 - Non provision against PMI-00283 |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-03-22 | 2016-03-21 11:42 | -1 | 2015-12-09 16:34 | Consents - General | 1000 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | The Contractor has yet to comply with contractual obligations for implementation of PMI-00283 issued on 27/10/2015. Accordingly PMI-00283 instructs the Contractor to provide ‘read only’ access in ‘Aconex’ for __. Such access being required from the date of this instruction until the completion of the Cxxx works. [Access is required to ensure that the requirement of the provisions of the conditions of the contract clause Z11 are being met] See also meeting notes from meeting held on 5th June 2015 attached.
| 05SY - Systemwide | Cxxx-NCR-000080 | NCR | __s Industries Factory Visit and FAT |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-03-10 | 2016-03-03 09:30 | -7 | 2015-12-10 16:09 | Architectural - Doors | 1500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Upon a __ Industries Factory visit 1) Disconnect between office and shop floor including, Cxxx documentation on shop floor, relevant drawings not with the traveller, no Cxxx project folder loose paper around the office, no superseded section 2)Products not labelled with the project number, part number and the material type 3)Sections did not pass the FAT including no transit frame on test door, no seals around door vent (to prevent water ingress), gap greater than 3mm between door leaves and door frame
| 05SY - Systemwide | Cxxx-NCR-000082 | NCR | Materials Compliance (MCR) |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-06-29 | 2016-06-29 09:25 | 0 | 2015-12-17 15:31 | Materials - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Project Manager’s instruction Cxxx-PMI-00136 was issued on 22nd April 2015 instructing the Contractor to adopt a Material Compliance Records (MCR) process detailed in documents: • CRL1-XRL-N2-GPD-CR001-50007 Rev 3.0 Demonstration of Materials Compliance Procedure. • CRL1-XRL-Z-GUI-CRG0150002 Rev 1.0 eB Material Compliance Records – Initiator User Guide It has become apparent that the Contractor has failed to effectively implement the PMI in ensuring that products are covered by a harmonised European Standard or European Technical Assessment and therefore obtaining a Declaration of Performance and a CE mark where appropriate in accordance with Construction Product Regulations, thereby meeting the requirements for legislation which has been mandatory from 1 July 2013. For this reason a NCR has been raised.
| 05SY - Systemwide | Cxxx-NCR-000083 | NCR | Low 28 days Concrete Strength |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-03-21 | 2016-03-21 11:47 | 0 | 2015-12-22 11:23 | Track - Track Bed | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | 2nd stage concrete - Thames tunnel EB Ring 905-972 Cubes results from the testhouse at 28 days are 32.8 and 33.1MPa for a 40MPa requirement.
| 05SY - Systemwide | Cxxx-NCR-000084 | NCR | Low 28 days concrete strength - Thames tunnel EB Ring 1034 |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-03-13 | 2016-03-10 10:05 | -3 | 2016-01-13 14:51 | Track - Track Bed | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | 2nd stage concrete - Thames tunnel EB Ring 1034 Cubes results from the testhouse at 28 days are 38.3 and 36.8MPa for a 40MPa requirement.
| 05SY - Systemwide | Cxxx-NCR-000086 | NCR | Low 28 days concrete strength - Thames tunnel EB Ring 1550-1633 |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-03-15 | 2016-03-10 10:16 | -5 | 2016-01-15 12:13 | Track - Track Bed | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | 2nd stage concrete - Thames tunnel EB Ring 1550-1633 Cubes results from the testhouse at 28 days are 39.6 and 38.9MPa for a 40MPa requirement.
| 05SY - Systemwide | Cxxx-NCR-000087 | NCR | Rejected Cantilever type I drop tube by Crossrail |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-06-20 | 2016-06-20 10:11 | 0 | 2016-02-23 20:42 | Over Head Line Electrification - Over Head Line Electrification General | 500 |  | Design | Reject | 4 (0.5-3k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | Drop tube cantilever type I has been rejected by Crossrail because Drawing Cxxx-__-R6-DDD-CRG03-00054, shows a vertical drop tube that requires anchor bolts working in tension with chemical anchor bolts. This is not acceptable for Crossrail as chemical anchor bolts cannot be used in vertical (tension) applications.
| 05SY - Systemwide | Cxxx-NCR-000088 | NCR | Adjustable drop tube fixing is manufactured out of tolerances by Sugremin |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-05-25 | 2016-05-04 13:40 | -21 | 2016-02-23 21:35 | Over Head Line Electrification - Over Head Line Electrification General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Drawing Cxxx-__-R6-DDD-CRG03-00024 says that dimension of G (L=62.5 ±1.5 mm). G dimension is out of tolerance for one of 5 inspected pieces. 60 mm recorded whereas the minimum should be 61 mm (tolerance of 1.5 mm included)
| 05SY - Systemwide | Cxxx-NCR-000089 | NCR | Surface concrete chipped at crack inducer joint location in Custom House Station |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-04-17 | 2016-02-18 12:06 | -59 | 2016-01-18 14:27 | Track - Track Bed | 2000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Surface track slab concrete has been chipped at a crack inducer joint in Custom House Station, Westbound at CH17090. Metal shape used for creating the transversal cut in the crack inducers joints, was embedded in the concrete surface, and when it has been removed, it has chipped the concrete.
| 05SY - Systemwide | Cxxx-NCR-000090 | NCR | Mechanical Failure of Drive Sprocket |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-02-29 | 2016-02-25 12:38 | -4 | 2016-01-18 15:22 | Electrical - General | 5000 |  | Damaged | Repair | 3 (3-6k) | Complete | Material/Preservation Problems - Other | Completed |  | An issue occurred with a possible loose nut/bolt assembly on a welded sprocket attached to the drive train. The hydraulic drive sprocket is welded into a connection plate that is bolted directly to the drive. The axle sprocket is constructed of 2 halves. A solid plate is permanently fixed to the axle and the 2 halves of the sprocket are fixed directly to this plate each using 2 pins and 2 bolts. The holes in the sprocket and plate are threaded. From investigation it appears that one of the fixing bolts used to secure one half of the large Axle Sprocket was not in place during the movement. Due to this missing bolt the sprocket was allowed to move which damaged the thread (flattened) of the remaining bolt and eventually working its way loose. The now loose half of the sprocket has then locked the drive chain in some way. The machine was still being propelled forwards at this time and so the hydraulic drive was still applying a torque to the drive sprocket, in an attempt to continue to apply traction, which resulted in significant overstressing and eventual fracture of the weld. The failure is primarily a result of a maintenance failing to check and secure the bolts.
| 05SY - Systemwide | Cxxx-NCR-000092 | NCR | Rail damages - Zones 1 & 2 |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-03-29 | 2019-03-25 11:57 | -4 | 2016-01-22 12:00 | Track - Rails and Sleepers | 5000 |  | Damaged | Rework | 3 (3-6k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | Some superficial marks/damages on the top of the rails have appeared on both rails at different locations along Zones 1 & 2.
| 05SY - Systemwide | Cxxx-NCR-000093 | NCR | Rails Damages - Zones 3 & 4 |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-03-29 | 2019-03-25 12:04 | -4 | 2016-01-25 14:13 | Track - Rails and Sleepers | 6000 |  | Damaged | Rework | 3 (3-6k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | Some superficial marks/damages on the top of the rails have appeared on both rails at different locations along Zones 3 & 4.
| 05SY - Systemwide | Cxxx-NCR-000094 | NCR | Damaged Sleepers due to Machine Derailment |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-05-17 | 2017-05-08 10:20 | -9 | 2016-01-29 15:38 | Track - Rails and Sleepers | 11000 |  | Damaged | Rework | 2 (6-60k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Thames Tunnel – Westbound - R765 to R772 (roughly 11m).
| 05SY - Systemwide | Cxxx-NCR-000098 | NCR | FST De-bonding Product Not Accepted |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-04-28 | 2016-03-07 11:20 | -52 | 2016-01-29 16:21 | Track - Track General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | As a result of inspection, the product Ecocure WW has been used as a de-bonding product which is not accepted by Crossrail. FTS Lite westbound tunnel, slabs W1, W2, W3 and W4 between ch. 4219.100 -4416.700 MCR FTS de-bonding products Cxxx-__-R4-LRC-CRG03-50005 Rev. 1 has been approved by Crossrail for the use as a de-bonder for the construction of FTS. The products approved for use are: W__O Concrete Sealer Water Based and Sandex Trade Fine Textured Matt Paint
| 05SY - Systemwide | Cxxx-NCR-000099 | NCR | Water ingress through track slab at CH17997 WB |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-12-05 | 2017-12-04 14:43 | -1 | 2016-02-01 21:37 | Track - Track Bed | 5000 |  | System Defect | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | It has been noted that a slow trickle of water is coming through the track slab at Connaught Tunnel WB approx. CH17997 between trackslab and tunnel wall.
| 05SY - Systemwide | Cxxx-NCR-000100 | NCR | Concrete Train Calibration - 3rd December 2015 |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-06-22 | 2016-06-21 14:55 | -1 | 2016-01-28 15:06 | Track - Track General | 5000 |  | Equipment Breakdown | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | A calibration for the concrete train was carried out on 3rd December 2015 to obtain calibration results within the permitted tolerances through the range of the weighers without any restrictions. The scope of the calibration included the aggregate, cement, water weighers to full range capacity including the volumetric admixture dispenser. During the course of the calibration the following was identified: Cement Load Cells 1) The cement loadcell on the far right hand side of the control room has come loose and is not carrying its share of the hopper load. (No Sensitivity) 2) Cement weigh hopper appeared to have dropped at the front and also does not seem to be level. ie (loadcells closest to the control room) 3) The torsion bars that prevent the hopper from swaying from side to side in the front of the hopper are currently acting as a wedge between the solid structure and the cement weigher resulting in the hopper binding. (loadcell loosing sensitivity) Water Loadcells The water span test failed to provide an acceptable level of accuracy to within required tolerances. The torsion bars were also found to be causing binding. An attempt was made to free the binding bars with little success. They require removal and refurbishing. The calibration of the loadcells had to be abandoned as the inspection highlighted a number of issues that required repairing before the accuracy of the loadcells could be determined. It is noted that subsequent to the on-going issues encountered with obtaining train calibration, the STS track construction continued.
| 05SY - Systemwide | Cxxx-NCR-000101 | NCR | Manufacture of Shear Keys for FTS commenced before acceptance by CRL |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-05-27 | 2016-05-25 11:50 | -2 | 2016-02-01 21:27 | Track - Track General | 10000 |  | Documentation and Records | Rework | 2 (6-60k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | All shear keys for all Floating Track Slabs (Lite, Station and Barbican). Shear Keys have been produced/manufactured by Gerb and partly delivered without having prior acceptance of the ITP by __/CRL.
| 05SY - Systemwide | Cxxx-NCR-000102 | NCR | Concrete batches out of tolerance |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-05-31 | 2016-05-31 14:48 | 0 | 2016-02-03 12:16 | Track - Track Bed | 1000 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | 2nd stage concrete slab track in the Thames Tunnel on the Eastbound as per attached batching records.
| 05SY - Systemwide | Cxxx-NCR-000103 | NCR | Hole on the concrete surface - North Woolwich Portal - Westbound CH 19403 |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-05-25 | 2016-05-10 12:33 | -15 | 2016-02-09 19:32 | Track - Track Bed | 1500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | There is a hole on the concrete surface of the track slab of the Westbound at CH 19403 (see attached picture).
| 05SY - Systemwide | Cxxx-NCR-000104 | NCR | Connaught Tunnel Drainage |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-07-04 | 2018-07-20 10:11 | 16 | 2016-02-10 10:30 | Civil - Drainage | 6000 |  | Design | Use As-Is | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | At locations on the eastbound track within Connaught, the cess drainage channel is so shallow that water has been seen propagating onto the track slab surface up to the Delkor baseplates. The Direct Fix Track open drainage channels constructed at Connaught tunnel were constructed without first providing evidence / assurance that the design complies with the accepted design standards and fully integrates with the design of interfacing systems. In respect of the Contractors designed works, one of the key duties to be undertaken includes demonstrating and providing evidence to assure that the Contractor’s design meets the requirements set out in the Works Information by undertaking design reviews and Design Gate Reviews.
| 05SY - Systemwide | Cxxx-NCR-000108 | NCR | Unsatisfactory Inspection of EB Plumstead CMS Tray-to-Bracket Fixings |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-04-01 | 2016-03-30 15:03 | -2 | 2016-02-17 12:14 | Electrical - Cable Management | 10000 |  | Incorrect Installation | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | A formal inspection of the EB tunnel CMS and bracketry was requested by the Contractor under IRF M&E-BRK-EB-001, and performed by the Project manager (__, __ and __) with the Contractor's representative (__) on 16th February 2016 at 1100hrs. As part of this inspection, it was noted that the CMS trays had been fixed to the unistrut arms using 8mm diameter penny washers instead of the DIN126-A10.5 (nominal diameter 20mm) washers as identified in the Contractor's WMS Cxxx-__-O1-GMS-CRG03-50040 R2 (transmitted to Crossrail for Information Only on 3rd February 2016). As a result of this deviation from the installation methodology, the following non-conformances were observed: 1. The Contractor’s installation team are unable to fully torque the M6 nuts to the required 6.5Nm level identified in section 3.8 of the ITP Cxxx-__-E-ITP-CRG03-50001 R3 without causing deformation of the tray around the slots. 2. The Contractor's installation team have torqued the nuts to 6Nm, in deviation from the ITP, yet this lower torque has caused deformation of the tray around numerous slots. 3. In some cases, the 8mm penny washers have partially pulled through the tray slots on one edge. Notwithstanding the obvious fact this forms a failed and insecure fixing, this has the potential to damage the anti-corrison coating through mechanical friction beyond any of its “self-healing” capabilities. It should be noted that a penny washer of 20mm diameter as described in the WMS would bridge the return flanges of the unistrut arm, and prevent the bolt head from deforming the tray when correctly torqued. The Contractor is required to replace the non-conforming 8mm washers with 20mm diameter Din125-A10.5 as per the WMS. The Contractor is also to perform an assessment of all fixing locations where the 8mm washers have been mechanically pulled through the CMS tray to determine if the Magnelis anti-corrosion coating has been damaged, and recommend remedial action (including potential replacement) for any damaged sections of CMS.
| 05SY - Systemwide | Cxxx-NCR-000110 | NCR | Factory Acceptance Testing – Supplier Document Control (Atticrose) |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-05-17 | 2016-04-20 10:54 | -27 | 2016-02-17 16:16 | Materials - General | 1500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Not Defined | Completed |  | N__ Test records require review. Non Destructive test records not authorised, not available on site, results poorly worded. There is no details of the subcontractors business address or contacts. The report fails to uniquely identify equipment used.
| 05SY - Systemwide | Cxxx-NCR-000111 | NCR | Ladder Rack-Welding Defects |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-03-10 | 2016-03-08 16:46 | -2 | 2016-02-25 09:58 | Electrical - Cable Management | 5000 |  | Material | Reject | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Ladder Rack from __ – Poor quality Welding with signs of rust (weld repair __ paint not carried out correctly)
| 05SY - Systemwide | Cxxx-NCR-000112 | NCR | No concrete cube sample to test the strength of pour number 54 |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-05-22 | 2016-05-18 11:10 | -4 | 2016-02-22 14:09 | Track - Track General | 500 |  | Equipment Breakdown | Use As-Is | 4 (0.5-3k) | Complete | Supervision - Other | Completed |  | 2nd stage concrete - Thames tunnel CH19000 to 19002. On 11/02/2016, 6m3 of concrete were poured before a mechanic incident on the concrete train forced the production to stop. By this time, the set of cubes was not made yet.
| 05SY - Systemwide | Cxxx-NCR-000113 | NCR | ROC Rigid bar out of tolerances- Cariboni |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-03-22 | 2016-03-07 15:51 | -15 | 2016-02-23 22:40 | Electrical - OHLE | 500 |  | Manufacturing Defect | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | ROC Rigid bar out of tolerances- Cariboni Issue: Rigid bar 10m length are out of tolerance. Requirement: 10m +2mm -3mm Result: 10m +5mm -5mm
| 05SY - Systemwide | Cxxx-NCR-000114 | NCR | Management of Materials, Plant and Equipment Procedure sitting at a Code 2 for over 3 months |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-04-07 | 2016-04-04 09:11 | -3 | 2016-02-24 13:40 | Track - Track General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | During a planned Crossrail surveillance undertaken on 23rd Feb 2016 which looked at readiness review documentation and material compliance relating to the Floating Track Slab (FTS) works, it was identified that Management of Materials, Plant and Equipment for Permanent Works Procedure Cxxx-__-R5-GPD-CRG03-50030 which controls the management of goods onto site, has been at a Code 2 Decal since November 2015. Works Information Vol 2B Part 14 states “In the case of the first submission of a deliverable, in this section, for the Project Manager’s acceptance, the Project Manager replies within 4 weeks of the date of submission. Any further revisions, submissions and responses by the Contractor or Project Manager shall be made within the period for reply.” Under Crossrail Document Management Procedure CRL1-XRL-Z3-GPD-CR001-50001 (Rev 3) a Code 2 Decal stands for “Not Accepted, revise and resubmit. Work may proceed subject to incorporation of the changes indicated”.
| 05SY - Systemwide | Cxxx-NCR-000115 | NCR | Failure to provide internet connectivity at Canary Wharf Site Office |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-04-27 | 2016-04-27 09:10 | 0 | 2016-02-24 13:49 | Utilities Engineering - Telecomms | 500 |  | System Defect | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | The contractor became principal contractor of Canary Wharf Station on 9th September 2015 and under works information volume 2B, section 17.3.7 the contractor is required to provide internet connectivity. This has meant that Crossrail Field Engineers have not been able to work from the site office and this as also impacted the site based care and custody contractor from fully fulfilling their duties.
| 05SY - Systemwide | Cxxx-NCR-000116 | NCR | Mandatory Readiness Review and Contract Management Gates not undertaken prior to commencing Floating Track Slab (FTS) works |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-05-10 | 2016-04-22 13:34 | -18 | 2016-02-24 13:45 | Track - Track General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | During a planned Crossrail surveillance undertaken on 23rd Feb 2016 which looked at readiness review documentation and material compliance relating to the Floating Track Slab (FTS) works, it was identified that no Mandatory Readiness Review using the Contract Management Gates system had been undertaken and duly completed prior to commencing FTS works in November 2015 as defined in __ Contract Quality Plan Cxxx-__-O4-STP-CR001-50001 (Rev 6) under the below clauses: “16.13.5 Mandatory Readiness Reviews All off-site fabrication, on-site installation or specific high risk activities requiring accepted plans or other arrangements shall be controlled using the Contract Management Gates system described below. The __ Project Manager, in consultation with the Supply Package Manager, shall prepare a schedule of readiness reviews ref: template Cxxx-__-TMP-000046 to include all relevant stages and activities within the supplier or subcontractor’s scope of works. The Supply Package Manager shall ensure that each supplier or self-delivery team whose scope of work includes such activities is informed of these requirements and only proceeds with the activity when authorised to do so by the issue of a completed and authorised Gate. Prior to Starting Off-Site Fabrication/Assembly (Contract Management Gate 6) No manufacture may commence until all relevant pre-requisites are in place; including accepted designs, scheduled FATs, accepted test facilities, test plans and personnel or evidence of UKAS accreditation of test facilities is provided. Using template Cxxx-__-TMP-000033, the Supply Package Manager and the __ Project Manager shall agree the pre-requisites to be demonstrated for each gate. Prior to Starting New Installation Activity (Contract Management Gate 7) No work may commence until all relevant pre-requisites are in place. The person responsible for supervising the work must obtain confirmation that all necessary method statement approvals, ITPs, permits have been developed and authorised as necessary before briefing them to the installers and allowing work to commence. Provided that all conditions remain consistent, the readiness review for an activity may remain effective over a number of locations. Using template Cxxx-__-TMP-000034, the Supply Package Manager and the __ Project Manager shall agree the pre-requisites to be demonstrated for each gate. Prior to Undertaking a Single High Risk Activity (Contract Management Gate 7) Where a specific activity involving heightened quality risk, is to be undertaken, a task-specific readiness review will be required. The __ Project Manager shall identify the requirement for these reviews and enforce their delivery. The Supply Package Manager shall facilitate this process and shall use template Cxxx-__-TMP-000034 for this purpose.” It was also noted that the personnel who attended the surveillance responsible for managing the FTS works including documentation were not aware of the Contract Quality Plan requirements concerning Mandatory Readiness Review and Contract Management Gates.
| 05SY - Systemwide | Cxxx-NCR-000117 | NCR | Damaged Ducts For Under Track Crossings (UTXs) - East of Tottenham Court Station |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-05-31 | 2016-05-13 12:04 | -18 | 2016-02-24 15:02 | Track - Track General | 1000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | There are several places east of Tottenham Court Road Station (CRL) where several ducts for UTX were found to be damaged. These also included ducts with steel sleeves.
| 05SY - Systemwide | Cxxx-NCR-000118 | NCR | Non use of Drill depth guide |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-03-18 | 2016-03-18 10:46 | 0 | 2016-02-26 09:43 | Electrical - Cable Management | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Drill depth gauge not in use as specified in M/S. In use instead is electrical tape which can move and unstick with dust and use.
| 05SY - Systemwide | Cxxx-NCR-000119 | NCR | Mis-Alignment of drilled holes and Walkway Brackets |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-05-18 | 2016-03-08 16:54 | -71 | 2016-02-29 15:11 | Mechanical - Mechanical Engineering General | 1000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | The setting out of the holes has been carried out manually. The holes were drilled using a 14mm drill bit. When the Walkway brackets have been fixed to the walls by the top and bottom fixing due to accumulation of human error in the marking out and drilling of the holes, some of the holes within the bracket have been covered partially by the bracket. In the worst case the holes was 5mm behind the bracket. The holes have been identified, and marked as not to use and new locations for holes have been identified.
| 05SY - Systemwide | Cxxx-NCR-000120 | NCR | Damaged Sleepers - WB - CH 20590 |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-03-29 | 2017-01-25 14:56 | -63 | 2016-03-01 18:13 | Track - Rails and Sleepers | 3000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Sleeper damage on WB Thames Tunnel – circa ch WB 20590 (ring 1118 - 1120)
| 05SY - Systemwide | Cxxx-NCR-000121 | NCR | Incorrect rebar fabrication - FTS Bottom Steel reinforcement Slab W3 barmark 01 |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-05-30 | 2016-03-08 17:05 | -83 | 2016-03-01 16:51 | Track - Track General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The reinforcement drawing for FTS Slab W3 shows 6 bars mk 01 in the bottom level. 7 bars mark 01 have actually been installed.
| 05SY - Systemwide | Cxxx-NCR-000122 | NCR | STS sleepers damaged post track slab concreted |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-09-27 | 2017-08-18 12:25 | -40 | 2016-03-03 11:10 | Track - Rails and Sleepers | 5000 |  | Material | Rework | 3 (3-6k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Custom House Station and VDP ,Track Slab, EB and WB (EB 16705, EB 17158, WB 16986, WB 16996, WB 17173) The silicon ring in charge of sealing the concrete block with the rubber boot for the STS Sleepers, are damaged or broken, creating a gap where dirt could fill it. (Pictures attached)
| 05SY - Systemwide | Cxxx-NCR-000123 | NCR | FTS Steel reinforcement for the lateral restraints |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-06-24 | 2016-06-21 13:07 | -3 | 2016-03-08 15:06 | Track - Track General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | FTS Reinforcement details _ Lateral restraint for slab type 1 – 2 – 3 – 4 – 5 – 6 The new bar schedules C03 have been issued (10/2015) after the call off of the steel (08/2015) based on the bar schedules C02. Also the bar schedules Cxxx-OVE-R4-DDJ-CR001_Z-84292 still show C02 whereas there are differences between the 2 issues of the C02 revision. The lateral restraints have been built based on the call off schedules (C02). Cxxx-OVE-R4-DDL-CR001_Z-84292 C02 differ to the new C02 1 + 1 barmark 08 have been installed instead of the 2 barmark 51 + 2 barmark 54 on type 1 1 + 1 barmark 08 have been installed instead of the 2 barmark 52 + 2 barmark 53 + 2 barmark 51 + 2 barmark 55 on type 2 2 + 2 barmark 08 have been installed instead of the 2 + 2 barmark 51 + 2 barmark 54 + 2 barmark 56 on type 3 Cxxx-OVE-R4-DDL-CR001_Z-84296 C03 2+2 barmark 08 have been installed instead of the 2 + 2 barmark 51 + 2 barmark 57 + 2 barmark 55 on type 4 2+2 barmark 08 have been installed instead of the 2 + 2 barmark 51 + 2 barmark 57 + 2 barmark 55 on type 5 2+2 barmark 08 have been installed instead of the 2 + 2 barmark 51 + 2 barmark 57+ 2 barmark 55 on type 6
| 05SY - Systemwide | Cxxx-NCR-000124 | NCR | HAS blocks boot/gasket damage |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-07-21 | 2017-06-22 08:28 | -29 | 2016-03-10 14:47 | Track - Rails and Sleepers | 1000 |  | Damaged | Reject | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | Victoria Dock Portal to Limmo Shaft section on the Eastbound. The side of the plastic boot/gasket of the HAS blocks are slightly damage. This could be due to handling problems. However the sealant is not affected at all.
| 05SY - Systemwide | Cxxx-NCR-000125 | NCR | Excess and damaged galvanising to FTS jacking frames. |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-06-14 | 2016-06-13 10:33 | -1 | 2016-03-09 11:46 | Track - Track General | 5000 |  | Manufacturing Defect | Reject | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | During the inspection of jacking frames delivered on 26/02/2016 non-compliant galvanising finish was identified on 12 No of jacking frames, 393, 394, 395, 405, 408, 409, 411, 412, 417, 421, 422, 424. Jacking frames for FTS Lite have excessive galvanising left in holes for threaded rods and also chipped galvanising around the edges of the holes. Another 9 No jacking frames were found 397, 718, 720, 722, 735, 739, 743, 745, 750 non compliant in a subsequent delivery.
| 05SY - Systemwide | Cxxx-NCR-000126 | NCR | Authorisation for concreting not signed by QC Inspector |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-06-07 | 2016-03-11 12:44 | -88 | 2016-03-09 12:30 | Track - Track General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | The Hold Point “Authorisation for Concreting” QCR6ST was not signed by the QC Inspector prior to the concreting starting. The area had already been inspected and only the VMS run was required to confirm that the track geometry was compliant just ahead of the pour. The results of the VMS was good and the Field Manager gave the authorisation to start concreting without waiting for the QC Inspector to review.
| 05SY - Systemwide | Cxxx-NCR-000127 | NCR | Cut Longitudinal Rebar - Slab W1 |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-05-16 | 2016-04-04 08:12 | -42 | 2016-03-17 10:49 | Track - Track General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Rebar(Bar mark 30) was cut at all UTX locations of slab W1. See attached picture. First Slab (W1) of FTS Lite WB track CH4219.1 – CH4268.5
| 05SY - Systemwide | Cxxx-NCR-000128 | NCR | Damaged Upstand - FTS Area |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-12-31 | 2017-11-21 15:19 | -40 | 2016-03-17 11:32 | Track - Walkways | 3000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Two concrete upstands were damaged during the fixing of the metal ramps that cover the braking block gaps. See attached pictures. Westbound tunnel, FTS Lite work front, approximately slab W10 (ring 2736).
| 05SY - Systemwide | Cxxx-NCR-000129 | NCR | Time exceedance between batching and placing of concrete - Shuttles - 14/03/2016 |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-06-30 | 2016-06-28 08:14 | -2 | 2016-03-22 22:50 | Track - Track General | 1000 |  | Design | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | On the 14/03/2016 at Westbourne Park Site: Track installation section between Royal Oak Portal and Paddington Station Section concreted: EB from CH 0+596 – 0+628 . Time between batching concrete time 11:17,and concrete placing time has been exceeded 103 min, 16:00. Concrete Mix used was M5-2R.
| 05SY - Systemwide | Cxxx-NCR-000130 | NCR | Time exceedance between batching and placing of concrete - Shuttles - 15/03/2016 |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-06-30 | 2016-06-28 08:15 | -2 | 2016-03-22 22:53 | Track - Track General | 1000 |  | Design | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Not Defined | Completed |  | On the 15/03/2016 at Westbourne Park Site: Track installation section between Royal Oak Portal and Paddington Station. Section concreted: EB from CH 0+628 – 0+660 . Time between batching concrete time 9:19, and concrete placing time has been exceeded 41 min, 13:00.Concrete Mix used was M5-2.
| 05SY - Systemwide | Cxxx-NCR-000131 | NCR | Concrete Upstand Damaged |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-06-29 | 2016-05-18 11:06 | -42 | 2016-03-22 10:06 | Track - Track General | 1000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Bored Tunnel Section, between Royal Oak Portal and Paddington Station, EB, CH 0+653 Left Side. Concrete upstand chipped because of jig installation. (Picture Attached)
| 05SY - Systemwide | Cxxx-NCR-000132 | NCR | commencement of works without IFC drawing |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-08-11 | 2016-08-24 12:33 | 13 | 2016-04-13 15:11 | Systems - Other | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | Works have begun at risk in the Thames tunnel and also NE spur with regards to CMS and walkways brackets. Associated drawings being are not yet IFC.
| 05SY - Systemwide | Cxxx-NCR-000133 | NCR | Procedure IFC management of drawings on Site does not cover BaseStone software |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-07-20 | 2016-07-13 11:04 | -7 | 2016-03-29 15:11 | Systems - Other | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | BaseStone software now widely used on site not incorporated into Procedure for IFC drawings on site Cxxx-__-O4-GPD-CRG03-50054
| 05SY - Systemwide | Cxxx-NCR-000134 | NCR | S13710-03-0014 L2 Driving Wedge Machining. Dimensions out of drawing tolerance. |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-04-12 | 2016-04-06 13:54 | -6 | 2016-03-29 10:13 | Track - Track General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Other | Completed |  | See attached inspection record. Dimension features, C-G-J-L-M-N-R-S-T-W. Out of tolerance dimensions highlighted in red.
| 05SY - Systemwide | Cxxx-NCR-000135 | NCR | S13710-03-0023 L2 Cast in Shelf Machining. Dimensions out of drawing tolerance. |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-04-21 | 2016-04-04 08:20 | -17 | 2016-03-29 10:14 | Track - Track General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Other | Completed |  | See attached inspection record. Dimension features, M. Out of tolerance dimensions highlighted in red. Bracket Serial Nos. L2-06-0053/L2-06-0045/L2-06-0061/L2-06-0051/L2-06-0058.
| 05SY - Systemwide | Cxxx-NCR-000136 | NCR | Spindle embedded in the track slab |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-07-27 | 2016-04-11 11:11 | -107 | 2016-03-31 11:58 | Track - Track General | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | One spindle from a jig has been embedded on the track concrete slab between two sleepers at CH 16879 on the EB (Victoria Dock Portal). (Picture attached)
| 05SY - Systemwide | Cxxx-NCR-000137 | NCR | Damaged galvanising on drainage cover plates |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-07-20 | 2016-07-05 09:23 | -15 | 2016-03-31 15:36 | Track - Track General | 2000 |  | Material | Reject | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | It has been noted that during inspection of the storage area in EBX and WBX for the installation on FTS Lite, Station and Barbican, that some white rust/oxidation on the edges and corners of the drainage cover plates, galvanising peeling off the edges has occured.
| 05SY - Systemwide | Cxxx-NCR-000138 | NCR | Time exceedance between batching and placing of concrete - Shuttles - 23/03/2016 |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-06-30 | 2016-06-27 12:55 | -3 | 2016-04-01 08:45 | Track - Track General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | On the 23/03/2016 at Westbourne Park Site: Track installation section between Royal Oak Portal and Paddington Station Section concreted: EB from CH 0+775-0+795. Time between batching concrete time 9:24, and concrete placing time has been exceeded 51 min, 13:15 . Concrete Mix used was M5-2. Concrete from trucks 3rd and 4th , transferred from the Train B (two cisterns train) to Train A (big buffer train) and poured between the section 0+775-0+795.
| 05SY - Systemwide | Cxxx-NCR-000139 | NCR | Dry Concrete poured in the Track Slab - Shuttles - 23/03/2016 |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-07-20 | 2016-07-21 13:54 | 1 | 2016-04-01 09:05 | Track - Track General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | On the 23/03/2016 at Westbourne Park Site: Track installation section between Royal Oak Portal and Paddington Station Section concreted: EB from CH 0+790-0+810. Concrete poured looked very dry, clearly out of tolerance of the F5 workability requirement. (picture attached)
| 05SY - Systemwide | Cxxx-NCR-000140 | NCR | Method Statements not submitted to Crossrail prior to commencement of works |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-07-03 | 2016-07-04 07:55 | 1 | 2016-04-04 16:00 | Systems - Other | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Whilst undertaking a routing inspection of the of site documentation to support the works at Westbourne Park a review of the temporary M&E documents was carried out to validate the review and acceptance control measures implemented by the Contractor. When checking the temporary M&E documentation the following documentation non-compliances were present: • Photo ME2: Cxxx-__-O1-GMS-CRG03-50058 rev 1.0: Document NOT PRESENT in EB and shown as a ‘Placeholder’ only, therefore not submitted to CRL. • Photo ME3: Cxxx-__-O1-GMS-CRG03-50057 rev 1.0: Document NOT PRESENT in EB and shown as a ‘Placeholder’ only, therefore not submitted to CRL. • Photo ME4: Cxxx-__-O1-GMS-CR086-50002 rev 2.0: Decal 3 – NOT ACCEPTED. Revise and resubmit. WORK MAY NOT PROCEED Although the documents may have existed within the __ management system Aconex, the documents had not been submitted to Crossrail for information in accordance with the Contractors M/S Schedule (Cxxx-__-O1-TSC-CRG03-50001) and existed as only a ‘Placeholder’ within the eB structure. In the instance of M/S ref Cxxx-__-O1-GMS-CR086-50002, this had been submitted for review and acceptance and a Code 3 'Not Accepted' response returned. Works had commenced without first addressing CRL comments and resubmitting the document for acceptance.
| 05SY - Systemwide | Cxxx-NCR-000141 | NCR | Concreting with track gauge non-compliant to requirement - WBP - 01/04/16 |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-07-10 | 2016-04-27 15:55 | -74 | 2016-04-11 13:42 | Track - Track General | 1500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On the 01/04/16 at Westbound Park Site, Section between Royal Oak- Paddington Station, Eastbound tunnel, Ch: 0+922 to 0+924. Wide gauge of 1439mm found on the range described above, due prop positioning and jigs not in squareness.
| 05SY - Systemwide | Cxxx-NCR-000142 | NCR | Concreting with track gauge non-compliant to requirement - WBP - 04/04/16 |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-12-31 | 2016-04-27 15:59 | -248 | 2016-04-11 14:13 | Track - Track General | 1500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On the 04/04/16 at Westbound Park Site, Section between Royal Oak- Paddington Station, Eastbound tunnel, CH: 0+975.500 to 0+975.750. Wide gauge of 1438.6 mm found in between two jigs at a fishplate location EB CH: 0+975.500 to 0+975.750
| 05SY - Systemwide | Cxxx-NCR-000143 | NCR | Damaged S&C C16 due to derailment |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-09-28 | 2017-09-11 08:44 | -17 | 2016-04-13 16:14 | Track - Turnouts | 10000 |  | Damaged | Rework | 2 (6-60k) | Complete | Supervision - Other | Completed |  | VDP (Victoria Dock Portal) EB (Eastbound) on Turnout C16. Damaged S&C parts as per attached list and pictures following a derailment of the a bogie.
| 05SY - Systemwide | Cxxx-NCR-000144 | NCR | VSD heat rejection figures |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-10-26 | 2016-10-05 09:11 | -21 | 2016-04-13 15:34 | Electrical - Electrical Engineering General | 2500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The VSD supplier, __, have issued revised heat rejection figures (Cxxx-__-C-XDS-CRG03-50002 v3) for the VSD’s. These new figures result, in the majority of locations, in the heat emission limits being exceeded by significant amount
| 05SY - Systemwide | Cxxx-NCR-000145 | NCR | Excessive galvanising on M16 threaded bars. |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-07-13 | 2016-06-13 10:49 | -30 | 2016-04-14 14:25 | Track - Track General | 1500 |  | Manufacturing Defect | Reject | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During the inspection of threaded bars delivered on 24/03/2016 non-compliant galvanising finish to thread was identified on M16 threaded bars which will prevent from nuts being tightened on the bars and torqued before jacking of the slabs.
| 05SY - Systemwide | Cxxx-NCR-000146 | NCR | Catchpit lateral drainage too close to HAS Blocks |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-07-14 | 2016-06-13 10:52 | -31 | 2016-04-15 12:28 | Track - Track General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On the 08/04/16 in the Thames Tunnel EB between CH19838 - 19834, drainage formwork has drifted during concreting and is close to the HAS block (see pictures attached)
| 05SY - Systemwide | Cxxx-NCR-000149 | NCR | __ supplier (AllTask) non FORS delivery |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-05-25 | 2016-05-19 10:48 | -6 | 2016-04-21 13:57 | Logistics - Logistics - General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Cxxx __ operatives received delivery vehicle from All task today delivering scaffold for GYB site The driver did not have a crossrail driver badge and we were advised he was booked on a course. New drivers are permitted to attend up to 5 times, so that was not a problem, but it would mean the driver was not as conversant with Crossrail requirements as he should have been. The vehicle was inspected and found to have the side sensors not works. The side sensors had apparently been dissarmed? The driver was able to make them work after doing some items of work. Vehicles sensors are a key 5 items on the ‘Crossrail compliance criteria so the vehicles was recorded as non compliant. Cxxx representative asked the driver and manager if they had performed an inspection of Crossrail items. They had not. They advised they had complete their own statutory checks. the Cxxx representative at the __ holding area reminded them that it is expected that a Crossrail specific inspection is undertaken by the driver before starting on a Crossrail as detailed on page 5 of the enclosed driver briefing. The driver had a copy of this document, or part of it, with the delivery address on it.
| 05SY - Systemwide | Cxxx-NCR-000150 | NCR | No procedure in place which defines roles, responsibilities and requirements for the management of equipment maintenance across the Cxxx project. |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-06-29 | 2016-06-28 08:20 | -1 | 2016-04-26 10:20 | Logistics - Logistics - General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | A planned Crossrail surveillance was undertaken on 6th, 20th and 22nd April 2016 which looked at __s management of equipment maintenance across the project. During the surveillance, the following procedures were made available to demonstrate equipment maintenance coverage; ‘Management of Materials, Plant and Equipment for Permanent Works’ Cxxx-__-R5-GPD-CRG03-50030 and ‘Management of Materials, Plant and Equipment for Temporary Facilities’ Cxxx-__-R5-GPD-CRG03-50006. The two procedures are subsequently referenced in the Contract Quality Plan Cxxx-__-O4-STP-CR001-50001 with respect to the management of equipment that would impact the quality of the works. On reviewing the procedures it was identified that asides from a definition of the term ‘equipment’, there was no mention or capture with respect to the roles, responsibilities and requirements for the management of equipment, from hired to purchased equipment across the varying site disciplines, and including compliance with the legal requirements such as PUWER and LOLER. The procedures referred in the main to the management of goods in as produced by the stores manager. Furthermore, on discussing with the following __ personnel, Plant Manager (hired equipment), Maintenance Manager (hired equipment), Asset Register Owner and Track Equipment Engineer, none were aware of the procedures existing. Works Information Vol 2B Part 20 states “The Contract Quality Plan shall be developed in accordance with the guidelines set out in ISO 10005:2005 and as appropriate …. Incorporate a monitoring system for procurement, maintenance and condition of equipment, plant and materials to ensure that contract objectives can be fulfilled”. __ Contract Quality Plan Part 11.9 states “Installation equipment that has the capacity to impact on the quality of the works must be specified and procured, operated and maintained to ensure that it has and retains the capability to function as required to meet contract requirements; further reference in the Management of Materials, Plant and Equipment for Permanent Works”. As the CQP referenced procedure makes no mention to maintenance requirements this NCR was raised resulting from the surveillance. The lack of procedure was prevalent with __ personnel not knowing who was directly responsible for certain elements of equipment on site.
| 05SY - Systemwide | Cxxx-NCR-000151 | NCR | Maintenance sections of the Temporary Asset Register not completed as required. |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-06-29 | 2016-06-30 15:15 | 1 | 2016-04-26 10:22 | Logistics - Logistics - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | A planned Crossrail surveillance was undertaken on 6th, 20th and 22nd April 2016 which looked at __s management of equipment maintenance across the project as required by the Works Information. During the surveillance the current __ Temporary Asset Register (excel file) was made available where it was identified that the following headings covering ‘equipment maintenance’ were left blank with respect to each piece of purchased equipment held on site; ’Responsible Person’, ‘Maintenance Required’ and ‘Maintenance Been Undertaken’. The register covers equipment recorded as being on site as far back as 12-18 months, as such the management of this section has not been undertaken as required for a significant period of time. Works Information Vol 2B Part 14.4.4.5 states “The Contractors management of plans for the works shall include procedures for the management of such temporary assets that shall include …. Maintenance of a temporary asset register that identifies each asset purchased, its unique identification number …. the location of the asset and the person responsible for its safe keeping, any maintenance requirements including the interval of such maintenance”. To ensure the Asset Register is maintained fully to incorporate the respective maintenance fields as required by the Works Information, this NCR was raised.
| 05SY - Systemwide | Cxxx-NCR-000152 | NCR | Omission of Maintenance for MGP #1 |  | Contr | ALC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-05-31 | 2016-05-13 12:11 | -18 | 2016-04-27 08:06 | Construction Health & Safety - Construction Health & Safety General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | During the joint CRL/__ surveillance of Plant & Equipment Management on 22/04/2016, it was observed that there was no evidence that MPG#1 had received the weekly or 250 hours maintenance inspections defined in the MPG O&S Manual. MPG#1 has been on site and operating since approx. October / November 2015.
| 05SY - Systemwide | Cxxx-NCR-000156 | NCR | FTS Lite Braking block Reinforcement cage |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-06-14 | 2016-06-13 10:55 | -1 | 2016-05-16 20:36 | Track - Track General | 500 |  | Manufacturing Defect | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | FTS Lite Braking Block locations. The nominated distance from the edge of the slab to the bars mentioned above is between 80-130mm. These bars are also positioned incorrectly in one side of the cage. See photographs attached.
| 05SY - Systemwide | Cxxx-NCR-000157 | NCR | Clearance between catchpit frame and sleeper out of tolerance - CH 1+117 EB |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-08-16 | 2016-06-13 11:04 | -64 | 2016-05-18 09:04 | Track - Track General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Westbound Park Site, Section between Royal Oak- Paddington Station, Eastbound tunnel, Catch pit placed on CH 1+117 EB Clearance between the catch pit frame and the two rubber boot sleepers are 55 and 58 mm. Pictures attached
| 05SY - Systemwide | Cxxx-NCR-000158 | NCR | Track damage due to derailment at Connaught |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-03-31 | 2017-03-23 10:28 | -8 | 2016-05-19 22:51 | Track - Track General | 50000 |  | Damaged | Rework | 2 (6-60k) | Complete | Material/Preservation Problems - Other | Completed |  | The following damages have been identified on the EB between CH18050 and CH18215 following the derailment of the cement wagon on the 17/05/2017 when the concrete train was going back to the Plumstead railhead at the end of the shift in the morning (see attached pictures): - Damaged concrete slab - Broken/damaged baseplates and fastenings - Crushed PRD plates A detailed report will follow.
| 05SY - Systemwide | Cxxx-NCR-000159 | NCR | Defective Welding on Manufactured Shear Keys |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-08-22 | 2016-07-19 07:48 | -34 | 2016-05-24 16:18 | Track - Track General | 50000 |  | Manufacturing Defect | Reject | 2 (6-60k) | Complete | Material/Preservation Problems - Other | Completed |  | Following Cxxx-NCR-000101 for the manufacturing of the shear keys before acceptance of the ITP. Some additional testing has been carried out on 2 samples to confirm that the units are meeting the requirements. During destructive tests a situation concerning the welding of the steel bar into the collar of the bolt of the lower shear key part was discovered. Due to pre-production error, a small gap between the inserted bar and the inner collar surface was left in parts. This gap is causing an undefined situation on the welding Root. This situation is not acceptable on this welding part, leading to the decision of GERB to declare this product "unfit for use"
| 05SY - Systemwide | Cxxx-NCR-000160 | NCR | Turnout C16, Cracks in Stage 2 Concrete |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-09-28 | 2017-09-27 10:30 | -1 | 2016-05-26 16:10 | Track - Track Bed | 5000 |  | Design | Rework | 3 (3-6k) | Complete | Previous Construction - Other | Completed |  | Turnout C16 at Custom House, EB Track Between turnout bearers F1545L and F1546L Cracks have appeared in the Stage 2 concrete slab adjacent to cracks which have already been repaired with flexible sealant.
| 05SY - Systemwide | Cxxx-NCR-000161 | NCR | Excessive top cover to reinforcement in W1 slab FTS |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-06-22 | 2016-06-21 13:10 | -1 | 2016-05-27 15:07 | Track - Track General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | East end of FTS Lite slab in westbound tunnel. Approx. 10m in length of FTS type 2 at the eastern end of W1 Top cover is approx. 120 to 145mm in area at the east stop end of W1
| 05SY - Systemwide | Cxxx-NCR-000162 | NCR | Systemwide Cross Passage Door Face out of tolerance |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-08-31 | 2016-08-25 11:12 | -6 | 2016-05-27 16:00 | Civil - Civil Engineering General | 1500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | It has come to the contractor’s attention that the concrete collar in the cross passages, to which cross passage doors are to be fixed, is out of plumb by up to 20mm. __ has provided sample images of Cross Passage Door 19 Eastbound, where the bottom of the door is exactly 5mm away from the concrete, whilst the top of the bulkhead door is away from the concrete by approximately 20mm. The same is true for CP16E. __ expect this across the majority of the cross passage door openings.
| 05SY - Systemwide | Cxxx-NCR-000163 | NCR | Cross Passage Door 16 and 19 Westbound: Face out of tolerance |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-07-14 | 2016-06-30 15:17 | -14 | 2016-05-27 16:06 | Civil - Civil Engineering General | 2500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | In addition to Cxxx-NCR-000162, the contractor would like to raise an additional NCR, to capture the fact that the concrete face of the concrete collar in Cross Passages 16 Westbound and 19 Westbound is out of plumb by approximately 40mm. The top of the bulkhead touches the concrete where the bottom of the door is away from the concrete by 40mm. Please note the door bulkhead bolts to the concrete collar.
| 05SY - Systemwide | Cxxx-NCR-000164 | NCR | Damaged sleepers due to tractorail derailment |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-08-22 | 2017-07-24 10:12 | -29 | 2016-06-01 15:24 | Track - Track General | 10000 |  | Damaged | Rework | 2 (6-60k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Following the derailment of the Tractorail and while in the process of re-railing it 3 Standard Track Slab S312 sleepers have been damaged. Please see attached pictures.
| 05SY - Systemwide | Cxxx-NCR-000165 | NCR | Manufacturing of type K bearings without accepted ITP in place |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-09-09 | 2016-09-08 13:34 | -1 | 2016-06-01 15:41 | Track - Track General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Manufacture of “Type K” bearings commenced by GERB and majority already delivered to Cxxx storage area in Old Oak common.
| 05SY - Systemwide | Cxxx-NCR-000166 | NCR | Bar mark 11 on E14 delivered with incorrect length |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-06-16 | 2016-06-16 07:54 | 0 | 2016-06-02 15:21 | Track - Track General | 1000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | The bar mark 11 of the FTS E14 slab on the East bound track has been delivered with a horizontal length of 1180 mm.
| 05SY - Systemwide | Cxxx-NCR-000167 | NCR | Missing reinforcement for catchpits of Cxxx designed area (ch.14323-14248) |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-07-07 | 2016-07-11 07:43 | 4 | 2016-06-07 12:36 | Track - Track General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | EB between VDP to Canary Wharf , chainage 14281 \ mark E836 Reinforcement not installed according to Cxxx-OVE-R4-DDD-CR001_Z-88608
| 05SY - Systemwide | Cxxx-NCR-000168 | NCR | Poor track slab concrete finish - WB - CH 1+002 to 1+095 |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-09-05 | 2016-09-02 15:36 | -3 | 2016-06-07 12:51 | Track - Track General | 2000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Track Section concreted btw CH 1002-1095 WB, has a very pour concrete finish, there are numerous high and low spots, finish around sleepers and jigs is not properly done with voids around spindles/sleepers and sleepers/rails covered in concrete.
| 05SY - Systemwide | Cxxx-NCR-000169 | NCR | Track slab surface damage at Canary Wharf Station Eastbound due to formwork striking |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-09-08 | 2016-09-08 14:24 | 0 | 2016-06-10 08:44 | Track - Track General | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Canary Wharf Station EB Ch 13630 to 13886 The edge of the slab has been damaged all along the station while striking formwork to create drainage channels. This has been potentially caused by: - Early striking of formwork (concrete too fresh) - Bad condition of steel gullies - Great depth of drainage channels at low points See attached pictures.
| 05SY - Systemwide | Cxxx-NCR-000170 | NCR | Two box-outs for E&B pipes missing at Canary Wharf Station EB |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-11-11 | 2016-11-14 10:55 | 3 | 2016-06-10 08:51 | Track - Track General | 4000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | Canary Wharf Station EB Ch13635 and ch 13757 There are no box-outs left in the concrete slab for installation of E&B pipes at the two locations mentioned. The box-out formwork was accidentally removed prior pouring concrete.
| 05SY - Systemwide | Cxxx-NCR-000171 | NCR | Break out of first stage concrete at Paddington station, WB track, exposing reinforcement |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-11-02 | 2016-09-08 09:20 | -55 | 2016-06-13 15:15 | Track - Track Bed | 3000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | Paddington station WB track. FIRST STAGE CONCRETE. Trench area next to catchpit Ch: 1+300. Concrete broken out 30mm depth from catchpit edge “outlet location”, for a length of 1800mm in a gradient of 1:60, leaving H16 rebar exposed for 300mm, undamaged though
| 05SY - Systemwide | Cxxx-NCR-000172 | NCR | Longitudinal bars not going through lateral restraints |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-07-06 | 2016-07-04 10:15 | -2 | 2016-06-14 08:29 | Track - Track General | 1000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | W1 West bound track. Only one 32 mm bar is going through the lateral restraint.
| 05SY - Systemwide | Cxxx-NCR-000173 | NCR | Cross Passage Door 16 Eastbound: Finish Floor Level too high |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-06-15 | 2017-07-24 11:35 | 39 | 2016-06-15 12:22 | Civil - Drainage | 1000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | In addition to Cxxx-RFI-000831 the contractor would like to raise an NCR, to capture the fact that the finish of the drainage channel in cross passage 16 eastbound is approximately 30mm too high, leading to the cross passage doors clashing with the drainage upon opening. This is illustrated more clearly in the images below. The doors have been fitted using a reference point of 5mm above the FFL (finish floor level) which indicates an issue with the finished floor level within the cross passage, rather than a Quality Control issue with the door installation. Furthermore the survey of this area has demonstrated that the built concrete onsite at the CP16EB Doors is 50mm higher than expected.
| 05SY - Systemwide | Cxxx-NCR-000174 | NCR | Work commencing on site without accepted documentation |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-07-13 | 2016-07-04 07:59 | -9 | 2016-06-15 14:15 | Electrical - Cable Management | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Works commenced in the Woolwich Box without accepted Method Statement and ITP.
| 05SY - Systemwide | Cxxx-NCR-000175 | NCR | Concrete Train Calibration Frequency |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-07-27 | 2016-07-27 08:53 | 0 | 2016-06-16 10:54 | Civil - Track | 1000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | The contractor has not followed the requirements of “Concreting with concrete train ITP” Cxxx-__-O4-ITP-CRG03-50091 v3.0 item 2.3 “Concrete Train Calibration”. The ITP states the concrete train shall be calibrated every month for the first 3 months (i.e. January, February and March 2016) and after that once every 6 months. Contractor shall calibrate the weight measurement devices for aggregates, cement and water, in addition to calibrating admixture dispenser. Based on the calibration reports that Crossrail have received from contractor for 2016, these requirements have not been followed. This NCR has been raised because of the following reasons: 1. Water weight measurement device was not calibrated in March 2016. 2. Cement weight measurement device was not calibrated in March 2016. 3. Aggregate weight measurement device was not calibrated in January and March 2016. 4. Admixture dispenser was not calibrated in January and March 2016. 5. Crossrail have not been invited for calibrating the concrete train which is a hold point. Calibration Reports from January 2016 to April 2016 provided to CRL are attached.
| 05SY - Systemwide | Cxxx-NCR-000176 | NCR | Concreting train water weighing system calibration out of tolerance |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-07-27 | 2016-07-19 12:18 | -8 | 2016-06-16 11:12 | Civil - Track | 500 |  | Equipment Breakdown | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Based on the attached concrete train calibration report dated 18/05/2016 (Cert No. 18900), all of the readings of the water weigh scale have been out of tolerance with errors between 4.4% and 20%. This is against the requirement of the attached QSRMC (Quality and Product Conformity Regulations) section 7.6 which sets a 3% tolerance.
| 05SY - Systemwide | Cxxx-NCR-000177 | NCR | Bar marks 9 and 24 not installed in Braking blocks |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-07-12 | 2016-06-29 09:51 | -13 | 2016-06-17 09:40 | Track - Track General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Braking block assemblies (FTS lite east and westbound tunnels) BM 24 in __ types 1-3 and BM 09 in __ types 4-6 have not been installed
| 05SY - Systemwide | Cxxx-NCR-000178 | NCR | __ 32F Fibre Optic Cable Damage |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-08-17 | 2016-07-19 11:56 | -29 | 2016-06-20 09:58 | Communications and Control Systems - Fibre Optic Network | 5000 |  | Damaged | Repair | 3 (3-6k) | Complete | Management Problem - Not Defined | Completed |  | On Monday 6th June 2016, 3 drums of __ 32F Fibre Optic Cable (Drum No.: R376728-001, R376728-002 and R376728-003) were delivered to Gate 1, OHLE Compound in Plumstead. The delivery was inspected by __ and __ of Cxxx and Clive Hardy of Cxxx. At the time of delivery, a visual inspection of the three drums was carried out and it was noted that cables on all drums were adequately covered, the drums were damage free and the cables were not exposed, as illustrated in Figure 1. Further to the visual inspection, the test reports and certificate of conformity issued with the delivery were studied before the quality assurance document (QAD-108) was completed by the __ and the delivery was accepted. On Wednesday 15th June, __ supervisor noticed on a site visit that 3 Fibre Optic cable drums had been moved to a different section of the compound. A visual inspection of the relocated drums was undertaken and the damages were raised with Cxxx’s Electrical Engineer. The assets were inspected by a Cxxx Engineer and the following damages were noted; casing on one of the drums (Drum No.: R376728-003) was relatively loose, the cable was exposed, scuffed and the insulation was damaged as highlighted in Figure 2 and Figure 3. Detailed Report with pictures is attached to this NCR.
| 05SY - Systemwide | Cxxx-NCR-000179 | NCR | Bar Mark 05 of the Breaking Block not compliant to __ |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-07-26 | 2016-07-08 07:43 | -18 | 2016-06-21 12:27 | Track - Track General | 500 |  | Material | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | Type 2 braking block at W1, WB chainage 4246.400, left hand side of the centre line. BM 05 height measured on site as 180-190 mm. This has an impact on the links that go around it (BM 35) which are in some places loose and others position not in the exact location as detailed in the drawing in order for it not to be loose.
| 05SY - Systemwide | Cxxx-NCR-000180 | NCR | Lack of back plate on Lifting beam bracket |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-09-29 | 2016-09-27 12:54 | -2 | 2016-06-22 15:57 | Mechanical - Mechanical Engineering General | 1000 |  | Manufacturing Defect | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | __/__s had an issue with one of the trolley's not running true. It was found that the bracket directly above the issue had it's back plate missing. This has not been correctly supplied by Lifting Systems. The running of the trolley has now been reqtified and __ have supplied the attached report to confirm that the bracket is well within engineering tolerances.
| 05SY - Systemwide | Cxxx-NCR-000181 | NCR | __s fixings over-torqued |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-09-06 | 2016-08-16 08:08 | -21 | 2016-06-27 15:09 | Materials - General | 1500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | __s have delivered to TCR site a __ HIT-Z-R fixing which is not an approved product. __s site team have gone ahead and installed at +4 and +2. The HIT-Z-R is a superior fixing to the approved HIT-V which should have been used. The issue arose from uncontrolled __ drawing changes, where a superior product was sourced by designers, but was not communicated to __ or the rest of Konrcranes.
| 05SY - Systemwide | Cxxx-NCR-000182 | NCR | Over-torqued HITLI fixings |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-09-27 | 2016-07-21 15:50 | -68 | 2016-07-21 07:35 | Materials - General | 2000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | __s have over-torqued the HIT-Z-R fixings at Lv +4 beam brackets. __s operatives used the Values supplied by their designers in the ITP which were for Lind Adaptors at 147Nm.
| 05SY - Systemwide | Cxxx-NCR-000183 | NCR | FTS Temporary Works Serrated Washers |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-09-20 | 2016-07-06 07:27 | -76 | 2016-06-24 08:37 | Track - Track General | 1000 |  | Workmanship | Reject | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | Some 4 mm pitch serrated washers have been installed between W1 and W6 CH4219-CH4515 in lieu of the 6 mm serrated washers associated with the temporary baseplate.
| 05SY - Systemwide | Cxxx-NCR-000184 | NCR | Damaged HAS sleepers |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-02-03 | 2017-01-30 10:39 | -4 | 2016-06-24 16:55 | Track - Rails and Sleepers | 20000 |  | Damaged | Rework | 2 (6-60k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | HAS section between Paddington and Bond Street WB. CHs: 1575.6 -1739.4 Damage to the upper edge on 19 HAS sleepers.
| 05SY - Systemwide | Cxxx-NCR-000185 | NCR | HV cable containment appears to be too flexile |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-09-20 | 2016-08-08 07:39 | -43 | 2016-06-27 14:58 | Electrical - Cable Management | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The HV cable containment as shown on drawing Cxxx-__-E-DDD-CR001-90001 has been observed to be excessively flexible at the ends by Cxxx, though there are no defined pass / fail criteria for this parameter. Cxxx have raised concerns as to how the containment would behave in a short circuit. It should be noted that the containment has been seen without the lids on it, which would stiffen the ladder.
| 05SY - Systemwide | Cxxx-NCR-000186 | NCR | __s Testing of runway beams |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-10-21 | 2016-10-14 14:11 | -7 | 2016-06-28 13:14 | Mechanical - Lifts | 500 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Supervision - Not Defined | Completed |  | __s is quoting an old Specification for Testing of Runway beams. (The ITP quotes BS 2853:1957 ) konecranes to include updated version of BS 2853:2011 into their testing procedure.
| 05SY - Systemwide | Cxxx-NCR-000189 | NCR | BMs 03 & 07 of W1 Braking Blocks are not in the bed |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-07-27 | 2016-07-14 15:34 | -13 | 2016-07-04 13:47 | Track - Track General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | W1 (Westbound chainages 4241.221 and 4246.421) It has been identified that some BMs 03 (a, b and c) and 7 (a, b and c) of the type 2L braking blocks of W1 do not go around BMs 05 and 06 respectively as detailed in the drawing Cxxx-OVE-R4-DDL-CR001_Z-84291 C03.
| 05SY - Systemwide | Cxxx-NCR-000190 | NCR | BMs 22, 23, 34 and 35 of W1 braking blocks |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-07-18 | 2016-07-11 10:48 | -7 | 2016-07-04 13:50 | Track - Track General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | W1 (Westbound chainages 4241.221 and 4246.421) BMs 22, 23, 34 and 35 of the type 2L braking blocks in W1 have not being installed as per the drawing Cxxx-OVE-R4-DDL-CR001_Z-84291 C03. Additionally, BMs 34 & 35 have being installed with the laps on the top rather than on the bottom.
| 05SY - Systemwide | Cxxx-NCR-000191 | NCR | Expansion Joint Bent During Concreting EB CH 18805 |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-10-31 | 2017-09-25 13:29 | -36 | 2016-07-05 08:09 | Track - Track Bed | 3000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Track concrete Slab located on EB CH 18805. 2nd stage Expansion Joint bent, during the concrete pour. The expansion joint is broken. One part of it seems to have fallen during the concreting activity, provoking a crack from the edge of the concrete slab up to the sleeper’s boot.
| 05SY - Systemwide | Cxxx-NCR-000192 | NCR | Crack in 2nd stage concrete slab through the STS sleeper WB 18810 |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-07-21 | 2017-08-02 15:37 | 12 | 2016-07-05 08:42 | Track - Track Bed | 3000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Open section between North Woolwich Portal and Connaught East Westbound tunnel, CH: 18810 Track Slab has been cracked in the proximity of a STS sleeper, close to a crack inducer wrongly installed. Closer Top Crack Inducer installed, was not rightly fitted, without the full 75mm cut on top surface, without originating the weak point in the slab, therefore without creating the crack in this position. Crack width 1mm approx.
| 05SY - Systemwide | Cxxx-NCR-000193 | NCR | Drainage Pipe Paddington WB |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-04-28 | 2017-05-18 14:10 | 20 | 2016-07-07 12:10 | Track - Track General | 2000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Paddington station. WB track. Ch: 1+535 // 1+552 The central longitudinal drainage pipe route had been fixed as per design levels & required gradient. During concrete pour operation the pipeline got lifted making it impossible to fix. See attached picture.
| 05SY - Systemwide | Cxxx-NCR-000194 | NCR | Damaged Transversal Drainage Channel WB CH 2112 |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-11-29 | 2016-07-08 07:50 | -144 | 2016-07-05 16:26 | Track - Track General | 1000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Bored Tunnel section, WB CH 2112 RH, between Paddington and Bond Street. Damaged concrete transversal drainage channel going into catch pit Drainage damaged on 610x220 mm concrete surface with 100mm depth.
| 05SY - Systemwide | Cxxx-NCR-000196 | NCR | Cross Passage 16: Water in cross passage door crate |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-08-10 | 2016-07-27 12:46 | -14 | 2016-07-08 09:23 | Architectural - Doors | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper handling of material | Completed |  | M Turnpenny noted that upon delivery to Cross Passage 16, one of the Cross Passage door crate was discovered to have a large amount of rainwater inside, which had to be drained before installation took place.
| 05SY - Systemwide | Cxxx-NCR-000197 | NCR | CMS post produced to wrong values |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-12-07 | 2016-10-05 09:18 | -63 | 2016-07-11 08:51 | Electrical - Cable Management | 50000 |  | Manufacturing Defect | Repair | 2 (6-60k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | It has come to the engineering team's attention that approximately 140No. CMS posts were manufactured to the wrong stiffness values given by __ (email attached). Some of these posts (116No.) have been installed in the Woolwich Box (East and Westbound), the remaining are stored at Plumstead Gate 4 (24No.) Once the error was discovered, production was stopped and the remaining posts were then manufactured using right values.
| 05SY - Systemwide | Cxxx-NCR-000198 | NCR | Cross Passage Door Westbound: 16 RHS Paint Deformity |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-09-21 | 2016-09-19 13:29 | -2 | 2016-07-08 09:32 | Architectural - Doors | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper handling of material | Completed |  | From a recent site survey it has been noticed that there is a paint deformity on one of the Cross Passage Door leaves. The top edge of the door leaf seems to have visible unsmooth surface texture and discolouring. The paint looks to have bubbled and slightly thinned in thickness shown by a translucent colour. For more information and pictures, please refer to M Turnpenny's report attached.
| 05SY - Systemwide | Cxxx-NCR-000199 | NCR | Damaged sleepers due to jigs strike by train |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-03-14 | 2017-03-15 09:13 | 1 | 2016-07-11 10:59 | Track - Rails and Sleepers | 10000 |  | Damaged | Rework | 2 (6-60k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Stepney Green – Canary Wharf East bound (Ring Number 1752 – 1754) CH 12561 (mark 1753). 2 sleepers have been damaged. See attached pictures.
| 05SY - Systemwide | Cxxx-NCR-000200 | NCR | Rail fastenings damaged due to MEWP trailer derailment |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-11-16 | 2016-11-16 16:03 | 0 | 2016-07-11 14:55 | Track - Rails and Sleepers | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | One rail clip damaged in the WB near CP19.
| 05SY - Systemwide | Cxxx-NCR-000201 | NCR | NCR rebar installed at an angle between manholes E16 |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-08-27 | 2016-08-18 09:04 | -9 | 2016-07-13 09:06 | Track - Track General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | BM 19 is installed at an angle to maintain minimum 30 mm cover to each access hole cover. See attached picture.
| 05SY - Systemwide | Cxxx-NCR-000202 | NCR | Damaged Concrete Upstand due to MPG incident – FTS EB ring 2662 |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-04-28 | 2017-04-18 08:20 | -10 | 2016-07-14 15:19 | Track - Track General | 1500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Concrete upstand damaged at FTS EB ring 2662 due top MPG incident. See attached pictures.
| 05SY - Systemwide | Cxxx-NCR-000204 | NCR | Oversized gantry lifting beam TCR-E Lv -1.5 |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-10-26 | 2016-10-20 11:12 | -6 | 2016-07-19 12:32 | Materials - General | 5000 |  | Design | Reject | 3 (3-6k) | Complete | Management Problem - Inadequate administrative control | Completed |  | WHILST PREPARING TO INSTALL THE GANTRY CRANE LIFTING BEAM FOR GANTRY CRANE LB09009 IT WAS DISCOVERED THAT THE LIFTING BEAM WAS IN FACT TOO LONG TO FIT INTO THE SPACE GIVEN. FURTHER INVESTIGATION REVEALED THAT THE DESIGN GIVEN TO THE MANUFACTURER WAS IN FACT THE WRONG DIMENSION. WHILST PREPARING TO INSTALL THE GANTRY CRANE LIFTING BEAM FOR GANTRY CRANE LB09009 IT WAS DISCOVERED THAT THE LIFTING BEAM WAS IN FACT TOO LONG TO FIT INTO THE SPACE GIVEN. FURTHER INVESTIGATION REVEALED THAT THE DESIGN GIVEN TO THE MANUFACTURER WAS IN FACT THE WRONG DIMENSION
| 05SY - Systemwide | Cxxx-NCR-000205 | NCR | Ladder and tray deflection on the open route |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-11-02 | 2016-11-04 11:44 | 2 | 2016-07-19 18:01 | Electrical - Cable Management | 5000 |  | Material | Rework | 3 (3-6k) | Complete | Material/Preservation Problems - Other | Completed |  | The CMS containment tray and ladder rack are deflecting due to thermal expansion from the heat. The area affected was first noted as deflecting due to perceived thermal expansion on 18/07 and inspected on 19/07 – the ambient temperature at the time of the inspection between 14.00 and 15.00 was c. 33 degrees Centigrade. The Ladder and 150mm tray on the East bound trace was observed to deflect primarily at 18m from chainage marker ch. 18605 with an expansion joint located at 12-13 brackets away (at 3.185m spacing = 38.22-41.405m. Additional deflection was noted on the 150mm tray on the length of tray adjacent to the expansion joint – wrap around couplers are to be installed on all 150x75mm tray replacing the straight couplers provided.
| 05SY - Systemwide | Cxxx-NCR-000206 | NCR | Under Torquing at CWS |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-09-27 | 2016-07-29 11:40 | -60 | 2016-07-21 07:40 | Materials - General | 2000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The __ Fixings at CWS Lv 0 for the 5T were under-torqued by 100Nm. This was because of incorrect torque values supplied by __s designers. This has since been reqtified (NCR 000182)
| 05SY - Systemwide | Cxxx-NCR-000207 | NCR | Injectable mortar behind Brackets |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-01-25 | 2017-01-31 11:37 | 6 | 2016-07-21 13:56 | Materials - General | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Due to the installation process, injectable mortar is hardening between concrete surface and brackets which makes the Gantry/beam brackets sit slightly proud of the fixing surface.
| 05SY - Systemwide | Cxxx-NCR-000208 | NCR | Surface painting of __ Dampers and fittings |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-10-26 | 2016-10-18 12:00 | -8 | 2016-07-22 12:02 | Mechanical - Heating Ventilation & Air Conditioning | 6000 |  | Manufacturing Defect | Reject | 3 (3-6k) | Complete | Material/Preservation Problems - Not Defined | Completed |  | Upon delivery of __ dampers and equipment at WHI today, serious issues around the painted surface treatment was observed. In order for the dampers to attain the design life, an added layer of Galvanisation paint was proposed and accepted. During the FAT test in Malaysia in May, __ was shown finished Dampers in the workshop as examples of our product. Once the first crate was opened, it s clear that nearly all items have some form of painting defect. (See Images)
| 05SY - Systemwide | Cxxx-NCR-000209 | NCR | __ Fan de-galzanising |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-09-14 | 2017-07-21 10:00 | -55 | 2016-07-28 06:59 | Mechanical - Heating Ventilation & Air Conditioning | 3000 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | There is galvanisation coming away from one welding joint on the motor support struts of No2 fan. It seems a welded area has not been cleaned properly before the galv'ing so it has not adhered to the surface. See images.
| 05SY - Systemwide | Cxxx-NCR-000210 | NCR | __ Installation Drawings for Gantry Crane at Canary Wharf |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-11-30 | 2016-11-28 16:20 | -2 | 2016-08-01 13:38 | Systems - Other | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | During a surveillance, it was found that drawing Cxxx-__-M-DWG-CRG03-50008 Rev ‘E’ which was Code 2 on eB since January 2016. The drawing in the drawing pack was Rev ‘F’ plus redlines and drawing Cxxx-__-M-DWG-CRG03-50012 for 6T Gantry Crane with Electric Wire Hoist was not on eB at all. The contractor should undertake a review of all manufacturing drawings for this package of works to ensure that all are code 1 on eB.
| 05SY - Systemwide | Cxxx-NCR-000212 | NCR | Inadequate records to support ITP |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-08-30 | 2016-08-08 07:44 | -22 | 2016-08-01 15:04 | Systems - Other | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | There was no record available to evidence that hold points 1.3 (MCR Acceptance) and 2.1 (Drawings at IFC Status) of the ITP had been satisfactorily completed.
| 05SY - Systemwide | Cxxx-NCR-000213 | NCR | Bearing plates and screws lifted when jacking W1 |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-10-01 | 2016-09-29 14:41 | -2 | 2016-08-02 08:42 | Track - Track General | 500 |  | Material | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Slab W1, Westbound chainages 4219-4268 Some of the bearing plates were lifted with the slab W1 during the jacking operations. Some of the screws of other bearing plates are protruding from the bearing plate level; it is believed that the bearing plate came up with the slab dragging the screws with it and when it came down the screws stayed in the same position – higher than the bearing plate which came down to its nominal position laying on the first stage concrete. This issue has been investigated jointly by __, CRL and Cxxx on site on 29/07/2016. The outcome of the agreement was captured using a Site Observation form from __’s Procedure for IFC and management of drawings on site Cxxx-__-O4-GPD-CRG03-50054. The Site observation is attached to this NCR as well as pictures of the bearing plates that came up and a general layout drawing (Cxxx-OVE-R4-DDA-CR001_Z-81004 C06) marked up with the location of the non-compliant ones.
| 05SY - Systemwide | Cxxx-NCR-000214 | NCR | No evidence that the test equipment used for the SAT was within calibration due dates - __s Gantry Cranes Canary Wharf |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-08-29 | 2016-08-09 08:02 | -20 | 2016-08-01 15:39 | Systems - Other | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | There were two pieces of equipment used on the SAT of the __s Gantry Cranes at Canary Wharf. One was a Fluke 1503 Insulation Tester s/n 18470023, the other was a Fluke 114 True RMS Multimeter s/n 16640338. Neither of these pieces equipment had the calibration due date completed on the form prior to sign off of the SAT report (by both __ and __s) because at the time it was unclear if the equipment was within its calibration period.
| 05SY - Systemwide | Cxxx-NCR-000215 | NCR | Flow Table Test Values for W1 Out of Specifications |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-11-30 | 2016-11-25 12:34 | -5 | 2016-08-02 08:48 | Track - Track General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Two of the concrete loads poured on the night of Thursday 14/07/2016 in W1 FTS Lite WB CHs 4219-4268 had an out of spec flow table test value. Please see the table below. No Delivery Ticket No Batch time Flow table test value Remarks 3 72172674 20:38 710 mm Concrete cubes were taken for this load 8 72172827 23:21 710 mm
| 05SY - Systemwide | Cxxx-NCR-000216 | NCR | Concrete placed exceeded the maximum time allowed from batch time (W1) |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-11-30 | 2016-11-29 09:53 | -1 | 2016-08-02 09:00 | Track - Track General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | W1 FTS Lite WB CHs 4219-4268 The concrete transfer to the pump was completed 3 hours 51 minutes after batch time exceeding by 1 the maximum time allowed
| 05SY - Systemwide | Cxxx-NCR-000217 | NCR | Concrete load workability test out of spec was poured in W2 |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-11-30 | 2016-11-29 09:55 | -1 | 2016-08-02 09:07 | Track - Track General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | W2 FTS Lite WB CHs 4268-4317 The flow table test carried out on the 6th concrete load of the night came out as 700 mm. This is outside of the allowed range of 630 +/- 50 mm. The load was however accepted and poured in W2 slab.
| 05SY - Systemwide | Cxxx-NCR-000218 | NCR | Poor concrete finish and level around some baseplates at W1 |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-04-28 | 2017-04-19 13:07 | -9 | 2016-08-02 09:14 | Track - Rails and Sleepers | 3000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | W1 slab, Westbound chainages 4219-4268. At some locations of slab W1, the concrete level is under the required level within the baseplate pad. Some of the pads have been removed for inspection and large voids of trapped air have been found underneath. Pictures attached.
| 05SY - Systemwide | Cxxx-NCR-000219 | NCR | Spindles embedded in W2 |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-11-30 | 2016-11-23 09:52 | -7 | 2016-08-02 09:28 | Track - Track General | 3000 |  | Equipment Breakdown | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | W2 – Precise location of the spindles that are embedded will be provided by the Production team. Spindles broken when they were being released from the slab and therefore a part of them is embedded in the slab.
| 05SY - Systemwide | Cxxx-NCR-000220 | NCR | Lateral restraint reinforcement setting out altered during concreting at W2 |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-11-30 | 2016-11-09 11:44 | -21 | 2016-08-02 09:36 | Track - Track General | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Left hand side (low side) of W2 at ring 2493, WB CH 4299.82 The lateral restraint reinforcement has moved during the concreting operations from its setting out position. There is no concern for the stability/secureness of the reinforcement when fixed and therefore this is deemed to be an isolated issue.
| 05SY - Systemwide | Cxxx-NCR-000221 | NCR | Upstand damaged by jig prop bolt |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-05-31 | 2017-06-05 10:58 | 5 | 2016-08-02 09:42 | Track - Track General | 2500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Right hand side of W2 at Ring 2502 approximately at Westbound CH 4295 The upstand has been damaged by a jig prop bolt after the slab W2 was concreted. Picture attached.
| 05SY - Systemwide | Cxxx-NCR-000222 | NCR | Concrete chipped out after removing formwork W1-W2 |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-10-31 | 2016-10-24 10:13 | -7 | 2016-08-02 09:49 | Track - Track General | 2500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Slabs W1 and W2 between Westbound Chainages 4219-4317 The top surface of slabs W1 and 2 chipped out when the formwork was released at the end of W1 and W2 and slightly on the top longitudinal edges of both slabs. It seems like the reason behind the chipping out at the stop end location is due to the formwork being cut flush with the slab prior striking it. Note: The formwork was striked 4 days after the slabs were concreted which is contrary to the 7 days specified in the Method Statement. This is believed not to have had an impact on the concrete chipping out as the compressive strength value recorded in Appendix 11 of the CPS for Heavy Weight concrete for FTS areas Cxxx-__-R4-RSP-CRG03-50062 rev 2.0 is 18.8 MPa at 2 days and the lowest value from the concrete cubes made from W1’s concrete pour is 36.3 MPa. According to the KF10 section KF10.3226 b) ‘Where the concrete compressive strength is confirmed by tests on concrete cubes stored under conditions detailed in the Method Statement that simulate the field conditions, then formwork supporting concrete in bending may be struck when the cube strength is 10N/ mm² or three times the stress to which it will be subjected, whichever is the greater.’ Therefore 4 days is a reasonable time to strike the formwork as the concrete strength according to the tests would be greater than 13.33MPa
| 05SY - Systemwide | Cxxx-NCR-000223 | NCR | Trays not attached to bracket in Thames Tunnel WB |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-08-31 | 2016-08-12 07:18 | -19 | 2016-08-03 14:38 | Electrical - Cable Management | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During IRN Inspection Walk Out, it was noted that one bracket at Ring 249 was too low for tray to be fixed onto it. This was duly noted and added to the ROWL (Cxxx-__-O4-LRC-CRG03-50013).
| 05SY - Systemwide | Cxxx-NCR-000224 | NCR | Small Number of Brackets in Thames Tunnel WB installed slightly too high or too low |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-09-07 | 2016-08-11 10:32 | -27 | 2016-08-03 14:56 | Electrical - Cable Management | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During IRN Inspection Walk out it was noted that in certain locations the holes drilled by the drilling rig were slightly out of position. In particular ring 323 too high, 325 too low, 633 to high, 660 too low, 968 too low, 1030 too low. This was noted on the ROWL (Cxxx-__-O4-LRC-CRG03-50013). All trays installed is still secured to bracket, just at slightly higher/slightly lower positions.
| 05SY - Systemwide | Cxxx-NCR-000225 | NCR | Greasing of Slide Chairs for Switches and Crossings |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-12-06 | 2016-11-14 11:03 | -22 | 2016-08-05 08:14 | Track - Turnouts | 1000 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | The slide chairs including the rollers for all the switches and crossings in VDP/Custom House area (C11 to C16) have been greased. See attached pictures.
| 05SY - Systemwide | Cxxx-NCR-000226 | NCR | UTXs have been lifted during the W1 slab jacking |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-11-16 | 2016-11-16 13:58 | 0 | 2016-08-05 08:21 | Track - Track General | 2500 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Slab W1, Westbound chainages 4219-4268 The UTXs have been lifted during the slab jacking operations. Please find the attached pictures.
| 05SY - Systemwide | Cxxx-NCR-000227 | NCR | Unfinished Concreting W3 |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-10-06 | 2016-09-26 14:51 | -10 | 2016-08-07 21:37 | Track - Track General | 3000 |  | Incomplete Works | Reject | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Slab W3 FTS Lite WB CHs 4317.922-4321.300 After number of technical difficulties with the pour there was a shortfall in the volume of concrete delivered to the work face of slab W3. This led to the area of approx. 3.4m in length, approximately 200mm in depth over full slab width (3440mm) being not fully covered by concrete up to designed level/top of concrete.
| 05SY - Systemwide | Cxxx-NCR-000228 | NCR | Measurement checks for Flash Butt Welding (FBW) have been completed using a non-calibrated straight edge and engineer’s square. |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-10-25 | 2016-09-21 08:08 | -34 | 2016-08-08 10:32 | Track - Welding | 1000 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Following a planned Crossrail Quality surveillance undertaken on 22 July 2016 which looked at the Flash Butt Welding operation, the ‘Exit Note’ requested calibration certificates for the digital thermometer, engineer’s square and straight edge. Post-surveillance, __ provided an up to date calibration certificate for the digital thermometer used on site. However, no evidence was provided of calibration for the engineer’s square and a Certificate of Conformance (CoC) was provided for the straight edge. The "Calibration and Measurement Traceability for Construction Materials Testing Equipment: UKAS Publication ref: LAB 21" specifies that the straight edge and engineers’ square requires yearly ‘Level 3’ in-house calibration checks. A ‘Level 3’ check requires an in-house test “performed by a competent person, using appropriately calibrated equipment to a documented procedure”. Based on the above, the CoC provided by the Contractor was not a calibration record, as detailed on the document itself. As such, there was no verifiable evidence available to assure that the measuring equipment being used on site is within its required tolerance limits. This NCR was raised to ensure the measuring equipment is calibrated and confirmed as still within tolerance.
| 05SY - Systemwide | Cxxx-NCR-000229 | NCR | Voids and Honey Combing Locally Found in W3 After Striking the Formwork |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-11-23 | 2016-12-15 11:36 | -343 | 2016-08-09 09:58 | Track - Track General | 350000 |  | Material | Reject | 1 (>60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | W3, westbound CH4317.922-4367.325 • After striking the formwork (Sat, 06/08/2016) on W3, __ identified a number of areas where there are voids and honey combing to the concrete. In places the re-bar is also exposed. • These areas are typically located in the arris on the internal face of the access chamber for the jacking points (see photographs attached) and are between tunnel rings no’s 2520 – 2509. • The cause of this event is (in __’s opinion) a combination of the following: o Highly congested re-bar configuration locally, preventing free flow of the concrete and adequate vibration. o The characteristics of the concrete, heavy-weight 3.7t/m3. o Technical difficulty in pumping significant distances (circa 500m to W3). • __ confirm that works to W3 were carried out in accordance with the RAMS and within all specified limits.
| 05SY - Systemwide | Cxxx-NCR-000230 | NCR | Gauge rate of change out of tolerance in W3 |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-03-31 | 2016-09-26 14:51 | -186 | 2016-08-10 22:02 | Track - Track General | 500 |  | Incorrect Installation | Reject | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Around westbound chainage 4363 (W3) The gauge rate of change was processed by the VMS as exceeding the contractual tolerance around westbound chainage 4363. It was assessed that the reading in this location were caused by a joint in the track (fishplate) and therefore it is expected to get compliant readings in this area once the LWRs are installed. Note: The FTS is cast with temporary baseplates which will be swapped by the permanent ones before the installation of the LWR.
| 05SY - Systemwide | Cxxx-NCR-000231 | NCR | Drilling into Water-proof membrane |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-07-05 | 2017-08-15 13:00 | 41 | 2016-08-11 13:10 | Communications and Control Systems | 5000 |  | Damaged | Rework | 3 (3-6k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | 4no-75mm bolts drilled into water proofing layer to install the communication aerial for FTS concrete local radio system, in VD3, ETH. Bondstreet.
| 05SY - Systemwide | Cxxx-NCR-000232 | NCR | Energisation of CWS 5T Gantry Crane |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-09-20 | 2016-08-17 08:13 | -34 | 2016-08-11 13:33 | Mechanical - Mechanical Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | The crane in question at Canary Wharf has been energised in a temporary state using a temporary power supply for load testing purposes. The installation has been carried out as per the ‘__s – Underslung and Light Crane - Installation ITP - Cxxx-__-O4-ITP-CRG03-50029’ There was no IRN in place for this energisation as per the Cxxx T&C procedure
| 05SY - Systemwide | Cxxx-NCR-000233 | NCR | Cable falling from cable rack and the cable has been damaged |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-02-07 | 2017-02-03 11:09 | -4 | 2016-09-02 09:18 | Electrical - Power Distribution | 10000 |  | Damaged | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In Eastbound Thames Tunnel (Tray 8, Ring number 1289, chain 20236) Below 3 no OHLE Cables came off the rack during the installation. As a result, the cables were damaged after fell down. Type of cable: 26/45kv Cable –LSOH 240mm Aluminum Core + Copper Screen Negative Return. 1- CR146-OLE-00074 (329mt). Drum number: 25kV-C-E/B_TFS_26 2- CR146-OLE-00004 (328mt). Drum number: 25kV-C-E/B_NF_26 3- CR146-OLE-00016 (327mt). Drum number: 25kV-C-E/B_NFS_26
| 05SY - Systemwide | Cxxx-NCR-000234 | NCR | Lack of assurance documenation for WOO Fans |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-11-30 | 2016-09-29 08:36 | -62 | 2016-08-15 08:30 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | __ had Fans delivered to Woolwich site without the accompanying factory documentation. Cxxx-__-H-DWG-CRG03-50016 Drawings are not code 1 FAN FAC for the WOO fans incomplete Cxxx-__-K1-GPD-CRG03-50001 incomplete
| 05SY - Systemwide | Cxxx-NCR-000235 | NCR | Clearance between HAS Sleepers boots and 1st stage concrete |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-11-21 | 2016-09-29 14:28 | -53 | 2016-08-23 11:40 | Track - Track General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Previous Construction - Other | Completed |  | Location: Bored Tunnel Section, between Paddington Station and Bond Street Station WB track. After identifying that the clearance between FSC and HAS Sleepers Boots, on the Track Section 3616-3680WB, was less than 70mm on the 50% of the sleepers (with the Track Vertical Alignment set at -10mm), Track Team decided to lift the track around 8mm, setting the vertical alignment at -2mm, (Tolerance 0 to -20mm), getting just 3% of the sleepers below 70mm, (60 and 65mm). Survey attached.
| 05SY - Systemwide | Cxxx-NCR-000236 | NCR | All spring washers are NOT A2 (304) stainless steel |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-12-01 | 2016-10-28 08:29 | -34 | 2016-09-01 14:12 | Over Head Line Electrification - Over Head Line Electrification General | 1000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | According to result of XRF analysis by __, all spring washers, which had been received from supplier __ Ltd., are NOT A2 (304) stainless steel. Some of them have been tested randomly and found 203 grade by __.
| 05SY - Systemwide | Cxxx-NCR-000237 | NCR | Slab W5 concrete damage at shear keys area |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-10-22 | 2016-10-20 09:29 | -2 | 2016-08-23 16:33 | Track - Track General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Concrete suffered minor damaged when striking off the formwork, this resulted in a non-conformance to the concrete level and finish.
| 05SY - Systemwide | Cxxx-NCR-000238 | NCR | Steelwork pre-drilled 12mm holes out of tolerance |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-01-18 | 2017-01-11 13:53 | -7 | 2016-08-25 07:12 | Materials - General | 2500 |  | Material | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | At CWS East Level -3 the tunnel Side Attenuator steelwork beams B302/B305 have several pre-drilled hole which seems to be out of alignment as per the Fabrication drawings. these issues were confirmed with __ of CRL CWS TVS team.
| 05SY - Systemwide | Cxxx-NCR-000239 | NCR | __ Bracket Galvanisation thickness non compliance |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-11-30 | 2016-10-20 11:15 | -41 | 2016-08-25 14:37 | Materials - General | 10000 |  | Manufacturing Defect | Reject | 2 (6-60k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Upon testing galv thickness of the TTD brackets from __ at Lv -3, all brackets and 6mm shims have been found to be much lower than the 114 microns required. *See images
| 05SY - Systemwide | Cxxx-NCR-000240 | NCR | Incomplete documentation during delivery |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-09-28 | 2016-09-26 07:28 | -2 | 2016-08-26 13:31 | Over Head Line Electrification - Over Head Line Electrification General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | During the Cariboni delivery regarding the ROC aluminium pieces, delivery note and packing list missing the information which creates a confusion at site.
| 05SY - Systemwide | Cxxx-NCR-000241 | NCR | Westbourne Park __ lab facility temperatures exceeding BS allowable. Non calibrated thermometers also being used. |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-09-30 | 2016-09-26 11:33 | -4 | 2016-08-26 15:15 | Track - Track General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | A planned Crossrail surveillance was undertaken on 26th August 2016 to look at activities associated with STS concreting using the concrete shuttles. Whilst witnessing testing activities at WBP, the laboratory facility was visited which is being used to store manufactured cubes for the STS works. On inspection, the laboratory max/min thermometers recorded the following temperatures for Environmental - 27.8 degrees and the Water Bath - 25 degrees. BS EN 12390-2 states the following allowable temperature ranges for the both conditions; Environmental 20+-5 degrees and Water Bath 20+-2 degrees. Both the witnessed values at the time of the visit exceeded the British Standard allowable temperatures. At the time of the visit, recently manufactured cubes were being stored in the facility. Curing in these condition could impact the long term strength gain of these cubes, potentially resulting in non conforming results that are not representative of the placed concrete. Further more, the two thermometers contained no serial number to allow traceability back to the calibration record. Only one thermometer contained a calibration 'sticker'. This was dated March 2015, outside of the yearly calibration requirement.
| 05SY - Systemwide | Cxxx-NCR-000242 | NCR | STS track installation ITP has been at a Code 2 decal for 5 months |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-09-23 | 2016-09-26 07:29 | 3 | 2016-08-26 15:23 | Track - Track General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | A planned Crossrail surveillance was undertaken on 26th August 2016 to look at activities associated with STS concreting using the concrete shuttles. On reviewing ITP Cxxx-__-O4-ITP-CRG03-50079 for the Track Installation, it was identified that Revision 3 which is being used on site has been at a Code 2 decal since March 2016. The Contractual Period of Reply is 14 days (Works Information Part 14). Furthermore, Revision 1 is showing as the 'current' and 'approved' version on eB where Revision 3 showing as 'draft' and 'not approved' is being used on site. As the comments have yet to be addressed for Revision 3 this NCR resulted from the surveillance due to the significant period without action.
| 05SY - Systemwide | Cxxx-NCR-000243 | NCR | Slab W4 spindle holes are not grouted prior to slab jacking |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-10-30 | 2016-10-20 12:06 | -10 | 2016-08-31 16:32 | Train - General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | 4 No of spindle holes have not been filled with grout prior jacking.
| 05SY - Systemwide | Cxxx-NCR-000244 | NCR | Slab W6 not installed correctly |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-01-31 | 2017-01-11 13:56 | -20 | 2016-08-31 17:04 | Train - General | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | One of the baseplates in W6 (CH 4466.480, south side) was installed and cast with the inclination set in the wrong direction, the baseplate is horizontally rotated 180°
| 05SY - Systemwide | Cxxx-NCR-000245 | NCR | Bearing steel plates lifted during the jacking of slab W2 |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-09-28 | 2016-09-27 14:57 | -1 | 2016-08-31 17:21 | Track - Track General | 5000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the jacking operation of the slab a total of 7 bearing steel plates came up with the slab of the first stage concrete (See attachment for location detail of the lifted bearing steel plates).
| 05SY - Systemwide | Cxxx-NCR-000246 | NCR | Concreted Track with Vertical Alignment non-compliant to requirement |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-03-30 | 2017-03-31 08:07 | 1 | 2016-09-01 12:42 | Train - General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Location: Bored Tunnel Section, between Paddington Station and Bond Street Station, WB track, CHs: 2615-2639 & 2642-2661. Track section concreted with the absolute vertical alignment out of tolerance +2mm maximum.
| 05SY - Systemwide | Cxxx-NCR-000247 | NCR | Catch pit formwork broken while concreting |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-11-30 | 2016-11-30 13:11 | 0 | 2016-09-01 13:54 | Track - Track General | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Location: Bored Tunnel Section, between Paddington Station and Bond Street Station, WB, CH 3+616. Due to the catchpit formwork was not well fixed, during concrete pouring, concrete pushed the formwork, displacing it , and getting inside the catchpit hole and drainage pipe. (Pictures Attached)
| 05SY - Systemwide | Cxxx-NCR-000248 | NCR | Optical Fibre Cable Displacement in Thames Tunnel WB |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-03-31 | 2017-01-10 10:50 | -80 | 2016-09-12 15:25 | Electrical - General | 10000 |  | Damaged | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On 24/08/16 three sections of Fibre Optic cable between Woolwich Box and North Woolwich Portal Westbound became dislodged from the supporting cable tray as detailed below: • Cable Number: CR146-DAT-0018, 96c Fibre Optic, was dislodged, reinstalled on tray, no visual damage noticed. • Cable Number: CR146-DAT-0020, 12c Fibre Optic, between WOL – CP17 was dislodged, reinstalled onto Tray 2, possible damage at Ring No: 1241. • Cable Number: CR146-DAT-0022, 12c Fibre Optic, between CP17 – CP16 was dislodged, reinstalled onto Tray 2, possible damage at Ring No: 1230 & 1241.
| 05SY - Systemwide | Cxxx-NCR-000249 | NCR | Slab W9 FTS Lite WB, chainages 4614.319-4619.000 (W9 west end) |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-10-31 | 2016-11-01 10:23 | 1 | 2016-09-01 15:45 | Track - Track General | 6000 |  | Incomplete Works | Repair | 3 (3-6k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | Similar to Cxxx-NCR-000227 - After a number of technical difficulties with the pour on the night of Thursday 01/09/2016 there was a shortfall in the volume of concrete delivered to the work face of slab W9. This led to the area of approx. 5m in length, approximately 150- 200mm in depth over full slab width (3440mm) being not fully covered by concrete up to designed level.
| 05SY - Systemwide | Cxxx-NCR-000250 | NCR | Upstand concrete cracked in Paddington |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-12-01 | 2016-11-04 11:06 | -27 | 2016-09-02 17:00 | Track - Track General | 2500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | First stage concrete upstand have been cracked due the drilling to fix bolts for brackets/props. Photograph attached.
| 05SY - Systemwide | Cxxx-NCR-000252 | NCR | Aerial earth wire damaged |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-12-15 | 2016-12-07 11:09 | -8 | 2016-09-06 11:39 | Electrical - OHLE | 5000 |  | Damaged | Rework | 3 (3-6k) | Complete | Material/Preservation Problems - Improper handling of material | Completed |  | Aerial Earth Wire was damaged in Plumstead Portal at KP 22.730, Drop Tube XRA/22/706. - During the wiring operation, the external aluminium wires of the AEW was found damaged due to the low quality of the coiling of the drum. The cable sleep on the drum and the wire was broken on it. The damaged part of the wire in the drum was almost inside of the coil (approximately 60 meter wire was left inside the drum) - AEW clamping from the damaged area to the anchor cannot be done and final AEW anchor in Plumstead Portal cannot be done at the moment.
| 05SY - Systemwide | Cxxx-NCR-000253 | NCR | Poor concrete finish and level around some baseplates at W2 and W3 |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-08-10 | 2017-07-24 16:02 | -17 | 2016-09-08 12:57 | Track - Track General | 3000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | W2 slab, Westbound chainages 4268-4392 At some locations of slab W2 and W3, the concrete level is under the required level within the baseplate pad. Some of the pads have been removed for inspection and large voids of trapped air have been found underneath.
| 05SY - Systemwide | Cxxx-NCR-000254 | NCR | Poor concrete finish and level around some baseplates in FTS Lite |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-05-31 | 2017-07-25 10:04 | 55 | 2016-09-08 12:58 | Track - Track General | 3000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Westbound chainages 4367-5157 At some locations of slab W4, the concrete level is under the required level within the baseplate pad. Some of the pads have been removed for inspection and large voids of trapped air have been found underneath.
| 05SY - Systemwide | Cxxx-NCR-000255 | NCR | 7 days concrete strength result of W9 |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-06-28 | 2017-06-16 06:42 | -12 | 2016-09-08 16:31 | Track - Track General | 350000 |  | Material | Reject | 1 (>60k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Slab W9 FTS Lite. Some of the concrete cubes crushed at 7 days do not have required strength of 35N/mm2. See attached reports.
| 05SY - Systemwide | Cxxx-NCR-000256 | NCR | Addition of water to Ready Mix Concrete on site without approved procedure |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-11-24 | 2016-11-23 10:07 | -1 | 2016-09-22 21:23 | Track - Track General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | FTS Lite, Westbound There were some small volume of water added to the ready mix concrete after flow testing at BOS pumping station, under supervision and control of the batching plant, at the request of __ to optimise the flow target. This was in agreement with __ and the Short Notice Change Cxxx-__-O1-CCN-Cxxx-50007. Date / Slab / Ticket No / Fleet No / Volume / Added water 15.08.2016 / W5 / 72382591 / 6908 / 4.5 / 20 15.08.2016 / W5 / 72382618 / 1813 / 4.5 / 15 01.09.2016 / W9 / 72489605 / 6215 / 4.5 / 30 05.09.2016 / W10 / 72518117 / 8708 / 4.5 / 15 However this has not been approved by CRL.
| 05SY - Systemwide | Cxxx-NCR-000258 | NCR | FTS - Lite and Station Control Documentation |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-11-25 | 2016-11-25 08:56 | 0 | 2016-09-13 11:27 | Civil - Track | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Cxxx-__-R4-ITP-CRG03-50005 3.0 - Inspection and Test Plan -Construction of Floating Track Slab - FTS- Lite and Station has been at Code 2 since 5th July 2016 and therefore the comment close out has not taken place within the anticipated period for reply. Furthermore, there are a number of operational critical documents that still haven't found there way onto eB and remain as placeholders, these are as follows:- Cxxx-__-R4-CCN-CRG03-50017 1.0 Cxxx - Short Notice Change for Method Statement Floating Track Slab [FTS] Lite and Station (Placeholder) Cxxx-__-R4-CCN-CRG03-50019 1.0 Cxxx - Application of Debonding agent prior pouring operation (placeholder) Cxxx-__-R4-CCN-CRG03-50020 1.0 Cxxx - Concrete pouring methodology (Placeholder) Cxxx-__-R4-CCN-CRG03-50023 1.0 Cxxx - SNC - Lateral restraint installation (placeholder) Cxxx-__-R4-CCN-CRG03-50024 1.0 Cxxx - SNC - Striking of FTS (placeholder) Cxxx-__-O1-RGN-Cxxx-50001 1.0 - Set up and Safe Use of Static Concrete Pumps at Bond Street ETH Site is shown as Code 3, it is understood that a later version (revision 2.0) which is code 1 has still not made its way onto eB.
| 05SY - Systemwide | Cxxx-NCR-000259 | NCR | W7 incorrect inclination of one baseplate |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-01-18 | 2017-01-11 14:02 | -7 | 2016-09-13 16:35 | Track - Track General | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | FTS Lite, Westbound, slab W7 Ch 4537. One baseplate at Chainage 4537 / south side was installed and cast in with the incorrect inclination.
| 05SY - Systemwide | Cxxx-NCR-000260 | NCR | W8 concrete level out of tolerance |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-05-31 | 2017-07-27 11:17 | 57 | 2016-09-15 16:50 | Track - Track General | 2000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | FTS Lite, Westbound, slab W8 In few places in areas of high cant of the track concrete level was cast up to 10mm higher than top of HDPE pad.
| 05SY - Systemwide | Cxxx-NCR-000261 | NCR | Woolwich East Tunnel Ventilation Fan - Access Hatch |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-02-22 | 2017-02-24 13:46 | 2 | 2016-09-15 12:33 | Systems - Ventilation and Pressure Relief | 5000 |  | Manufacturing Defect | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A site visit was conducted on 5th September 2016 to inspect the recently delivered tunnel ventilation fans at Woolwich Station (East) and to observe the current layout and orientation in relation to the final position. Upon inspection of the fan units it was noted that a large access hatch had been installed in the upper section of the fan (see attached photographs). Upon cross reference __ (__) drawing reference Cxxx-__-H-DWG-CRG03-50016 (1.0) it is evident that the access hatch should have been installed in the lower half of the fan unit.
| 05SY - Systemwide | Cxxx-NCR-000263 | NCR | Lateral Braking Block Bearings L2 manufactured out of tolerance |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-11-29 | 2016-09-29 10:09 | -61 | 2016-09-16 10:38 | Track - Track General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Floating Track Slab - Lateral Braking Block Bearings L2 manufactured out of tolerance During the FAT inspection of L2 lateral bearings, a good proportion (circa 80%) of bearings were oversize - Dimension 99mm +/- 1.5mm Size variations between 0.2mm to 0.6mm
| 05SY - Systemwide | Cxxx-NCR-000264 | NCR | Catchpit metal frame clearance - EB track, chainage 1+267 |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-12-15 | 2016-12-15 12:06 | 0 | 2016-09-16 09:40 | Track - Track General | 2500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | STS drainage - catchpits - EB track, chainage 1+267 Due a rigid formwork built around this catchpit, after the first TMD/VMS survey run. A second one was attempted but undertaken on night shift, with no joiners available to support the task. Then, the catchpit frame spacers were removed in order to allow track vertical alignment to drop to design TMD values, leaving the sleeper tie-bar just touching on top of the metal frame, 2-3mm clearance in the best areas.
| 05SY - Systemwide | Cxxx-NCR-000265 | NCR | Rebar from W1 stop end cast in W2 |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-05-31 | 2017-06-14 08:27 | 14 | 2016-09-16 15:12 | Track - Track General | 5000 |  | Workmanship | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Floating Track Slab W2 CH 4268.5-4317.9 During jacking of slab W2 it was discovered that a piece of rebar was installed in the first stage to fix stop end to on slab w1. This piece of rebar was not removed and therefore cast into second stage concrete of slab W2. This has been lifted and is hanging from jacked slab. Please see the attached sketch.
| 05SY - Systemwide | Cxxx-NCR-000266 | NCR | W2 - UTXs jacked up with the slab |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-12-15 | 2016-11-08 12:29 | -37 | 2016-09-16 15:34 | Track - Track General | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Floating Track Slab - W2 CH 4268.5-4317.9 The UTXs’s protections have been jacked up with the slab, dragging the UTX ducting with it
| 05SY - Systemwide | Cxxx-NCR-000267 | NCR | Damaged Vertical Elastomeric Bearings Type A & B |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-12-19 | 2016-12-13 10:50 | -6 | 2016-09-20 14:07 | Track - Track General | 5500 |  | Damaged | Reject | 3 (3-6k) | Complete | Material/Preservation Problems - Improper handling of material | Completed |  | 9No type A and 2No type B bearings were damaged during handling and transportation to worksite in the Westbound tunnel.
| 05SY - Systemwide | Cxxx-NCR-000268 | NCR | OHLE Drilling - Incorrect Orientation |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-07-17 | 2017-07-20 10:37 | 3 | 2016-09-21 15:53 | Electrical - Cable Management | 1000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Hole orientations of the As-Drilled holes, intended for the OHLE drop tube in the section 15100-15860 EB tunnel (VDP-CWS), have been drilled incorrectly – were the bracket to be fitted the dropper would not be drop downwards as intended. The drilling done has been carried out by the drill rig. The data file which has been uploaded to the rig by the survey team and checked by the OHLE design team, prior to drilling, appears to have been incorrect. The Rig team do not have any way to change the data once it is on the rig. The mistake was noticed when a supervisor who is also involved in the erection of the drop tubes noticed that the 2 hole part of the drill pattern was above the 1 hole part, where it should be below, by this time around 800m had been drilled.
| 05SY - Systemwide | Cxxx-NCR-000269 | NCR | No concrete cube sample to test the strength of pour number 21 |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-10-27 | 2016-10-14 10:22 | -13 | 2016-09-22 15:19 | Track - Track General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | Thames tunnel EB CH20289-20267 On 25/11/2015, we poured 10.5m3 of concrete before a mechanic incident on the concrete train forced us to stop the production. By this time, the set of cubes was not made yet.
| 05SY - Systemwide | Cxxx-NCR-000270 | NCR | Flood Wall - Bay 12 Works Connaught |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-03-29 | 2017-03-31 08:08 | 2 | 2016-09-27 08:32 | Structural Engineering - Concrete Member | 2500 |  | Material | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The works consist of constructing an outstanding section (Bay 12) of reinforced concrete flood wall on the open section of the trace between Connaught tunnel and North Woolwich portal. (adjacent to Albert Road and Factory Road). The placement of concrete for the wall was to be carried out in one continuous pour using an S3 mix, slump 90 to 140mm). During the course of concrete placement for Bay 12 wall, the pour had to be abandoned due to an issue arising with the workability of the concrete (the exact root cause still to be determined). See attached photographs for more details.
| 05SY - Systemwide | Cxxx-NCR-000271 | NCR | Packing shim bent on a side chair of C16 |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-01-18 | 2016-11-04 12:14 | -75 | 2016-09-29 10:33 | Track - Turnouts | 2500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | 11th slide chair of C16 switch (beside the 3rd temporary stretcher bar). The packing shim is bent as per attached picture.
| 05SY - Systemwide | Cxxx-NCR-000272 | NCR | CPS for NWC (Mix 4) has been at a Code 2 decal for in excess of 2 months |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-12-14 | 2016-12-20 11:16 | 6 | 2016-10-03 09:57 | Civil - Track | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | A planned Crossrail surveillance was undertaken on 28th September 2016 to look at Floating Track Slab (FTS) documentation and concreting (Bay W11). During this visit, the Component Product Specification (CPS) for the Normal Weight Concrete (Mix 4) was tabled. On checking, the CPS (Cxxx-__-R4-RSP-CRG03-50067) has been at a Code 2 decal for over 2 months. The comments refer to inadequate Drying Shrinkage testing, and no demonstration of 12hr Compressive Strength compliance. The re-submission to address the comments had yet to take place per the Works Information requirements.
| 05SY - Systemwide | Cxxx-NCR-000273 | NCR | __ water addition process for FTS (detailed in SNC) not followed for FTS pour W11 |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-02-08 | 2017-01-23 07:50 | -16 | 2016-10-03 10:01 | Civil - Track | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | A planned Crossrail surveillance was undertaken on 28th September 2016 to look at Floating Track Slab (FTS) documentation and concreting (Bay W11). On witnessing testing at Bond Street pumping station, the first batch of normal weight concrete recorded a flow of 560mm. Following the result, 50 litres of water was added to the batch at the request of the __ FTS Technical Manager via radio. At that time, __ had not been consulted to seek the maximum allowable water that could be added on site. A further retest after the addition of water recorded 570mm, and a third recorded 590mm. The process flow for water addition within Short Notice Change (SNC) Cxxx-__-O1-CCN-Cxxx-50007 states the following; if a flow is recorded as <600mm on site, the batch will be rejected. Furthermore, it stipulates that __ would be called to confirm the max allowable water to be added (it was stated that confirmation was only going to be sought if the mix became compliant following the addition of water). Although the first batch was subsequently rejected, in both instances, the accepted process within the SNC was not followed.
| 05SY - Systemwide | Cxxx-NCR-000274 | NCR | Incomplete Concrete Train Batching Weight Ticket |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-01-04 | 2016-11-04 15:13 | -61 | 2016-10-06 10:57 | Track - Track General | 500 |  | Software | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Bored Tunnel Section, between Stepney Green and Pulling Mill Lane Portal, EB, CH 11+821 – 11+855. Batching ticket information is missing due to the concrete train computer shut down unexpectedly and it could not be saved. (Document Attached)
| 05SY - Systemwide | Cxxx-NCR-000275 | NCR | PRD blocked by concrete in the cess of C9 Switch (STG EB) |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-06-28 | 2017-07-03 08:55 | 5 | 2016-10-12 10:42 | Track - Track General | 2500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | There was a gap of 10mm approximately between PDR and wall at the time of the concrete pour. The PRD is now full of concrete, Cess of C9 Switch (STG EB), Left hand side (North). 2 other PRDs have been found with some concrete.
| 05SY - Systemwide | Cxxx-NCR-000276 | NCR | Use of concrete load outside of consistency acceptance criteria (W11) |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-02-22 | 2017-01-31 16:42 | -22 | 2016-10-06 21:19 | Track - Track General | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | A flow result of over 700 mm was recorded from the third load of normal weight concrete used to cast W11, delivery note: 72680224. This value is above the maximum value that can be measured in accordance with ‘BS EN 12350-5:2009 Testing fresh concrete Part 5: Flow table test’ which makes the acceptance of this load non-compliant. The standard states under ‘Section 6 Procedure’ that the maximum dimension of the concrete spread is to be measured parallel to the table edges and therefore as the table is 700 mm this is the maximum value that can be assessed with this test. __ accepted this load as it was assessed on site that the consequences of rejecting it would have a much bigger impact on the quality of the slab – the concrete plant had already started batching the HWC. There were no signs of segregation observed in the concrete and it was visually deemed good for pumping and placing by Camfaud – subcontractor in charge of the pumping operation. 4 No concrete cubes were taken from this load. Note: the concrete spread was measured diagonally as 740-760 mm
| 05SY - Systemwide | Cxxx-NCR-000277 | NCR | Shortfall of concrete on E2 |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-12-01 | 2016-11-25 08:57 | -6 | 2016-10-06 21:30 | Track - Track General | 5000 |  | Incomplete Works | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Similar to Cxxx-NCR-000227, there was a shortfall in the volume of concrete delivered to the work face of slab e2. This led to the area of approx. 2 m in length, approximately 120mm in depth over full slab width (3440mm) being not fully covered by concrete up to designed level/top of concrete.
| 05SY - Systemwide | Cxxx-NCR-000278 | NCR | NWC mix used on E1 not produced in accordance with the CPS |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-01-04 | 2016-12-21 12:00 | -14 | 2016-10-06 21:44 | Train - General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | __ has modified the concrete mix design for normal weight concrete in order to improve the consistency and pumpability of the mix. __ failed to update the CPS prior slab E1’s concrete pour. As a result of this, the concrete mix used to cast this slab is non-compliant with the Normal Weight Concrete CPS rev 1.0 which the ITP Cxxx-__-R4-ITP-CRG03-50005 rev 4.0 identifies as the controlling document for the station part of this slab. Please see below the differences between the concrete mix design and the one used to cast E1. • Master Glenium 920: Increased from 1 % (as per CPS) to 1.1 % • A retarter from the same chemical company as the super plasticizer has been added to the mix (at 0.3% of the cement content)
| 05SY - Systemwide | Cxxx-NCR-000279 | NCR | Slab W11 honeycombing |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-12-06 | 2016-11-25 09:00 | -11 | 2016-10-07 06:14 | Track - Track General | 5000 |  | Design | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | FTS Lite, Slab W11, manhole No 5 and No 6. Some honeycombing present on formed surface inside of two manholes (No5 and No6 from east side) see attached pictures.
| 05SY - Systemwide | Cxxx-NCR-000280 | NCR | Some bearing plates not installed prior E1 concrete pour |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-01-14 | 2017-12-15 11:59 | -30 | 2016-10-07 06:26 | Track - Track General | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | E1 Eastbound chainages 3924.800 – 3974.200 The bearing plates on slab E1 were installed as per the typical arrangement of 4 No bearing plates per manhole as opposite to what is detailed in the general layout drawing Cxxx-OVE-R4-DDA-CR001_Z-81052 C05 – different bearing layout due to transition between standard track slab and floating track slab. There is a total of 10 No bearing plates that were not installed prior concreting, please see the attached sketch for the location of these.
| 05SY - Systemwide | Cxxx-NCR-000281 | NCR | Attenuator Module Installation drawing error |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-12-14 | 2016-10-20 14:33 | -55 | 2016-10-10 15:44 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Design | Reject | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | The first attenuators delivered to site from __ Acoustics were not correct as per the installation drawings.. This was a result of an incorrect Installation drawings. The Modules were labelled correctly on the Fabrication GA's i.e module ATT 01, 04, 06 etc. but were incorrect on the submitted Installation drawing, so when __ thought they were calling off ATT 01, it was actually ATT 03, and called off ATT 03 was actually ATT 01. The Installation drawing was incorrectly turned by 90 degrees.
| 05SY - Systemwide | Cxxx-NCR-000282 | NCR | Damaged CMS Bracket in Thames Tunnel WB |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-06-11 | 2017-06-15 06:22 | 4 | 2016-10-10 15:26 | Electrical - Cable Management | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | During an IRN inspection of the Woolwich Box WB CMS it was noted that a CMS bracket in the Thames Tunnel WB was twisted at chainage 21085 (ring 822). As the area did not fall under the precise limits of the IRN and as the Thames Tunnel WB had already been signed off, it was agreed with CRL that the NCR would be raised to capture this observation.
| 05SY - Systemwide | Cxxx-NCR-000283 | NCR | __ Steelwork __ HIT V-F Holding down rods. |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-03-06 | 2017-03-01 16:56 | -5 | 2016-10-11 09:28 | Materials - General | 5000 |  | Material | Rework | 3 (3-6k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | __ are using the __ threaded rods for the TSA steel work embedded into the slab that are on the Approved Installation ITP Cxxx-__-O4-ITP-CRG03-50030. These rods are not on the MCR and have a Galvanisation value of 43um Minimum, which does not meet a C4 environment values
| 05SY - Systemwide | Cxxx-NCR-000284 | NCR | Qualification Testing of RF195 baseplate for Enhanced Track not in accordance with procedure |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-01-24 | 2016-12-15 12:14 | -40 | 2016-10-11 13:02 | Track - Rails and Sleepers | 5000 |  | Material | Reject | 3 (3-6k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | __ representative undertook an inspection of the EN qualification testing of a prototype of the RF195 baseplate at the testing lab of TMT in China on 12/09/2016. The qualification testing of the RF195 baseplate was underway it was discovered that the stiffness and repeated load testing elements of the testing was not being undertaken in accordance with document number TF195-TP-001 - Delkor Rail Alt 1 RF195 Qualification Test Procedure. The stiffness and repeated load testing underway deviated from the procedure in the following ways: • The RF195 baseplate is fixed to a steel test bench, while the test procedure requires a concrete slab. • The fastening screws on the steel test bench are 8.8 grade on one side; and on the other side 4.8 grade. This is related to the point above, as a different fixing arrangement is necessary since a concrete block is not being used. As a consequence, the performance of the actual embedded screw spike is not being tested. • The plastic material used for the base pad below the baseplate is white. The material used in the final assembly is black and has a scalloped shape.
| 05SY - Systemwide | Cxxx-NCR-000285 | NCR | Non-Compliant Top Crack Inducers on PML Portal EB |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-07-21 | 2017-07-06 10:12 | -15 | 2016-10-11 15:40 | Track - Track General | 3000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Pudding Mill Lane Portal, EB, CHs: 14159 to 14593. During the inspection of the area located in the North Eastbound from chainages 14159 to 14593 at Pudding Mill Lane Portal, All the cuts made above the bottom crack inducers are not compliant with the design, with depths between 5mm and 40mm, increasing highly the risk to get crack on the second stage concrete. (Report Attached)
| 05SY - Systemwide | Cxxx-NCR-000286 | NCR | Concrete late hardening due excess of retardant additive |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-04-04 | 2016-11-09 11:46 | -146 | 2016-10-12 15:47 | Track - Track General | 2500 |  | Equipment Breakdown | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | EB track section, in between chainages: 2+385 to 2+415 Due a break down on the buffer wagon. Train crew decided to pour inside the buffer drum 20lt of retardant additive SPLAS/RET, under the event of getting rid of the concrete inside. The buffer had already contained 11m³ of fresh concrete drum. However the mechanical problem in the buffer was quick sorted and fixed out, therefore the pour resumed, using up the mix already in the drum (with extra retardant additive). After 24hrs, the section poured in between chainages 1385 & 1415, – Area equivalent to the concrete poured with extra retardant additive – had not hardened accordingly. Showing visual aspect of moisture and presenting a sandy consistency and softness.
| 05SY - Systemwide | Cxxx-NCR-000287 | NCR | Cores on concrete track slab without engineering response acceptance |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-01-10 | 2017-01-09 12:15 | -1 | 2016-10-12 15:59 | Track - Track Bed | 3000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | EB track section, in between chainages: 2+385 to 2+415 Due an issue with retardant additive in concrete (Cxxx-NCR-000286 raised) Production team has proceeded under their responsibilities and without any confirmation from Design or Quality team, to take core samples on six locations within the range of the abnormal concrete to test to compressive strength at 28 days – Photos attached.
| 05SY - Systemwide | Cxxx-NCR-000288 | NCR | Rail inclination out of tolerance (E4) |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-11-13 | 2016-11-15 10:07 | 2 | 2016-10-14 10:54 | Track - Track General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | E4 (eastbound chainages 4201- 4235) During E4’s pre-pour inspection, the rail inclination was found to be slightly out of tolerance in several jigs. The lowest value was found by tunnel ring 2413; 2.21° on the right hand side rail and 2.26° on the left hand side. This low value was isolated to just one of the jigs being the average of the other out of tolerance readings 2.50 °– circa 0.11° out of tolerance. At least 5 screws that lock the rail inclination were found loose. The slab was concreted as it was assessed that the deviation is marginal. Note: There is no rail inclination tolerance set by the Specification (Cxxx-OVE-R4-RSP-CR001-50001). __ set the inclination tolerance to ±0.25° which may be more conservative than required
| 05SY - Systemwide | Cxxx-NCR-000289 | NCR | HWC specific trial and production testing has not been completed as required by Specification KF10 for the FTS works. |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-03-31 | 2017-03-31 08:14 | 0 | 2016-10-17 10:16 | Civil - Track | 2000 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | A planned Crossrail surveillance was undertaken on 28th September 2016 to look at Floating Track Slab (FTS) documentation and concreting (Bay W11). During this visit, KF10 HWC testing requirements were discussed. At the time of the surveillance it was stated around 10 HWC pours had been completed. KF10.4302 defines testing requirements during production; in particular compressive strength, consistence, oven dry density, fresh density and bleed including sampling frequencies and test locations. KF10.4301 clearly defines the testing required during trial mixes. It was noted that only flow testing (at batcher and point of delivery) and compressive strength testing is being completed as detailed in the ITP. The specification asks for fresh density to be carried out on each batch at the point of delivery and at discharge from the pump. Furthermore, a bleed test is required on 1 out of every 5 batches at delivery. The ITP does not reference this testing. Moreover, the specification also defines a sampling frequency for compressive strength testing as 1 in every 5 batches. A HWC batch comprises of 4.5m3. HWC compressive strength cube sampling is being done to a rate of 1 set per 50m3. The sampling rate does not align with the rate of the KF10 specification. There is currently no agreed relaxation in place for such testing and frequencies associated which are not being met (see above). The surveillance identified that a) no bleed or segregation testing had been completed during trials (KF10.4301); b) no production testing (bleed and fresh density) had been completed for the HWC pours completed to date (KF10.4302), and c) no evidence existed of agreed relaxation of such testing and frequencies (a and b). A Site Observation form had been produced with the intention of seeking clarification from Cxxx; an email response from Nigel Caswell dated 3rd October stating that an RFI should be submitted to CRL to enable clarification to be captured. No RFI has been produced with such clarification. In addition, __ are a self certifying Contractor; a Code 1 decal on the ITP and CPS does not relive the Contractor of their obligation to comply with the Contract requirements. The responsibility for undertaking or clarifying such testing lies with __.
| 05SY - Systemwide | Cxxx-NCR-000290 | NCR | OHLE and AEW components (Batch 2) delivered and installed with the Factory Acceptance Test (FAT) Report at a Code 3 decal. |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-12-07 | 2016-12-07 09:10 | 0 | 2016-10-17 11:29 | Over Head Line Electrification - Supports | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | A planned Crossrail surveillance was undertaken on 14th October 2016 to look at OHLE and AEW bracket/ drop tube installation from Plumstead Railhead. FAT reports were provided during the documentation review; Cxxx-__-O4-RGN-CRG03-50036 (Batch 1) and 50111 (Batch 2). Batch 1 was at a Code 1 decal and Batch 2 was at a Code 3 decal. When questioned, it was stated that Batch 2 steelwork components had been delivered to the Plumstead storage facility from Sugremin, even though the FAT report was at a Code 3 decal. Furthermore, on visiting the storage facility, there was no separation between the FAT Batches with components mixed together. It was also stated that components from Batch 2 had been installed within the works. The Works Information is clear that FATs shall be satisfactorily completed before any shipment to site. The fact that Batch 2 components had been delivered and installed in the works highlights a significant breakdown in the management of the FAT process.
| 05SY - Systemwide | Cxxx-NCR-000291 | NCR | No Pull Out testing has been completed on OHLE and AEW fixings installed within the Thames Tunnel bored section as required by the ITP. |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-12-21 | 2016-12-16 10:12 | -5 | 2016-10-17 11:32 | Over Head Line Electrification - Supports | 3000 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | A planned Crossrail surveillance was undertaken on 14th October 2016 to look at OHLE and AEW bracket/ drop tube installation from Plumstead Railhead. During the site visit, pull out testing was discussed for the fixings installed within the Thames Tunnel section of the works (Plumstead to North Woolwich Portal) – Eastbound. ITP Cxxx-__-E-ITP-CRG03-50001 (Rev 5) Inspection Number 3.5 states a requirement for Pull Testing on mechanical anchors at a frequency of 1 in every 40 fixings. During the discussions, it was stated that no Pull Testing had been completed on the fixings installed within the bored tunnel section of the Thames Tunnel works which sits under the remit of the __ Mechanical Team. As a result, the workmanship and fixing load performance (28.0kN) has yet to be confirmed as acceptable.
| 05SY - Systemwide | Cxxx-NCR-000292 | NCR | Canary Wharf East TSA |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-01-25 | 2017-01-26 15:56 | 1 | 2016-10-17 13:07 | Materials - General | 5000 |  | Material | Rework | 3 (3-6k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | During installation of __ attenuators in Canary Wharf East Shaft by Hargreaves it was noted that the Spun galv M10 set screws, washers and nuts have been supplied to bolt the attenuator modules together and to the supporting steelwork. The fixings have been tightened to a torque of between 50 and 56Nm. Despite this, the thread in the nuts has stripped. We believe this to be a result of the nuts being tapped oversize after coating. This results in insufficient thread engagement in some instances, thus reducing the stripping torque of the assembly. The actual thread on the bolt samples we have isn’t damaged; on closer inspection it’s just shiny from interaction with the nut. It has also been noted that only one washer was utilised per nut and bolt. There should be two, as per the detailed drawings.
| 05SY - Systemwide | Cxxx-NCR-000293 | NCR | LIVERPOOL STREET |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-11-30 | 2016-11-28 11:13 | -2 | 2016-10-17 14:03 | Shafts - Shafts General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate resources | Completed |  | Installation for the lifting beams and gantries have commenced at Liverpool St East, with the first delivery of materials took place on 10/10/16. The TVS QC (--) was informed about this delivery on 30/09/16. He was advised to supervise -- in completing their quality checks, but declined to attend. The ITP Cxxx-__-O4-ITP-D061-50003 states the delivery check sheet is a hold point for __ QA. The first pull-out test on the anchors was completed on 11/10/16, to which CRL quality team (--) was invited to and attended. -- was present in the site office at the time of the test. He checked the calibration certs for the pull-tester were okay then declined to witness the test. The ITP Cxxx-__-O4-ITP-D061-50003 states that pull-out tests are to be carried out on with 25% of all resin and mechanical anchors and are a hold point for __ QA.
| 05SY - Systemwide | Cxxx-NCR-000294 | NCR | The goods received from sub-supplier Jointing Technologies were mixed for different contracts- Cxxx and Cxxx. |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-12-18 | 2016-11-04 11:16 | -44 | 2016-10-19 12:04 | Electrical - OHLE | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | __ received mixed goods for Cxxx and Cxxx contracts on same pallet from sub-supplier. It creates confusion at site and wasting time to understand which product belongs to which Contract.
| 05SY - Systemwide | Cxxx-NCR-000295 | NCR | Track Installed out of tolerance at PML Portal EB |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-01-18 | 2016-11-10 10:07 | -69 | 2016-10-20 12:30 | Surveying - Surveying General | 5000 |  | Incorrect Installation | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Friday afternoon 14/10/2016, survey team, setting track on the EB at Marshgate Bridge reported that the horizontal deviation from design was -30mm, after an investigation carried out, the Surveyor discovered that the track was in fact set at -30mm, he had also investigated and found that the likely cause of the problem was the use of an incorrect survey control file. So the concrete was cancelled. A re-survey was done along the entire EB portal to identify the extent of the issue, it has been confirmed that the deviation from design (Horizontal Absolute Variation) started at Ch 14277, reaching -10mm at Ch14345 and continuing up to -31mm at Ch14608, giving a total out of tolerance concreted track length of 263m. Additional to this, it has been assessed that the Horizontal Rate of Change over 10m is out of tolerance also, between CH 14318 and 14335 (QCR-9A STG-PML STS-EB-A-14277-14372 attached ). Pre-pour TMD/VMS carried out pre-pour was compliant on this area. All other track geometry and rate of change parameters remain well within tolerance, the results from the As-Built can be seen in the attached QCR-9A sheets.
| 05SY - Systemwide | Cxxx-NCR-000296 | NCR | FTS - BM 09 of type 4 lateral restraints in E5 found non-compliant after the slab was concreted |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-01-18 | 2016-11-08 12:47 | -71 | 2016-10-20 20:50 | Track - Track General | 500 |  | Manufacturing Defect | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | A number of Lateral restraints BMs 09 have been bent incorrectly by the supplier and delivered to site; the width of the top parts of the bars has been measured on site as circa 225 mm, non-compliant against the 115 mm figure detailed in the __. These bars have been used in 4 number lateral restraints in E5 installed between chainage 4248 and 4284 on the high side of the slab. This issue has been identified after the slab was concreted. Note: The same issue was identified in other lateral restraints of the eastbound tunnel. This will be covered by a different NCR.
| 05SY - Systemwide | Cxxx-NCR-000297 | NCR | FTS - Barbican reinforcement not bent in accordance with __ (W43, E48 and E47) |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-02-28 | 2017-02-09 15:29 | -19 | 2016-10-20 20:56 | Track - Track General | 2500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Reinforcement for slabs W43, E48 and E47. Some reinforcement bars for FTS Barbican have not being bent in accordance with the __. The reinforcement was delivered to site and fixed by the steels fixers who noticed the discrepancies during the installation. Please see the details below. 1. West bound: • Slab W43, Cxxx-OVE-R4-DDJ-CR001_Z-84607 C02: BM 52 (wrong shape) 2. East bound: • Slab E48 , Cxxx-OVE-R4-DDJ-CR001_Z-84601 C02: Bar mark 52 is 205 high instead of 225 high, Bar mark 54 is 420 high instead of 350 high, Bar mark 58 is 240 high instead of 225 high • Slab E47, Cxxx-OVE-R4-DDJ-CR001_Z-84614 C01: Bar mark 52 is 205 high instead of 225 high, Bar mark 54 is 420 high instead of 350 high
| 05SY - Systemwide | Cxxx-NCR-000298 | NCR | FTS - BM 09 of type 4 lateral restraints non-compliant on the eastbound track (E6, E8) |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-12-19 | 2016-12-08 12:25 | -11 | 2016-10-20 20:59 | Track - Track General | 1000 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | E6 and E8 high side between chainages 4270- 4298 and 4352-4397 respectively. A number of Lateral restraints BMs 09 have been bent incorrectly by the supplier and delivered to site; the width of the top parts of the bars has been measured as circa 225 mm, non-compliant against the 115 mm figure detailed in the __. These bars have been installed in 4 No lateral restraints in E6 and 6No in E8 on the high side of the slab between EB chainages 4270- 4298 and 4352-4397 respectively. Note: The same issue was identified at the same time in 4 No lateral restraints that had been concreted already – covered by a different NCR (No 296)
| 05SY - Systemwide | Cxxx-NCR-000299 | NCR | Crack appeared on Track Slab (Transition STS / C15) |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-10-27 | 2017-09-27 15:07 | -30 | 2016-10-20 21:17 | Track - Track Bed | 5000 |  | Design | Repair | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | Connaught West, WB, CH: 17348 (Transition btw STS and C15). Track Slab has been cracked in the proximity of a STS sleeper, close to a first stage construction joint and a Transversal Drainage Channel. Crack width 5mm approx. See attached pictures.
| 05SY - Systemwide | Cxxx-NCR-000300 | NCR | Damage to the Mashgate Lane Bridge |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-10-31 | 2018-10-05 12:05 | -26 | 2016-10-21 09:40 | Structural Engineering - Surface Treatment | 10000 |  | Damaged | Rework | 2 (6-60k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Pudding Mill lane Portal – Mashagate bridge WB. Painting damaged and concrete wall broken.
| 05SY - Systemwide | Cxxx-NCR-000301 | NCR | Contract Management Gate 7 (Readiness Review) had not been undertaken prior to commencing OHLE and AEW installation activities. |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-11-30 | 2016-11-29 10:18 | -1 | 2016-10-24 10:23 | Over Head Line Electrification - Supports | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | A planned Crossrail surveillance was undertaken on 14th October 2016 to look at OHLE and AEW bracket/ drop tube installation from Plumstead Railhead. During the surveillance, it was identified that the Contract Management Gate 7 had not been undertaken and duly completed prior to commencing OHLE bracket and supports installation, and AEW cable installation, as defined in __ Contract Quality Plan Cxxx-__-O4-STP-CR001-50001 (Rev 7) under the below clauses. “16.13.5 Mandatory Readiness Reviews All off-site fabrication, on-site installation or specific high risk activities requiring accepted plans or other arrangements shall be controlled using the Contract Management Gates system described below. The __ Project Manager, in consultation with the Supply Package Manager, shall prepare a schedule of readiness reviews ref: template Cxxx-__-TMP-000046 to include all relevant stages and activities within the supplier or subcontractor’s scope of works. The Supply Package Manager shall ensure that each supplier or self-delivery team whose scope of work includes such activities is informed of these requirements and only proceeds with the activity when authorised to do so by the issue of a completed and authorised Gate. Prior to Starting New Installation Activity (Contract Management Gate 7) No work may commence until all relevant pre-requisites are in place. The person responsible for supervising the work must obtain confirmation that all necessary method statement approvals, ITPs, permits have been developed and authorised as necessary before briefing them to the installers and allowing work to commence. Provided that all conditions remain consistent, the readiness review for an activity may remain effective over a number of locations. Using template Cxxx-__-TMP-000034, the Supply Package Manager and the __ Project Manager shall agree the pre-requisites to be demonstrated for each gate. Prior to Undertaking a Single High Risk Activity (Contract Management Gate 7) Where a specific activity involving heightened quality risk, is to be undertaken, a task-specific readiness review will be required. The __ Project Manager shall identify the requirement for these reviews and enforce their delivery. The Supply Package Manager shall facilitate this process and shall use template Cxxx-__-TMP-000034 for this purpose.”
| 05SY - Systemwide | Cxxx-NCR-000302 | NCR | No Compliance Matrix produced for OHLE and AEW components as required by Approval and Acceptance of Materials Procedure. |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-02-01 | 2016-11-29 12:52 | -64 | 2016-10-24 10:25 | Over Head Line Electrification - Supports | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | A planned Crossrail surveillance was undertaken on 14th October 2016 to look at OHLE and AEW bracket/ drop tube installation from Plumstead Railhead. On discussion during the surveillance, and in post surveillance follow up meetings, it was identified that no Compliance Matrix had been produced for the OHLE and AEW Components installed in the works. Procedure for Approval and Acceptance of Materials, Products and Plant Cxxx-__-O4-GPD-CRG03-50016 Rev 2, which is referenced in the Contract Quality Plan, states the following: “6.3.3 Material & Product Compliance Each __ Project Manager shall appoint a member of their team to administer the materials and product compliance process within their remit. For each item on the MPS, the designer shall identify all specified material and product requirements for which evidence of compliance is required. The designer shall list the specified criteria on a compliance matrix for each item of material or product. The procurement manager shall include the compliance matrix in each ITT, for completion by each prospective supplier. Suppliers shall provide all relevant documentation to support their completed compliance matrix. Where applicable, this shall include: ISO 9001:2008 Certification (UKAS), CE Marking Declaration, UKAS (or equivalent) Testing Certification, 3rd party approvals (e.g. __, LUL), Data Sheets, Test Reports The designer shall review each supplier’s completed compliance matrix to evaluate compliance of the proposed product or material and shall indicate acceptability in the tender evaluation. Evidence of compliance must be provided to Cxxx for: ‘standard’ items - before the order is placed unless additional testing or approval is required to establish conformity, in which case evidence of conformity must be provided before ordered product is called off ‘bespoke’ manufactured or fabricated items - before Cxxx gives the supplier permission to start manufacture or fabrication.” It was also noted that those responsible for administering the works were not aware of this procedure and its requirements, as such, the communication of procedural requirements should also be looked at as part of the close out to this NCR.
| 05SY - Systemwide | Cxxx-NCR-000303 | NCR | Training certificates not provided for operatives undertaking pull testing at ROP |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-12-14 | 2016-12-07 11:11 | -7 | 2016-10-25 09:07 | Over Head Line Electrification - Supports | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | A planned Crossrail surveillance was undertaken on 14th October 2016 to look at OHLE and AEW bracket/ drop tube installation from Plumstead Railhead. During the surveillance test records were provided for pull testing of brackets installed at Royal Oak Portal by the OHLE team. The test records showed that testing was carried out by operative __s. Following request during the surveillance and on multiple occasions post exit meeting the training certificate / evidence of training was not be provided. As such competence and validity of the results could not be demonstrated.
| 05SY - Systemwide | Cxxx-NCR-000305 | NCR | Subcontractor Damage to Dampers, CWS |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-12-14 | 2016-12-21 12:06 | 7 | 2016-10-27 11:35 | Materials - General | 1000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | Prior to lifting activities carried out by __ Ltd, from Level 0 to Level -4, West Shaft, it has been discovered that the use of lifting chains, and not straps as required, has resulted in minor scratches and indents on up to 4 No# Tunnel Isolation Damper modules. The largest scratch found is approximately 50mm x 6mm. Footprints have also been discovered on various Damper modules.
| 05SY - Systemwide | Cxxx-NCR-000306 | NCR | __s __ Anchor Pull-out Test Values |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-11-30 | 2016-12-01 12:05 | 1 | 2016-10-25 14:05 | Structural Engineering - Testing | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Gantries Tag No# 16005, 16006, 16008 & 16009 The above gantry __ anchors of the brackets are pull-out tested to 12 kN instead of 13 kN according to __s setting out drawing Cxxx-__-Y-DWG-D061-50009. Gantries were then installed and proof load tested to 125% of SWL per site acceptance files without any issues.
| 05SY - Systemwide | Cxxx-NCR-000307 | NCR | FTS slab E6 7 days concrete strength results at 7 days |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-12-20 | 2016-12-08 13:54 | -12 | 2016-10-25 18:10 | Track - Track General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Two sets of cubes were crushed at 7 days. 2 out of 6 concrete cubes strength results are slightly (6.8% and 3.5%) less than required strength of 35N/mm2. (cube No 4 result is within 0.003% of 35kN/mm2) 1. 32.6 N/mm2 2. 33.8 N/mm2 3. 36.9 N/mm2 4. 34.9 N/mm2 5 39 N/mm2 6. 36.6 N/mm2
| 05SY - Systemwide | Cxxx-NCR-000308 | NCR | Delivery and Installation of Tunnel Vent Attenuators |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-02-22 | 2017-02-27 12:50 | 5 | 2016-10-26 09:33 | Systems - Ventilation and Pressure Relief | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Installation of the tunnel side attenuators at CWS-W has been completed and the Atmosphere side attenuators at WHI-E Station East Shaft has commenced without first obtaining the necessary approvals from the Project Manager. The Installation Procedure - Tunnel Vent Attenuators reference Cxxx-__-H-GPD-CRG03-50008 is still under review and will be returned to the Contractor with comments ‘Not Accepted’. It is also noted that the attenuator GA drawings are at code 1 on the basis that the design will not change following the ALARP demonstration (see below), the structural steelwork drawing reference Cxxx-__-H-DWG-D061-50011 is at Code 2 and as such the Contractor does not yet have a fully approved design. The Handling and Rigging Procedure reference Cxxx-__-H-GPD-CRG03-50012 which details the safe handing and placement of the attenuators is currently a ‘Placeholder’ on the Employers document management system (eB) and remains outstanding. Furthermore, there are outstanding matters relating to Cxxx-PMI-00490 issued on 17th June 2016 requesting the Contractor to produce a comparative risk assessment for the removal of splitters from an in situ module, verses removable splitters from a relocated module (i.e. to remove the module and relocate to a safe place, unbolt and remove the splitters, replace the splitters, reseal all screw openings and return module to its location). The Risk Assessment is required prior to commencement of installation to demonstrate that __'s attenuator proposal is ALARP and to show the methodology is consistent with the RAMs analysis.
| 05SY - Systemwide | Cxxx-NCR-000309 | NCR | Damage to Attenuator |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-01-18 | 2017-01-20 09:28 | 2 | 2016-10-27 11:56 | Materials - General | 5000 |  | Damaged | Rework | 3 (3-6k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | __ Atmosphere side Attenuator was delivered to WHI-E on 25/10/16. It was noticed a dent on the underside of one of the module once it was installed. This could only be inspected once the module was installed on the steelwork from the level below. The module was lifted one by one, of the pallets from the ground to the roof and landed on timber and pallet trucks by __ & __ crane team. It was then skated the module on the roof to the inside the vent shaft using Gantry crane 17001 and placed onto the top of the ASA steelwork by __. During the joint walk around by __/CRL the dent was spotted from the ground below. It’s not sure how the dent was occurred. During delivery it was sitting on the pallet and therefore, there was no access to inspect until it was installed.
| 05SY - Systemwide | Cxxx-NCR-000310 | NCR | Post baseplate does not fit on the top of the concrete lip at Connaught Tunnel |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-07-14 | 2017-05-24 15:59 | -51 | 2016-11-30 08:51 | Electrical - Cable Management | 5000 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The CMS is posts mounted in the ramps of Connaught tunnel as per drawing. The posts have a specific baseplate to suit the concrete structure of the ramps. During setting out, it was observed that at chainage 18500 to 18580 approx) that the base plate does not fit on the top of the concrete lip. The base plate is 410mm deep; however, the depth of the plinth does not have a constant size as assumed in design (minimum depth to be confirmed after survey - at a specific area we measured 230mm). Approximatively 25 posts cannot be fitted. Note: Although some posts have now been manufactured it is likely that these posts can be used elsewhere.
| 05SY - Systemwide | Cxxx-NCR-000311 | NCR | FTS - Leak of concrete from E5 onto E6 |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-12-01 | 2016-11-01 15:47 | -30 | 2016-11-01 15:32 | Track - Track General | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Approximately between Eastbound chainages 4300 and 4302. During E5’s concrete pour there was a concrete leak through the stop end – most likely a gap between the drainage channel plate and the stop end. The concrete spread through the drainage channel onto E6 up to the first bearing shaft. This issue was identified when E5’s stop end was removed in order to re-fix it in readiness for E6’s concrete pour.
| 05SY - Systemwide | Cxxx-NCR-000312 | NCR | Steelwork installed at incorrect location |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-11-15 | 2016-11-10 09:51 | -5 | 2016-11-01 16:31 | Structural Engineering - Steel Member | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On 31st October 2016, __ and CRL carried out a site inspection on the Tunnel Side Attenuator. West Shaft steelwork as part of the Inspection and Test with __ Ltd (HDL) in anticipation for Tunnel Side Attenuator delivery on 1st November 2016. Upon the dimensional check which was being carried out by HDL on the critical 4 centre holes, it was discovered that TSA/B and TSA/C had incorrect dimensions when carrying out the diagonal checks, with discrepancies of up to 30mm (tolerance allows up to 4mm). Further investigation to this has shown that __ (Steelwork Contractors) have installed 2 x 5m beams in the incorrect location.
| 05SY - Systemwide | Cxxx-NCR-000313 | NCR | Top arm of CMS bracket slightly bend |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-11-30 | 2016-11-28 11:26 | -2 | 2016-11-02 09:56 | Electrical - Cable Management | 500 |  | Manufacturing Defect | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | During pre-IRN walkthrough and inspection of the CMS installation at Limmo Shaft Eastbound, it was noted that the top arm of one of the CMS brackets was slightly out of position. Closer inspection confirmed that the arm had most likely been welded incorrectly.
| 05SY - Systemwide | Cxxx-NCR-000314 | NCR | FTS - No concrete delivery record for a pour of complimentary part of slab W9 |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-01-17 | 2016-12-13 10:53 | -35 | 2016-11-03 09:33 | Track - Track General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Complimentary pour to finish slab W9. No record of concrete delivery taken during the pour and no copy of delivery notes kept in file.
| 05SY - Systemwide | Cxxx-NCR-000315 | NCR | FTS - Not enough cubes taken from same load during the pour of complementary part of slab W9 |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-01-17 | 2016-11-08 12:49 | -70 | 2016-11-03 09:37 | Track - Track General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | Complimentary pour to finish slab W9. Only 5 cubes taken from the same load instead of 10, 5 other cubes were taken from second load.
| 05SY - Systemwide | Cxxx-NCR-000316 | NCR | Incorrect UTX pipe installation - Bond Street Station EB track, CH 3+701 |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-02-08 | 2017-01-09 12:18 | -30 | 2016-11-03 10:43 | Track - Track General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | UTX located as per drawings at EB ch 3+704 have been relocated to EB ch 3+701 (there is another UTX as per drawings), and installed in the same UTX box of ch 3+701 not allowing enough space for concrete coverage between pipes. Photograph attached.
| 05SY - Systemwide | Cxxx-NCR-000317 | NCR | Incorrect Lifting Technique of Attenuators |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-12-14 | 2016-12-08 13:48 | -6 | 2016-11-04 11:04 | Structural Engineering - Steel Member | 3000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | On the 24th October 2016 __ mechanical equipment installation contractor __ started to take delivery of the Atmosphere Side Attenuators (ASA) for the Cambridge Heath Shaft at Whitechapel Station East. The delivery came via __ off site storage facilitator ClipFine and was transported using a low loader lorry. Once on site, lifting eyes were secured to the modules, and the lifting chains from the Tier 1 __’s crawler cranes attached. Each module was then individually lifted to the landing deck. These were all text book lifts and in accordance with the __s installation procedure. At this point the Attenuators were manoeuvred under the __ crane lifting beam where each module was then lifted into its final position. Up to 15 modules were installed at which point all works were instructed to STOP as it was determined that the lifting technique was not in accordance with the manufactures approved procedures. The use of an incorrect process has launched a joint investigation between __ / __s / __ to confirm the cause and effect. Following further discussion with the manufacture, they have confirmed that the incorrect lifting methodology may apply excessive loads to the Attenuator casing. In extreme conditions, this could cause deformation / damage to the module.
| 05SY - Systemwide | Cxxx-NCR-000318 | NCR | Concrete Finish clashes with installed Cross Passage Door in Cross Passage 17 & 18 |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-01-18 | 2016-11-28 15:50 | -51 | 2016-11-04 16:41 | Civil - Civil Engineering General | 3000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | Upon installation of a cross passage door in Cross Passage (CP) 18, it transpired that the door would not fully open into the tunnel. The door clashed with the concrete, even though the concrete had been cut out prior to allow for the door to open. After this problem was observed an additional survey was carried out at CP17, where the same problem was noted. CP17 has already been remediated, prior to any doors being installed.
| 05SY - Systemwide | Cxxx-NCR-000319 | NCR | OHLE Holes incorrectly drilled in running tunnel between CWS to STG |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-06-23 | 2017-07-06 10:13 | 13 | 2016-11-04 16:58 | Electrical - Cable Management | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A site walk revealed that several OHLE bracket holes have been drilled in between two tunnel ring joints. It was also observed that holes were drilled within the no drill zones. About 50% of all the holes drilled between Canary Wharf Station (west end) to Cross Passage 10 are affected by this error.
| 05SY - Systemwide | Cxxx-NCR-000320 | NCR | I__ lids broken for C9 and C10 turnouts (STG EB & WB) |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-06-23 | 2017-07-03 09:03 | 10 | 2016-11-07 12:02 | Track - Turnouts | 1000 |  | Material | Reject | 4 (0.5-3k) | Complete | Discipline/Workmanship - Error by manufacturer in shipping or marking | Completed |  | The lids on both sides of the In Bearer Clamp Locks for both C9 and C10 turnouts (STG EB & WB) are broken. The lids are made from fibre glass. Note: The central lid is made from steel.
| 05SY - Systemwide | Cxxx-NCR-000321 | NCR | FTS - E9 7 days concrete strength results |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-12-14 | 2016-12-08 13:57 | -6 | 2016-11-08 16:52 | Track - Track General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | FTS Lite Slab E9. Two sets of cubes were crushed at 7 days. 2 out of 6 concrete cubes strength results are 5% and 8% less than required strength of 35N/mm2.
| 05SY - Systemwide | Cxxx-NCR-000322 | NCR | FTS - W14 7 days concrete strength results |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-12-14 | 2016-12-08 13:59 | -6 | 2016-11-08 17:35 | Track - Track General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Not Defined | Completed |  | FTS Lite Slab w14. Two sets of cubes were crushed at 7 days. 1 out of 6 concrete cubes strength results is 1.5% less than required strength of 35N/mm2.
| 05SY - Systemwide | Cxxx-NCR-000323 | NCR | FTS - E3 concrete between kerb and FTS prior to jacking |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-12-14 | 2016-12-08 14:02 | -6 | 2016-11-08 17:51 | Track - Track General | 1000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | FTS Lite, Slab E3, North side. Ch. 4038.500, Ring No 2296. Small area of about 1m in length between side shutters and FSC kerb is filed with concrete preventing formwork removal.
| 05SY - Systemwide | Cxxx-NCR-000324 | NCR | FTS - E1 foreign object in the concrete |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-04-27 | 2017-04-18 08:52 | -9 | 2016-11-10 09:17 | Track - Track General | 2000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | FTS Lite & Station Slab, E1. Single piece of timber cast into permanent works in area underneath of second from east end of slab E1 baseplate / south side.
| 05SY - Systemwide | Cxxx-NCR-000325 | NCR | FTS - damage to shear keys lower part thread |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-02-09 | 2016-12-13 10:56 | -58 | 2016-11-11 08:38 | Track - Track General | 3000 |  | Damaged | Reject | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | During installation of shear keys some of the thread of lower part was found to be damaged by initial driving of the bolts into the thread. Damaged items removed and not incorporated into the permanent works. 4No so far.
| 05SY - Systemwide | Cxxx-NCR-000326 | NCR | Damaged Walkway Brackets |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-07-06 | 2017-06-16 10:21 | -20 | 2016-11-17 17:37 | Tunnelling - Walkways | 2000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | There are four damaged evacuation walkway brackets in the STG to PML Eastbound trace, located at ring numbers: 530, 558, 583, 954. The damage was caused by a clash with the MPG during track installation.
| 05SY - Systemwide | Cxxx-NCR-000327 | NCR | Wrong ducts installed at PML, EB 13967, (E&B) |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-02-09 | 2017-02-09 14:25 | 0 | 2016-11-11 15:56 | Track - Track General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Bored Tunnel Section, between Stepney Green and Pudding Mill Lane Portal, EB, CH 13+967. 2 ducts O/D 50mm were installed from the wall to 4 foot instead of 63mm as per drawing Cxxx-__-R4-DDD-CRG01_Z-10100. See attached picture.
| 05SY - Systemwide | Cxxx-NCR-000328 | NCR | FTS - W13 incorrect inclination of baseplate |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-02-12 | 2017-01-11 14:10 | -32 | 2016-11-14 15:45 | Track - Track General | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | FTS Lite, Westbound, slab W13 Ch 4834. One baseplate at Chainage 4834 / south side was installed and cast in with the incorrect inclination.
| 05SY - Systemwide | Cxxx-NCR-000329 | NCR | FTS - W1-W10 some reinforcement HOOK bars not installed in Braking blocks areas. |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-02-12 | 2017-02-03 11:12 | -9 | 2016-11-14 15:56 | Track - Track General | 5000 |  | Design | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | FTS Lite, Slabs W1 – W10 Bar marks 01 & 02 as shown on Cxxx-OVE-R4-DDD-CR001_Z-83236 Rev C02 were not in place prior to casting of main slab (Please note: upstands for the Braking blocks yet to be casts).
| 05SY - Systemwide | Cxxx-NCR-000330 | NCR | FTS - Eastbound tunnel Slab 13 foreign object cast in the concrete |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-05-05 | 2017-05-02 13:51 | -3 | 2016-11-16 20:33 | Track - Track General | 3000 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Single piece of timber cast into permanent works underneath the baseplate located on the north side of the third manhole from E12/13 stop end, ring number 2650 at approx. chainage 4605 of Eastbound tunnel Slab 13
| 05SY - Systemwide | Cxxx-NCR-000331 | NCR | HAS side protective pads not removed and concreted in |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-02-15 | 2017-01-24 15:20 | -22 | 2016-11-17 16:02 | Track - Track General | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Thames Tunnel, between Woolwich Station and North Woolwich Portal, EB, HAS section from CH 19+757 to CH 19+879. Small pieces of pads placed on the rubber boot edges of the sleepers in order to protect it from the cable ties, were not removed before concreting this section; consequently they were embedded in the concrete at rings 1560, 1563, 1568, 1573, 1575 & 1584. See attached picture.
| 05SY - Systemwide | Cxxx-NCR-000332 | NCR | Second Stage Cracks at the Open Section between NWP and Connaught East. |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-07-21 | 2017-08-01 12:18 | 11 | 2016-11-17 16:19 | Track - Track General | 10000 |  | Design | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Connaught East to NWP, EB/WB , CH 18712 to 19460 EB After a Crack Survey carried out on the Open Section, between North Woolwich Portal and Connaught East, it has been assessed that we have several cracks bigger than the required width (0.3mm).
| 05SY - Systemwide | Cxxx-NCR-000333 | NCR | Concrete Pour without Authorisation for Concreting signed off, PML WB |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-01-16 | 2017-01-16 12:10 | 0 | 2016-11-17 17:24 | Track - Track General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Track Section between Stepney Green and PML Portal (13285-13491)WB. After the provisional authorisation for concreting signed off between 13285 to 13405 by External QC Inspector at 16:25. Last inspection was carried out by the other External QC Inspector at 19:30 , with a result of 31m more of track ready, just that due to some Trolleys on the track, so once the TMD/VMS Operator was happy with the Track Geometry btw this area, the final authorised area was approved. (CH 13285 to 13436). Track Team, even without the internal quality control carried out on further area, concreted up to CH 13491 (55m more than the authorised).
| 05SY - Systemwide | Cxxx-NCR-000334 | NCR | FTS - W3 shortfall of concrete |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-01-25 | 2017-01-20 09:32 | -5 | 2016-11-18 11:25 | Track - Track General | 5000 |  | Incomplete Works | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Slab W3 FTS Lite WB CHs 4317.922-4326. Due to batching plant breaking down there was a shortfall in the volume of concrete delivered to the work face of slab W3. This led to the area of approx. 8m in length, approximately 250mm in depth not being fully concreted to top level.
| 05SY - Systemwide | Cxxx-NCR-000335 | NCR | FTS – Footprints on some westbound floating track slabs |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-05-31 | 2017-07-20 10:39 | 50 | 2016-11-21 17:31 | Track - Track General | 1000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A number of footprints have been identified in the westbound track floating track slabs W12-W16, mostly on W16 due to personnel stepping over the slabs prior concrete hardening.
| 05SY - Systemwide | Cxxx-NCR-000336 | NCR | CP 11 Threshold Channel not deep enough to fit the door closing mechanism. |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-01-31 | 2017-01-31 11:17 | 0 | 2016-11-22 10:21 | Systems - Cross-passage Doors | 3000 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Previous Construction - Improper As Built | Completed |  | Cross Passage Doors have a threshold closing mechanism along the base of the door frame, from undertaking a site survey at CP11, it was noticed that the threshold channel was not deep enough to fit the door closing mechanism. At the base of the EB Cross Passage 11 opening, we require a narrow channel with a total of 90mm from the finished floor level. This channel is designed to fit the door closing mechanism; it currently ranges from 57-65mm from final floor level which is not deep enough and will not accommodate the door mechanism. : We require the threshold channel to be lowered by approx. 33 – 25mm.
| 05SY - Systemwide | Cxxx-NCR-000337 | NCR | Site-manufactured bends used on site |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-01-23 | 2016-12-01 09:28 | -53 | 2016-11-28 11:35 | Electrical - Cable Management | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During a joint __ & CRL inspection of the CMS at Canary Wharf Station Eastbound it was observed that in 4 locations 4no of trays (trays 4, 5, 6 & 7) were bend on site to suit site conditions (angle of approx. 12 degrees). Whilst one side of the tray had been cut and jointed with an additional support bracket, the other side was bend. Please see picture attached.
| 05SY - Systemwide | Cxxx-NCR-000338 | NCR | TVS baseplate fabricated incorrectly and installed within the works at CWS west shaft level -3. |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-09-20 | 2017-10-10 14:08 | 20 | 2016-11-25 10:35 | Structural Engineering - Steel Member | 500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | A planned Crossrail surveillance was undertaken on 18th November 2016 to look at the TVS steelwork installation at Canary Wharf Station. The sample installation that was chosen was on Level -3 of the west shaft. It was noted during the site survey that one of the installed baseplates only contained 3 holes (see photo) as opposed to the 4 required on the fabrication drawings. It was discussed during the surveillance that some of the installed baseplates were going to need bespoke brackets in order to avoid any clashes with rebar during drilling. Irrespective of whether a bespoke bracket may be installed, this installation highlights a breakdown in the material checking process at both the fabrication yard and on site. ISO 9001 7.4.1 Purchasing Process states “The organization shall ensure that purchased product conforms to specified purchase requirements”. Inspection number 2.5 of the fabrication ITP, Cxxx-__-O4-ITP-CRG03-50027 Rev 3, states a 100% checking frequency of the steelwork during manufacture with an output of a __ inspection record sheet. As this surveillance was based on a sample there may be other steelwork installed that does not meet requirements. The contractor should undertake a review of installed steelwork to ensure compliance. In addition the materials checking process at the supplier’s fabrication yard should be reviewed to identify the root cause.
| 05SY - Systemwide | Cxxx-NCR-000339 | NCR | Pull Out Test - Strain Gauge Defect |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-12-21 | 2016-12-19 14:03 | -2 | 2016-11-24 12:15 | Mechanical - Mechanical Engineering General | 500 |  | Damaged | Reject | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | HAT 28 pull-out tester strain gauge (ref. 19375) Impact-resistant glass damaged - equipment damage
| 05SY - Systemwide | Cxxx-NCR-000340 | NCR | TVS beam/baseplate connection arrangement not installed as per drawing detail. |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-04-14 | 2017-06-05 12:56 | 52 | 2016-11-25 10:36 | Structural Engineering - Bolted Connections | 2000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A planned Crossrail surveillance was undertaken on 18th November 2016 to look at the TVS steelwork installation at Canary Wharf Station. The sample installation that was chosen was on Level -3 of the west shaft. During the site inspection it was noted that the installation drawing detail (Cxxx-__-H-DWG-CR143-50020) showing the connection between the beam and baseplate did not match what was installed. The detail on drawing *50020 showed the arrangement to be washer, half nut followed by nut. However the arrangement that had been installed on site was washer, nut followed by half nut (see photo). During the post exit meeting this issue was discussed with __ who are installing the steelwork. It was stated that the arrangement had been identified and changed prior to installation as it was not possible to achieve the required torque with the half (locking) nut on first. It was stated that this change had been agreed verbally however no evidence was provided to show that this change had been agreed and recorded via the correct change process. ISO 9001 7.3.7 Control of Design and Development Changes states “Design and development changes shall be identified and records maintained. The changes shall be reviewed, verified and validated, as appropriate, and approved before implementation”. The Cxxx Design Management Plant, Cxxx-__-Y-STP-CRG03-50001 Rev 8, states “Every change (including RFI, PMIs, NCR, and FCD not followed by a new version of the document) has to be red-marked by the Construction Manager (and in accordance with the Management of Redlines Procedure CRL1-XRL-Z-GPD-CR001-50010). All observations will be issued by the Construction Manager to the Site Quality Staff that will assess whether it needs to be raised to the design office”. Clause 17.1 shows the process of managing changes. This NCR has been raised as this process had not been followed in this instance.
| 05SY - Systemwide | Cxxx-NCR-000341 | NCR | TVS beem to concrete slab connections over torqued. |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-05-03 | 2017-04-27 08:45 | -6 | 2016-11-25 10:37 | Structural Engineering - Bolted Connections | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | A planned Crossrail surveillance was undertaken on 18th November 2016 to look at the TVS steelwork installation at Canary Wharf Station. The sample installation that was chosen was on Level -3 of the west shaft. During the exit meeting torque records were produced showing the grade 5.8 M20 fixings had been torqued to 200Nm. The installation ITP, Cxxx-__-O4-ITP-CRG03-50030 Rev 3, states a requirement of 150Nm for theses fixings under point 3.9. On checking revision 2 of the installation ITP it was noted that there is no mention of torqueing for the grade 5.8 fixings. The ITP only covered grade 8.8 stainless steel fixings. As such, based on this information, the fixings have been over torqued introducing potential risk to the performance of these fixings and the resin. On clarification with the __ technical department it was found that the maximum allowable torque for HIT-V-F-5.8 M20x260 fixings with the HIT-HY 200-A resin is 150Nm (see data sheet attached). The maximum allowable torque is referenced in the data sheet for the 200-A resin. As such it is unclear as to what the impact of over torqueing may be on the cured resin.
| 05SY - Systemwide | Cxxx-NCR-000342 | NCR | OHLE foundation works started without approved ITP |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-01-27 | 2016-12-15 12:32 | -43 | 2016-11-29 08:25 | Over Head Line Electrification - Catenary Masts | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Pile installation and pad foundation for OHLE started without approved ITP.
| 05SY - Systemwide | Cxxx-NCR-000343 | NCR | FTS - Slab W17 shortfall of concrete poured in main slab |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-01-24 | 2016-12-08 14:07 | -47 | 2016-11-25 17:28 | Track - Track General | 500 |  | Incomplete Works | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | There were a number of blockages within the concrete pumping pipeline which resulted in technical difficulties. Consequently, there was a shortfall in the volume of concrete delivered to westbound slab 17 on the night of 21/11/2016. 4.5 linear meters of slab W17 were not fully cast to the required level during the main slab concrete pour. Consequently, a construction joint will be introduced in the slab.
| 05SY - Systemwide | Cxxx-NCR-000344 | NCR | FTS - 7 day concrete cube strength results for FTS Slab E2 shortfall area |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-02-23 | 2016-12-15 12:35 | -70 | 2016-11-25 17:44 | Track - Track General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Not Defined | Completed |  | Three cubes from FTS E2 were crushed at 7 days with an average compressive strength result of 32.6MPa which is 7% lower than the required strength of 35 MPa at 7 days. Please see enclosed the concrete cube test report.
| 05SY - Systemwide | Cxxx-NCR-000345 | NCR | Failure to update Comm__ents Delivery Tracker (C__) at required frequency |  | Contr | ALC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-01-27 | 2017-01-24 10:24 | -3 | 2016-12-02 14:46 | Consents - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | __ has not been loading evidence onto the Comm__ents Delivery Tracker (C__), in accordance with the Comm__ents Compliance Plan.
| 05SY - Systemwide | Cxxx-NCR-000346 | NCR | Graffiti to Sprayed Concrete Lining of tunnel |  | Contr | ALC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-01-31 | 2017-01-20 09:30 | -11 | 2016-12-02 15:22 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Painted graffiti has been discovered in the Eastbound tunnel, Bond Street, Western end just after the portal to the running tunnel. Photo attached.
| 05SY - Systemwide | Cxxx-NCR-000347 | NCR | Insufficient Galvanise Thickness |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-05-03 | 2017-04-12 09:47 | -21 | 2016-12-06 15:04 | Structural Engineering - Surface Treatment | 6000 |  | Incomplete Works | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | A site visit was carried out by __ on 05/12/16 to carry out an informal inspection on Draft Relief Steelwork progress. During this visit, a galvanise thickness test was carried out using an __ Galvanise Thickness Tester. The __ TVS Specification states that all steelwork is to be galvanised to 115 microns unless stated otherwise. As per CI-00028, the wall brackets for the Draft Relief Damper Shaft are to be galvanised to 140 microns. Following the site visit mentioned above, all brackets within the DRD Shafts do not meet the required thickness of 140 microns to meet the required C5 environment category.
| 05SY - Systemwide | Cxxx-NCR-000348 | NCR | TVS steelwork designed to 30 year life where Cxxx drawing states 40 year life. |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-11-30 | 2018-01-08 14:36 | 39 | 2016-12-08 09:29 | Structural Engineering - Structural Engineering - General | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | A planned Crossrail surveillance was undertaken on 18th November 2016 to look at the TVS steelwork installation at Canary Wharf Station. The sample installation that was chosen was on Level -3 of the west shaft. During the exit and post exit meetings confirmation of the steelwork design life was requested. On multiple occasions the surveillance was directed to the Cxxx TVS Specification, Cxxx-MMD-O8-RSP-CR001-00003, and the Cxxx TVS Specification, Cxxx-__-H-RSP-CRG03-50006. In particular the clauses on design life which states the following “The design life of plant and equipment shall be 30 years, unless stated otherwise”. Following this it was asked whether the steelwork formed part of this 30 year design life; however no evidence was provided to confirm this. It was noted however that the Tunnel Ventilation Steelwork, General Notes & Abbreviations, Cxxx-__-M-DDJ-CR001_Z-10000, which was provided during the surveillance, states under point G5; “The design life of the structural supporting steelwork is 40 years. This has been specified to match the maximum specified design life of the equipment”. The Cxxx TVS Spec was accepted August ‘14 where as the drawing was IFC (C01) in June ‘16. It was stated by __, the __ steelwork sub-contractor, that they had been instructed by __ to design to a 30 year design life, which is a non-conformance based on the 40 year design life stated in the general notes drawing. No evidence was provided with regards to agreement of the 30 year design life.
| 05SY - Systemwide | Cxxx-NCR-000349 | NCR | Incorrect Steelwork Drawing Detail |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-03-30 | 2017-03-27 13:18 | -3 | 2016-12-08 09:47 | Structural Engineering - Bolted Connections | 2500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | __ have now completed the installation of the Tunnel Side Attenuator steelwork, East and West Shaft, Canary Wharf Station. Upon inspection by __, it was realised that the ‘half nut / full nut’ arrangement which was stated on the drawing, did not match the on-site installation (design stated that the half nut was to be fixed first, with the full nut working as the lock nut / second fixing). Please note that the drawing which this inspection related to is Cxxx-__-H-DWG-CR143-50020, but this arrangement also occurs on all TTD, DRD, ASA and FID steelwork drawings. Upon investigation with the __ Site Manager, it was stated that the drawing showed an arrangement which simply wouldn’t be feasible and it was agreed verbally between the __ Site Manager and Site Supervisor that the installation would be carried out as; ‘Washer, full nut, with the half nut acting as the lock nut’.
| 05SY - Systemwide | Cxxx-NCR-000350 | NCR | Damage to Attenuators |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-03-30 | 2017-03-31 10:44 | 1 | 2016-12-08 17:06 | Materials - General | 10000 |  | Manufacturing Defect | Rework | 2 (6-60k) | Complete | Material/Preservation Problems - Not Defined | Completed |  | Following the inspection on 15 Attenuators which were installed at WHI-E carried out by __ engineer on 28/10/16, it has become apparent that 9 of Attenuators required repair at the factory due to bulging, poor joining, poor galvanising on the welded brackets and uneven measurements on the top of the splitters. As a result all 9 of the Attenuators were transported back to the factory to undertake the repair. Asset Number Numbers as follows: D061-TVS-00034-004 D061-TVS-00034-006 D061-TVS-00034-007 D061-TVS-00034-008 D061-TVS-00034-009 D061-TVS-00034-010 D061-TVS-00034-016 D061-TVS-00034-018 D061-TVS-00034-019
| 05SY - Systemwide | Cxxx-NCR-000351 | NCR | Steelwork to Concrete Clash |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-05-03 | 2017-08-07 11:00 | 96 | 2016-12-15 16:35 | Materials - General | 1000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The steelwork within the Draft Relief Damper shaft, East and West Shaft, Canary Wharf Station has now commenced installation and is near completiton. During the installation of this steelwork, it was discovered that 2nr steelwork beams and 1 wall bracket could not be installed due to a clash with the RC slab. The clash has occurred within the West Shaft WB DRD (B713) and the East Shaft WB DRD (B712).
| 05SY - Systemwide | Cxxx-NCR-000352 | NCR | FTS Lite - 3 number Inspection chamber durbar frames |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-03-15 | 2017-02-21 16:40 | -22 | 2016-12-15 19:58 | Track - Track General | 1000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | 3 No frames as shown on 24999-7 have been modified by original manufacturer Atticrose to be similar to frames shown on 24999-8. This is a non-authorised change to the design. The modifications were carried in Atticrose’s facilities where all original FTS frames were previously manufactured. The works were undertaken in accordance with the code 1 approved ITP – see ITP “Cxxx-__-O4-ITP-CRG03-50101 v2.0” for reference. The hot dip galvanising was completed as per LWI 54. The frames were modification with minor deviations as noted in: 1. Dimension of shorter side is now 760mm rather than 750mm, that is the opening in the manhole is 10mm bigger in total, additional 5mm to each side. 2. Profile of the RSA on the shorter side is 75mm by 50mm rather than 100mm by 50mm. 3. Smaller size RSA as noted in point 2 results in the stud level being 15mm higher which leads to studs on short side being set at 45mm (original level as per 24999) rather than 60mm. 4. Due to modification of longer side from 1300mm to 1100mm, the dimension to the stud is now 74mm from the edges rather than 100mm. We note that is the stud is as per the original weld with no modifications and the weld was inspected in the original manufacturing process.
| 05SY - Systemwide | Cxxx-NCR-000353 | NCR | Mode of transport non-compliant - Attenuators |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-02-23 | 2017-02-24 14:31 | 1 | 2016-12-16 16:48 | Mechanical - Mechanical Engineering General | 5000 |  | Supervision/Management | Reject | 3 (3-6k) | Complete | Material/Preservation Problems - Improper handling of material | Completed |  | The supplier __ presented the Attenuators bridging 2 lifting pallets, which is an incorrect method of loading. Any attempt to lift the attenuators in this position would risk damage to the items and hence the delivery was rejected and returned to suuplier by Clipfind.
| 05SY - Systemwide | Cxxx-NCR-000354 | NCR | FTS – Braking Block rebar cut in W1 |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-03-22 | 2017-01-23 07:52 | -58 | 2016-12-19 20:06 | Track - Track General | 1000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | BM 32 c in W1’s braking block on the north side at chainage 4246.32 has been cut off as shown in the attached picture. The bar seemed to clash with the braking block stud position and this seems to be the reason why it was cut. Cutting the bar has not been authorised by the designer.
| 05SY - Systemwide | Cxxx-NCR-000355 | NCR | FTS - Slab E21 shortfall of concrete poured in main slab |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-03-28 | 2017-02-06 14:57 | -50 | 2016-12-21 10:02 | Train - General | 25000 |  | Supervision/Management | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the shift on the night of 19/12/2016, a number of blockages within the concrete pumping pipeline occurred during placement of the concrete, consequently there was a shortfall in the volume of concrete delivered to eastbound slab E21. Approx. 4 linear meters of slab E21 were not fully cast to the required level during the main slab concrete pour. As a result of the concrete shortfall a construction joint will be introduced into the slab. In addition, approximately 250m of pipeline had to be replaced as a result of the hardened concrete which could not be cleared during the pour.
| 05SY - Systemwide | Cxxx-NCR-000356 | NCR | FTS - Concrete delivered to slab E20 exceeded the 4 hour workability retention period |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-03-31 | 2017-04-05 09:35 | 5 | 2016-12-21 12:16 | Track - Track General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Due to a blockage in the pipe of the pour of slab E20, 12m3 of concrete was poured which had exceeded the 4 hour workability window. The batch time of the first batch of 8m3 of concrete was 18:02 and discharge into the pipe took place at 20:05. The batch time of the second batch of 8m3 of concrete was 18:15 and discharge into the pipe took place at 20:35. The time at which the first concrete was received at the end of the pipeline was 23:45. Therefore the first batch of concrete was at least 5 hours and 43 minutes old, and the second batch at least 5 hours 30 minutes old. 4m3 of the second batch was not poured into the slab.
| 05SY - Systemwide | Cxxx-NCR-000358 | NCR | FTS - Damaged scre__ikes dowels |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-07-12 | 2017-08-15 13:02 | 34 | 2016-12-21 11:43 | Track - Track General | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The top part of some scre__ikes dowels in W2, W14 and W16 were damaged when lifting the HDPE pads for inspection of the concrete surface, see photos attached.
| 05SY - Systemwide | Cxxx-NCR-000359 | NCR | Support Steelwork Anchors |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-03-30 | 2017-03-31 14:27 | 1 | 2016-12-21 14:46 | Structural Engineering - Steel Member | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | The steel to concrete fixings installed for the ASA support steelwork do not match the fixings specified in the Code 1 approved design drawing. The drawing specifies 14mm Diameter __ HUS3-H Screw Anchors 75mm Length at 48mm, 65mm and 65mm for the connections of the column baseplates to floor, column head plates to soffit and cross-members to wall respectively. It was verbally agreed with the __ design team that the fixings would be changed to those listed in the technical requirements below (and matching those used for the remaining steelwork and lifting beam installations systemwide) in order to meet the 40 year life requirements for all equipment materials and fixings. The fixings have approved MCRs.
| 05SY - Systemwide | Cxxx-NCR-000360 | NCR | Support Steelwork Locator Incorrect Drilled Holes |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-03-08 | 2017-03-07 16:13 | -1 | 2016-12-21 16:20 | Materials - General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Following a manufacture error the 2 no. highlighted locator holes were drilled in the incorrect position on the steelwork.
| 05SY - Systemwide | Cxxx-NCR-000361 | NCR | No evidence of equipment calibration provided for Hydra-Capsule FTS jacking operations |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-06-05 | 2017-05-22 13:19 | -14 | 2017-01-03 12:27 | Track - Track General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | During surveillance of the FTS jacking operations (ref: Cxxx-SUR-0057) it was observed that there was no evidence of calibration for the equipment being used to control the FTS jacking operations. Opportunity has been provided to the contractor to produce relevant certification but none has been received to date.
| 05SY - Systemwide | Cxxx-NCR-000362 | NCR | No evidence of competence or qualification records provided for Hydra-Capsule FTS jacking engineer |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-04-03 | 2017-03-27 13:21 | -7 | 2017-01-03 12:46 | Track - Track General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | During surveillance of the FTS jacking operations (ref: Cxxx-SUR-0057) it was observed that there was no evidence of competence or qualification records provided for Hydra-Capsule FTS jacking engineer. Opportunity has been provided to the contractor to produce relevant certification but none has been received to date.
| 05SY - Systemwide | Cxxx-NCR-000363 | NCR | No evidence of equipment calibration provided for digital calliper used on measuring thickness of FTS bearings |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-04-03 | 2017-03-22 08:57 | -12 | 2017-01-03 13:27 | Track - Track General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | During surveillance of the FTS jacking operations (ref: Cxxx-__-O4-RGN-CRG03-50196) it was observed that there was no evidence of calibration for digital calliper used on measuring thickness of FTS bearings. Opportunity has been provided to __ Quality site team to produce relevant certification but none has been received to date.
| 05SY - Systemwide | Cxxx-NCR-000364 | NCR | FTS - 7 day concrete cube strength results for FTS Slab E21 |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-04-04 | 2017-01-20 10:33 | -74 | 2017-01-04 10:14 | Track - Track General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Three concrete cubes from E21 were crushed at 7 days with an average compressive strength result of 32.7MPa which is 6.6% lower than the required minimum strength of 35 MPa
| 05SY - Systemwide | Cxxx-NCR-000365 | NCR | Defective Koncecranes electric chain hoist's control transformer PCB |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-03-30 | 2017-03-31 14:19 | 1 | 2017-01-05 11:46 | Electrical - Electrical Engineering General | 500 |  | Damaged | Reject | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On commissioning of the 09007 runway beam, the __s site engineers established that the electric chain hoist's control transformer PCB (printed circuit board) was defective. On investigation they established that it had broken away from its mountings. The control transformer PCB will have to be replaced with new one. This defect can only be attributed to damage in transport as the control transformer printed circuit board in enclosed and not accessible without the use of tools.
| 05SY - Systemwide | Cxxx-NCR-000366 | NCR | Infill Drainage Level higher at Open Section-Connaught East |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-06-09 | 2017-02-20 12:09 | -109 | 2017-01-10 19:15 | Track - Track General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Distance from bottom of the infill channel to track SOP is 490mm (20 mm too high).From 19100 to 19263 (aprox) EB Chainages
| 05SY - Systemwide | Cxxx-NCR-000367 | NCR | Installation of Pumped Tunnel Drainage and Fire Main to Non-IFC Drawings |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-04-22 | 2017-05-22 15:33 | 30 | 2017-01-12 15:02 | Mechanical - Public Health Engineering | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | Installation of the Pumped Tunnel Drainage and Fire Main has commenced within the Thames Tunnel at risk in the absence of IFC drawings. Works are being installed to P0X revision drawings. Relevant drawings for the Thames Tunnel and the South East Spur are as follows: Tunnel Fire Main • Sector 16 Cxxx-__-M-DDA-CR001_Z-11701 to Cxxx-__-M-DDA-CR001_Z-11707 – Tunnel Drawings • Sector 17 Cxxx-__-M-DDA-CR001_Z-11601 to Cxxx-__-M-DDA-CR001_Z-11607 – Tunnel Drawings • General Details Cxxx-__-M-DDD-CR001_Z-17031 to Cxxx-__-M-DDD-CR001_Z-17036 – Standard Layout Drawings and Details Note – any changes to the Hydrant Bracket and Anchor Bracket will be covered by an FDC Tunnel Pumped Drainage • CP11 to CWS-W Cxxx-__-P-DDA-CR001_Z-13381 to Cxxx-__-P-DDA-CR001_Z-13383 – Tunnel Drawings Cxxx-__-P-DDL-CR001_Z-20012 – Cross Passage Interface Drawing • CP13 to CWS-E Cxxx-__-P-DDA-CR001_Z-13391 to Cxxx-__-P-DDA-CR001_Z-13392 – Tunnel Drawings Cxxx-__-P-DDL-CR001_Z-20009 – Cross Passage Interface Drawing • CP17 to WOO-W Cxxx-__-P-DDA-CR001_Z-13401 to Cxxx-__-P-DDA-CR001_Z-13402 – Tunnel Drawings Cxxx-__-P-DDL-CR001_Z-20006 – Cross Passage Interface Drawing • CP18 to WOO-E Cxxx-__-P-DDA-CR001_Z-13411 to Cxxx-__-P-DDA-CR001_Z-13412 – Tunnel Drawings Cxxx-__-P-DDL-CR001_Z-20003 – Cross Passage Interface Drawing • General Details Cxxx-__-P-DDE-CR001_Z-13050 & Cxxx-__-P-DDD-CR001_Z-13113 – Anchor Bracket Design (note both drawings are the same) Note – any changes to the Hydrant Bracket and Anchor Bracket will be covered by an FDC.
| 05SY - Systemwide | Cxxx-NCR-000368 | NCR | Concrete Pour without IFC Drawings |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-04-20 | 2017-04-10 08:21 | -10 | 2017-01-10 19:16 | Track - Track General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Track team has poured Whitechapel Station plus C8 Turnout without IFC Drawings: • Cxxx-__-R4-DDA-D061_Z-10001 WhitechapelStation-TrackGeneralArrangementSheet1of2 • Cxxx-__-R4-DDA-D061_Z-10002 WhitechapelStation-TrackGeneralArrangementSheet2of2 • Cxxx-__-D-DDA-D061_Z-10007 WhitechapelStation-DrainageConceptandDetails • Cxxx-__-D-DDB-D061_Z-10008 WhitechapelStation-DrainageCatchpitDetails • Cxxx-__-R4-DDB-D061_Z-10003 WhitechapelStation-CrossSectionsS1&S2ChainageEB10320 • Cxxx-__-R4-DDB-D061_Z-10004 WhitechapelStationCrossSectionsS3&S4ChainageEB10466 • Cxxx-__-R4-DDL-CR092_Z-10500 WhitechapelCrossover-PointsC7&C8TrackGeneral Arrangement • Cxxx-__-R4-DDL-CR092_Z-10501 WhitechapelCrossover-PointsC7&C8DrainageGeneral Arrangement
| 05SY - Systemwide | Cxxx-NCR-000369 | NCR | Tunnel Holes Spacing - Drilling Rig |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-06-06 | 2018-06-04 09:55 | -2 | 2017-01-10 15:41 | Mechanical - Mechanical Engineering General | 50000 |  | Incorrect Installation | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | A full spacing survey has been carried out during Walkway bracket installation in the North East Spur Eastbound (Pudding Mill Lane to Stepney Green Junction). It appeared that the 3200mm was not respected 100%, gaps of up to 3350mm were recorded. However the current design and procurement schedule of planks and handrails are not flexible enough to allow larger gaps in between the walkway brackets. The concern was also raised by __ - walkway subcontractor that there is a lack of quality inspection of the drilling rig holes. __ is only carrying out spot checks of the holes spacing.
| 05SY - Systemwide | Cxxx-NCR-000370 | NCR | Wrong Installation Longitudinal Drainage Pipe at Paddington Station EB |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-02-02 | 2018-01-31 08:14 | -2 | 2017-01-10 19:17 | Track - Track General | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | After an inspection of catchpits finishing, we have found that the water is not running through the internal drainage pipe from catchpit ch 1346 to catchpit ch 1311 as per mentioned documents. Level of standing water at catchpit ch 1346 is above of the bottom level of the lateral drainage channel. Photographs attached.
| 05SY - Systemwide | Cxxx-NCR-000371 | NCR | C7-C8 crossover alignment out of tolerance within the turnout C8. |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-06-23 | 2017-08-17 09:57 | 55 | 2017-01-10 19:18 | Track - Turnouts | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | The through alignment/mainline of C8 is in conformance however the deviated alignment (C7-C8 Crossover) slowly goes out of absolute tolerance in horizontal position only throughout the turnout and reaches 5mm outside of the horizontal tolerance by the end of C8 deviated line. It is still a smooth movement however the absolute gradually does go up to +15mm horizontal.
| 05SY - Systemwide | Cxxx-NCR-000372 | NCR | __ - Method Statement not available |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-05-03 | 2017-07-11 07:22 | 69 | 2017-01-11 11:14 | Track - Track General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Surveillance completed on 10/01/2017 (Ref: Cxxx-__-O4-RGN-CRG03-50197 v1.0) concluded that __ did not have an in-date and approved method statement for the works
| 05SY - Systemwide | Cxxx-NCR-000373 | NCR | __’s sampling plan and procedures not available |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-05-03 | 2017-04-27 14:32 | -6 | 2017-01-11 11:38 | Track - Track General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | During surveillance of concrete testing at Plumstead lab (ref: Cxxx-__-O4-RGN-CRG03-50197 v1.0) it was observed that __’s sampling plan and procedures were not available
| 05SY - Systemwide | Cxxx-NCR-000374 | NCR | FTS - Honeycombing on the underside of the jacked slab W11 |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-05-11 | 2017-04-18 08:55 | -23 | 2017-01-11 17:54 | Track - Track General | 5000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Honeycoming has been found on the surface of the underside of the jacked slab W11 on the left hand side of manhole 1 at CH 4714 facing BOS. Please see the attached pictures.
| 05SY - Systemwide | Cxxx-NCR-000375 | NCR | Westbound Draft Relief Damper Steelwork |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-05-03 | 2017-05-02 13:58 | -1 | 2017-01-13 14:25 | Structural Engineering - Structural Engineering - General | 1000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | 4No# brackets for the westbound draft relief steelwork were installed in the incorrect position as per the details on Cxxx-__-H-DWG-D061-50025 Rev E. The brackets should have been installed in accordance with the latest drawing Cxxx-__-H-DWG-D061-50025 Rev F instead.
| 05SY - Systemwide | Cxxx-NCR-000376 | NCR | Sleeper boot loose on concreted track. |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-06-12 | 2017-06-16 07:11 | 4 | 2017-01-13 17:24 | Track - Track General | 2500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Location: Bored Tunnel Section, between Canary Wharf Station and Stepney Green Cavern, WB, CH 11+724. LH Side Sleeper boot. Sleeper rubber boot has been found detached from the concrete sleeper block after post-pour quality inspection. (Approx: 9mm from the required position) .See attached picture.
| 05SY - Systemwide | Cxxx-NCR-000377 | NCR | CMS Brackets in Limmo Shaft EastBound |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-06-14 | 2017-06-16 07:13 | 2 | 2017-01-17 11:51 | Electrical - Cable Management | 2500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 1- It is observed that the wrong type of CMS bracket has been installed in Limmo Shaft Eastbound. Double channel uprights (Bracket Type 3) are specified on drawing Cxxx-__-E-DDC-CR144_SH011_Z-30003 above the no-drill zones, but single channel uprights (Bracket Type 1) have been installed. See Cxxx-__-E-DDD-CR144_SH011_Z-31000 for further bracket details. 2- The cantilever arms supporting the CMS level transitions are fixed using only 1 of the 2 bolts, due to the orientation of the tray. These additional single bolt cantilever arms have been installed for guidance only, not for structural compliance. However, it is still mandatory to have 2 bolt cantilever brackets at maximum span of 3.185m, therefore additional (2 bolt) structural support is required at the transition sections.
| 05SY - Systemwide | Cxxx-NCR-000378 | NCR | E21 Reinforcement Damaged during Rework of Concrete Shortfall |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-04-17 | 2017-02-07 10:29 | -69 | 2017-01-17 13:14 | Track - Track General | 20000 |  | Damaged | Rework | 2 (6-60k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | During the shift on the night of 19/12/2016, a number of blockages within the concrete pumping pipeline occurred during placement of the concrete, consequently there was a shortfall in the volume of concrete delivered to eastbound slab E21. The proposed corrective action in this instance was to remove any bad concrete - not well placed/compacted. Drill and fix u-bars similar to Cxxx-NCR-000277 engineering response - the distribution and installation details of the u-bars to be confirmed by the Designer. During the course of the rework (in preparing the construction joint) the remaining slab reinforcement was damaged by the hand held breakers and as a result approximately 150No. nicks and dents to the steel bars have been formed, which may compromise the structural characteristics of the steel bars and therefore the structural integrity of the slab.
| 05SY - Systemwide | Cxxx-NCR-000379 | NCR | FTS – Concrete mix used to concrete lateral restraints and braking blocks not in accordance with ITP |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-04-17 | 2017-02-09 14:37 | -67 | 2017-01-17 13:13 | Track - Track General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | The mix used to concrete 4 No lateral restraints and 4 No braking blocks in the westbound tunnel is not in accordance with the ITP __-R4-ITP-CRG03-50005 rev 5.0. Please refer to the Component Product Specification Cxxx-__-R4-RSP-CRG03-50075 rev 1.0 for details of the mix used. Concrete delivery ticket: 73309921 Location: 4 braking blocks at W1, chainages 4241.12 and 4246.42 respectively. Lateral restraints: W1: L1-06-084 W8: L1-06-340 W10: L1-06-259, L1-06-235, L1-06-043 and L1-06-384
| 05SY - Systemwide | Cxxx-NCR-000380 | NCR | Water ingress on Track Slab at Limmo Shaft |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-12-19 | 2017-12-06 15:57 | -13 | 2017-01-18 17:09 | Track - Track General | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | External Phenomenon - Other | Completed |  | Location: WB track, Points 3&4 chainages 15690 , 15719 EB track, Points 1&2 chainages 15654 , 15620 On 09th of December 2016, Track External Quality Team, made an inspection at the areas mentioned above, as result has found water leak coming to the Track Slab in 4 different points. Four cracks have appeared on the second stage concrete, at the intersection between tunnels and Shaft , where the water is coming through.
| 05SY - Systemwide | Cxxx-NCR-000381 | NCR | Commencing works without an accepted drawing. |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-03-05 | 2017-02-09 14:40 | -24 | 2017-01-19 14:44 | Materials - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | The installation of the Fan support Steelwork has now commenced at Canary Wharf Station, Level -2, TVS. In this instance, the steelwork has been manufactured, delivered to site and installation has started without the steelwork being coded by Crossrail.
| 05SY - Systemwide | Cxxx-NCR-000382 | NCR | Tunnel Holes Spacing - Drilling rig |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-07-24 | 2018-07-20 12:14 | -4 | 2018-03-07 15:59 | Electrical - Cable Management | 50000 |  | Workmanship | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A full spacing survey has been carried out during Walkway bracket installation in the North East Spur Eastbound, following reports that the gap between the brackets is greater than 3.2m. The survey revealed that in isolated locations we have a gap of up to 3350mm were recorded. The concern was also raised by __ - walkway subcontractor that there is a lack of quality inspection of the drilling rig holes. __ is only to carry out spot checks of the holes spacing.
| 05SY - Systemwide | Cxxx-NCR-000383 | NCR | FTS - Rebar cut in Braking Block upstands on FTS W2 & W3 |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-04-20 | 2017-02-07 11:23 | -72 | 2017-01-20 18:23 | Track - Track General | 1000 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | 1 no. bar mark 27c has been cut in both braking blocks on the north side of slab (2 no bars in total) W3 as shown in the photo attached to accommodate the stud of the braking block assembly. However, the bars were cut prior to informing the designers. Bar mark 13 of __ located at ring 2492 on south side has been cut more than the accepted 32mm (as per engineering response to site observation 110) Bar mark 04c and 04a of __ located at ring 2489 on north side side have been cut The cutting of these bars has not been authorised by the designer. Please see below the details of the exact locations. FTS Lite Westbound slab 3 - 2 no braking block upstands on the north side, ring numbers 2518 and 2521. The cut rebar is located on the east side of the braking blocks. FTS Lite Westbound slab 2 - 1 no braking block upstand on the north side, ring number 2489. 1 no braking block upstand on the south side, ring number 2492
| 05SY - Systemwide | Cxxx-NCR-000384 | NCR | Damaged Attenuator |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-05-08 | 2017-05-08 15:47 | 0 | 2017-01-24 17:22 | Mechanical - Mechanical Engineering General | 5000 |  | Damaged | Rework | 3 (3-6k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Following the completion of the Tunnel Side Attenuators at Canary Wharf Station TVS, Level -4, West Shaft, it has been highlighted that Attenuator CW/W/TSA/2271/ATT04 has been damaged either during or prior to installation.
| 05SY - Systemwide | Cxxx-NCR-000385 | NCR | Installation of CMS brackets commenced without a passed Design Gate (Air Shaft Mini Gate) |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-03-21 | 2017-03-06 11:22 | -15 | 2017-01-24 20:42 | Electrical - Cable Management | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | It has been observed that the installation of CMS brackets commenced in the Connaught Tunnel without a passed Design Gate (Air Shaft Mini Gate) and as such without IFC drawings.
| 05SY - Systemwide | Cxxx-NCR-000386 | NCR | Anchor Fixings used in Connaught Tunnel without formal authorisation from CRL |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-05-12 | 2017-04-27 14:35 | -15 | 2017-01-24 20:55 | Electrical - Cable Management | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | During a recent CRL inspection of the CMS in Connaught Tunnel, it has come to light that chemical anchors were used in tension to fix the CMS brackets to the ceiling of the tunnel.
| 05SY - Systemwide | Cxxx-NCR-000389 | NCR | Suspected Rust on TSA Steelwork |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-05-24 | 2017-07-06 10:15 | 43 | 2017-01-25 16:02 | Materials - General | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | External Phenomenon - Not Defined | Completed |  | The Tunnel Side Attenuator Steelwork is completed at Canary Wharf Station; however, discolouration has been identified on beam TSA-B/2372 (B301). It has not yet been confirmed whether the defect identified is a result of oxidization as further inspection must be carried out by the Steelwork contractor.
| 05SY - Systemwide | Cxxx-NCR-000390 | NCR | ESS NCR001 - Lifting Beam LB20002 clash |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-04-05 | 2017-04-05 15:37 | 0 | 2017-01-25 17:44 | Structural Engineering - Bolted Connections | 5000 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | Upon completion of installation of the Gantry Crane LB20002, it was noted the bridge (or runway) beam clash with the primary structure bolts of a bracket.
| 05SY - Systemwide | Cxxx-NCR-000391 | NCR | Hold Point Not Carried Out |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-03-30 | 2017-03-31 08:16 | 1 | 2017-01-25 17:32 | Structural Engineering - Testing | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | During the dimensional check of the Draft Relief Damper Steelwork as part of __ ITP witness point, it was observed that Crossrail were not invited to witness the hold point for __ Steelwork ITP to carry out the same activity.
| 05SY - Systemwide | Cxxx-NCR-000392 | NCR | Steel column misalignment |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-04-03 | 2017-03-31 14:24 | -3 | 2017-01-26 10:58 | Materials - General | 5000 |  | Incomplete Works | Rework | 3 (3-6k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | The TID outer columns, which do not have the 8mm front plate welded to them are positioned and been installed out of line with the central columns. Therefore the current erection situation means the 5 columns do not have a front flush face as required to allow the damper installation.
| 05SY - Systemwide | Cxxx-NCR-000393 | NCR | FTS - Absence of consistency test performed on concrete for a number of lateral restraints and braking block upstands |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-04-27 | 2017-02-07 11:29 | -79 | 2017-01-27 13:49 | Track - Track General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | The flow test has not been carried out on the concrete used in the first four concrete pours of braking blocks and lateral restraints. Please see below the concrete ticket references of affected concrete for this NCR. - 73309921 (Pour date 12/01/2017) - 73249395 (Pour date 21/12/2016) - 73202793 (Pour date 14/12/2016) - 73174886 (Pour date 09/12/2016) Please see the attached document for traceability of the assemblies.
| 05SY - Systemwide | Cxxx-NCR-000394 | NCR | W11 Braking Block assembly cannot be installed as per design |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-04-27 | 2017-03-22 09:01 | -36 | 2017-01-27 18:58 | Track - Track General | 2000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | The stud on the kerb side of one of W11's braking block assembly (W11 North ring 2767) clashes with the reinforcement of the kerb and cannot be installed.
| 05SY - Systemwide | Cxxx-NCR-000395 | NCR | FTS Station W12 non-compliant cover to reinforcement. |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-05-31 | 2017-06-28 15:58 | 28 | 2017-01-27 19:12 | Track - Track General | 1000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Cover to U-bars BM06 (in pairs) in W12's braking block pocket in the north east side has 15mm cover.
| 05SY - Systemwide | Cxxx-NCR-000396 | NCR | Bracket for LB14002 (Beam) manufactured Out of Tolerance |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-03-30 | 2017-04-05 09:38 | 6 | 2017-01-30 11:31 | Materials - General | 3000 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The position B brackets for LB14002 (Beam) have been designed and manufactured 65mm short of what they should be. Drawing Cxxx-__-Y-DWG-C101-50003 page 15, the bracket is shown with a height of 600mm. However, this should be 665mm as per drawing page 5.
| 05SY - Systemwide | Cxxx-NCR-000397 | NCR | Draught Relief Damper Anchor Material |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-03-01 | 2017-02-15 15:25 | -14 | 2017-01-30 16:06 | Structural Engineering - Steel Member | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Per Crossrail’s Works Information the anchors/fixings to fix TROX dampers to the slab or supporting steelwork should be of hot dipped galvanised steel. However, a __ HST3-R mechanical stainless steel anchor was used during installation by __. These anchors were procured/instructed by __ use as is instead of the TROX supplied anchors.
| 05SY - Systemwide | Cxxx-NCR-000400 | NCR | CP18 EB Door Panel Damage |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-05-09 | 2017-05-09 15:35 | 0 | 2017-02-08 16:23 | Systems - Cross-passage Doors | 5000 |  | Damaged | Repair | 3 (3-6k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Cross Passage 18 Eastbound Door was signed off during an IRN inspection (with __, CRL and __s Industries). At the time no door damage was present. During a recent site inspection, it has been noted the door skin panel has been caught by an object and has slightly bent the door skin panel as per the attached photos. The door damage is at the bottom left corner, next to the hinge looking from the trace/tunnel.
| 05SY - Systemwide | Cxxx-NCR-000401 | NCR | Wrong size base plate slots & Washers |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-03-23 | 2017-03-23 14:57 | 0 | 2017-02-01 16:32 | Structural Engineering - Steel Member | 500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | During the Torque Test at level 5 it was noted some of the slots were drilled on the base plates for the westbound draught relief damper steelwork were the wrong size than it’s referred in the drawing Cxxx-__-H-DWG-D061-50025. The drawing states all the slots on the base plates have to be 22mm. However, some of the slots are up to 25mm. Also noticed was the washers used for the anchors through the slots appeared too small. When the torqueing force is applied on the nut, this caused the washers to bow inside the slot.
| 05SY - Systemwide | Cxxx-NCR-000402 | NCR | PTD & Fire Main installation without approved MCR |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-12-06 | 2017-11-28 14:40 | -8 | 2017-02-01 16:21 | Materials - Approval | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | Installation of Pumped Tunnel Drainage and Fire Mains has commenced within the Thames Tunnel without approved MCRs for Couplings, Section Valves and Hydrants.
| 05SY - Systemwide | Cxxx-NCR-000403 | NCR | Acceptance of Non-conforming Material / Delivery |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-03-29 | 2017-03-29 10:04 | 0 | 2017-02-01 15:41 | Mechanical - Mechanical Engineering General | 500 |  | System Defect | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | __s representatives accepted the delivery of material relating to the installation of Fixed Lifting Beams (LB08009-16)that deviated from the Crossrail accepted material list contrary to section 6.6.1 of the ITP (Cxxx-__-O4-ITP-D061-50003). At the point where the material was checked and found to differ, all work should have ceased.
| 05SY - Systemwide | Cxxx-NCR-000404 | NCR | Installation not matching the accepted drawing |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-10-25 | 2017-10-09 09:46 | -16 | 2017-02-01 17:32 | Mechanical - Mechanical Engineering General | 3000 |  | Design | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | __s representatives have installed Fixed Lifting Beams LB08009-16 In a manner that does not correspond to the accepted Crossrail drawings. This is due to a manufacturing change by __s design team without first gaining acceptance from Crossrail.
| 05SY - Systemwide | Cxxx-NCR-000405 | NCR | Torque Test Failure LB08009-16 |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-07-27 | 2017-06-23 09:37 | -34 | 2017-02-01 16:27 | Mechanical - Mechanical Engineering General | 5000 |  | Design | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | During a planned ITP hold point a test / inspection of the fixings securing the fixed lifting beams LB08009-16 faied to maintain their integrity. upon installation of the lifting beams to the fixings, it was found that the round washers that were installed did not offer enough surface area coverage that would have been acceptable. The drilled holes in the beam plates were of a similar size to the round washers. The __ installers had introduced a square washer that was installed between the nylon washer and the round washer to afford greater surface area, however this caused the nylon washer which sits proud of the fixing plate by 3mm to be crushed against the corner of the drilled holes and causing it to fail which in turn released the torque in the fixing.
| 05SY - Systemwide | Cxxx-NCR-000406 | NCR | Cantilever crane LB09007 not matching drawing |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-04-27 | 2017-04-27 15:26 | 0 | 2017-02-01 17:33 | Mechanical - Mechanical Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Cantilever crane LB09007 has been installed in a manor that does not match the Crossrail drawing Cxxx-__-M-DWG-N105-50005. In the drawing it shows that the electric motor is located nearest to the wall and the manual trolley is located nearest to the opening. It has been noted that during commissioning the motor and the trolley had been installed in reverse (the motor nearest to the opening). When asked why the motors position has been changed the response was it would give better traction when the crane is loaded.
| 05SY - Systemwide | Cxxx-NCR-000407 | NCR | PLU Portal W/B OHLE Support drilling at wrong locations |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-06-23 | 2017-06-29 09:09 | 6 | 2017-02-22 10:32 | Over Head Line Electrification - Supports | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | 1. OHLE Support drilling at PLU Portal W/B chainage from Ch.22897 to Ch.22650 was drilled at wrong location 2. Survey team marked chainage on rails and added a mark on concrete slab (nail) to be used by OHLE team to report the centre of the support on portal soffit. Since at various locations, the marks (nails) could not be installed exactly under the centre point of the support (on portal soffit), Survey team would produce a document (offset table) to give for each marks (nails) an offset value, i.e. towards the track or away from the track. However, the document was sent by email, has been missed by OHLE team and OHLE team has drilled according to marks (nails) on site, without taking into account the necessary offset values. As a result, support drillings have been done at the good chainage but not at the good distance from track centre.
| 05SY - Systemwide | Cxxx-NCR-000408 | NCR | Non-compliant materials installed on LB08004 |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-04-27 | 2017-04-11 10:26 | -16 | 2017-02-01 17:33 | Mechanical - Mechanical Engineering General | 1000 |  | Manufacturing Defect | Reject | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Upon inspection of the steelworks and fittings it was found that materials used for the construction of the gantry beam trolleys was not in conformance of the required specifications. Fixings used for the manual gantry trolley are showing signs of corrosion both on the bolt head and the threaded end section, this is contrary to the Painting and anti-corrosion procedure Cxxx-__-O4-GPD-D061-50001
| 05SY - Systemwide | Cxxx-NCR-000409 | NCR | FTS - 2 no. braking block (L2) assemblies in W17 contaminated with concrete |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-06-01 | 2017-05-17 09:33 | -15 | 2017-02-01 18:51 | Track - Track General | 1000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Concrete has seeped through the shuttering during the pour of the upstand and has contaminated the braking block (L2) stainless steel components and bearing. Please see below the details of the location. 1 no. L2 __ assembly on east side of South __ upstand at chainage 5036 (ring 3053) of FTS westbound tunnel. 1 no. L2 __ assembly on east side of North __ upstand at chainage 5036 (ring 3053) of FTS westbound tunnel.
| 05SY - Systemwide | Cxxx-NCR-000410 | NCR | Atmosphere Side Attenuator Steelwork Grout |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-05-17 | 2017-06-05 13:22 | 19 | 2017-02-02 07:51 | Structural Engineering - Grouting | 5000 |  | Incomplete Works | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | First pour of the grout to seal the underside of the ASA steelwork was too high and submerged one of the PFC members. This pour should have just been to the underside of the PFC member. As it is submerged in grout and also a thermal expansion joint, there is a risk that the beam may not expand, per design, under extreme temperature conditions.
| 05SY - Systemwide | Cxxx-NCR-000411 | NCR | W43 voiding under baseplate |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-04-30 | 2017-04-11 10:30 | -19 | 2017-02-02 11:33 | Civil - Track | 1000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | W43 slab, Westbound chainages 8047 -8063 At some locations of slab W43, large (>30%) voids of trapped air have been found underneath baseplate when they have been lifted to remove temporary track.
| 05SY - Systemwide | Cxxx-NCR-000412 | NCR | FTS Baseplates delivered to site without FAT report |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-06-07 | 2017-05-22 15:39 | -16 | 2017-02-02 14:35 | Track - Rails and Sleepers | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Rail Baseplates have been delivered to site without the FAT being carried out.
| 05SY - Systemwide | Cxxx-NCR-000413 | NCR | FTS – Marginally out of tolerance concrete cover to reinforcement in slab W40 |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-05-03 | 2017-04-05 09:50 | -28 | 2017-02-02 21:16 | Track - Track General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Background information: In order to make different levels on Barbican top of slabs as per Design requirements, __ raised Cxxx-FCD-000151 to capture formal acceptance of the use of longitudinal reinforcement as main support for this formwork. A nut is welded for this purpose between two reinforcement bars of diameter 16 mm and approximately 150 mm of length which are attached transversally to the main longitudinal reinforcement. This nut accommodates a threaded bar which supports the metal formwork above with vertical adjustments possible via thread. This method leads to the nut welded to the two short bars being incorporated into the permanent works. The treaded bar is removed once concrete sets off. During W40’s pre-pour inspection it was identified that in some locations of the slab – please see the attached sketch – the clearance between the above mentioned short transversal reinforcement bars and top of concrete was marginally below 30 mm which is the minimum concrete cover requirement – circa 25 mm. Please see the attached picture. __ assessed that this would not cause any detrimental effect to the slab durability due to the short length of the bars and compliant concrete cover to the structural reinforcement and assessed that the pour could go ahead as this could be easily dealt with post-concreting by applying a coat of Cementitious coating 851 or similar if required by the Designer. Please see attached the product data sheet.
| 05SY - Systemwide | Cxxx-NCR-000414 | NCR | Unaccepted ITP revision used in Evacuation Walkway Brackets installation SAF file |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-04-07 | 2017-02-16 16:00 | -50 | 2017-02-06 10:28 | Track - Walkways | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | The Evacuation Walkway Brackets installation ITP (Cxxx-__-Y-ITP-CRG03-50001) has been revised to include the installation of the Evacuation Walkway System as a whole. The current accepted revision for this ITP number on EB is revision 2.0, however the SAF file contained 2 further revisions; Rev3.0 “Evacuation Walkway Brackets Installation” and Rev4.0 “Evacuation Walkway System Installation” neither of which has been submitted to Crossrail for approval.
| 05SY - Systemwide | Cxxx-NCR-000415 | NCR | Tunnel Pump Drainage Method statement Non-Compliant |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-04-12 | 2017-04-11 10:33 | -1 | 2017-02-07 16:40 | Mechanical - Piping | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | On Monday 6th February 2017 a planned surveillance was performed at Plumstead on the Tunnel Pump Drainage documentation and ongoing installation of materials. During the inspection of the Method Statement it was found to have a Decal Code 2. Which is contrary of section 6.1.2 of the ITP Cxxx-__-O4-ITP-CRG03-50175.
| 05SY - Systemwide | Cxxx-NCR-000416 | NCR | Tunnel Pipe Drainage Pipes Non-compliant |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-04-12 | 2017-04-05 14:07 | -7 | 2017-02-08 11:45 | Mechanical - Piping | 10000 |  | Manufacturing Defect | Reject | 2 (6-60k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | On Monday 6th February 2017 A planed Surveillance of the Pumped Tunnel Drainage was undertaken between tunnel ring numbers 757 and 677 in the Westbound tunnel 300 meters short of Woolwhich Station. One of the tasks in the Surveillance was to measure the thickness of the galvanisation of the DN100 Pumped Tunnel Drainage pipes. The thickness of the galvanisation is to be not less than 75 µm as stated in the Galvanised Steel Pipe Material Compliance Supporting Documentation - Cxxx-__-M-LRC-CRG03-50002 v2.0 Six locations for tests were chosen: Ring 728, 726, 724 and ring 757 where two pipes and a nipple underwent testing. All of the DN100 tunnel drainage pipes tests returned results that were outside of the Crossrail acceptance parameters. Each test included measuring the galvanisation at the top, front, bottom and back of the pipe.
| 05SY - Systemwide | Cxxx-NCR-000417 | NCR | Damage to Galvanisation of __s Steelwork |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-05-03 | 2017-05-11 09:57 | 8 | 2017-02-08 15:52 | Mechanical - Mechanical Engineering General | 3000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | On Wednesday 1st February a planned inspection of steel work that has been installed by __s at Tottenham Court Road revealed numerous imperfections in the Galvanised Protective coating. These imperfections include but are not limited to scratches, gouges, chipped galvanised coating and insufficient galvanised coating. LB9008 A & B: A)The runway beam nearest to the centre is showing signs of damage to the lower surface of galvanised coating. B) The runway that is located nearest the wall has signs of damage. There is a large scratch that has removed the galvanising protection to expose bare metal. LB9001 Both runway beams have small areas of damage to galvanised coating. LB9005 There is severe damage to the galvanised protection on the lower side edge of the runway beam. There are signs of damage to the galvanised protection that produced a low reading on the coating thickness test equipment. It has been recommended that __s need to inspect all installed works and perform repairs in accordance of the accepted procedure.
| 05SY - Systemwide | Cxxx-NCR-000418 | NCR | NCR Wrong Spacing on inside HAS Catchpits (Thames Tunnel) |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-10-31 | 2017-10-09 09:40 | -22 | 2017-02-15 15:39 | Civil - Track | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Thames tunnel, between North Woolwich Portal and Woolwich Station, EB, Around CH 19+796 and CH 19+837 There are two areas where the spacing is out of tolerance. The first one is located around Ch 19796 where the spacing between sleepers is: 647mm, 648mm and 662mm on one side and 644mm, 650mm, 661 mm on the other side. The second one is located around Ch 19837 where the spacing between sleepers is: 657mm, 662mm and 656mm on one side and 653mm, 662mm, 659mm on the other side. See attached sketch.
| 05SY - Systemwide | Cxxx-NCR-000419 | NCR | Cable installation in Cross Passages in Thames Tunnel commenced without a CMS IRN in place |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-04-11 | 2017-04-05 14:10 | -6 | 2017-02-16 09:24 | Electrical - General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | In addition to an EWN that has been raised on this matter already, the contractor would like to raise this NCR. __ would like to inform the Supervisor that a few metres of cable have been installed and coiled on Cross Passage cable tray that has not yet achieved the IRN in CP 16, CP17 & CP 18.
| 05SY - Systemwide | Cxxx-NCR-000420 | NCR | Unathorised Installation of Handrail on Platform at Bond Street |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-03-28 | 2018-02-09 13:36 | -47 | 2017-02-16 14:05 | Systems - Other | 2500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | On the 5th February 2017, the Station Contractor at Bond Street notified Crossrail that scaffold tubes have been drilled and fixed on the Westbound tunnel along the platform nosing. Subsequently it was confirmed that __ carried out the temporary works installation without prior consultation with FDC Cxxx. There is a potential that the GFRP reinforcement used in the platform construction may have been damaged during installation. It has been confirmed that Cxxx were not consulted prior to the installation and they now have concerns about the proximity of drilled holes and fixings to the GFRP bars cast in to the platform concrete.
| 05SY - Systemwide | Cxxx-NCR-000421 | NCR | Missing segregation of dissimilar metals |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-05-05 | 2017-06-05 13:25 | 31 | 2017-02-16 14:47 | Structural Engineering - Joints | 500 |  | Incomplete Works | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the joint surveillance site visit carried out by CRL/__ at WHI, it was noted that no segregation existed between the HDG brackets and the stainless steel anchors on the DRD’s. The risk is that when dissimilar metals are in contact in a corrosive environment, one of the metals experiences accelerated galvanic corrosion while the other metal remains galvanically protected and this can cause of loss of durability. With no segregation in place, the design life may be adversely affected.
| 05SY - Systemwide | Cxxx-NCR-000423 | NCR | FTS Lite & Station – FTS concrete stuck to first stage post-jacking of E21 |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-04-21 | 2017-04-05 10:20 | -16 | 2017-02-20 18:59 | Track - Track General | 5000 |  | Damaged | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A small section of FTS concrete, approximately 55mm depth (maximum), 250mm length and 200mm width, has broken away from the main slab during jacking and is fixed to the first stage concrete
| 05SY - Systemwide | Cxxx-NCR-000424 | NCR | FTS Lite & Station – Concrete fixed to bearing plate and subsequent void in underside of the slab E22 |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-05-21 | 2017-04-18 09:06 | -33 | 2017-02-20 22:23 | Track - Track General | 5000 |  | Damaged | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Concrete has remained stuck to the bearing plate when jacking the slab – coverage of approximately 20% of the area of the bearing plate. Subsequently, there is a void left on the underside of the slab at this location where the vertical bearing will sit. Please see below the details of the bearing plate location. North side of Eastbound tunnel, north east bearing plate of Manhole 6 (from E21/22 end), Chainage approx. 5028
| 05SY - Systemwide | Cxxx-NCR-000425 | NCR | OHLE bracket positioned at the wrong location at Woolwich Station W/B track |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-06-23 | 2017-06-29 09:29 | 6 | 2017-02-22 10:41 | Electrical - OHLE | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | 1. OHLE brackets have been positioned at the wrong location at Woolwich Station W/B track (XRA/21/027, XRA/21/101 and XRA/21/103) 2. Mistake on the OHLE layout (Cxxx-__-R6-DDA-CR147_Z-02500 P01) and on the ROC Drilling data book (Cxxx-__-XDS-CR146-50003 Rev 3.0)
| 05SY - Systemwide | Cxxx-NCR-000426 | NCR | FTS Barbican – Spring housing embedded in concrete (W38) |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-05-22 | 2017-03-15 09:20 | -68 | 2017-02-21 18:57 | Track - Track General | 1000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 1 number spring housing is embedded and a void has been formed in the surface of the concrete at an incorrect location, reducing the cover to the reinforcement at this location. Please see the attached picture. Location: FTS Barbican, Westbound tunnel, the first spring housing from the W37-38 interface on the north side of slab W38 at chainage 7926
| 05SY - Systemwide | Cxxx-NCR-000427 | NCR | FTS - Minor damage to FSC kerb surface W7 to W11 |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-06-14 | 2017-07-26 08:22 | 42 | 2017-02-21 19:08 | Track - Track General | 2500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | One side (north) of FSC kerbs was transversely saw cut to create 30mm deep breaking out line. This is required on “non-platform” sides of tunnel, but accidently was saw cut on both in W7 to W11.
| 05SY - Systemwide | Cxxx-NCR-000429 | NCR | FTS Barbican – Concrete strength under requirements at 7 days |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-06-22 | 2017-03-22 09:04 | -92 | 2017-02-22 17:21 | Track - Track General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | A number of concrete cube test results have not achieved 35 MPa at 7 days as required by the ITP. The concrete was sampled from slabs W42, W40, E37, W39, E47, W36, W38, E46, W35, E45, W34 and E44. The lowest value is 27 MPa. Please see the attached spread sheet which shows all the non-compliant results and the date when the 28 days results are expected for each sample.
| 05SY - Systemwide | Cxxx-NCR-000430 | NCR | Hole in Track weld no259 |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-05-23 | 2017-05-25 15:28 | 2 | 2017-02-22 21:55 | Civil - Track | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | STG – PML EB branch, Ch 11868 EB There is a hole in the running edge of the weld that was identified by the Weld inspector. The weld is therefore rejected.
| 05SY - Systemwide | Cxxx-NCR-000431 | NCR | STS - Jig stuck in Concrete at Ch 12395 EB |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-05-25 | 2017-03-15 11:38 | -71 | 2017-02-24 14:06 | Track - Track General | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | One jig is stuck in the concrete at Ch 12395 EB. See attached picture.
| 05SY - Systemwide | Cxxx-NCR-000432 | NCR | Damages to Track Slab by OHLE Survey Nails |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-07-21 | 2017-07-21 09:59 | 0 | 2017-02-25 12:09 | Track - Track General | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Damages to the track slab by OHLE/Survey Nails from VDP to CWS – Ch 14273, 13987, 13989 EB (Could be elsewhere as well. These damages can appear on the second stage concrete or on the first stage concrete).
| 05SY - Systemwide | Cxxx-NCR-000433 | NCR | Existing lateral drainage for shaft concreted in |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-06-26 | 2017-06-23 14:08 | -3 | 2017-02-25 16:04 | Track - Track General | 1000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Stepney Green Cavern, Trolley parking area EB. Existing lateral drainage for shaft drainage has been covered with infill concrete during pour. Photograph attached.
| 05SY - Systemwide | Cxxx-NCR-000434 | NCR | Linear strength at 28 days not compliant |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-05-26 | 2017-04-07 14:23 | -49 | 2017-02-25 16:29 | Track - Track Bed | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Chainages 10454 to 10303, potentially 9704 to 8991 (strength results by the end of February). On 12/01/17 : 28 days mean 50.59 < 28 days target 51.11 (Standard Variation 7.51) On 13/01/17 : 28 days mean 50.91 < 28 days target 51.09 (Standard Variation 7.50) On 14/01/17 : 28 days mean 52.23 < 28 days target 52.47 (Standard Variation 8.42)
| 05SY - Systemwide | Cxxx-NCR-000435 | NCR | Paddington TSA Steelwork Pull Test Values |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-11-20 15:46 | 2017-08-22 15:47 | -90 | 2017-03-02 08:01 | Systems - Ventilation and Pressure Relief | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Inspection points not adequate | Completed |  | Crossrail FE was invited on 1/3/17 for a pull test on the fixings for TSA steelwork installed by __ at Paddington West Shaft. 15 minutes before the test the Crossrail FE was informed that __ had been struggling to find a pull test value for these anchors and the __ site team finally come to the conclusion that the pull test value is zero. It was concluded that because the only force applied on the anchors is the shear force it was then decided that a pull test is not required to be done. __ then cancelled the pull test and installation was carried on. Further investigation was carried out by CRL FE and it was noted that the zero value for the tension load is taken from a design calculation document which has not submitted to or accepted by Crossrail. Also it was not clarified in the document on which basis the tension force is calculated. Considering that very similar arrangement of the steelwork have been installed by other Contractors in other locations and all of them have been pull tested, it is recommended to re-calculate the applied forces on the anchors and seek specialised advice from the manufacturer. Item 6.3.10 of the ITP Cxxx-__-O4-ITP-CRG03-50158 Rev 3.0 asks for a pull test to be carried out and therefore it's not acceptable to skip the pull test.
| 05SY - Systemwide | Cxxx-NCR-000436 | NCR | Corrosion of Draft Relief Damper Framework |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-04-17 | 2017-03-15 09:45 | -33 | 2017-03-06 07:52 | Mechanical - Mechanical Engineering General | 1500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Not Defined | Completed |  | The cross-member of the galvanised steel work at TCR DRD East Level +2 is showing signs of corrosion where the top plate is attached to the main cross-member. Signs of rust a present at the end of the beam and signs of rust are present through some of the top holes (photos are attached to this NCR)
| 05SY - Systemwide | Cxxx-NCR-000437 | NCR | __ HV rod/HY 270 resin anchors fixed into brick mortar bed joint at various locations in Connaught Tunnel for CMS bracketry |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-05-10 | 2017-05-04 10:03 | -6 | 2017-03-03 09:15 | Mechanical - Mechanical Engineering General | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | A planned Crossrail surveillance was undertaken on 2nd March 2017 to look at manual drilling and bracket installation at Connaught Tunnel. During the site visit it was identified that __ HV rods with HY 270 resin had been installed into the brick mortar bed joint at various locations within the tunnel, in particular EB Ch17800 – Ch17700 where installation of J hangers was progressing (see photos attached). It was noted that __ were installing against a string line set out by __ operatives. Drawing Cxxx-__-E-DDD-CR001_Z-30008 which is referenced in the Method Statement states in the notes; “Fixings are into bricks, not mortar joints, at a minimum of 35mm from the edge of brick”. This is also stated in the __ product data sheet. As the surveillance was based on a sample, it is unclear whether this installation is the same in other areas within the tunnel.
| 05SY - Systemwide | Cxxx-NCR-000438 | NCR | HWC poured with a PFA variant and All-in mix NOT accepted on any CPS |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-04-02 | 2017-04-05 10:06 | 3 | 2017-03-03 16:12 | Track - Track General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | At the locations listed below, HWC was poured with the use of the ALL-IN aggregate mix. - Slab E16 Cast 01/12/2016 - Slab W36 Cast 03/02/2017 - Slab W38 Cast 03/02/2017 - Slab W40 Cast 21/02/2017 At the locations listed below, HWC was poured with the use of a PFA variant (Grade N) not accepted in any CPS. - Slab E36 Cast 27/02/2017 - Slab W29 Cast 28/02/2017 - Slab W27 Cast 28/02/2017 - Slab E35 Cast 01/03/2017 - Slab W26 Cast 02/03/2017 - Slab W24 Cast 02/03/2017 - Slab E34 Cast 03/03/2017
| 05SY - Systemwide | Cxxx-NCR-000439 | NCR | Incorrect Nut / Bolt Arrangement - DRD |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-04-26 | 2017-05-05 11:49 | 9 | 2017-03-04 10:37 | Mechanical - Mechanical Engineering General | 3000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Canary Wharf Station, level -4, West Shaft: Upon the inspection of the Draft Relief Damper Steelwork within the Westbound, West Shaft, it has become apparent that the half nut first/full nut second arrangement which has been specified within the approved drawing, has been installed incorrectly with the arrangement being full nut first, half nut second.
| 05SY - Systemwide | Cxxx-NCR-000440 | NCR | Steelwork resin anchor failure |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-08-24 | 2017-08-24 16:07 | 0 | 2017-03-04 11:38 | Mechanical - Mechanical Engineering General | 3000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Liverpool Street Station, Bloomfield Box, Platform +1 TID-E/1411: The Sub-Contractor, __ was carrying out work, installing TID-E/1411 supporting steelwork as per Cxxx-__-H-DWG-C101-50011 rev 1.0 When carrying out torqueing (80kN/m) to an installed stud. A section of concrete broke away from the surface area surrounding the stud. On inspection it was found that: 1. The required embedment depth of 90mm for the stud had not been reached, only 50mm of the stud had been embedded. 2. The wrong length of stud had been used, 140mm rather than 190mm. 3. There were large packer plates embedded in the concrete. The concrete has sheared across the face of these plates The shorter stud has been used in error, owing to mix-up in different sizes for various uses (190mm for floor fixings, and 140mm for wall fixings).
| 05SY - Systemwide | Cxxx-NCR-000441 | NCR | ASA Steel Work not grouted as per design |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-09-27 | 2017-10-11 16:03 | 14 | 2017-03-06 09:28 | Mechanical - Mechanical Engineering General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | __ have grouted around the anchoring plates for the ASA steel work at Tottenham Court Road East on Level +3 which differs from the Crossrail accepted design. There is minimal ground surface between the steel work and floor to allow a complete grouting of the steel work. __ design are currently working on a solution which is acceptable to Crossrail.
| 05SY - Systemwide | Cxxx-NCR-000442 | NCR | MCR acceptance of __ Supplier Mechanical Anchor Fixings |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-11-01 | 2017-11-30 14:45 | 29 | 2017-03-07 12:57 | Systems - Ventilation and Pressure Relief | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | An MCR has not been submitted for the anchor fixings used with the __ dampers. The fixings are provided with the __ dampers and manufactured by a __ supplier. CRL-MCR-001834 has been accepted for the Dampers. In section 1.4.2 of the supportive information appended to this MCR it details “…M12 anchor bolts manufactured from hot dipped galvanised steel shall be provided for damper installation directly to the civil works…”. This MCR does not go as far to demonstrate the anchor is CE marked, supplier is ISO 9001 or equivalent accredited, meets the environmental requirements, etc. As this is a critical item, and as with all other anchor fixings used, a separate MCR is required.
| 05SY - Systemwide | Cxxx-NCR-000443 | NCR | Uncaptured Post Gate Change – Self Supporting Dampers |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-10-31 | 2017-09-29 08:13 | -32 | 2017-03-07 13:05 | Systems - Ventilation and Pressure Relief | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Since Tunnel Ventilation Design Gate 3 a number of dampers have undergone post gate design development. This NCR refers to one particular change where all dampers were required to be fixed to secondary steelwork. Design has since progressed to allow certain damper arrangements to be self supporting, allowing for the removal of this secondary steelwork. This design change requires technical assurance and that the design gate 3 has not been impacted. This change needs to be accepted by the Project Manager, as defined within the __ Design Management Plan section 7.6.2.
| 05SY - Systemwide | Cxxx-NCR-000444 | NCR | __ Lifting Beams |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-04-08 | 2017-04-07 13:26 | -1 | 2017-03-09 10:26 | Mechanical - Mechanical Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Supervision - Other | Completed |  | The lifting beam sub-contractor __s have not been completing the required QADs at the time of a ITP witness point, but at a later date. This has resulted in an incorrect value being written into KC-QAD-003 sheet. The Lindapters For LB14009, LB140011 & LB14015 were torqued to 285Nm but the value of 147Nm was entered onto the QAD sheet.
| 05SY - Systemwide | Cxxx-NCR-000445 | NCR | TVS Lifting Beams and Gantries |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-05-08 | 2017-08-10 10:43 | 94 | 2017-03-09 12:27 | Mechanical - Mechanical Engineering General | 1000 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | The setting out, drilling and assembly of a number of lifting beams and gantries was undertaken at Farringdon prior to the setting out and assembly drawings being issued to __ on Aconex for Information.
| 05SY - Systemwide | Cxxx-NCR-000446 | NCR | FTS Lite – Voiding and cracks in lateral restraint upstands |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-06-07 | 2017-06-14 09:55 | 7 | 2017-03-09 18:59 | Track - Track General | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | There are several cracks and voids within the surface of the concrete cast in some lateral restraint upstands cast on 27/02/2017 between slabs E4 and E11. Some defects have been repaired prior to the problem being flagged to the Site Engineer. Please see attached some pictures of the upstands and see the table below for the location of these and comments on each one of them. Slab North/South:CH Assembly reference Comment E4 N:4204.581 L1-06-445 Voiding (partially repaired) E4 N:4213 L1-06-148 Void E5 N:4241.085 L1-06-236 Voiding (repaired) E6 N:4298.198 L1-06-278 Voiding (repaired) E7 N:4339.811 L1-06-198 Cracks E8 S:4360.617 L1-06-390 Voiding E8 N:4389.226 L1-06-368 Cracks E8 N:4397.029 L1-06-408 Cracks
| 05SY - Systemwide | Cxxx-NCR-000447 | NCR | FTS Barbican - Voids under baseplate pads |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-06-08 | 2017-05-17 09:51 | -22 | 2017-03-10 14:51 | Track - Track General | 2500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | During the lifting of baseplate pads for inspection of the concrete surface underneath on FTS Barbican it was identified that the maximum percentage of acceptable entrapped air/voids was exceeded on slabs W38, W40, W41, W42, E40, E41, E43, E47. Two or three No baseplates have been checked in these slabs to date. Please see attached some pictures of the concrete surfaces.
| 05SY - Systemwide | Cxxx-NCR-000448 | NCR | Installation of Non-Conforming Fixing |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-10-25 | 2017-10-25 14:25 | 0 | 2017-03-13 14:57 | Materials - Approval | 1000 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | __ have installed TVS Steelwork using Non-Conforming fixings
| 05SY - Systemwide | Cxxx-NCR-000449 | NCR | TCR - West ASA Steel Work not grouted as per design |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-09-27 | 2017-10-11 16:04 | 14 | 2017-03-13 16:27 | Mechanical - Mechanical Engineering General | 1000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | The steelwork has been installed with a small gap between the steelwork and the slab. This means a grout solution for providing the seal cannot be used. A Z-bracket design will need to be detailed by __ in order to provide the seal.
| 05SY - Systemwide | Cxxx-NCR-000450 | NCR | Tunnel Fire Main T Junctions Non-Compliant |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-05-31 | 2017-05-31 10:42 | 0 | 2017-03-13 16:44 | Systems - Fire Detection systems and Mains | 5000 |  | Material | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | The Fire Main T Junctions galvanisation thickness has been tested using the MPI method and found to be non-compliant on the DN100 pipe section.
| 05SY - Systemwide | Cxxx-NCR-000451 | NCR | TID Steelwork has been sealed using non compliant foam / mastic |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-05-30 | 2018-05-11 11:55 | -19 | 2017-03-14 15:10 | Mechanical - Mechanical Engineering General | 3000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the installation of the TID steelwork __ used Foam / Mastic to seal Metal to Metal / Metal to concrete with gaps that exceed 15mm, this is contrary to section 6.3.9. of the ITP Cxxx-__-O4-ITP-CRG03-50158
| 05SY - Systemwide | Cxxx-NCR-000453 | NCR | __ HV 270 resin anchors for Connaught Tunnel have been over torqued |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-09-27 | 2017-09-27 10:34 | 0 | 2017-03-15 11:29 | Mechanical - Mechanical Engineering General | 1000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | A planned Crossrail surveillance was undertaken on 2nd March 2017 to look at manual drilling and bracket installation at Connaught Tunnel. During the site visit it was stated by __ that they where using a Makita Impact Wrench to torque tighten the resin anchors; settings of 45Nm and 25Nm were mentioned however this was not verified. The installation ITP (Cxxx-__-O4-ITP-CRG03-50120 Rev 2) refers to a torque requirement of 30Nm. Due to the inconsistencies, information regarding actual applied torque vs the required torque as stated by __ was requested post surveillance. It was confirmed by __ (meeting between __ and __ dated 10th march 2017) that the __ Hit 270 resin anchors require a max torque of 8Nm. It was further confirmed by __ that the anchors had been torqued to 12Nm by __ following checking over the weekend (11th and 12th March). It was noted by __ that a torque wrench had been used, and not the Makita Impact Wrench following discussion with __ senior management. Based on the checks by __ as part of the Exit Note closure, the anchors have been torqued in excess of the manufacturers recommended parameters (12Nm vs 8Nm). As such, based on this information, the fixings have been over torqued introducing potential risk to the performance of these fixings, in particular the bond between the fixing and the resin. In addition, the ITP references an incorrect torque parameter (30Nm) and this will need to be amended as part of the closure.
| 05SY - Systemwide | Cxxx-NCR-000454 | NCR | __ Quality Not Present During ITP Hold Points |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-04-12 | 2017-04-11 10:37 | -1 | 2017-03-16 14:18 | Mechanical - Mechanical Engineering General | 1000 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | __ Quality have failed to attend site when requested to witness ITP hold point.
| 05SY - Systemwide | Cxxx-NCR-000455 | NCR | WHI-W Westbound Tunnel Isolation Damper Steelwork |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-04-21 | 2017-05-08 10:27 | 17 | 2017-03-22 14:46 | Mechanical - Mechanical Engineering General | 2000 |  | Design | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On 8.3.17 the __ design team were advised by __ team that one of the vertical columns on the WB TID steelwork was fabricated incorrectly. Several holes were drilled in the incorrect place and two plates were welded on the wrong end of the beam.
| 05SY - Systemwide | Cxxx-NCR-000456 | NCR | Concrete falls into existing UTX pipe during concrete pour. |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-05-30 | 2018-05-02 15:44 | -28 | 2017-03-17 18:55 | Track - Track General | 2000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | C8 White Chapel Station Ch 160 crossover. During infill pour process, one of the UTX pipes for M&E installations came out of his position when the concrete reached three centimetres in height. As a result, some concrete falls into the plastic tube. (Attached Photos).
| 05SY - Systemwide | Cxxx-NCR-000457 | NCR | TVS – Lifting Beams and Gantries |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-06-20 | 2017-08-10 10:48 | 51 | 2017-03-20 17:59 | Mechanical - Mechanical Engineering General | 5000 |  | Manufacturing Defect | Rework | 3 (3-6k) | Complete | External Phenomenon - Other | Completed |  | When steel has been unpacked and previously obstructed areas exposed __ have observed area of corrosion / poor quality galvanisation / flaking galvanisation of Lifting Beam LB12002.1 (beam mark FW21B2). __s to investigate the cause of the issue and rectify as soon as possible to minimise impact on construction programme. Refer to photos Howard unable to attach photos please refer to email referenced to this NCR.
| 05SY - Systemwide | Cxxx-NCR-000458 | NCR | Voids underneath of baseplates pads, at Marshgate Lane Bridge (DFT) . |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-04-20 | 2017-04-05 10:18 | -15 | 2017-03-21 18:30 | Track - Track General | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Marshgate Lane Bridge , EB(14593-14610) and WB(14763-14782), DFT, PML Portal At the QC Inspection for the voids underneath of the baseplates, as per ITP Cxxx-__-R4-ITP-CRG03-50001 rev6 , ITEM 6.5.3, 30% of the baseplates were already repaired, without following the previous steps described on the ITP.
| 05SY - Systemwide | Cxxx-NCR-000459 | NCR | FTS Barbican – concrete levels at shear keys in slabs W28, W29 |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-08-29 | 2017-08-01 14:36 | -28 | 2017-03-23 17:00 | Track - Track General | 3000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | It has been identified that the concrete level was cast below the shear keys bottom plate in some Barbican type floating track slabs. Please see the attached pictures and survey showing the extents and location of the voids under the shear keys.
| 05SY - Systemwide | Cxxx-NCR-000460 | NCR | FTS Barbican – Timber cast underneath baseplate in slab W21 |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-06-25 | 2017-04-27 15:28 | -59 | 2017-03-27 16:55 | Track - Track General | 2500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | A single piece of timber has been cast into permanent works underneath a baseplate in W21. Please see below details of the location. Westbound Slab 21, 6th baseplate on the left hand side (from high to low chainage) from the W21-22 joint, approx. chainage 7464.4
| 05SY - Systemwide | Cxxx-NCR-000461 | NCR | FTS Barbican – Incorrect inclination of baseplate in slab W20 |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-11-01 | 2017-11-08 14:57 | 7 | 2017-03-27 17:09 | Track - Track General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | One of the baseplates in slab W20 has not been installed correctly prior being cast. The inclination is incorrect; the G reference in the baseplate should be on the 4 foot side so that the baseplate is inclined inwards.
| 05SY - Systemwide | Cxxx-NCR-000462 | NCR | Materials were returned from Site to Yard in unacceptable condition without any paperwork in place |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-06-28 | 2017-06-19 14:48 | -9 | 2017-03-29 12:53 | Over Head Line Electrification - Over Head Line Electrification General | 5000 |  | Damaged | Reject | 3 (3-6k) | Complete | Management Problem - Inadequate administrative control | Completed |  | ROC cantilevers were returned from Site to the OHLE Yard in unacceptable condition. Cantilevers for ROC were stacked in inappropriate way and some of the insulator presented stains, footprints, and damaged. * When Site people returned those materials, they didn't even notify the Yard people. They left the materials in the Yard without any notification and no signed paper in place regarding returned material. * As a general issue, Site people do not sign any document when they receive the material from the Yard to Site to confirm if they receive the material in good condition, and also same missing documentation when they return any material from Site to Yard. Due to lack of evidence in terms of document communication between Site and Yard, there is a risk for the traceability of damaged products.
| 05SY - Systemwide | Cxxx-NCR-000463 | NCR | TID dampers short linkage at Woolwich |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-05-10 | 2017-05-17 09:59 | 7 | 2017-03-29 14:34 | Mechanical - Mechanical Engineering General | 5000 |  | Manufacturing Defect | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Inadequate/insufficient tooling. | Completed |  | The Tunnel Isolation Dampers at Woolwich East have been installed and when trying to connect the dampers together for the actuator to action the two dampers, the installer realised that the linkage shaft on one damper were 20 mm short. This stopped the completion of the dampers and will need to be re worked on site. Photos of the defect have been attached
| 05SY - Systemwide | Cxxx-NCR-000464 | NCR | Rigid bar registration is out of tolerance between Plumstead and North Woolwich Portal |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-06-28 | 2017-07-20 10:41 | 22 | 2017-03-30 16:17 | Over Head Line Electrification - Over Head Line Electrification General | 5000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | The issue has been identified at XRA/22/619 WB but there is a risk that the same issue might be found at different locations between Plumstead Portal and North Woolwich Portal Westbound. According to control sheets the height and stagger are within tolerance. However, there are evidences that the information on check sheets is not correct and the actual registration does not comply with the design. * The tolerance for height and stagger is ±10mm. According to the control sheets the height is between 4.25 and 4.26 (4.25m is the design value). However when we went there to check the splicing between XRA/22/611 (Ch 22 635) and XRA/22/619 (Ch 22670) we found that the actual height at XRA/22/619 is 4.29m (+40mm).
| 05SY - Systemwide | Cxxx-NCR-000465 | NCR | Cariboni goods received with unacceptable packing and some goods showing marks. |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-04-29 | 2017-04-27 15:31 | -2 | 2017-03-30 09:34 | Logistics - Logistics - General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper handling of material | Completed |  | Open route Cantilevers for ROC were stacked in an inappropriate way inside the boxes delivered.
| 05SY - Systemwide | Cxxx-NCR-000466 | NCR | Wrong drilling angle on tunnel surface |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-08-31 | 2017-07-26 10:00 | -36 | 2017-05-23 14:26 | Over Head Line Electrification - Over Head Line Electrification General | 3000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Wrong drilling angle has been observed on tunnel surface between Pudding Mill Lane and Stepney Green. Therefore, when the support is installed, the plate and the bolt head are not fully in contact.
| 05SY - Systemwide | Cxxx-NCR-000467 | NCR | Rigid Bar Splicing too close to support in two consecutive spans |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-07-09 | 2017-07-26 14:13 | 17 | 2017-03-31 11:22 | Over Head Line Electrification - Over Head Line Electrification General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | North Woolwich portal to Plumstead, Westbound from ch. 21803 – ch. 21814. Rigid Bar Splicing is at 0.7m from XRA/21/801 support (13% of span length) and 0.6m from XRA/21/803 support (11% of span length). The design positions are 1.15 and 1.1m respectively. The Bar between XRA/21/803 and 805 is too long (6.15m instead of 5.25m).
| 05SY - Systemwide | Cxxx-NCR-000468 | NCR | Wrong methodology of GREASING during the ROC contact wire insertion |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-07-09 | 2017-07-26 09:45 | 17 | 2017-03-31 12:26 | Over Head Line Electrification - Over Head Line Electrification General | 5000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Between Plumstead and North Woolwich Portal, the grease inserted by brush instead of by automatic pump. - There is a potential risk if the grease doesn't cover the contact wire fully which might create corrosion (oxidation) in future because of 2 different material in contact (between bar and contact wire). - Using brush is not the appropriate method for greasing.
| 05SY - Systemwide | Cxxx-NCR-000470 | NCR | Whitechapel - Welded Plates Low Galvanisation Readings |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-08-02 | 2017-07-28 14:41 | -5 | 2017-03-31 15:35 | Structural Engineering - Steel Member | 3000 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | WHI-E TID/UPD; WHI-W WB TID; EB TID Steelwork On 27/03/17 galvanization readings were conducted by the __ Whitechapel team using a calibrated micrometre instrument. It was found that galvanisation thickness readings on the welded fin plates on UKB/UKPFC beams and welded plates to UKB beams were consistently low. In addition, the low readings had some relation to the surface of the plates which seemed to be reflective or ‘mirror’ like. See attached photos:
| 05SY - Systemwide | Cxxx-NCR-000471 | NCR | Concrete Mix Design for OHLE Foundations is missing |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-07-09 | 2017-07-20 15:30 | 11 | 2017-03-31 15:59 | Civil - Civil Engineering General | 1000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Concrete Mix Design for OHLE Foundations is missing,
| 05SY - Systemwide | Cxxx-NCR-000472 | NCR | Sleeper tie bar damaged while unloading the LWR |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-01-31 | 2017-09-28 09:29 | -125 | 2017-04-03 11:32 | Track - Track General | 5000 |  | Damaged | Rework | 3 (3-6k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | WHI-LIS section EB Ch. 9+627 Sleeper tie bar has been damaged while unloading LWR causing a visual scratch on the tie bar,and the galvanisation could be damaged
| 05SY - Systemwide | Cxxx-NCR-000473 | NCR | PML Portal mast foundation 732 wrong bolt's position |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-05-31 | 2017-06-01 09:44 | 1 | 2017-04-03 18:27 | Over Head Line Electrification - Over Head Line Electrification General | 5000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | 1. Bolts are incorrectly installed at Pudding Mill Lane Portal mast foundation XR/14/732 at chainage 14648, 2. Incorrect revision of the drawing Cxxx-__-R6-DDB-CR094_PT002_Z-00534 have been taken into account for the setting out of the anchor bolts (Rev P02 instead of revision P03/C01). 3. Not followed the Inspection and Test Plan OHLE Pad Foundation Installation- Cxxx-__-O4-ITP-CRG03-50178
| 05SY - Systemwide | Cxxx-NCR-000474 | NCR | FTS Lite - Voiding within the concrete kerb adjacent to a braking block assembly (L2) |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-07-03 | 2017-05-04 10:38 | -60 | 2017-04-04 10:51 | Track - Track General | 2500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Voiding is present in the concrete kerb adjacent to one of the braking block assemblies. The voiding is located at the base of the braking block assembly and as a result, the face and base of the braking block assembly’s cast-in shelf were not embedded as per Cxxx-OVE-R4-DDD-CR001_Z-83235 Rev C03. Please see below the details of the location. Eastbound Tunnel, Slab 13, South East Braking Block upstand chainage 4624.550, Eastern assembly.
| 05SY - Systemwide | Cxxx-NCR-000475 | NCR | __s cable drums without cover and Drums label and ID not matching |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-08-31 | 2017-08-10 09:34 | -21 | 2017-05-23 14:29 | Over Head Line Electrification - High Voltage Power Supply | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Information on stamped ID on wooden drum and information on attached Label on drum is not matching. Labelling and ID not matching for 25kV (12 Drums) Labelling and ID not matching for 1kV (11 Drums) Reliable information for cable drums is no available and no identification to allocate drums can be done. * Cable drums without cover to protect cable and some scratches are on some cables. Some scratches on cables were visible and some can be done due to lack of cover to protect them. Cable Drums without being covered (45 Drums) Cable with some scratches (2 Drums) * Pulling of cable as allocation cannot be identified.
| 05SY - Systemwide | Cxxx-NCR-000476 | NCR | Exposed Linkages on __ Damper Face Mounting Couplings |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-07-05 | 2017-08-31 14:36 | 57 | 2017-04-06 10:08 | Mechanical - Heating Ventilation & Air Conditioning | 2000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Cover plate missing exposing linkages on __ Damper Face Mounting Couplings
| 05SY - Systemwide | Cxxx-NCR-000477 | NCR | Fire Main UTX Pipe dislodged Stepney Green Carvern WB |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-05-24 | 2017-05-24 16:14 | 0 | 2017-04-07 11:33 | Mechanical - Mechanical Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The Stainless Steel UTX tunnel fire main pipe at Stepney Green WB cavern was dislodged during concrete pouring and has now risen approximately 20mm off the tunnel wall. The UTX pipe was mounted on concrete “mars bars” to allow concreting continuity around the pipe and to be cast in situ. This can be seen in the attached report (prior to pour) and also shows timber spacing’s used on wall surfaces, to allow flanged sections to be bolted. After the concrete was poured, the UTX pipe rose and can be seen in the attached pictures.
| 05SY - Systemwide | Cxxx-NCR-000478 | NCR | Whitechapel West Lifting Beam 16009 - Incorrect Placement |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-05-24 | 2017-07-20 15:33 | 57 | 2017-04-07 14:39 | Tunnelling - Tunnelling General | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Lifting beam LB16009 has been installed in the wrong position by __s at WHI-W at level 6. It appears that is has been erected behind the eastbound under platform extract dampers, rendering it useless. See photos attached:
| 05SY - Systemwide | Cxxx-NCR-000479 | NCR | FTS Barbican – Iron cover and frame not installed on slabs W20 & E24 prior concreting |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-07-06 | 2017-07-26 09:53 | 20 | 2017-04-07 17:33 | Track - Track General | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A Polypipe polypropylene frame and 300mm diameter ductile iron cover shall be installed on top of each of 4 no. recessed spring housings within the 4 foot of Barbican slabs at the transition areas. This frame and iron cover were not installed in 8 locations prior to casting the slabs. (4 no. locations on slab W20 and 4 no. locations on slab E24). A void former was in place during the concrete pour and so access to the spring housing is available. However, the void is currently insufficient in size to enable the installation of the polypropylene frame and ductile iron cover.
| 05SY - Systemwide | Cxxx-NCR-000480 | NCR | FTS Barbican – Baseplate dowels protrude concrete surface underneath baseplate HDPE pads |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-01-14 | 2018-01-08 15:01 | -6 | 2017-04-07 17:43 | Track - Track General | 5000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During an inspection of the voids under baseplate pads in FTS Barbican it was identified that some of the plastic dowels protrude up to 6mm from the concrete surface underneath the HDPE pad. The problem occurs consistently every 12 baseplates (both left and right side) which coincides with the length of the temporary rail - implying that this was the location of a fishplate used to connect the temporary rails. Where fishplates are installed, the baseplate clips cannot be installed. Instead, the baseplate is secured to the rail using threaded bars attached to the screw spikes and bolted to a plate on top of the rail. Further investigation is necessary to confirm the root cause and the extents of the issue. It is expected that this same issue is present in FTS Lite were the same method to install the baseplate at the fishplate locations was used – to be confirmed.
| 05SY - Systemwide | Cxxx-NCR-000481 | NCR | FTS Barbican - voids under baseplates |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-07-06 | 2017-05-17 10:01 | -50 | 2017-04-07 17:49 | Track - Track General | 2000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | During the lifting of baseplate pads for inspection of the concrete surface underneath on FTS Barbican it was identified that the maximum percentage of acceptable entrapped air/voids was exceeded on slabs E24, W21, W24, W29, W30, W32, W34 and W35.
| 05SY - Systemwide | Cxxx-NCR-000482 | NCR | FTS Lite and Station - voids under baseplates |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-07-06 | 2017-06-06 13:04 | -30 | 2017-04-07 17:58 | Track - Track General | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the lifting of baseplate pads for inspection of the concrete surface underneath on FTS Lite and Station Eastbound tunnel it was identified that the maximum percentage of acceptable entrapped air/voids was exceeded from slabs E4 to E23. Two or three No baseplates have been checked in these slabs to date. Please see attached some pictures of the concrete surfaces.
| 05SY - Systemwide | Cxxx-NCR-000483 | NCR | __s Lifting Beams Trolley Axels |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-08-31 | 2018-09-13 09:46 | 13 | 2017-04-10 14:54 | Materials - General | 168000 |  | Material | Rework | 1 (>60k) | Complete | Material/Preservation Problems - Other | Completed |  | __s have installed manually operated trollies on various Lifting Beam runways that include a Axel pin/bolt that does not meet the accepted anti-corrosion specification. A list of all affected locations / lifting beams has been attached to this NCR. A Technical drawing showing an exploded view of the trolley and the Axel pin/bolt (item 17) is attached.
| 05SY - Systemwide | Cxxx-NCR-000485 | NCR | FTS Barbican – 7 day compressive strength for slab E25 |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-06-09 | 2017-05-17 10:02 | -23 | 2017-04-10 18:04 | Track - Track General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | The average compressive strength results at 7 days for slab E25 is 31.7MPa, which does not reach the required 35MPa as stated in the ITP
| 05SY - Systemwide | Cxxx-NCR-000486 | NCR | Failed Factory Acceptance Test – Pressure Doors Canary Wharf Station TVS |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-10-02 | 2017-10-09 11:06 | 7 | 2017-04-18 14:08 | Mechanical - Mechanical Engineering General | 3000 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | On Wednesday 29th March 2017, A Factory Acceptance Test was carried out for the Single Leaf Pressure Doors at Canary Wharf Station TVS. The test was carried out in line with the FAT Procedure (Cxxx-__-O1-GMS-CR143-50027) which states doors are to be tested up to 3kPa (in 0.5kPa increments). During the test, it was witnessed that the testing rig to facilitate this test, did not manage to achieve the 3kPa required to carry out this test. Furthermore, it was also witnessed that the seals within the doors did not manage to maintain the seal at approximately 1.5kPa (visualised by smoke machine). Because of this reason, __ are to reject the results of this Factory Acceptance Test for single Pressure Doors.
| 05SY - Systemwide | Cxxx-NCR-000487 | NCR | TVS Dampers delivered and installed with the Factory Acceptance Test (FAT) Report at a Code 3 decal. |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-06-15 | 2017-06-01 14:29 | -14 | 2017-04-19 11:41 | Mechanical - Mechanical Engineering General | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | A planned Crossrail surveillance was undertaken on 16th February 2017 to look at TVS Damper installation at Canary Wharf Station. Post surveillance the FAT report was provided; Cxxx-__-H-RGN-CRG03-50082 (Rev 1) dated May 2016 refers. On checking eB it was identified that the FAT report was at a Code 3 decal. A Code 3 decal stands for ‘Not Accepted. Revise and resubmit. Work may not proceed’. ITP *50084 inspection number 6.1.6 states a requirement for ‘FAT of Dampers’ at a frequency of ‘Prior to Delivery to Site’ with the parameter ‘Code 1 FAT Report’. This is also a Hold Point for ‘Quality Control’ and ‘__ Quality Assurance’. Based on this, the damper installation is at risk until the FAT is deemed acceptable. The fact that the Dampers had been delivered and installed in the works highlights a significant breakdown in the management of the FAT The Works Information is clear in that FATs shall be satisfactorily completed before any shipment to site. Works Information Vol 2B Part 28; 28.2.2.1 Phase 1 - Factory Acceptance Tests states “Factory acceptance tests (FATs) shall be satisfactorily completed by the Contractor before shipment to the Site and/or the Working Areas of any item of Plant and Materials in order to verify that it and its components are fit for its or their intended use and otherwise comply with the Works Information. The factory acceptance tests are carried out by the Contractor, and in accordance with the Contractor’s accepted method statements, quality plan and test procedures.”
| 05SY - Systemwide | Cxxx-NCR-000488 | NCR | Offsite welding inspection records for lifting beam works not alignment with accepted ITP |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-09-04 | 2017-08-10 10:53 | -25 | 2017-04-19 12:10 | Structural Engineering - Structural Engineering - General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | A planned Crossrail surveillance was undertaken on 16th March 2017 to look at Lifting Beam and Gantry installation at TCR Station. As part of the surveillance, __/__ were requested to provide off-site fabrication records (welding and galvanizing) for steelwork installed at GYB +4. Post surveillance, __ provided ‘Weld Plan’ records as evidence of this (see attached). On checking it was identified that the Weld Plan records being generated are not in alignment with those deliverable records included within approved ITP Cxxx-__-O4-ITP-CRG03-50028. The ITP refers to the completion of check sheet QAD007 for these inspections. In addition, the Weld Plan records provide no traceability to the steelwork which they refer to. This was queried with __ and __ with no response provided after multiple requests spanning 5 weeks. NCR raised from surveillance to ensure rectification.
| 05SY - Systemwide | Cxxx-NCR-000489 | NCR | Pull test training records not provided for operatives as requested during a CRL surveillance |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-08-09 | 2017-07-20 11:28 | -20 | 2017-04-19 12:14 | Structural Engineering - Structural Engineering - General | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | A planned Crossrail surveillance was undertaken on 16th March 2017 to look at Lifting Beam and Gantry installation at TCR Station. Pull test records were made available which showed pull testing had been carried out by the following operatives: - S.Otibicu - T.Vasiliavsia It was stated that __ training had been carried out for all __ Operatives. A request was made for these training records. Following multiple post surveillance requests spanning 5 weeks, no evidence of training records has been provided. Works Information Vol 2B Part 20.8 states: The Contractor shall ensure that staff nominated for undertaking sampling, inspection and testing activities are appropriately trained and competent to carry out the particular activities to which they have been assigned. The Contractor shall maintain records of training and competence and make such records available to the Supervisor for inspection upon request. As none have been provided, it could not be verified that those who undertook testing were competent to do so. As __ have failed to supply the post surveillance records as required by the surveillance, this non-conformance was raised.
| 05SY - Systemwide | Cxxx-NCR-000490 | NCR | Runway beam steelwork strengthening plate fabrication inconsistencies at TCR |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-09-19 09:40 | 2017-08-22 09:43 | -28 | 2017-04-19 12:20 | Structural Engineering - Structural Engineering - General | 500 |  | Manufacturing Defect | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Not Defined | Completed |  | A planned Crossrail surveillance was undertaken on 16th March 2017 to look at Lifting Beam and Gantry installation at TCR Station. On checking the works it was identified that plates at GYB level +4 had been fabricated with no hole in the centre (see pic 1), whilst plates at WTH level -2 showed holes of varying diameter in the centre (see pic 2). A post surveillance request was made for clarification. It was stated that fabrication at GYB level +4 was completed by Lifting Systems Ltd whilst WTH level -2 and current steelwork fabrication is completed by __. As to the purpose of the hole, the following response was provided by __ and __, and forwarded by Dave Beggs (__) to __ via email; “It is good practice to provide ‘blow holes’ in fabrications which include seal welding. The fabricator we used for the majority of the steelwork at the GYB did not specify or recommend these in the fabrications, however the fabricator we used for all the WTH steelwork did. Therefore 10mm holes were drilled to allow air to escape during the galvanising process, where the beams are heated to circa 450oC. We are advised that failure to provide blowholes may result in deformation of the structure or damage to the weld”. Following review of this response, __ and __ were requested to provide evidence of inspections/assessments for the Lifting Systems Ltd plates to assure that no damage has been encountered (including potential for latent defects), and the design life will be met where holes have not been drilled. This request was made as all weld inspections are completed pre galvanizing, whereby __ response states failure to provide holes may result in defects during the galvanizing process. Following multiple requests, no information has been provided. As __ have failed to supply the post surveillance information as required by the surveillance, and due to the inconsistencies with the fabrication at TCR, this non-conformance was raised.
| 05SY - Systemwide | Cxxx-NCR-000491 | NCR | Sump Cover Installation commenced without approved RAMS |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-06-26 | 2017-06-13 08:39 | -13 | 2017-04-27 10:09 | Mechanical - Mechanical Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Works began on CP18 Sump Cover installation before an accepted Code 1 Method Statement (Cxxx-__-O1-GMS-CRG03-50029) was in place.
| 05SY - Systemwide | Cxxx-NCR-000492 | NCR | Installation of Sump Covers commenced without approved ITP |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-06-26 | 2017-05-30 14:39 | -27 | 2017-04-27 10:10 | Mechanical - Mechanical Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Installation of Sump covers in CP18 commenced without a code 1 ITP (Cxxx-__-O4-ITP-CRG03-50089).
| 05SY - Systemwide | Cxxx-NCR-000493 | NCR | Manufacture of Sump Covers without approved Manufacturing ITP |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-06-26 | 2017-05-02 13:48 | -55 | 2017-04-27 10:12 | Mechanical - Mechanical Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Manufacturing of sump cover components for CP18 commenced before an accepted code 1 Manufacturing ITP (Cxxx-__-O4-ITP-CRG03-50088) was in place.
| 05SY - Systemwide | Cxxx-NCR-000494 | NCR | Bending Test BT35 failed to achieve minimum deflection. |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-06-21 | 2017-06-07 10:16 | -14 | 2017-04-25 17:13 | Track - Welding | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | The test affects the production of the w/c 20/02/17: 14 welds done between chainages 11400-12010 EB (Canary Wharf to STG EB). The results provided for BT35 are: - Minimum load: 1719 kN --> compliant - Minimum deflection: 15.83mm --> non-compliant - Loading rate: 94 kN/s --> compliant
| 05SY - Systemwide | Cxxx-NCR-000495 | NCR | Cracked bearer No 43 . on Turnout C7 |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-11-29 | 2017-11-17 08:56 | -12 | 2017-04-25 17:22 | Civil - Track | 5000 |  | Manufacturing Defect | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | WHI Cavern Eastbound. Bearer 43 of C7 turnout. Crack on top of the bearer from dowel top dowel.
| 05SY - Systemwide | Cxxx-NCR-000496 | NCR | TFM Section Valve Handwheel |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-09-01 | 2017-09-11 12:17 | 10 | 2017-04-27 09:57 | Mechanical - Mechanical Engineering General | 2500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Section valve labelling on the handwheels is the wrong way around. Denoted direction to close the valve actually opens the valve. The correct direction is currently indicated only by the flag position.
| 05SY - Systemwide | Cxxx-NCR-000497 | NCR | Canary Wharf Station TVF Steelwork Installation Design Changes |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-10-12 | 2017-10-12 11:58 | 0 | 2017-04-28 15:45 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | During the installation of the TVF steelwork at the Canary Wharf station east and west shafts, subcontractor __ used a different revision (J) of the accepted drawing Cxxx-__-H-DWG-CR143-50030 (H) (East) & Cxxx-__-H-DWG-CR143-50018 (G) (West) which factors a potential deviation from the CRL accepted drawings. The new drawings were not submitted to Crossrail for review and acceptance prior to it being used for the works. All of the torque & pull test parameters differ from the accepted design.
| 05SY - Systemwide | Cxxx-NCR-000498 | NCR | Deviation from Accepted Tunnel Ventilation Fan SteelworkDesign |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-04-12 | 2018-04-10 06:44 | -2 | 2017-04-28 16:45 | Systems - Ventilation and Pressure Relief | 1000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | During inspection of the installed fixings for the tunnel ventilation fan support steelwork at both east and west shafts of the Canary Wharf station, it was identified that the fixings were torque tested to parameters which differ to what is stated in the accepted design Cxxx-__-H-DWG-CR143-50030 (H) (East) & Cxxx-__-H-DWG-CR143-50018 (G) (West). Torque of 948Nm and 881Nm were applied to the M24 bolts for the fixed connections and sliding connections respectively as opposed to the 1.22kNm & 1.136kNm M24 torque parameter stated in the accepted drawing.
| 05SY - Systemwide | Cxxx-NCR-000499 | NCR | TVS Steelwork Deviation from Design - M22/M24 anchors |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-11-22 | 2017-11-03 11:16 | -19 | 2017-05-03 13:14 | Structural Engineering - Steel Member | 2500 |  | Manufacturing Defect | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | A combination of M22 & M24 has been used for the bracket to steelwork connection , which is contrary to the installation drawing that indicates M24 bolts (Cxxx-__-H-DWG-CR143-50030).
| 05SY - Systemwide | Cxxx-NCR-000501 | NCR | TVS Steelwork Deviation from Design - Nut/Half Nut installed |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-09-12 | 2017-08-24 14:36 | -19 | 2017-05-03 13:31 | Structural Engineering - Bolted Connections | 2000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | TVF steelwork design for the fan trolley/track above the steelwork shows a single bolt and nut arrangement, whereas half & full nuts have been installed (Cxxx-__-H-DWG-CR143-50030 / Cxxx-__-H-DWG-CR143-50018)
| 05SY - Systemwide | Cxxx-NCR-000502 | NCR | No Manufacturing ITP for Evacuation Walkway Extruded Aluminium Components |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-09-15 | 2017-08-18 13:41 | -28 | 2017-05-04 15:22 | Tunnelling - Walkways | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | The aluminium components that are manufactured by __ have no manufacturing ITP (at any stage of readiness) submitted to __/CRL for acceptance despite numerous requests. These components include (but are not limited to) the Planks, Plank Joiners, Kick Plate, Hand Rail. A complete list of standard extruded components and their drawings are listed in the CAT II Check Certificate (Cxxx-__-Y-CER-CRG03-50014). Some of these components have now been test fitted in the Thames tunnel between the Plumstead portal and Woolwich Station.
| 05SY - Systemwide | Cxxx-NCR-000503 | NCR | Whitechapel Westbound Tunnel Isolation Damper Module – Deformed High Temperature Switch Box supporting steelwork |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-08-17 | 2017-09-27 10:36 | 41 | 2017-05-04 15:03 | Mechanical - Heating Ventilation & Air Conditioning | 3000 |  | Damaged | Reject | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper handling of material | Completed |  | On 3.5.17 the __ on site received delivery of some Tunnel Isolation Damper Modules. Upon removal of the surrounding packaging it was noticed that module no.4 of 9 was deformed. It appears that a considerable force has impacted the high temperature switch box itself (see photos) causing the supporting steelwork of the switch box to deform.
| 05SY - Systemwide | Cxxx-NCR-000504 | NCR | Missing Track Authorisation for Concreting Forms |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-05-30 | 2017-05-25 15:36 | -5 | 2017-05-10 09:24 | Track - Track General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Through site surveillance and compilation of SAF evidence it has been identified that some Authorisation for Concreting checksheets (QCR6) are incomplete in some cases in the area between Victoria Dock Portal and Stepney Green as per attached matrix.
| 05SY - Systemwide | Cxxx-NCR-000505 | NCR | FTS - Damaged UTX at W9 |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-06-28 | 2017-06-06 13:06 | -22 | 2017-05-04 16:49 | Track - Track General | 1000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During W9’s demolishing works, one of the under track crossing pipes has been damaged on the left hand side towards high chainage at tunnel ring No 2692. Please see the attached pictures.
| 05SY - Systemwide | Cxxx-NCR-000506 | NCR | ROC components batch numbers haven’t been recorded |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-08-16 | 2017-05-11 09:01 | -97 | 2017-05-08 10:40 | Over Head Line Electrification - Over Head Line Electrification General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | ROC components batch numbers haven’t been recorded so far. Location: Plumstead to Stepney Green and from Pudding Mill Lane to Stepney Green (all supports, cantilevers and rigid bar installed). Also Cantilevers already assembled in the yard at Plumstead.
| 05SY - Systemwide | Cxxx-NCR-000507 | NCR | Damaged Sleepers due to Machine Derailment |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-09-29 | 2017-10-02 08:24 | 3 | 2017-05-09 10:31 | Civil - Track | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Some Standard Track Slab S312 sleepers are damaged due to a machine derailment (chipped concrete blocks). In some of them, the angled guide plate is also damaged. Reinforcement has not been exposed. See attached a report.
| 05SY - Systemwide | Cxxx-NCR-000508 | NCR | Sleepers Sateba S312 S3 installed instead of Sateba S312 S1 |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-10-06 | 2017-10-06 14:01 | 0 | 2017-05-09 11:01 | Civil - Track | 5000 |  | Planning | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | 8 first rows of sleepers Sateba S312 S3 from ch 22987 up to ch 22981.5 (transition area) have been installed instead of Sateba S312 S1, internal pads have been changed for pads of Sateba S312 S1. As per the CPS for STS Sleepers ,difference between S3 and S1 is just the pads width/stiffness. Email confirmation from Sateba technical department attached. Photograph attached.
| 05SY - Systemwide | Cxxx-NCR-000509 | NCR | Sleepers Sateba S312 without sealant at Plumstead Portal |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-09-26 | 2017-10-12 12:03 | 16 | 2017-05-09 11:17 | Civil - Track | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | During QC inspection previous to the concrete pour, have been noted that several numbers of sleepers had not proper sealant fixed to the booted sleepers (due to long time sleepers installed at PLU Portal).In order to avoid entrance of concrete to the boots, protection tape has been installed. Proper sealant to be installed after concrete pour(Korapop as per MS Reparation of Twin Block Sleepers). .
| 05SY - Systemwide | Cxxx-NCR-000510 | NCR | Tunnel Isolation Dampers at TCR GYB installed in incorrect position |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-02-28 | 2018-02-13 10:56 | -15 | 2017-05-09 14:30 | Mechanical - Mechanical Engineering General | 3000 |  | Incorrect Installation | Reject | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | During a recent visit to TCR GYB it was noted that the Tunnel Isolation Dampers have been installed in a manner that is not in accordance with the accepted design drawings Cxxx-__-M-DDA-N105_WS093_4-10005 and Cxxx-__-M-DDB-N105_WS093_Z-10002 (it is also noted that drawing Cxxx-__-M-DDA-N105_WS093_4-10005 shows that there is a wall missing beside the Eastbound and Westbound TIDs, however the Westbound wall has been constructed). The TID’s have been located forwards of the aperture designed to encapsulate the steelwork which causes future problems for airtight sealing of the TID’s and both are now situated directly under the attenuators. A sketch of the TID has been attached for reference.
| 05SY - Systemwide | Cxxx-NCR-000512 | NCR | Mast installation commenced prior to acceptance of mast foundation certification |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-08-08 | 2017-05-17 09:46 | -83 | 2017-05-10 15:57 | Over Head Line Electrification - Over Head Line Electrification General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | 1. Mast installation commenced prior to the acceptance of mast foundation certification 2. Masts have been installed at foundation XR/14/730, XR/14/731 and XR/14/732 at Pudding Mill Lane Portal
| 05SY - Systemwide | Cxxx-NCR-000513 | NCR | Mast installation commenced prior to acceptance of mast foundation certification-Plumstead Portal |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-08-08 | 2017-05-17 09:48 | -83 | 2017-05-10 16:09 | Over Head Line Electrification - Over Head Line Electrification General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | 1. Mast installation commenced prior to the acceptance of mast foundation certification 2. Masts have been installed at Pile foundations XRS/22/001, XRS/22/002, XRS/22/003 AND Pad foundations, XRS/22/005, XRS/22/006, XRS/22/007, XRS/22/008, XRS/22/009, XRS/22/011, XRS/22/012
| 05SY - Systemwide | Cxxx-NCR-000514 | NCR | OHLE piles installed out of tolerance |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-09-12 | 2017-09-27 10:38 | 15 | 2017-05-15 09:35 | Over Head Line Electrification - Over Head Line Electrification General | 5000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | In Westbourne Park XRW/01/005RA & XR/00/008R. The piles installed out of tolerance in WBP. OHLE piles should have been installed to Easting & Northing co-ordinates as set out by the surveyor.
| 05SY - Systemwide | Cxxx-NCR-000515 | NCR | LF3 Separation Connaught East Brickwork EB |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-08-23 | 2017-06-07 10:19 | -77 | 2017-05-15 18:26 | Electrical - Cable Management | 6000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Leaky Feeder 3 has been installed in the East brickwork of Connaught tunnel (eastbound) with approximately 75mm separation to the lighting tray (T1), instead of the required minimum of 150mm.
| 05SY - Systemwide | Cxxx-NCR-000516 | NCR | Damage to (Cxxx) Cable label |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-08-14 | 2017-06-19 13:46 | -56 | 2017-05-16 13:28 | Communications and Control Systems - Fibre Optic Network | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | This defect was observed by Ian Mathers (__ Cxxx). This damaged cable label is located on a coil of cable in the FOSCC-1 near to the Plumbstead portal. The damage was caused during the installation of the cable. The defect was not picked up at the time of installation and therefore was not corrected at the time.
| 05SY - Systemwide | Cxxx-NCR-000517 | NCR | Concrete spread on the rails |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-09-26 | 2017-08-01 15:31 | -56 | 2017-07-28 09:18 | Civil - Civil Engineering General | 1000 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | It’s been brought to attention that the ROC rails loaded on OH2 stillages and the wagons as well were contaminated with concrete splatter and snots.
| 05SY - Systemwide | Cxxx-NCR-000518 | NCR | UTX missing for earthing and bonding works |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-08-30 | 2017-08-07 11:16 | -23 | 2017-06-16 16:25 | Electrical - General | 1000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Some UTXs missing for bar to bar earthing connection between Plumstead to Woolwich Station for various locations.
| 05SY - Systemwide | Cxxx-NCR-000520 | NCR | M&E ITP not updated for drilling |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-11-15 | 2017-08-15 14:13 | -92 | 2017-07-18 09:27 | Over Head Line Electrification - Over Head Line Electrification General | 1000 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Manual drilling in bored tunnel. OHLE was using M&E drilling ITP by Drilling Rig. * However, it has been decided to do the drilling manually instead of M&E's drilling rig. Before starting this activity, the ITP should have been reviewed to ensure that the works were covered. But this didn’t happen and the manual drilling activity started with the same ITP which used for the Drilling Rig.
| 05SY - Systemwide | Cxxx-NCR-000521 | NCR | TCR TID Incorrect Bolt Hole Location |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-09-27 | 2017-10-11 16:06 | 14 | 2017-05-16 15:55 | Materials - General | 3000 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Verification Problems - Inspection points not adequate | Completed |  | Upon installation of the TID's at TCR West it was found that the drilled holes in the __ Dampers were not as per the accepted design that was submitted for fabrication. The 4 corner TID's on both the East and West Bound have nine holes per damper that are in the incorrect position. Pictures of the damper hole pattern, drawing and upper parallel flange channel have been attached for reference.
| 05SY - Systemwide | Cxxx-NCR-000522 | NCR | Rails stored on sleeper tie bar |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-07-21 | 2017-05-30 14:43 | -52 | 2017-05-22 10:09 | Track - Rails and Sleepers | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Some rails have been found to be stored directly on the S312 sleeper tie bars in Stepney Green (see attached picture).
| 05SY - Systemwide | Cxxx-NCR-000523 | NCR | Track Switch & Crossing handling |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-08-07 | 2017-08-18 13:24 | 11 | 2017-06-08 12:39 | Track - Turnouts | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | It has been reported that some switches were being lifted using chains directly wrapped around the rails.
| 05SY - Systemwide | Cxxx-NCR-000524 | NCR | FAR-W TID-E, Incorrectly sized Pre-formed Damper holes on Columns B1 & B4 (__) |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-08-30 | 2017-09-11 09:00 | 12 | 2017-05-23 10:56 | Systems - Ventilation and Pressure Relief | 1000 |  | Manufacturing Defect | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The pre-fabricated holes, used to fix the damper modules to the steelwork, on columns B1 & B4 are the incorrect size. The damper holes are 22mm on these columns.
| 05SY - Systemwide | Cxxx-NCR-000525 | NCR | More than 4 open washers installed |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-08-31 | 2017-07-26 14:39 | -36 | 2017-05-23 13:56 | Over Head Line Electrification - Over Head Line Electrification General | 5000 |  | Incorrect Installation | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | More than 4 open washers installed 16148 CNW-VDP E/B 16315 CNW-VDP E/B 20955 PLU-NWP W/B 21053 PLU-NWP W/B. Maximum 4 open washers can be installed.
| 05SY - Systemwide | Cxxx-NCR-000526 | NCR | Cross Passage Fire Main Clash |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-08-30 | 2017-09-11 12:22 | 12 | 2017-05-23 14:44 | Mechanical - Piping | 5000 |  | Design | Repair | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | The cross passage fire main brackets have been installed at CP17 & CP18 using the walkway datum level; however are now supporting the pipework in front the pumped drainage ducting, which leaves insufficient space for the sump pipework to enter the cross passage. Refer to attached SOB for further details. There is a risk that similar issues may occur at all Cross Passages with sumps.
| 05SY - Systemwide | Cxxx-NCR-000527 | NCR | Drop Tubes clash with M&E Trays in PML Portal Eastbound |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-09-20 | 2017-07-26 14:10 | -56 | 2017-05-23 15:41 | Over Head Line Electrification - Over Head Line Electrification General | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Drop Tubes clash with M&E Trays in Pudding Mill Lane Portal Eastbound. The OHLE supports cannot be installed as they clash with the M&E tray.
| 05SY - Systemwide | Cxxx-NCR-000528 | NCR | Holes drilled with the wrong offset at Canary Wharf Station |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-09-20 | 2017-08-10 09:23 | -41 | 2017-05-23 15:55 | Over Head Line Electrification - Over Head Line Electrification General | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Holes drilled with the wrong offset at Canary Wharf Station Eastbound. The drilling positions must be set out following the offsets indicated in the survey spread sheet.
| 05SY - Systemwide | Cxxx-NCR-000529 | NCR | Cantilever type swapped in overlap |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-09-20 | 2017-07-27 11:21 | -55 | 2017-05-23 16:03 | Over Head Line Electrification - Over Head Line Electrification General | 2000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Cantilever type swapped in overlaps: 21349 PLU-NWP W/B 19817 PLU-NWP W/B Installation hasn't been done as per drilling data book. The cantilevers types are not correct in the overlaps indicated above. In consequence, the design stagger is not achievable.
| 05SY - Systemwide | Cxxx-NCR-000530 | NCR | Holes in no drilling zone in Eastbound |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-09-20 | 2017-08-10 09:28 | -41 | 2017-05-23 16:17 | Over Head Line Electrification - Over Head Line Electrification General | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Holes in no drilling zone. -4 locations between CWS and VDP Eastbound -1 location between STG and PML Eastbound
| 05SY - Systemwide | Cxxx-NCR-000531 | NCR | Traction Earth Bonding |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-09-01 | 2017-07-27 11:24 | -36 | 2017-05-24 12:40 | Electrical - Earthing & Bonding | 25000 |  | Workmanship | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | On 22nd May 2017, a routine inspection was conducted on the Contractors traction bonding installation between Plumstead and Woolwich Station, a number of non-conformities were observed at multiple locations along the route which had not been entered into the PTR system in accordance with the requirements contained within Works Information Volume 2B, Part 20.8 Inspection and Testing. Works Information Volume 2B – Part 20 – Quality Management 20.8 Inspection and Testing ‘The Contractor shall implement QSPs to verify conformance with the Works Information. The Contractor’s verification is accomplished by examinations, tests, measurement and inspection and by verifying records including those of his Subcontractors and suppliers. Unless otherwise accepted by the Supervisor, the Contractor shall enter each NCR, including sub-contractor NCRs, in the PTR system.’ ‘Nominated Contractor personnel, accepted by the Supervisor, shall produce a schedule of inspections to identify Defects and shall raise snagging lists or outstanding works lists at appropriate inspection and acceptance stages to record work that has not been completed correctly or which is outstanding. Defects identified during the inspection and included in these lists shall also require NCRs to be raised.’ From the inspection carried out on 22nd May 2017, the following non-compliances have been observed at multiple locations along the route (see attached photographs for further details) - Long barrelled lugs have been over crimped, resulting in splayed cables ends - Unclipped cables - No LSZH heat shrinking tubing - Exceedance of bending radius on cables - Cables not installed in the prescribed CMS route - Untorqued and loose rail connections - Loose Spider Plates - Improperly installed HPS-1R fixings throughout the trace. Following the inspection, it was ascertained that the traction bonding installation was carried out during February 2017, a review of PTR, the Contractors ITP QCR’s and ROWL database did not contain the items identified above.
| 05SY - Systemwide | Cxxx-NCR-000532 | NCR | Design life of TVS Attenuators might not be met in several locations |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-05-02 | 2018-04-10 06:54 | -22 | 2017-05-25 16:45 | Mechanical - Heating Ventilation & Air Conditioning | 50000 |  | Design | Repair | 2 (6-60k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Through review and investigation of experience on the temporary tunnel ventilation, juxtaposed to our complete system design (including the suppliers post gate design), __ that acting together there is a risk that design life of the components in some specific arrangements, may not be met, and as such there is a non-conformance with the WI.
| 05SY - Systemwide | Cxxx-NCR-000533 | NCR | Cracked bearer No 34 . on Turnout C6 |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-03-30 | 2018-01-18 17:06 | -71 | 2017-05-26 08:48 | Civil - Track | 5000 |  | Supervision/Management | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Fisher Street Shaft, Eastbound. Bearer No 34 of C6 turnout. Crack on top of the bearer through the internal fastenings. Additional cracked bearer identified after QC Inspection. Bearer no 620 (Picture attached)
| 05SY - Systemwide | Cxxx-NCR-000534 | NCR | C5/C6 Deviated lines – designed cant not achievable within long bearers |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-09-03 | 2017-06-07 10:26 | -88 | 2017-05-26 10:17 | Civil - Track | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | Deviated Line of C5 : CH 22 -34 Deviated Line of C6 : CH 108-153 Cant of installed deviated track not as designed. However due to the grade of 2.5% it is not possible to set cant perpendicular to track C/L at 0 on both the through and deviated routes. This induced cant is calculated at around 3-6mm.
| 05SY - Systemwide | Cxxx-NCR-000535 | NCR | Woolwich West Box - Tunnel Isolation Dampers not fitting together due to clash between limit switch and linkage cover |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-08-30 | 2017-07-24 10:28 | -37 | 2017-06-01 07:14 | Systems - Ventilation and Pressure Relief | 2500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | 2 No of the Tunnel Isolation Dampers in Woolwich West box Eastbound (provided by __) delivered on site do not fit onto the previously installed steelwork. This is due to a clash between the limit switch and the linkage cover plate on the adjacent damper.
| 05SY - Systemwide | Cxxx-NCR-000539 | NCR | WOO-W Tunnel Side Attenuators Splitters not fitting in the room |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-11-20 09:49 | 2018-01-05 15:43 | 46 | 2017-06-01 09:45 | Systems - Ventilation and Pressure Relief | 5000 |  | Design | Repair | 3 (3-6k) | Complete | Verification Problems - Inspection points not adequate | Completed |  | The last two splitters in the installation of the Tunnel Side Attenuator Bank in Woolwich West do not fit into the room.
| 05SY - Systemwide | Cxxx-NCR-000540 | NCR | WOO-W Tunnel Side Attenuators Floor support different from approved drawing |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-10-12 | 2017-10-10 14:17 | -2 | 2017-06-02 14:58 | Systems - Ventilation and Pressure Relief | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | The Tunnel Side Attenuators floor support have been delivered and installed on a design that is different than the one approved.
| 05SY - Systemwide | Cxxx-NCR-000541 | NCR | Out of spec flow table test result for an STS pour |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-08-29 | 2017-07-27 11:25 | -33 | 2017-06-02 16:19 | Track - Track General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | One of the concrete loads used on 01/06/2017 between chainages 4065 and 4128 for an STS pour was tested as 530 mm – 10 mm out of tolerance from the range set in the ITP (540-640 mm). The details of the load are as follows: mix reference: M5-2R, concrete delivery note: 365495, time of test: 10:17, batch time: 09:47. __ decided to use the load as it was assessed that it would be on no detrimental effect to the permanent works. The assessment was based on the criteria below. • Marginally out of tolerance flow table test (10 mm) • Confirmation from __ that the batching quantities were within tolerance prior using the load • The load would be mixed with another load already in the shuttles train • The load was less than one hour old from batching time when tested. • The mix contains a retarder and superplasticizer, the workability time for this mix is 5.5 hours 4 No cubes have been taken from this load.
| 05SY - Systemwide | Cxxx-NCR-000542 | NCR | Cracked bearer no 65 at C10 (Stepney Green) |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-12-22 | 2017-08-02 15:39 | -142 | 2017-06-05 11:05 | Civil - Track | 5000 |  | Workmanship | Reject | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | After a Quality Inspection at C10 Turnout, It was noticed that bearer no65 has a crack (1.5mm width aprox) along the check rail baseplate. (Pictures attached)
| 05SY - Systemwide | Cxxx-NCR-000543 | NCR | Damages S312 sleeper’s tie bars due to MPV derailment |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-12-22 | 2017-08-02 15:42 | -142 | 2017-06-05 11:36 | Civil - Track | 5000 |  | Damaged | Rework | 3 (3-6k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | From VDP to CWS – Ch 15885. EB 5no of S312 Sleepers Tie Bars have been damaged due to the MPV derailment.
| 05SY - Systemwide | Cxxx-NCR-000544 | NCR | Fire Hydrant Bolt Clash |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-07-27 | 2017-07-06 12:58 | -21 | 2017-06-07 12:21 | Mechanical - Mechanical Engineering General | 2000 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | During installation of the Fire Hydrants in Thames Tunnel a clash between the head of the hydrant bolts and the hydrant branch flange plate was observed. This affects 4no. bolts per hydrant. To enable installation to continue, the bolts were inverted, however it is not possible to fully tighten the nuts without the end of the bolt clashing with the flange plate. See attached photos for detail.
| 05SY - Systemwide | Cxxx-NCR-000545 | NCR | CMS Fixing Arrangement CWS EB |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-11-30 | 2017-11-22 11:00 | -8 | 2017-06-08 15:22 | Electrical - Cable Management | 10000 |  | System Defect | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | At Canary Wharf Station EB Cxxx has installed 1.6m length directly wall mounted __ supports into the cast-in __ channel of the station contractor using 2No. M12 Hex bolt and __ Channel nuts in order to hold T8 ladder T7 tray and T6 tray. It has been observed that although the channel nuts have been fixed in tension, slight differences between the __ & __ designs mean that channel nuts do not fully engage (ie the grooves in the channel nut do not bite into the edge of the Channel). Therefore there is a risk that, over time, vibration from running trains could result in loosening of the channel nuts. Risk to the current install in the short term is considered negligible as the fixings are held in tension and not exposed to any significant vibration.
| 05SY - Systemwide | Cxxx-NCR-000548 | NCR | TCR-E UPED Support Steelwork - M16 anchors used |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-09-27 | 2017-06-22 09:07 | -97 | 2017-06-19 15:36 | Systems - Ventilation and Pressure Relief | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | On the Under Platform Extract Damper supporting steelwork M16 anchors were used where the drawing detailed M20 anchors.
| 05SY - Systemwide | Cxxx-NCR-000549 | NCR | TCR-E UPED steelwork M16 anchors |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-08-01 | 2017-06-22 09:12 | -40 | 2017-06-13 16:16 | Systems - Ventilation and Pressure Relief | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | M16 anchors were used instead of M20 anchors.
| 05SY - Systemwide | Cxxx-NCR-000550 | NCR | TG WB Unprotected Stainless Steel Fire Main UTX |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-10-17 | 2017-08-09 08:39 | -69 | 2017-06-14 09:10 | Civil - Civil Engineering General | 5000 |  | Supervision/Management | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | During a joint IRN inspection (CRL & __ Cxxx) of the Cable Management Systems installed within Stepney Green Cavern West Bound, it was noted that the Stainless Steel Fire Main UTX hasn't been adequately protected at each bolted flanged coupler when exiting the primary concrete and has been left with open ends unprotected and exposed to contamination and damage (refer to attached photos). Early investigations have revealed that asset protection used by the M&E site team may have been removed at STG WB during a concrete pour. It has transpired that the pipe work team protected the pipe after the installation (see attached for an example) and that the protection was most likely removed during the pour (We’ve already raised NCR 477 to capture the fact that the pipe has moved). Closer inspection of the Stainless Steel Fire Main revealed that contamination has indeed occurred at one end and is visible as a accumulated trail of dust and debris that falls approximately 2m into the pipe before coming to rest against a plastic bag that contains dust masks! The presence of contaminant material within the Fire Main if unidentified and left could impact the correct operation of the system and lead to valve leakage due to valve seats not closing fully due to the ingress of dust or to cause valves to become blocked. Also of major concern is the dried grout slurry that has been left over the end of the bolted flange coupler face surface, this has the potential to effect the seal of the flange as any presence of dirt or grit could adversely effect the ability of the gasket to conform and seal correctly around the flange causing the joint to fail under pressure. Additionally when it is know that there is a risk that foreign contaminations can be introduced to assets by work activities, then these risks are to be identified and suitable control measures allowed for during planning and incorporated into the RAMS / SSOW. __ are to action accordingly and advise CRL.
| 05SY - Systemwide | Cxxx-NCR-000551 | NCR | Damaged Direct Fix Fastening (Baseplates) - Connaught |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-09-15 | 2017-09-15 13:51 | 0 | 2017-06-14 14:00 | Track - Track General | 5000 |  | Material | Reject | 3 (3-6k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | Connaught Tunnel EB – 18186 to 18735 EB The part of the baseplate holding the T bolt of the clip was found broken after torqueing to final torque several locations: approx. 20 baseplates within the chainages mentioned before.
| 05SY - Systemwide | Cxxx-NCR-000552 | NCR | PAD - TTD Steel Installation Commencement Using Task Briefing |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-07-28 | 2017-07-21 11:08 | -7 | 2017-06-14 14:05 | Systems - Ventilation and Pressure Relief | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | __ have produced a Code 1 RAMS for the installation of their first phase of steelwork installation at PAD E&W (TID/UPE/TSA/DRD). A initiative for developing a safe system of work prior to works commencing is once a baseline RAMS is established as above, and when you are NOT introducing any new risks, and the content/undertaking of work concerning the RAMS remains the same, a task briefing is developed which supplements and is appended to the base RAMS as above, as was followed for the activity concerning the installation of the TTD steelwork. This task briefing has undergone __ and review and approval and is now signed and executed which formalises the safe system of work and is appended to the existing Code 1 RAMS. It was raised that despite the above, __ are carrying out work activity without a RAMS/SSOW in place.
| 05SY - Systemwide | Cxxx-NCR-000553 | NCR | BOS-E TVS - LB07009-12 clash |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-07-16 | 2017-07-17 07:56 | 1 | 2017-06-16 14:12 | Mechanical - Mechanical Engineering General | 3000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | During the installation of the FID steelwork a clash with the FID lifting beams LB07009-12 was noted. There was an error in the setting out drawing produced by __s that lead to the lifting beam being installed in the wrong position, although the accepted Technical design Cxxx-__-M-DWG-Cxxx-50005 has the correct setting out.
| 05SY - Systemwide | Cxxx-NCR-000558 | NCR | CUH to WOO Bay 12 documentation |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-07-19 | 2017-06-22 09:15 | -27 | 2017-06-21 10:33 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | Quality Verification record / checksheet 7.7 in the ITP Cxxx-__-O4-ITP-CR146-50002 lists HOLD point for CRL. This is now understood to be an error and should state WITNESS point.
| 05SY - Systemwide | Cxxx-NCR-000559 | NCR | Runway Beam impact damage at STG Shaft and Junction Cavern |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-08-30 | 2017-09-11 09:02 | 12 | 2017-06-21 13:58 | Systems - Ventilation and Pressure Relief | 5000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | A Runway Beam suffered slight deformation of the End plate owing to impact damage sustained during installation. Subsequently, a safety stand-down was instructed by the ventilation systems project manager and a review of all scheduled installation methodologies undertaken.
| 05SY - Systemwide | Cxxx-NCR-000560 | NCR | Cracked Bearers on Turnouts: C13, C14, C15 and C16. |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-11-29 | 2017-09-12 08:47 | -78 | 2017-06-22 17:07 | Civil - Track | 2500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Cracked bearers at Open Section’s Turnouts C13, C14, C15, C16. After a Quality Inspection carried out on the open section between Victoria Dock Portal and Connaught West compound, it was noticed that there were some cracks through the bearer’s fastenings (4no through the switch chairs and 24no through the check rails fastenings).
| 05SY - Systemwide | Cxxx-NCR-000561 | NCR | Sump catchpit connection wrongly installed |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-01-12 | 2017-11-23 14:41 | -50 | 2017-06-26 15:18 | Civil - Track | 2500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Farringdom Station WB ch 7+009 Space left during infill concrete process (catchpit) of 400 mm instead of 1200 mm. Wrong level of infill concrete. Photograph attached.
| 05SY - Systemwide | Cxxx-NCR-000562 | NCR | 6Foot PRD Discharge Points blocked by concrete at Victoria Dock Portal |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-12-13 | 2017-10-25 14:29 | -49 | 2017-06-26 15:27 | Civil - Track | 2500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Between Victoria Dock Portal to Custom House Station. Chainages: 16843, 16849, 16859, 16870, 16875 EB. Some Pressure Relief Drainage discharge points are blocked by concrete. (Please find attached Pictures)
| 05SY - Systemwide | Cxxx-NCR-000563 | NCR | FTS Lite & Station and FTS Barbican - Incorrect torque value for shear key bolts stated in ITP |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-12-20 | 2017-11-21 15:46 | -29 | 2017-06-26 16:28 | Track - Track General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The shear key bolts torque value is inconsistent between the ITPs and Gerb's installation manual. Gerb have confirmed the correct value is as per the installation manual, please see the attached email. Please see below the sections of the ITPs which incorrectly state a torque value of 1100 Nm, it should read 710 Nm. • Cxxx-__-R4-ITP-CRG03-50005 Rev 5 - Construction of Floating Track Slab (FTS) Lite & Station - Item 12.2 part c • Cxxx-__-R4-ITP-CRG03-50022 Rev 5 - Construction of Floating Track Slab (FTS) Barbican - Item 9.1 - Item 9.5 part d Note: No torque has been done on site to the incorrect value
| 05SY - Systemwide | Cxxx-NCR-000564 | NCR | Farringdon TVS - ETH - Steelwork VS Lifting Beam Clash - LB12003 Bridge Beam VS ASA Steelwork |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-09-25 | 2017-08-10 10:56 | -46 | 2017-06-27 17:21 | Mechanical - Mechanical Engineering General | 2000 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | Work Area: Farringdon East Ticket Hall TVS Level +1 ASA Steel vs LB12003 Description: The South-easternmost Column of the ASA Steelwork and the Bridge Beam of the Gantry Crane LB12003 Clash preventing the bridge beam from reaching the end stops in their current positions. The bridge beam does not appear to clash with the rest of the columns as they are offset from the south easternmost one providing additional clearance Proposed solution is to move the Crane End stops so that the gantry beam cannot clash with the secondary steelwork. This will reduce the long travel of the crane but will not impact upon the A&M strategy.
| 05SY - Systemwide | Cxxx-NCR-000565 | NCR | __ Connecta Lighting Cable sockets not aligning with the chainage markers |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-05-01 | 2018-04-30 13:19 | -1 | 2017-07-18 13:34 | Electrical - Lighting | 5000 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | The pre-moulded sockets have not aligned with the chainage markers in the Thames Tunnel ranging in deviation of upto 5m away from the chainage marker. This deviation only affects the first sockets on each luminaire string where the lux levels cannot be achieved. This is due to a result of the curvature and gradient of the tunnel. The following areas are affected: Thames Tunnel EB and WB excluding Plumstead Portal to Surface. North Woolwich Portal to Surface and Woolwich Station. Other location to be determined following installation. The separation between the sockets has been maintained in the tunnel. The specific affected areas are at the source end where the first socket in the tunnel will not provide the required lux levels at the tunnels eyes at the SSP’s.
| 05SY - Systemwide | Cxxx-NCR-000566 | NCR | BOS-E FID steelwork manufactured to wrong length |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-11-29 | 2017-08-22 15:49 | -99 | 2017-06-28 12:59 | Materials - General | 5000 |  | Manufacturing Defect | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Further to the commencement of the on-site installation works for the Bond Street East FID steelwork at level -3. It has come to __’s attention that the fabricated columns (mark numbers 101, 104 & 105) are 100mm to long.
| 05SY - Systemwide | Cxxx-NCR-000567 | NCR | Fire Main Anchor Bracket Bolt Depth |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-10-18 | 2017-10-17 08:30 | -1 | 2017-06-28 15:22 | Mechanical - Piping | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Anchor brackets have been installed in the following locations with insufficient thread protrusion of the __ M24x200mm HST3 bolts. Thames Tunnel EB. Anchors in sector 16, ring no.: • 915 • 1016 • 1115 • 1203 • 1451 • 1528 • 1607 Thames Tunnel WB. Anchors in sector 17, ring no.: • 482 • 1714 Anchors in sector 16, ring no.: • 1044 • 1358
| 05SY - Systemwide | Cxxx-NCR-000568 | NCR | Damaged CMS tray CUH WB |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-07-31 | 2017-07-06 13:47 | -25 | 2017-06-29 15:44 | Electrical - Cable Management | 2000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | During a joint inspection of ongoing works at CUH WB, it was noted that tray 6 had been damaged between posts PB03 & PB04.
| 05SY - Systemwide | Cxxx-NCR-000569 | NCR | Installation without an ITP |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-08-09 | 2017-07-11 07:32 | -29 | 2017-06-30 13:11 | Systems - Ventilation and Pressure Relief | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | The installation was completed without a code 1 ITP as required by Volume 2B part 20.8
| 05SY - Systemwide | Cxxx-NCR-000571 | NCR | Damage to TCR-W VSD |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-06-28 | 2019-05-16 12:25 | -43 | 2017-07-03 08:24 | Systems - Ventilation and Pressure Relief | 5000 |  | Damaged | Rework | 3 (3-6k) | Complete | Material/Preservation Problems - Improper handling of material | Completed |  | Upon unpacking one of the VSD's for TCR-W damage was noticed to the VSD casing.
| 05SY - Systemwide | Cxxx-NCR-000572 | NCR | VCS software compliance to BS EN 50128 |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-07-02 | 2018-08-03 12:23 | 32 | 2017-07-05 09:25 | Systems - Ventilation and Pressure Relief | 500 |  | Software | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The Works Information System Safety Plan (CRL1-XRL-O7-GST-CR001-00001) clause 4.5 states 'CRL (as sponsor) and Contractors are required to use recognised safety analysis methodologies based on the processes described in the EC Regulation on Common Safety Methods on Risk Evaluation & Assessment (Ref 22). Examples of recognised methodologies include those shown in the ORR Guidance to the EC Regulation, British Standards BS EN 50126 (Ref 18), BS EN 50128 (Ref19), BS EN 50129 (Ref 20) and BS EN 61508 (Ref 21), LU 1-526 (Ref 3) and in accordance with CRL Hazard Management Procedure (Ref 5)' Works Information TVS Performance Specification (Cxxx-MMD-O8-RSP-CR001-00002) clause 12.12.1 states 'The design of the VCS software shall be completed in accordance with best practice as exemplified in the relevant standards, specifically EN 61508', and TVS Equipment Specification (Cxxx-MMD-O8-RSP-CR001-00003) clause 12.1.1.1 states '[system software shall] conform to the safety integrity level requirements of Part 3 of EN 61508'. The Works Information clearly states that the VCS software can, and should, be developed to BS EN 61508. This is the approach adopted by the VCS Supplier. However __'s System Software Safety Plan (Cxxx-__-Z7-STP-CRG03-50003) makes numerous references to BS EN 50128 but no reference to BS EN 61508. This document has been accepted as 'code 1' by CRL.
| 05SY - Systemwide | Cxxx-NCR-000573 | NCR | PLU - as-built position is out of tolerance |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-08-28 | 2017-07-12 07:35 | -47 | 2017-07-03 15:08 | Civil - Drainage | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following drainage assets were installed out of design position by amount shown below: RR 6.01 RE – 25mm (rodding eye) RR 9.01 RE – 80mm (rodding eye) RR 5.02 RE – 30mm (rodding eye) RR 8.02 RE – 100mm (rodding eye) RR 1.02 MH – 200mm (Manhole RR1.02 MH) is 200mm out of position due to the length of concrete drainage pipe connected to it – installation in “out of tolerance” position allowed rockers and spigots to be installed with correct length. This was verbally agreed at the time of installation by CRL Works Engineer Sergio Pellicer.
| 05SY - Systemwide | Cxxx-NCR-000574 | NCR | PLU - Review of pre-construction activities |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-10-01 | 2017-07-12 07:36 | -81 | 2017-07-03 15:23 | Civil - Drainage | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | During the progressive site assurance it was noted that the following hold point 1.16 of the ITP Cxxx-__-O4-ITP-CR148-50002 Rev 2.0 was not reviewed by CRL representative.
| 05SY - Systemwide | Cxxx-NCR-000575 | NCR | PLU drainage manhole RR 1.02MH failed water test |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-10-03 | 2017-07-07 13:24 | -88 | 2017-07-05 16:41 | Civil - Civil Engineering General | 2000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Manhole RR 1.02MH did not pass water test as per 3.23 of ITP Cxxx-__-O4-ITP-CR148-50002 v2.0
| 05SY - Systemwide | Cxxx-NCR-000576 | NCR | HAS Catchpit Reinforcement Cover |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-03-01 | 2018-02-01 13:24 | -28 | 2017-07-06 09:40 | Track - Track General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | WB Ch 3616 Catchpit – HAS / STS Transition. There is not sufficient concrete between the frame and boot.
| 05SY - Systemwide | Cxxx-NCR-000577 | NCR | BOS-E Attenuator modules manufacturing defect |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-11-09 | 2017-10-17 08:36 | -23 | 2017-07-12 21:34 | Mechanical - Mechanical Engineering General | 500 |  | Manufacturing Defect | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | In accordance to the approved __s drawing Cxxx-__-H-DWG-CRG03-50019 and installation drawing BOS-E - 37580D 143A specifically for the atmosphere side attenuator modules, During the installation it has been identified that the modules for both rows ( front and back ) have been manufactured identical as opposed to mirrored units. As such when the attenuator modules were installed in line with the drawings, the outer flanges did not line up with the subsequent modules at the front and back. Further to the wrong orientation, when 6 modules were installed i.e 2 back columns of the ASA-A/0781 unit, it was also identified that the splinter arrangement for some of modules was incorrect and resulted in the air paths not lining up.
| 05SY - Systemwide | Cxxx-NCR-000578 | NCR | Secondary CMS HKD fixings |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-08-06 | 2017-08-08 14:20 | 2 | 2017-07-07 13:09 | Electrical - Cable Management | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | HKD fixings used for secondary CMS installation in zones 1&2.
| 05SY - Systemwide | Cxxx-NCR-000579 | NCR | Drilling pattern coordination between FID steelwork and ASTD transition |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-10-08 | 2017-10-06 12:11 | -2 | 2017-07-10 14:30 | Systems - Ventilation and Pressure Relief | 2500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | During the design coordination between the steelwork contractor, the transition manufacturer and __, the drilling pattern to fix the ASTD transition to the FID steelwork has been agreed between all. However while developing the two separate design, there has been miscommunication and the drilling pattern on the transition plate and the steelwork has been drilled differently.
| 05SY - Systemwide | Cxxx-NCR-000580 | NCR | Loose __ on HV Ladder |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-09-25 | 2017-08-01 12:34 | -55 | 2017-07-27 09:07 | Electrical - Cable Management | 500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During a joint IRN inspection with CRL it was noted that __ connected to the HV Ladder Rack is loose as seen in the attached photo. This has been identified between Paddington Station and Bond Street Station Eastbound, 15 loose brackets were recorded. Since these were not fixed within the shift this NCR has been raised.
| 05SY - Systemwide | Cxxx-NCR-000581 | NCR | Damaged HV Ladder Rack |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-12-31 | 2017-08-02 15:16 | -151 | 2017-07-18 13:05 | Electrical - Cable Management | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | During a joint IRN inspection of the HV ladder between ROP to BOS EB, damaged ladder was discovered at Cross Passage Transitions. It would appear that these were damaged during the delivery of CMS material to the CPs, which were dropped onto permanently installed assets.
| 05SY - Systemwide | Cxxx-NCR-000582 | NCR | Cross Passage Doors Type B&C FAT |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-11-30 | 2017-12-07 07:42 | 7 | 2017-07-10 15:28 | Systems - Cross-passage Doors | 1000 |  | System Defect | Rework | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | FAT tests of the type B & C cross passage doors were undertaken on Thursday 29th June and Thursday 6th July respectively. The following issues were observed: Type C doors: - on closing the door does not automatically latch in the fully position - Pressure relief dampers do not close automatically when door leaf latch close. - The door leaf was not fully latch closed from any position throughout the length of travel at a controlled speed of operation (20,45, fully open) - The pressure relief dampener does not close effectively to prevent smoke migration - The door does not close against a difference pressure of 85 nor 155 pa. - The door was slamming when closing at balance pressure - Gap between the door leaf leading edge and frame measured 12mm : these will have to be rechecked when the frame will be cut (testing required by __, __ to issue CI) - No electrical test was carried out (not wired up) Type B doors: - The testing rig configuration was not set up to achieve the performance required for the door self-closure against 155pa or 85pa. Due to the failure of the test of type C it does not give confidence on the success of this test for Type B doors.
| 05SY - Systemwide | Cxxx-NCR-000583 | NCR | TCR-E TTD Steelwork Clash |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-11-28 | 2017-12-12 16:43 | 14 | 2017-07-14 15:25 | Systems - Ventilation and Pressure Relief | 3000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Whilst installing the TTD support steelwork at TCR-E Level -0.5 a clash was identified between the fin plate of the steelwork wall bracket and the root radius of the I Beam (see attachment 1)
| 05SY - Systemwide | Cxxx-NCR-000584 | NCR | Earthing &Bonding cable bending radius not achieved |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-09-15 | 2017-08-24 16:04 | -22 | 2017-07-17 12:50 | Over Head Line Electrification - Earthing & Bonding | 1000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the installation of Earthing &Bonding 70mm2 black cable between PML and STG Westbound at chainages 13717, 13241 and ring number 123, bending radius of 225mm not achieved as per OHLE 1kV cable datasheets ref: Cxxx-__-R6-XDS-CRG03-50002 v1.0
| 05SY - Systemwide | Cxxx-NCR-000585 | NCR | Traction earth bars installed without Quality Control Records |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-09-15 | 2017-08-24 09:35 | -22 | 2017-07-17 12:49 | Over Head Line Electrification - Earthing & Bonding | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | No Quality Control Records were completed for traction earth bars installed at ch 14325, ch 13447 and ch 13455 between Pudding Mill Lane and Stepney Green Westbound as required by ITP Traction Earthing & Bonding–Activity 1 (Installation of Earth bars) ref: Cxxx-__-O4-ITP-CRG03-50184 v1.0 – 6.3.5 Earth bar installation: Earth bar installation check sheet QAD-OHLE-030-v1
| 05SY - Systemwide | Cxxx-NCR-000586 | NCR | Earth bar installed outside tolerance |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-09-15 | 2017-08-24 09:41 | -22 | 2017-07-17 12:48 | Over Head Line Electrification - Earthing & Bonding | 3000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Ch 12502 and ch 12066 PML to STG WB earth bars installed outside tolerance as per Method Statement: Traction Earthing & Bonding Installation ref: Cxxx-__-O1-GMS-CRG03-50181 v3.0 paragraph 6.5.3 Positioning of the earth bars, 6.5.3.1 Bored tunnel – ‘The earth bar on the evacuation walkway side shall be installed as shown below (300mm +/- 20mm) above walkway fixing).’ At the moment Ch 12502 earth bar is installed at 800mm and ch 12066 earth bar installed at 1000mm above walkway (see photo 14 - ch 12502 and 12 - ch 12066);
| 05SY - Systemwide | Cxxx-NCR-000587 | NCR | CP02 Westbound Cross Passage Door Galvanisation Spray Damage |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-10-01 | 2018-10-25 09:42 | 24 | 2017-07-18 15:14 | Systems - Cross-passage Doors | 2500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | The Westbound Cross Passage Door frame at Cross Passage 2 has been defaced with galvanisation (zinga) spray. See the attached photo for reference.
| 05SY - Systemwide | Cxxx-NCR-000588 | NCR | TVS Steelwork Bolted Connections |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-03-14 | 2018-04-13 08:53 | 30 | 2017-07-19 08:21 | Systems - Ventilation and Pressure Relief | 1000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | In regards to TVS Steelwork: - Steel-to-steel connections: __ has adopted a bolt with standard single full nut arrangement. - Threaded stud anchor fixing connections: __ and __ have adopted a standard single full nut only arrangement. These Supplier/Sub-Contractor design details, approved by the PC, do not meet requirements set in IFC drawing: Cxxx-__-M-DDJ-CR001_Z-10000. These bolting arrangement may not meet the TVS system design requirements.
| 05SY - Systemwide | Cxxx-NCR-000589 | NCR | __ TVS Duct FAT – Manufacture with unaccepted ITP |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-08-30 | 2017-08-07 11:04 | -23 | 2017-07-19 09:57 | Systems - Ventilation and Pressure Relief | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | The FAT for the TVS Transition Ducts, being supplied by __ and manufactured by Warren Services Ltd, was carried out on 05/06/2017. The manufacture began with a Code 2 manufacturing ITP (Cxxx-__-O4-ITP-CRG03-50116 Rev 3.0) without the comments formally addressed. During the FAT a rev 4.0 ITP was shown. Warren services and __ made it clear that the updated ITP was used during the manufacture. Upon quick review of the updated ITP, comments raised against the rev 3.0 ITP were found to be addressed and incorporated. However, the rev 4.0 ITP had not been formally submitted to Crossrail creating this non-conformance.
| 05SY - Systemwide | Cxxx-NCR-000590 | NCR | __ TVS Duct FAT – Manufacture without accepted Design |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-09-19 | 2017-12-15 12:44 | 87 | 2017-07-19 10:00 | Systems - Ventilation and Pressure Relief | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | The FAT for the TVS Transition Ducts, being supplied by __ and manufactured by Warren Services Ltd, was carried out on 05/06/2017. Manufacture commenced without an accepted design (Cxxx-__-H-DWG-N105-50006), this was due to a late submission.
| 05SY - Systemwide | Cxxx-NCR-000591 | NCR | __ TVS Duct FAT – Manufacture without accepted Welding Procedure |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-08-30 | 2017-08-07 11:07 | -23 | 2017-07-19 10:03 | Systems - Ventilation and Pressure Relief | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | The FAT for the TVS Transition Ducts, being supplied by __ and manufactured by Warren Services Ltd, was carried out on 05/06/2017. The welding procedure (Cxxx-__-O4-GPD-CRG03-50090) had not been submitted to Crossrail. At the FAT the welding procedure existed but was not submitted.
| 05SY - Systemwide | Cxxx-NCR-000592 | NCR | LIS-W Copper Greasing Anchor Fixings |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-08-11 | 2017-09-27 10:39 | 47 | 2017-07-19 15:22 | Structural Engineering - Bolted Connections | 2500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | The Sub-Contractor, __ complete installing TID-W supporting steel works. On carrying an installation inspection it was discovered that the base plate anchors of the steel work had been torqued with copper grease on the anchor thread.
| 05SY - Systemwide | Cxxx-NCR-000593 | NCR | Cable trough lids installed without any offset to overlap the troughing joints |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-09-17 | 2017-09-13 14:41 | -4 | 2017-07-19 12:52 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Part of Cxxx-FCD-000217 troughing works scope taking place along Eastbound and Westbound track at Plumstead railhead between chainage 23000 to 23456, cable trough lids were installed without any offset to overlap the troughing joints. Most of the new troughs were installed along existing route correctly laid as per attached photos
| 05SY - Systemwide | Cxxx-NCR-000596 | NCR | Post Gate Change of WHI-E ASA |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-12-12 | 2018-02-19 15:00 | 69 | 2017-07-21 09:07 | Systems - Ventilation and Pressure Relief | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | The design of the WHI-E Atmosphere Side Attenuators has been developed since Gate 3. The Attenuator module arrangement was changed from a depth of 3 modules (Cxxx-__-M-DDA-D061_WS107_B-10002 – C01) to a depth of 2 modules. The A&M (Cxxx-__-K2-STP-D061-50001 Rev 3.0) states the only route, which is to lower the module through the TVS Steelwork from level B to level A. Due to the increased module size, modules are too large to fit through the TVS Steelwork (dimensioned sketch attached). The entire module will not fit however individual splitters can be removed. Entire module removal is required for end of life or damaged asset replacement. Furthermore, lifting beam LB17002 sits in the middle of the level B void. If the modules were to fit through the TVS Steelwork, they would then clash with this lifting beam. This is two examples of missed design coordination with one asset. An impact assessment during the design development was seemingly not carried out.
| 05SY - Systemwide | Cxxx-NCR-000597 | NCR | Failed Damper Torque Check - East and West TVS |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-10-19 | 2017-09-11 12:00 | -38 | 2017-07-21 09:35 | Mechanical - Mechanical Engineering General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | As part ITP 'Cxxx-__-O4-ITP-CRG03-50084', a site visit took place to witness the final inspection of the Draft Relief Dampers (4no.) at Canary Wharf Station TVS, East and West Shaft. As part of QAD-093, a torque check on M12 fixings at 45N/m was carried out as specified within the TROX specification for supplied fixings. A total number of 5 fixings per Damper were tested at 45N/m, 20 in total, with approximately 80% of fixings failing the test. As a result of this, all 4 damper QAD sheets remain open with additional works required before final sign off.
| 05SY - Systemwide | Cxxx-NCR-000598 | NCR | Tunnel Isolation Dampers Under-Torqued - East and West TVS |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-10-19 | 2017-08-15 14:17 | -65 | 2017-07-21 10:00 | Mechanical - Mechanical Engineering General | 2500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | As part of 'Cxxx-__-O4-ITP-CRG93-50084' - QAD-093, a site visit was due to take place to carry out a torque check on all Tunnel Isolation Dampers, East and West Shaft, Canary Wharf TVS. __ HST3-R M12 were used for this installation and have a requirement of a 60N/m torque as per the __ data sheet. Prior to carrying out the site visit, the sub-contractor informed __ that all fixings to slab were in fact torqued to 45N/m and not 60N/m as specified. As a result of this, the inspection did not go ahead on the TID (8no.) and the sub-contractor is required to undertake rework before the final inspection can be carried out.
| 05SY - Systemwide | Cxxx-NCR-000599 | NCR | Missing waterproof sleve and missing geotextile at PML Pad Foundations |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-07-31 | 2018-06-11 13:43 | -50 | 2017-07-21 11:54 | Civil - Civil Engineering General | 5000 |  | Incorrect Installation | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Pudding Mill Lane-during the construction of pad foundations 730/731/732 designed waterproof sleeve 1000 mm from the top of foundation was missing all around. Also removed during temporary work Geotextile all around foundations 730/731/732 need to be re-instated and joint with existing one as per design. The work in the area are not completed and backfill not done to design level. Pad foundation top is exposed about 700 mm (See attached photos)
| 05SY - Systemwide | Cxxx-NCR-000600 | NCR | Installed Earthing cable completely covered by sprayed concrete |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-11-02 | 2017-11-13 15:14 | 11 | 2017-07-25 08:28 | Electrical - Earthing & Bonding | 2000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | Installed Earthing cable were completely covered by sprayed concrete lining during __ contracted works on both sides of Woolwich Station. It is deviation from original design but chipping out concrete is not good option as could easy damage EW cable. Please find attached picture.
| 05SY - Systemwide | Cxxx-NCR-000601 | NCR | S&C I__ Bearer out of position |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-11-01 | 2017-10-09 11:08 | -23 | 2017-07-25 13:17 | Track - Track General | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Location: S&C I__ Bearer on C5, C9 & C10 I__ bearer should be in the correct position to allow the installation of the POE. Even though the bearer spacing was within tolerance, the anchor plates that are bolted to the rails have been installed on the opposite sides (RH & LH). The anchor plates are not symmetrical and this has slightly shifted the bearer out of position which in turn prevented the installation of the POE. See attached pictures.
| 05SY - Systemwide | Cxxx-NCR-000602 | NCR | Bending Test BT51 failed to achieve minimum deflection. |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-10-01 | 2017-10-06 11:20 | 5 | 2017-07-25 13:42 | Track - Welding | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | The results provided for BT51 are: - Minimum load: 1647 kN --> compliant - Minimum deflection: 13.99mm --> non-compliant - Loading rate: 94 kN/s --> compliant The test affects the production of the w/c 26/05/17: 16 welds done between Limo Shaft to VDP EB.
| 05SY - Systemwide | Cxxx-NCR-000603 | NCR | New Concrete Mix M5-3 not approved |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-09-23 | 2017-09-27 10:53 | 4 | 2017-07-25 14:33 | Track - Track General | 1000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | Concrete ready mix M5-3 supplier TARMAC, has changed some material supplier for all its mixes. Construction Track Team has proceeded to pour the track without new CPS being approved. Areas concerned: ROP EB Ch 0+422 up to 0+470 and Ch 0+501 up to 0+506 ROP WB Ch 0+422 up to 0+476 and Ch 0+501 up to 0+506
| 05SY - Systemwide | Cxxx-NCR-000604 | NCR | Formwork installed instead of Catch pit frame. |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-02-28 | 2017-09-19 08:05 | -162 | 2017-07-26 09:20 | Track - Track General | 20000 |  | Incomplete Works | Rework | 2 (6-60k) | Complete | Management Problem - Improper resource allocation | Completed |  | In absence of catch pit frame in store, and in order to do not stop the production, construction track team have installed formworks instead of catch pit metal frame in order to proceed with installation after pour of concrete.(Not leaving enough space for frame metal fixings to the concrete, extrusion tang) Photographs attached. EB Ch: 5134, 5177, 5216, 5255, 5294, 5344, 5394, 5444, 5494, 5544, 5594, 5644, 5694, 5744, 5794, 5844, 5894, 5934, 5973, 6010
| 05SY - Systemwide | Cxxx-NCR-000605 | NCR | Damage to Tunnel Side Attenuator, East Shaft. |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-12-19 | 2018-01-10 09:02 | 22 | 2017-07-26 09:42 | Mechanical - Mechanical Engineering General | 5000 |  | Damaged | Repair | 3 (3-6k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | During a site inspection carried out by Chris Thomas (__) and Felix Ahatty (CRL), it was highlighted that major damage has been caused to 3no. splitters to the center module of TSA-B/2372. A closer visual inspection has shown that the 3 no. splitters have been distorted and bent (investigation pending).
| 05SY - Systemwide | Cxxx-NCR-000606 | NCR | M16x165 anchor bolts installed instead of M16x255 at Pudding Mill Lane Portal |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-08-26 | 2017-09-13 14:27 | 18 | 2017-07-27 14:21 | Electrical - OHLE | 2500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | As per design, at 7 locations in Pudding Mill Lane Portal (East and Westbound) is required to install M16x255 anchor bolts instead of the usual M16x165 bolts (this is explained in the OHLE Layout Details). However, the team did not check this information and complete the installation with the same bolts used in all the other locations at the portal.
| 05SY - Systemwide | Cxxx-NCR-000607 | NCR | No Inspection or Test Activities Being Carried Out As Per the ITP |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-10-25 | 2017-10-03 09:07 | -22 | 2017-07-27 14:41 | Electrical - Cable Management | 2500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | TVS Cable Management System installation works at Canary Wharf Station ventilation shafts are not carrying out inspection or test activities as per the ITP (Cxxx-__-O4-ITP-CRG03-50188 v3.0). The ITP (section 6.3.3) states that Pull tests shall be carried out on 10% of the mechanical anchor installation. These tests are not currently being conducted.
| 05SY - Systemwide | Cxxx-NCR-000608 | NCR | An Onsite Fabricated Tray Bend Has Been Used In The TVS CMS Installation |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-11-06 | 2017-11-02 09:15 | -4 | 2017-07-27 15:05 | Electrical - Cable Management | 2000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | During an inspection of the works covered by ITP: Installation of CMS within the TVS Shafts (Cxxx-__-O4-ITP-CRG03-50188) and Method Statement: Canary Wharf East & West Shafts CMS Install (Cxxx-__-E-GMS-CR143-50003) it was noted that a tray bend had been fabricated onsite. Only manufactured tray bends may be used on site.
| 05SY - Systemwide | Cxxx-NCR-000609 | NCR | AEW Damaged during installation |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-10-25 | 2017-09-13 13:19 | -42 | 2017-08-09 16:27 | Electrical - OHLE | 5000 |  | Damaged | Repair | 3 (3-6k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | AEW got damage during the unwinding between Stepney Green-Canary Wharf Westbound and Stepney Green-Pudding Mill Lane Westbound. The issue is under investigation to identify whether is a manufacturing defect or an incorrect installation.
| 05SY - Systemwide | Cxxx-NCR-000610 | NCR | Poor Quality Drilling at Connaught Tunnel |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-09-30 | 2017-10-03 09:10 | 3 | 2017-08-01 16:36 | Electrical - OHLE | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | It has been found during a Control Inspection that the quality of the drilling in Connaught Tunnel is very poor (both bounds). 50% of the locations need re works. We have different issues: 1) drilling angle (bolts not fully in contact with plate, especially in the anchor plate of the tie) 2) different sizes of bolts, some of them don’t allow the lucking nut to be installed 3) loose nuts 4) One location with excess of washers (probably to hide the red mark that shouldn't be visible)
| 05SY - Systemwide | Cxxx-NCR-000611 | NCR | Out of spec flow table test results at Whitechapel Station EB, STS Concrete Pour. |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-02-28 | 2018-01-31 10:39 | -28 | 2017-08-03 12:41 | Civil - Track | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | 5no Concrete Trucks with Flow table test out of spec, between 05 July and 19 July. At Whitechapel Station EB. See sketch attached
| 05SY - Systemwide | Cxxx-NCR-000612 | NCR | CON - Robust kerb under Silvertown bridge |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-02-28 | 2018-02-05 09:08 | -23 | 2017-08-03 15:22 | Civil - Civil Engineering General | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | During construction activities following items were not installed as indicated on "IFC by exception in CxxxXRL-O-RGN-CR001-50002" drawings: 1. Weep pipes were installed as a whole pipe rather than half round as shown on section 1 of Cxxx-OVE-S-DDL-CR146_Z-55510 C01 2. 25mm compressible was filler installed on top of existing pier to separate new kerb and existing pier, but "10thk hydrocell XL compressible layer" WAS NOT installed on the bottom part of Kerb's sides as shown on detail 1 of Cxxx-OVE-S-DDB-CR146_Z-55511 C01
| 05SY - Systemwide | Cxxx-NCR-000613 | NCR | CON - Robust Kerb documentation |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-01-31 | 2018-01-08 14:39 | -23 | 2017-08-03 15:20 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | ITP referred to during implementation of work on "Robust kerb in Silvertown bridge area" does not provide sufficient information/details for compliant "tests and inspections" to take place
| 05SY - Systemwide | Cxxx-NCR-000614 | NCR | Paint thickness CPD 9 |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-05-31 | 2019-04-16 07:19 | -45 | 2017-08-04 14:37 | Systems - Cross-passage Doors | 10000 |  | Manufacturing Defect | Rework | 2 (6-60k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | During a site inspection it was identified that the paint on the lower edge of the bulkhead is too thin. This appears to be a manufacturing defect instead of site damage.
| 05SY - Systemwide | Cxxx-NCR-000615 | NCR | WHI-W TVF Steelwork studs - Concrete Breakout via Torquing |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-01-10 | 2018-01-12 15:17 | 2 | 2017-08-08 15:46 | Mechanical - Heating Ventilation & Air Conditioning | 2000 |  | Material | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | On the 24/07/16 the subcontractor, __ Ltd, were installing the WHI-W TVF steelwork supporting steelwork in accordance with Cxxx-__-H-DWG-D061-50022 rev 1.0. The works involved installing M20 __ HIT-V-5.8F anchors with HIT-HY 200 resin to a depth of 90mm into concrete slab at level 3. Whilst carrying out the torqueing of the first bracket, there was a failure of the concrete around 1 out of 8 studs. This caused a section of the concrete which was approximately 150mm in diameter at the surface and 50mm deep to breakaway the stud. The studs were being torqued to 150N/m as per the design . Cxxx was contacted via email who provided the following response: 1. Level 3 slab has reached strength based on our concrete cube records; 2. I see there is a lot of drilled dust around the holes. We have had issues in the past where holes weren’t blown out properly resulting in failure. I note it appears to be an isolated incident , if they all failed in this area it ie those shown in picture 107 than I would be majorly concerned. 3. 1 out of 8 failed in this area. Most likely an isolated incident .If the other 7 have passed the pull test-this would be a good indication that the concrete has cured to the required strength. __ then pull tested further studs which passed so it was deemed an isolated incident. On the 4/08/17, a further two more studs were being torqued when the concrete failed again. __ design team was contacted and advised that engineers use the __ Profis program when doing the calculations and the fixing size, embedment was adequate for loadings provided by the fans.
| 05SY - Systemwide | Cxxx-NCR-000616 | NCR | Bond Street West LB06003/4 manufactured with insufficient clearance between the brackets and the beam |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-01-12 | 2018-02-21 07:55 | 40 | 2017-08-15 11:15 | Materials - General | 5000 |  | Manufacturing Defect | Rework | 3 (3-6k) | Complete | Verification Problems - Other | Completed |  | During the installation of the LB06003/4 at Bond Street West, it was noted that the bridge beam was manufactured with insufficient clearance between the brackets and the beam. As a result with the current installation the clearance is reduced to circa 7mm at each end which restricts the movement of the bridge beam.
| 05SY - Systemwide | Cxxx-NCR-000617 | NCR | Support brackets installed with incorrect embedment depths. |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-05-16 | 2018-05-10 14:01 | -6 | 2017-08-29 13:22 | Electrical - Cable Management | 1000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Support brackets for T1 & T2 at Plumstead Portal WB have been fixed into reinforced concrete using __ Hit-HY-200-A & HUS-Z-R M16 as per drawing Cxxx-__-E-DDD-CR001_Z-50002. The drawing states a minimum embedment depth of 150mm, however a site survey has indicated that not all fixings have been installed as per the drawing. See attached survey document for reference (measured values are protrusion of 240mm HUS-Z-R, i.e.: 90mm protrusion = 150mm embedment). From the survey results attached 5 sets of fixings have a protrusion of more than 90mm +10%. Theses fixings are numbers 5, 20, 30, 32 and 33 as numbered in the attached survey. These fixings have now been replaced and the NCR raised for traceability.
| 05SY - Systemwide | Cxxx-NCR-000618 | NCR | __s cable 25kV A-1 on the drum shorter than expected |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-12-03 | 2017-12-08 15:45 | 5 | 2017-08-25 15:55 | Electrical - General | 5000 |  | Supervision/Management | Rework | 3 (3-6k) | Complete | Material/Preservation Problems - Other | Completed |  | OHLE Negative Return Cable CR094-OLE-00014 from Drum 25 KV A-1. The cable should have been 500mt long according to all documentation by supplier. However during installation it was found to be only 460m long. Please find attachment.
| 05SY - Systemwide | Cxxx-NCR-000619 | NCR | Tottenham Court Road East Transition Clash with Structual Opening |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-01-17 | 2017-09-29 08:15 | -110 | 2017-08-17 10:58 | Mechanical - Mechanical Engineering General | 5000 |  | Design | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | Tottenham Court Road East Tunnel Side Transitions clash with the civils structural openings, thus can not be completed
| 05SY - Systemwide | Cxxx-NCR-000620 | NCR | Tottenham Court ROad East TTD access door clash |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-10-25 | 2017-10-10 14:24 | -15 | 2017-08-17 11:06 | Materials - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | TCR E TTD access doors clash with the civils structure and will not be accessible once fan steelwork is installed.
| 05SY - Systemwide | Cxxx-NCR-000621 | NCR | FTS Lite – Incorrect inclination of baseplate in slab W6 |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-01-19 | 2017-11-08 14:58 | -72 | 2017-08-17 14:01 | Track - Track General | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | The 23rd baseplate from W5/W6 interface on the south side of FTS Lite Westbound Slab 6 (Approx. chainage 4481) was installed and cast with the inclination set in the wrong direction (180 degrees in a horizontal plane from correct position)
| 05SY - Systemwide | Cxxx-NCR-000622 | NCR | DFT - Final Track Geometry (As-Built) non-compliant |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-11-27 | 2017-10-11 07:21 | -47 | 2017-08-29 12:47 | Track - Track General | 5000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | After an As Built survey was carried out on both bounds of Marshgate Lane Bridge, it has been noticed that there are some points where the cant is out of tolerance. Please find attached the survey.
| 05SY - Systemwide | Cxxx-NCR-000626 | NCR | FTS Barbican - Non-compliant installation of T-bolts and tension clamp on Eastbound Track Baseplates |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-12-22 | 2017-12-21 14:32 | -1 | 2017-09-12 13:46 | Track - Track General | 1000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Several baseplates (approx 10-20% per slab) along the FTS Barbican Eastbound track have been found to have a non-compliant tension clamp, T-bolts and nuts. In many cases, the gap between the clamp and rail foot is greater than 2mm and the T-bolt/nut has not been torqued to the required value. Several baseplates have loose T-bolts/nuts and in some locations, the nut is jammed on the bolt and cannot be removed by hand, which indicates that the thread is damaged.
| 05SY - Systemwide | Cxxx-NCR-000627 | NCR | Track- Water added on Concrete Truck on site. |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-03-12 | 2018-02-01 13:30 | -39 | 2017-09-13 16:28 | Track - Track General | 2000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Location: ROP WB/EB Ch 0+422 up tp 0+390 Water has been added on site to two Concrete Trucks (Concrete MIX M5-3) , supplier TARMAC, in order to obtain value of flow test above 540mm.
| 05SY - Systemwide | Cxxx-NCR-000628 | NCR | Track - Concreting with track Gauge and PLAN defect non-compliant to requirement. |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-04-25 | 2018-04-23 07:16 | -2 | 2017-09-13 16:27 | Civil - Track | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Location: ROP EB Gauge 0+381 up to 0+359 ROP WB Gauge 0+0+375 up to 0+371 / PLAN defect 0+384 up to 0+365 It has been noticed after Track Geometry Survey for C1-C4 (Scissor Crossing) that the gauges were narrow on the diamond area (1.425 m) . Points out of tolerance (2 in EB & 1 in WB) in the concreting area are about 1/1.5 mm out of tolerance. Please find attached Report.
| 05SY - Systemwide | Cxxx-NCR-000629 | NCR | Track : Flash Butt Welds Machine Graphs missing for Weld No395 to No404 (10 welds) |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-11-06 | 2017-10-06 09:57 | -31 | 2017-09-13 16:19 | Track - Welding | 500 |  | Incomplete Works | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | VDP Tunnel ,from Ch: 13925 to Ch: 14349 East bound Flash Butt Welds Machine Graphs missing for Weld No395 to No404 (10 welds)
| 05SY - Systemwide | Cxxx-NCR-000630 | NCR | Infill works on HAS area without a compliant pull off test. |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-05-30 | 2018-07-20 10:15 | 51 | 2017-09-13 16:44 | Track - Track General | 2500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Verification Problems - Not Defined | Completed |  | It have been done 10 pull off test (2 set of 5 test specimen) and 70% of the result is out of requirement (1,5 N/mm2). The test has been carried out after 7 days of placing the 32/40. However the test has been failed as a consequence of an adhesion failure between the adhesive layer and the dolly. Therefore the results don’t represent the quality of the chemical bounding, which __ is fully confident. The tensile stress are : 1. 1.22 N/mm2 6. 0.15 N/mm2 2. 0.51 N/mm2 7. 1.43 N/mm2 3. 0.97 N/mm2 8. 1.32 N/mm2 4. 1.43 N/mm2 9. 1.88 N/mm2 5. 1.58 N/mm2 10. 1.58 N/mm2
| 05SY - Systemwide | Cxxx-NCR-000631 | NCR | PLU RR drainage: Intermediate "Air testing single pipe runs" was not witnessed by CRL FE |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-12-15 | 2017-10-12 12:07 | -64 | 2017-09-19 11:05 | Civil - Drainage | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Sub-contractors works on "Intermediate air test" (before pipe backfill) was not witnessed by CRL FE (but witnessed by __'s site engineer) CRL FE was not officially invited to witness the intermediate air testing point 3.11 of ITP Cxxx-__-O4-ITP-CR148-50002 v2.0 , but has witnessed "Final air-test" of the same pipe runs as per point 3.25
| 05SY - Systemwide | Cxxx-NCR-000632 | NCR | Works carried out without IFC drawings |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-07-31 | 2018-08-01 10:20 | 1 | 2017-09-21 14:31 | Track - Track General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | During __ surveillance ref: Cxxx-__-O4-RGN-CR076-50002 it was found that construction works were carried out without IFC drawings in Westbourne Park transition slab to ballasted area. The following design drawings were reviewed: • Transition from Standard Slab Track to Ballast Track, Section S1, Ch305.000, Sheet 1 of 3Cxxx-__-R4-DDB-CR076_PT001_Z-10012 P02 • Transition from Standard Slab Track to Ballast Track Section S2 Cxxx-__-R4-DDB-CR076_PT001_Z-10014 P02 • Transition from Standard Slab Track to Ballast Track Section S3 Cxxx-__-R4-DDB-CR076_PT001_Z-10015 P03 • Transition from Standard Slab Track to Ballasted Track General arrangements Cxxx-__-R4-DDL-CR076_PT001_Z-10010 P02 • Ballast Retaining Wall RC Cxxx-__-R4-DDD-CR076_PT001_Z-10011 Details P01 • Ballast Retaining Wall BS Cxxx-__-R4-DDJ-CR076_PT001_Z-10001 P01 • ROP and C1-C4 Cxxx-__-R4-DDL-CR076_PT001_Z-10500 GA P03 Furthermore, works are being carried out in WBP ballasted track area without IFC drawings as per below package: Cxxx-__-R4-DDA-CR076_Z-10506; Cxxx-__-R4-DDA-CR076_Z-10202; Cxxx-__-R4-DDA-CR076_Z-10204; Cxxx-__-R4-DDL-CR076_MS005_Z-10020; Cxxx-__-R4-DDB-CR076_Z-00001; Cxxx-__-R4-DDB-CR076_Z-00002; Cxxx-__-R4-DDB-CR076_Z-00003; Cxxx-__-R4-DDB-CR076_Z-00004; Cxxx-__-R4-DDB-CR076_Z-00005; Cxxx-__-R4-DDB-CR076_Z-00006; Cxxx-__-R4-DDB-CR076_Z-00007; Cxxx-__-R4-DDA-CR076_1-10512; Cxxx-__-R4-DDA-CR076_1-10513; Cxxx-__-R4-DDA-CR076_1-10510; Cxxx-__-R4-DDA-CR076_1-10511; Cxxx-__-R4-DDD-CR076_SD005_Z-10025; Cxxx-__-R4-DDD-CR076_SD005_Z-10026; Cxxx-__-D-DDA-CR076_SD005_Z-00750; Cxxx-__-R4-DDL-CR076_SD005_Z-10010;
| 05SY - Systemwide | Cxxx-NCR-000633 | NCR | C11 Switch Blade – Failed Weld C1104 |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-12-10 | 2017-10-20 13:55 | -51 | 2017-09-21 09:15 | Track - Welding | 5000 |  | Equipment Breakdown | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Molten metal ran out onto the rail and slab during the Aluminothermic welding process of weld C1104 located on the C11 switch blade.
| 05SY - Systemwide | Cxxx-NCR-000634 | NCR | Whitechapel East TVF - Damage to fan grill |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-12-20 | 2017-12-20 11:12 | 0 | 2017-09-21 13:47 | Systems - Ventilation and Pressure Relief | 1000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | During installation it was noticed that the atmosphere side safety grill had been damaged.
| 05SY - Systemwide | Cxxx-NCR-000635 | NCR | Damaged Catenary Cable - Open Route at Chainage 18465 + 5m |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-01-12 | 2017-12-12 15:29 | -31 | 2017-09-22 11:32 | Over Head Line Electrification - Earthing & Bonding | 2000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper handling of material | Completed |  | TBC - Damaged Catenary Cable - Open Route at Chainage 18465 + 5m
| 05SY - Systemwide | Cxxx-NCR-000636 | NCR | Damaged cable trapped underneath remaining turns in the OHLE Cable Drum OHLE EB NF2-Cable No: CR512-OLE-00004 |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-02-27 | 2018-01-29 11:43 | -29 | 2017-09-22 17:11 | Electrical - OHLE | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper handling of material | Completed |  | Whilst installing Cable No: CR512-OLE-00004 from Joint 2 to the Disconnector in the West Bound trace, after approx. 400mts installed, from a drum of 502mts, works were stopped as the cable was found to be trapped underneath remaining turns. This at approx. Ch 11868, Ring 2232.
| 05SY - Systemwide | Cxxx-NCR-000637 | NCR | Whitechapel TID damper Cover Plates |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-02-28 | 2018-04-10 06:46 | 41 | 2017-09-26 09:42 | Materials - General | 1000 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | WHI - E TID - W damper linkage cover plate does not fully align with the damper
| 05SY - Systemwide | Cxxx-NCR-000638 | NCR | Use of closure rails at Plumstead Portal |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-10-26 | 2017-10-24 13:31 | -2 | 2017-10-09 15:34 | Track - Rails and Sleepers | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Short/closure rails have been used in the Plumstead Portal.
| 05SY - Systemwide | Cxxx-NCR-000639 | NCR | Woolwich East TID Damage |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-04-09 | 2018-03-26 14:55 | -14 | 2017-09-27 12:12 | Mechanical - Mechanical Engineering General | 1500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | After installation the Woolwich East TID dampers operated fully through their full range of movement. It has now become apparent that approximately 14 modules will not close properly. Upon investigation it was found that blades were clashing and there was a dent in at least 1No blade.
| 05SY - Systemwide | Cxxx-NCR-000640 | NCR | Type B doors delivered without FAT report and manufacturing files. |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-04-30 | 2018-03-26 09:41 | -35 | 2017-09-28 14:49 | Systems - Cross-passage Doors | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Type B doors have been delivered without receipt of FAT report and manufacturing files. This is not in compliance with procedures and the ITP. 1. FAT report not sent by the subcontractor prior to delivery. Cxxx-__-E-RGN-CRG03-50077 - Factory Acceptance Test Report - Cross Passage Doors (Type B) Cxxx-__-E-RGN-CRG03-50078 - Factory Acceptance Test Report - Cross Passage Doors (Type C) 2) Manufacturing files not sent by the subcontractor prior to delivery. Cxxx-___O4-LRC-CRG03-50031 - Cxxx Systemwide Main Works Manufacturing & Test Plan Deliverables Pack - Stepney Green Shaft Cxxx-___O4-LRC-CRG03-50040 - Cxxx Systemwide Main Works Manufacturing & Test Plan Deliverables Pack - Limmo Shaft
| 05SY - Systemwide | Cxxx-NCR-000641 | NCR | Bending Test BT60 failed to achieve minimum deflection |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-02-15 | 2017-11-15 15:58 | -92 | 2017-10-04 16:07 | Track - Welding | 5000 |  | Incorrect Installation | Use As-Is | 3 (3-6k) | Complete | Verification Problems - Other | Completed |  | The results of the bending test of sample BT60 gave a load in excess of the minimum requirement of 1520kN, however it failed to meet a minimum deflection of 20mm without fracture. The results provided for BT60 are: - Maximum load: 1698 kN --> compliant - Minimum deflection: 12.39mm --> non-compliant - Loading rate: 99 kN/s --> compliant
| 05SY - Systemwide | Cxxx-NCR-000642 | NCR | Earthing &Bonding cable bending radius not achieved |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-12-14 | 2017-12-07 10:13 | -7 | 2017-10-05 15:27 | Over Head Line Electrification - Earthing & Bonding | 1000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | During the installation of Earthing &Bonding 70mm2 black cable between CWS and VDP Eastbound at chainages 15248 and 14225, bending radius of 225mm not achieved as per OHLE 1kV cable datasheets ref: Cxxx-__-R6-XDS-CRG03-50002 v1.0
| 05SY - Systemwide | Cxxx-NCR-000643 | NCR | Earting & Bonding cables installed in Cxxx HV cable UTX |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-12-13 | 2017-12-07 10:14 | -6 | 2017-10-05 15:37 | Over Head Line Electrification - Earthing & Bonding | 1000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | During Earthing &Bonding pre IRN inspection for ComLot OLE-TEB-MNLEB-102L canary Wharf Eastbound Platform it was noted that at chainage 13880 (TSP-CNW-E/B-2a to TSP-CNW-E/B-2b) and chainage 13635 (TSP-CNW-E/B-1a to TSP-CNW-E/B-1b) connection cables ware installed using High Voltage Cable UTX.
| 05SY - Systemwide | Cxxx-NCR-000644 | NCR | sealant used on cross passage doors prior to MCR acceptance |  | Contr | COS | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-10-01 | 2018-09-12 07:45 | -19 | 2017-10-09 13:20 | Fire - Fire Systems & General | 2000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | __'s Cross Passage Door Installation sub-contractor, __s, have suggested and started using a different intumescent sealant product which is LUL compliant. Currently, the Type A Door MCR (Cxxx-__-O4-LRC-CRG03-50001) & Type B & C MCR (Cxxx-__-E-LRC-CRG03-50001) both stipulate ARBO XL1075 as the nominated fire resistant sealant to be installed at joints (i.e. between frame and concrete). However, ARBO XL1075 is not explicitly LUL compliant. Furthermore, the Tunnel Mechanical Systems Performance Specification (Cxxx-MMD-M-RSP-CR001-00001) Stipulates the following: "All plant shall be fire retardant, low-smoke and non-halogenated type. All electrical plant provided sub-surface shall comply with LU Standard 1-085, Fire Safety Performance of Materials and LU Manual of Good Practice G-085, Code of practice - Fire Safety of Materials and Fire Safety of Specific Items and Materials Used in the Underground." Hence, why __s proposed to use the following fire sealant product instead as it is an LUL approved product: Pyropro LST Intumescent Sealant An agreement between __s and __ was made to update the two MCRs referenced below, however, to date no MCR has been raised, which is why this NCR has been raised, to ensure the works are covered by this NCR until the MCR has been approved.
| 05SY - Systemwide | Cxxx-NCR-000645 | NCR | Damage to rail head due to milling machine malfunction |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-11-03 | 2017-11-08 15:00 | 5 | 2017-10-09 14:39 | Track - Rails and Sleepers | 5000 |  | Damaged | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Thames Tunnel, 22235 EB (Ring 203) The right hand copy finger that runs along the gauge side of the rail at the milling unit broke and the milling head started veering into the rail head causing a gouge to the running edge of the rail along a distance of about 1 meter (see attached pictures). The maximum metal removal depth on the running edge is 4.7mm. Attached is the profile measurement at the damaged location.
| 05SY - Systemwide | Cxxx-NCR-000646 | NCR | __ TVF 'Steel to Steel' Bolted Connections |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-03-01 | 2018-03-15 08:08 | 14 | 2017-10-09 15:51 | Systems - Ventilation and Pressure Relief | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | Within the recent SOB 00302 reply, MMD confirm that the following statement / requirement is acceptable: __ propose to use Gr8.8 preloaded fixings to satisfy Category C joint as per Clause 3.4.1(c), BS EN 1993-1-8:2005. Individual bolts preloads and torques will be noted on the drawings. During a review of the installations at Whitechapel, CWS and TCR it has been identified that 8.8SB non-preloaded bolts have been used for the fan steelwork. This is not in accordance with the above requirement. Within the EN 15048 Non-preloaded Structural Bolts it states that these bolts are identified as follows: Standard shall be labelled with: CE marking Lot number Reference to EN 15048-1 “SB” marking Identification number of the certified authority and manufacturer
| 05SY - Systemwide | Cxxx-NCR-000647 | NCR | Track- Absence of Quality Control Records at Ballasted Transition area. |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-11-22 | 2017-11-08 15:15 | -14 | 2017-10-10 19:18 | Civil - Track | 1000 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | Works at ballasted transition area have been carried out without submission of respective QCR’s as per ITP / deliverables
| 05SY - Systemwide | Cxxx-NCR-000648 | NCR | Torqueing of CWS inaccessible Fan Steel Bolts |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-11-30 | 2017-12-01 13:23 | 1 | 2017-10-11 10:55 | Systems - Ventilation and Pressure Relief | 1000 |  | Design | Rework | 4 (0.5-3k) | Complete | Verification Problems - Not Defined | Completed |  | With the Canary Wharf TVF steelwork drawings Cxxx-__-H-DWG-CR143-50018 (West) and Cxxx-__-H-DWG-CR143-50024 (East) is the statement, "For 2 inaccessible bolts - torque up to nominal value that can be achieved". This statement contradicts the approved installation ITP Cxxx-__-O4-ITP-CRG03-50030 which requires all bolts to be 100% torqued.
| 05SY - Systemwide | Cxxx-NCR-000649 | NCR | Calibration Certificate of Pull Out Tester expired |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-10-25 | 2017-10-12 13:45 | -13 | 2017-10-11 19:10 | Electrical - OHLE | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | The re calibration of the OHLE Pull Out Tester had to be done at the end of May 2017. However, the team did not send the tester for re calibration due to it was the only one available and they need it to carry on with the tests (the re calibration takes at least 1 week). In consequence, the dates on the control sheets show that the tests were carried out with an expired certificate. To ensure the reliability of the results, The supervisor tested 3 anchor bolts using the OHLE tester and a second tester borrowed from M&E. The results were exactly the same. As now all the pull out tests have been done, the OHLE tester has been sent for re calibration.
| 05SY - Systemwide | Cxxx-NCR-000650 | NCR | FTS - Broken bolts of access covers |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-10-31 | 2018-09-18 08:17 | -43 | 2017-10-12 12:47 | Track - Track General | 5000 |  | Damaged | Rework | 3 (3-6k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Whilst removing the steel access covers in FTS to clean under the slab, we have found that some bolt heads securing the access cover have sheared off, leaving the thread of the bolt embedded in the concrete. A further survey to be completed to determine the extent of the issue.
| 05SY - Systemwide | Cxxx-NCR-000651 | NCR | Damaged DFT Baseplates - Connaught |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-06-28 | 2018-07-20 10:17 | 22 | 2017-10-12 15:38 | Track - Track General | 1208000 |  | Material | Reject | 1 (>60k) | Complete | Material/Preservation Problems - Not Defined | Completed |  | Further to Cxxx-NCR-000551, an additional 30 baseplates have broken on the Eastbound track at Connaught between chainages 18660 - 17390. The nature of the break is the same as the previous NCR, where the T-bolt housing is snapping off from the baseplate.
| 05SY - Systemwide | Cxxx-NCR-000652 | NCR | LIS-E TTD - Work commencing without accepted drawing |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-01-31 | 2018-02-13 11:56 | 13 | 2017-10-13 14:02 | Systems - Ventilation and Pressure Relief | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Manufacture and installation of the tunnel side transition ducts took place without an accepted design - Cxxx-__-H-DWG-CR092-50001
| 05SY - Systemwide | Cxxx-NCR-000653 | NCR | PLU Separation Fence timber rails installation |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-12-17 | 2017-11-02 16:31 | -45 | 2017-10-18 10:49 | Civil - Civil Engineering General | 2000 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Rather than to be installed in front of the posts as per design, timber rails were cut short and installed between the posts.
| 05SY - Systemwide | Cxxx-NCR-000654 | NCR | Direct Fix Track, Connaught - Failed Ultrasonic Test of Weld |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-01-18 | 2017-10-27 08:24 | -83 | 2017-10-20 11:22 | Track - Welding | 3000 |  | Material | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | An Aluminothermic Weld (referenced ATW003, installed 20/09/2017) located on the left hand rail of the Eastbound direct fix track at chainage 18480 was tested by the Ultrasonic Testing team on 17/10/2017 and failed with a points score of 10 due to large signals emanating from the foot of the rail.
| 05SY - Systemwide | Cxxx-NCR-000655 | NCR | PAD-W TVF-A Steelwork Installation Centre Alignment |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-12-06 | 2017-12-04 14:45 | -2 | 2017-10-25 14:38 | Systems - Ventilation and Pressure Relief | 2500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | The TVF steelwork installation in Bay A and Bay C (TVF-A and TVF-C) has not been installed in the centre of the structural opening per the approved design. The steelwork currently sits circa 300mm away from the centre of the opening and will need to be realigned to the centre.
| 05SY - Systemwide | Cxxx-NCR-000656 | NCR | Derailment Containment on STS installed incorrectly - Custom House Station |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-02-28 | 2018-01-31 11:57 | -28 | 2017-10-30 10:24 | Track - Track General | 6000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The derailment containment on STS track at Custom House Station (Eastbound between CH 17165 – 17193 & Westbound between CH 17243 - 17270) has been installed along the opposite rail to that shown on the design.
| 05SY - Systemwide | Cxxx-NCR-000657 | NCR | Contamination damage to outer cable ladder due to exposure to ‘red marker spray’ paint |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-01-31 | 2017-11-01 15:42 | -91 | 2017-10-31 11:18 | Electrical - Cable Management | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | This item was identified during a joint OHLE IRN inspection on the 23/10/2017 at CH11469 As you can see from the picture paint covers the CMS in STG cavern. As was agreed with CRL this is to be recorded in the form of an NCR, but should not delay energisation. The Ladder rack manufacturer has since been consulted to provide assurance that the Magnellis coating is not effected. and has confirmed that the spray paint is not detrimental to the magnelis.
| 05SY - Systemwide | Cxxx-NCR-000658 | NCR | Cable drums delivered to site are not compliant to CRL specifications |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-02-28 | 2018-01-31 12:02 | -28 | 2017-10-31 11:45 | Electrical - Cable Management | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper handling of material | Completed |  | Please see attached photos of cable drums delivered to site, which are old and damaged. The cable looks as if it has been manufactured more than one year ago which is not compliant and may not be acceptable to CRL.
| 05SY - Systemwide | Cxxx-NCR-000659 | NCR | Track- 4no EG47 Sleepers Installed without anti-attrition pad at PLU Ballast Transition |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-01-31 | 2018-01-15 08:03 | -16 | 2017-11-01 13:25 | Track - Rails and Sleepers | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | 4no Sleepers installed at Plumstead Portal Transition Ballast-STS Westbound Track , between CHs: WB 23076-23084, without anti-attrition pad.
| 05SY - Systemwide | Cxxx-NCR-000660 | NCR | Tunnel Hole Spacing - Vertical Allignment |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-11-30 | 2018-10-05 13:59 | -56 | 2017-11-02 10:52 | Tunnelling - Walkways | 3000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | At certain locations walkway brackets have been installed at inconsistent heights due to variations in the drill rig holes. In locations where adjacent brackets are at different heights the installed fire main pipework does not sit on the fire main support arm.
| 05SY - Systemwide | Cxxx-NCR-000662 | NCR | Mechanical Back Drive Plates not installed con C1-C2-C3-C4 |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-03-05 | 2018-03-15 08:11 | 10 | 2017-11-07 15:12 | Track - Turnouts | 6000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | MS Plates have not been installed on switch bearers, which are preventing the installation of the POE. 3 Bearers per Switch, a total of 12 Bearers for C1-C4.
| 05SY - Systemwide | Cxxx-NCR-000663 | NCR | Paddington Scope Gap HILTI HIT-V_R NDZ |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-12-13 | 2018-01-15 14:10 | 33 | 2017-11-07 16:42 | Mechanical - Mechanical Engineering General | 2500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | HIT-V-R fixings installed at Paddington Station EB and WB, in conjunction with the HILTI HIT HY270, have been installed below the HILTI specified minimum No Drill Zone (NDZ) of 50mm. This affects a small proportion of the total fixings installed as part of Cxxx-PMI-001135.
| 05SY - Systemwide | Cxxx-NCR-000665 | NCR | DFT DC - Incorrect concrete mix cast |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-02-14 | 2018-01-18 09:55 | -27 | 2017-11-16 17:37 | Track - Track General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | The concrete mix which was cast on 04/10/2017 for the DFT derailment containment located in Connaught contained fibres which was not part of the specification for concrete in this area. This concrete was cast in the derailment containment on the Westbound track between CH 18262 - 18371
| 05SY - Systemwide | Cxxx-NCR-000666 | NCR | DFT DC - Batch time to end of pour time exceeded 2 hours |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-02-14 | 2018-01-18 16:32 | -27 | 2017-11-16 18:14 | Track - Track General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | The first batch of concrete (ticket ref: 19903414) for the pour of FTS derailment containment on 09/11/2017 exceeded the maximum 2 hours between batch time and end of pour time. The end time of pour finished 30 minutes after the 2 hour limit from batch time.
| 05SY - Systemwide | Cxxx-NCR-000667 | NCR | DFT DC - Balise box out installed in the incorrect location |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-02-28 | 2018-01-29 08:32 | -30 | 2017-11-16 18:32 | Track - Track General | 2500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | The reinforcement for the westbound track derailment containment in Connaught has been incorrectly installed and as a result, the balise has been installed in the incorrect location. This area has not yet been concreted.
| 05SY - Systemwide | Cxxx-NCR-000668 | NCR | PAD Tunnel Side Transition Duct - Equipment Labelling |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-05-31 | 2018-05-03 09:29 | -28 | 2017-11-17 09:38 | Systems - Ventilation and Pressure Relief | 1000 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Owing to a fabrication error, the steel plate equipment labels on the Tunnel Side Transition Ducts at PAD E and W in some instances have been labelled incorrectly - the labels currently label each Transition duct as a different transition asset than what it is.
| 05SY - Systemwide | Cxxx-NCR-000669 | NCR | WBP Formation Levels coordination in City End |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-05-16 | 2018-04-05 09:51 | -41 | 2017-11-20 12:37 | Track - Track General | 3000 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | WBP "City end" Formation works executed to the setting out information as per "civils" drawing, does not tie in with "track" formation levels calculated from the track model. Similar issue raised under Cxxx-EWN-03091, and instructed "that __jv co-ordinate formation design with existing information and deliver the formation works". See attached formation as-built file where datum for West end of "WBP city end area" Ch. 153-161 and East end Ch. 213 - 216 show formation levels being much higher than allowed tolerances, whole most of middle area is considerably low.
| 05SY - Systemwide | Cxxx-NCR-000670 | NCR | Welds less than 5m from slabs expansion joint on the FTS Barbican |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-12-22 | 2017-12-21 13:21 | -1 | 2017-11-20 11:42 | Track - Welding | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | 2 welds are 2.7m away from the slabs expansion joint between two FTS slabs E46 and E47 on the FTS Barbican on the EB.
| 05SY - Systemwide | Cxxx-NCR-000671 | NCR | Holes drilled by mistake in the web of the rail at E&B locations. |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-07-31 | 2018-07-25 12:00 | -6 | 2017-11-24 16:58 | Civil - Track | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Location: 14193 EB-NE RH, 13967 EB-SE RH, 12616 EB-NE RH Extra drills holes done at E&B Locations. The ultrasonic scanner showed defects next to bond holes at the locations stated above. These defects were caused by partially drilled holes next to final bond holes. It appears that they were drilled at the wrong location initially.
| 05SY - Systemwide | Cxxx-NCR-000672 | NCR | Scratches Present on Installed Pressure Doors at Level -6, Canary Wharf Station TVS |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-01-29 | 2018-01-08 15:03 | -21 | 2017-11-30 16:02 | Systems - Ventilation and Pressure Relief | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | As part of Cxxx-__-O4-ITP-CR143-50002, a final inspection was carried out on Level -6 Pressure Doors at Canary Wharf Station TVS. During the inspection, a number of these doors where shown to have scratches and chips to the protection coating of the frame a door leaf. The damage ranged from 2mm to 40mm in diameter.
| 05SY - Systemwide | Cxxx-NCR-000674 | NCR | Discoloration to Frame Fixings on Level -6 Pressure Doors at Canary Wharf Station TVS |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-01-29 | 2018-01-10 08:49 | -19 | 2017-11-30 16:12 | Systems - Ventilation and Pressure Relief | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | During an inspection as part of Cxxx-__-O4-ITP-CR143-50002, an observation was raised on D230036 (Pressure Door at Level -6). When inspecting the door frame, it was discovered that the structural threshold fixings have become discolored and potentially rusted. This is due to unwanted water ingress within this area which has since been resolved.
| 05SY - Systemwide | Cxxx-NCR-000675 | NCR | Deformed Seals on Pressure Doors at Level -6, Canary Wharf Station TVS |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-04-10 | 2018-02-16 09:02 | -53 | 2017-11-30 15:56 | Systems - Ventilation and Pressure Relief | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During an inspection as part of Cxxx-__-O4-ITP-CR143-50002, it was observed on the majority of Pressure Doors at Level -6 (18no. in total) that the pressure door seal has become deformed and did not sit flush within the door leaf when carrying our opening and closing. It is vital that the pressure seals sit flush and flat throughout the door frame to maintain the specified pressure requirement.
| 05SY - Systemwide | Cxxx-NCR-000676 | NCR | CWS-CMS - MCR conditions for HKD fixings are not met |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-04-25 | 2018-03-26 09:45 | -30 | 2017-12-05 11:50 | Systems - Ventilation and Pressure Relief | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | During an inspection on the CMS installed at Canary Wharf Station it was noted that __ HKD Standard tool-set flush anchors were used for CMS installation. According to CRL-MCR-003188, these anchors can only be used with following conditions: - HILTI Machine Setting Tool HKD-TE-CX is used to install the anchors. - Verification of the anchorage design by the manufacturer is provided; - To be used only when shallow embedment is essential. - To be used in concrete walls and floors but not ceilings. - Not to be used with either brick or concrete block. - All operatives to be trained and certificated. - Drill bit to be replaced as required by fixing manufacturer to ensure holes are neither over or undersized. - Contractor to select the most appropriate fixing in terms of corrosion resistance and mechanical load. - Pull out tests to be witnessed by CRL field engineer. Shallow embedment is not essential in the areas of installation and it's not clear if the rest of above conditions are met during the installation process.
| 05SY - Systemwide | Cxxx-NCR-000677 | NCR | Fire Hydrant Bolt Corrosion |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-03-28 | 2018-02-01 13:56 | -55 | 2017-12-07 13:52 | Systems - Fire Detection systems and Mains | 2000 |  | Material | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Not Defined | Completed |  | During a number of site inspections, it was noted that the galvanised bolts installed by the manufacturer (Walter Frank) connecting the hydrant outlets to the main body have started to corrode. This issue has been picked up in the Thames Tunnel, however some corrosion has also been found in the storage area. The fire hydrants were accepted under CRL-MCR-001963. Walter Frank have been contacted and they believe it is possible that the corrosion issue has been caused by the storage arrangements in the yard. However this will not affect the 25 year design life. Please find email from Walter Frank stating this point. It has been proposed that any corroded bolts will be cleaned with a wire brush to remove any surface corrosion and then painted with Galvanic paint for future protection. the status of these bolts will then be monitored to ensure the issue is resolved. These points were discussed with __ and __ on 07/12/17.
| 05SY - Systemwide | Cxxx-NCR-000678 | NCR | FAR E TSA Missing bolts due to no access |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-07-31 | 2018-07-09 06:42 | -22 | 2017-12-11 16:14 | Structural Engineering - Structural Engineering - General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | See attached drawing Cxxx-__-H-DWG-CRG03-50025 with mark ups and photos showing where the bolts between the modules could not be installed as the rope access team could not physically access these bolts. __s has confirmed that this is acceptable on condition that "the modules are pushed together with sufficient force that the flanges meet along their entire length, thus ensuring an airtight seal at the maximum design duty. Sealant must be applied to the flanges prior to closing the joint." The installer has confirmed this was done.
| 05SY - Systemwide | Cxxx-NCR-000679 | NCR | OHLE Earthing and Bonding connection not torqued |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-03-29 | 2018-02-06 16:01 | -51 | 2017-12-12 11:57 | Over Head Line Electrification - Earthing & Bonding | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | During Quality Surveillance for Earthing and bonding post installation checks ref: Cxxx-__-O4-RGN-CRG03-50288 v1.0 between Royal oak Portal and Paddington Eastbound, 1no bar to rail connection at chainage 1304 for TSP-PAD-E/B-1a was found loose and not torqued although marked as complete on both site and check sheet.
| 05SY - Systemwide | Cxxx-NCR-000680 | NCR | Positioning of Earth bar/Spider plate - Chainage location outside tolerance |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-02-21 | 2018-02-13 11:51 | -8 | 2017-12-12 12:15 | Electrical - Earthing & Bonding | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Supervision - Not Defined | Completed |  | During Surveillance inspection for Earthing and bonding post installation checks between Royal Oak Portal and Paddington Eastbound ref: Cxxx-__-O4-RGN-CRG03-50288 v1.0, TSP-CP1-E/B-1a with design ch 1024 has been installed at ch 1016 oustside tolerance for chainage location as per ITP ref:Cxxx-__-O4-ITP-CRG03-50184 v3.0 Paragraph 6.3.3.a It is suggested Acceptance parameters for ITP ref: Cxxx-__-O4-ITP-CRG03-50184 v3.0 Paragraph 6.3.3.a to be reviewed for chainage location and new revision issued to allow for a greater tolerance. Seek advice from design team
| 05SY - Systemwide | Cxxx-NCR-000682 | NCR | FAR E TVF Steel Gusset Plate Manufacturing Error |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-03-01 | 2018-03-06 16:05 | 5 | 2017-12-12 17:03 | Structural Engineering - Structural Engineering - General | 3000 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Verification Problems - Not Defined | Completed |  | See attached site GA drawings (P3) which show the gusset plate on steel B7 being manufactured facing the wrong direction.
| 05SY - Systemwide | Cxxx-NCR-000684 | NCR | Incorrectly installed power cables installed at TCR-E by __. |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-03-01 | 2018-02-07 17:39 | -22 | 2017-12-14 16:42 | Electrical - Cable Management | 2000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | The following power cables were installed to the wrong location at TCR-W By __: • Cxxx-PC-00000218 • Cxxx-PC-00000222 • Cxxx-PC-00000226 The cables were routed to the MCC though, as per design, they should have been routed to the FCR.
| 05SY - Systemwide | Cxxx-NCR-000685 | NCR | CMS installed through Fisher Street without an approved / assured design |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-04-30 | 2018-01-31 12:07 | -89 | 2017-12-14 15:27 | Electrical - Cable Management | 5000 |  | Documentation and Records | Use As-Is | 3 (3-6k) | Complete | Design Problem - Not Defined | Completed |  | __ would like to inform the client that CMS is being installed through Fisher Street and in the crossovers without an approved / assured design. To mitigate the above mentioned risk __ employ the same design principles as used elsewhere with SCL surface. The same bracket distances are adhered to and MCR approved __ bolts are used. Any changes to the current, ungated P-rev design have already been captured through Cxxx-FCD-000465 (reviewed by MMD), and will be recorded through redlines. In addition, CRL will be invited to inspect the installed works progressively as works continue to mitigate programme & quality risks.
| 05SY - Systemwide | Cxxx-NCR-000686 | NCR | Stepney Green - Level B5 - 18005 anchor bolts |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-01-10 | 2018-01-09 16:14 | -1 | 2017-12-17 14:36 | Structural Engineering - Bolted Connections | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | Has been identified that in __ Level B5 Lifting Beam 18005, all anchors bolts utilised __ HIT-V-R M20 x 260 long anchors in the floor have been ordered in the wrong size of 100 mm bigger . This is an typo error on the “Cxxx - __s - __ - Technical Design Drawings Cxxx-__-M-DWG-CR094-50005 V2.0” where the embedment depth for these anchors is 225mm instead of 125mm that is the correct embedment size, those anchors however have been ordered and installed based on the wrong size bolt and currently protruding from the slab level at around 130 mm. In the same Technical Design on the drawing checklist section and as well as in the setting out drawings document ''Cxxx-__-O4-LRC-CR094-50059'' there is stating the correct embedment size of 125mm and based on this correct size have been undertaken all calculations.
| 05SY - Systemwide | Cxxx-NCR-000687 | NCR | Track-WBPRH-W3-Damaged roller mounting bracket. (Point Operation Equipment) |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-04-17 | 2018-04-18 09:02 | 1 | 2017-12-18 10:07 | Civil - Track | 3000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Westbourne Park, S&C W3-W6, Ch 0+192, on bearer W304, and S&C W8, Bearer W804. Point Rod Roller Mounting Bracket has been damaged after Tamping activities.
| 05SY - Systemwide | Cxxx-NCR-000688 | NCR | Track-WBPRH-Aluminothermic Welding done in the wrong position. |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-03-01 | 2018-02-01 14:04 | -28 | 2017-12-18 10:15 | Civil - Track | 3000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Front of W9. Aluminothermic welding has been completed where a 6 Hole Glued Joint Rail should be installed.
| 05SY - Systemwide | Cxxx-NCR-000689 | NCR | Track-WBPRH- Failed Aluminothermic Weld at WBPRH. Turnback B. |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-04-25 | 2018-04-20 12:01 | -5 | 2017-12-18 10:24 | Civil - Track | 3000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Westbourne Park, Turnback B, Ch 0-171, TB06 During weld process an error have occurred, leaving a void and visible hole on the top of the rail.
| 05SY - Systemwide | Cxxx-NCR-000690 | NCR | FAR ATD Bolt Direction |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-01-03 | 2018-02-13 11:49 | 41 | 2017-12-20 10:37 | Structural Engineering - Structural Engineering - General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | As per Cxxx-FCD-000496, some of the bolts on the FAR ATDs are installed upside down (compared to the drawing). These connections are still torqued to the same requirements as per the ITP
| 05SY - Systemwide | Cxxx-NCR-000691 | NCR | Faulty tensorex unit in WBP |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-04-13 | 2018-01-08 15:07 | -95 | 2018-01-03 15:43 | Over Head Line Electrification - Over Head Line Electrification General | 1000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper handling of material | Completed |  | A faulty Tensorex unit has been supplied from the manufacturer. Please see attached pictures. Tensorex rivets in casing popped in Wesbourne Park. Rivets holding the casing closed that cover the internal spring have popped out causing the casing to open. Rivets should be intact and cover should be secure. * During the lifting process of the Tensorex out of its box, by the Linesmen at WBP, it was noticed that the casing had come apart, at this point another rivet popped and upon further inspection it was found that the other rivet was in the bottom of the box. 2x rivets popped in total.
| 05SY - Systemwide | Cxxx-NCR-000692 | NCR | FTS Barbican Eastbound – As-Built Survey – Cant deviation out of tolerance |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-04-05 | 2018-02-28 14:33 | -36 | 2018-01-05 13:46 | Track - Track General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | The as-built survey results for FTS Eastbound track show a cant deviation of 3mm at two locations taken at 2.5m intervals (between approx. CH 8015-8020, slab E47). This result is outside of the permissible variation of Cant from design for Slab Track of ±2mm
| 05SY - Systemwide | Cxxx-NCR-000693 | NCR | C11 Crossing – Damaged dowels in bearers |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-07-31 | 2018-09-04 06:44 | 35 | 2018-01-22 11:02 | Track - Track General | 1000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | During welding/de-stressing works, the thread of 3 number dowels inside the first three bearers of C11 (toe end) have been damaged. As a result, the chair screw is turning freely within the dowel and cannot be removed/tightened.
| 05SY - Systemwide | Cxxx-NCR-000694 | NCR | Bond Street Station CMS commenced without IFC drawings |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-05-31 | 2018-06-05 09:00 | 5 | 2018-01-18 10:03 | Electrical - Cable Management | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | Due to the immense programme pressures a decision was taken to commence station CMS installation without IFC drawings. This is not in line with the Works Information.
| 05SY - Systemwide | Cxxx-NCR-000695 | NCR | TCR Station CMS commenced without IFC drawings |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-05-31 | 2018-05-31 08:32 | 0 | 2018-01-18 10:13 | Electrical - Cable Management | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | Due to the immense programme pressures a decision was taken to commence station CMS installation without IFC drawings. This is not in line with the Works Information. Due to the immense programme pressures a decision was taken to commence station CMS installation without IFC drawings. This is not in line with the Works Information. Due to the immense programme pressures a decision was taken to commence station CMS installation without IFC drawings. This is not in line with the Works Information.
| 05SY - Systemwide | Cxxx-NCR-000696 | NCR | Farringdon Station CMS commenced without IFC drawings |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-05-31 | 2018-05-30 07:07 | -1 | 2018-01-18 14:11 | Electrical - Cable Management | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | Due to the immense programme pressures a decision was taken to commence station CMS installation without IFC drawings. This is not in line with the Works Information.
| 05SY - Systemwide | Cxxx-NCR-000697 | NCR | WOO-E scratch on VSD panels |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-06-28 | 2019-05-16 13:25 | -43 | 2018-01-18 11:27 | Electrical - General | 2000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | While delivering and moving the VSD panels at Woolwich East shaft, some scratches in the paint on one VSD panels have been noticed.
| 05SY - Systemwide | Cxxx-NCR-000698 | NCR | Liverpool Street CMS commenced without IFC drawings |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-05-31 | 2018-05-30 07:08 | -1 | 2018-01-18 14:52 | Electrical - Cable Management | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | Due to the immense programme pressures a decision was taken to commence station CMS installation without IFC drawings. This is not in line with the Works Information.
| 05SY - Systemwide | Cxxx-NCR-000699 | NCR | Whitechapel Station CMS commenced without IFC drawings |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-05-31 | 2018-06-05 09:11 | 5 | 2018-01-18 13:41 | Electrical - Cable Management | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Due to the immense programme pressures a decision was taken to commence station CMS installation without IFC drawings. This is not in line with the Works Information.
| 05SY - Systemwide | Cxxx-NCR-000701 | NCR | Paddington Station CMS commenced without IFC drawings |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-09-14 | 2018-07-30 12:55 | -46 | 2018-01-18 14:23 | Electrical - Cable Management | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | Due to the immense programme pressures a decision was taken to commence station CMS installation without IFC drawings. This is not in line with the Works Information.
| 05SY - Systemwide | Cxxx-NCR-000702 | NCR | LIS-E UPE-E Steelwork Installed in Incorrect Position |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-03-30 | 2018-05-08 13:51 | 39 | 2018-01-22 17:44 | Systems - Ventilation and Pressure Relief | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The Crossrail Field Engineer was invited to witness testing surrounding the completed secondary steelwork installation for the LIS-E (Blomfield) Under Platform Extract (UPE). It was found that the second set of completed steelwork was installed at LIS-W Westbound, instead of LIS-E Eastbound. The steelwork will require dismantling and reinstalling in the correct position.
| 05SY - Systemwide | Cxxx-NCR-000704 | NCR | WBP OHLE Works commenced without IFC drawings |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-06-28 | 2018-05-18 11:05 | -41 | 2018-01-23 16:08 | Over Head Line Electrification - Over Head Line Electrification General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | During __ surveillance on Westbourne park OHLE works ref: Cxxx-__-O4-RGN-CRG03-50288 Surveillance found all the following drawings used on site not IFC as required by ITP ref: Cxxx-__-O4-ITP-CRG03-50174 v3.0 paragraph 6.1.2 Chainage EB93 - XR/00/006 Cxxx-__-R6-DDB-CR076_SD005_1-00321 rev P03; Cxxx-__-R6-DDD-CR076_SD005_1-03210 rev P01; Cxxx-__-R6-DDD-CR076_SD005_1-03211 rev P02; Cxxx-__-R6-DDD-CR076_SD005_1-03212 rev P01; Cxxx-__-R6-DDD-CR076_SD005_1-03213 rev P01; Chainage EB79 - XR/00/005 Cxxx-__-R6-DDB-CR076_SD005_1-00319 rev P03; Cxxx-__-R6-DDD-CR076_SD005_1-03190 rev P01; Cxxx-__-R6-DDD-CR076_SD005_1-03191 rev P01; Cxxx-__-R6-DDD-CR076_SD005_1-03192 rev P01; Cxxx-__-R6-DDD-CR076_SD005_1-03193 rev P02; Cxxx-__-R6-DDD-CR076_SD005_1-03194 rev P01; Cxxx-__-R6-DDB-CR076_SD005_1-00353 rev P03; Cxxx-__-R6-DDD-CR076_SD005_1-03530 rev P01 this is only a sample of works taking place in the area at time of surveillance.
| 05SY - Systemwide | Cxxx-NCR-000705 | NCR | WBP OHLE works commenced without Conformity and Approval of Steelwork, cantilevers, Small Parts of Steel and HIT-Hy 200 A resin |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-06-28 | 2018-06-19 12:37 | -9 | 2018-01-23 16:22 | Over Head Line Electrification - Over Head Line Electrification General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | During Surveillance inspection for Westbourne Park OHLE works ref: Cxxx-__-O4-RGN-CR076-50004 it was found that OHLE works have commenced without a FAT report for Steelwork, cantilevers, Small Parts of Steel and without a MAR for HIT-Hy 200 A resin as required by ITP Inspection and Test Plan Mast Installation ref: Cxxx-__-O4-ITP-CRG03-50174 v3.0 paragraph 6.1.6 and 6.1.8
| 05SY - Systemwide | Cxxx-NCR-000706 | NCR | WBP OHLE masts torqued to the wrong value |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-03-30 | 2018-04-30 09:10 | 31 | 2018-01-23 16:30 | Over Head Line Electrification - Catenary Masts | 1000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Surveillance inspection ref: Cxxx-__-O4-RGN-CR076-50004 found XR/00/005 and XR/00/006 masts torqued as following M42 threaded rod 2965Nm for material steel grade 8.8 M30 threaded rod 1067Nm for material steel grade 8.8 (see check sheet attached) Instead of design values as follows: M42 threaded rod 4223Nm for material steel grade 10.9 M30 threaded rod 1515Nm for material steel grade 10.9 as per design drawings Cxxx-__-R6-DDD-CR076_SD005_1-03190 rev P01 and Cxxx-__-R6-DDD-CR076_SD005_1-03210 rev P01 and required by drawing Cxxx-__-R6-DDD-CRG03-15051 Please note this is just a sample and remaining masts in the area to be inspected for correct torque values
| 05SY - Systemwide | Cxxx-NCR-000707 | NCR | WBP OHLE reference numbers for mast, gantry, cantilever and drop tube are not recorded for traceability and referenced against the FAT report |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-06-20 | 2018-10-05 14:07 | 107 | 2018-01-23 16:39 | Over Head Line Electrification - Over Head Line Electrification General | 1000 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Surveillance inspection ref:Cxxx-__-O4-RGN-CR076-50004 found reference numbers for mast, gantry, cantilever and drop tube were not recorded for traceability and referenced against the FAT report as requested by Cxxx-__-O4-ITP-CRG03-50174 v3.0 paragraph 6.2.5, 6.3.1 and 6.6.1
| 05SY - Systemwide | Cxxx-NCR-000708 | NCR | Damaged to installed and IRN'd CMS |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-10-31 | 2018-08-15 13:45 | -77 | 2018-01-26 16:20 | Electrical - Cable Management | 1000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | Secondary CMS that has been installed to line up and allow cables to float onto T7 has been cut in place so that it now reaches T6, the cut is very rough, jagged and has not been galvanised, the earth bond to the primary tray has been removed.
| 05SY - Systemwide | Cxxx-NCR-000709 | NCR | Farringdon West TVF Steelwork 15no. HSFG Bolts missing __I Washers |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-03-26 | 2018-02-12 17:39 | -42 | 2018-01-25 13:02 | Structural Engineering - Structural Engineering - General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | 15no. __I washers were found to be missing from the HSFG bolts on the TVF steelwork on Farringdon west during the inspection by CRL.
| 05SY - Systemwide | Cxxx-NCR-000710 | NCR | Sump Covers - Lock Design on the Removable Plates |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-03-27 | 2018-03-27 07:54 | 0 | 2018-01-26 14:34 | Mechanical - Public Health Engineering | 3000 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During a joint inspection of the Sump Cover installation, it was noted that a helical screw with allen key bolt fixing design had been adopted as the means to lock and secure each sump cover plate. The sump cover plates need to be capable of removal to access and maintain the tunnel pumped drainage system below. The Tunnel Mechanical Equipment Specification (Cxxx-MMD-M-RSP-CR001-00002) section 4.5 calls for the locking device to be "operated using a 'T' Key". During the inspection a handful of locks were found to be stiff and requiring a lot of force to loosen. The concern surrounding this is an allen key connection is easy to burr or round-off (unlike star keys), leading to a unusable lock. The bolt would then need to have it's head drilled off, which would cause the helical screw to fall down the sump potentially damaging any assets below. The allen key size is also small (5-6mm) increasing the chances of rounding off. Furthermore, the design of the locking device is such that if the bolt is excessively unwound the helical screw will detach itself from the bolt, again falling down the sump potentially damaging any assets below. __ need to demonstrate that the current locking device satisfies all the requirements or provide a more robust locking device. One which will remain operational for the life of the sump cover (50 years) and which does not have the potential to damage assets if operated incorrectly.
| 05SY - Systemwide | Cxxx-NCR-000711 | NCR | TVS-BOS-E - VSD panels - damage to doors while delivering to FCR |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-09-30 | 2018-08-15 12:03 | -46 | 2018-01-26 17:43 | Electrical - LV Equipment | 2500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | BOS-E: the doors on both VSD panels have been damaged and need to be replaced. They were damaged while being transported to their final location, the Fan Control Room (FCR).
| 05SY - Systemwide | Cxxx-NCR-000712 | NCR | Royal Oak Portal CMS installation has commenced without IFC drawings. |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-06-28 | 2018-07-10 11:01 | 12 | 2018-01-29 15:22 | Electrical - Cable Management | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | Due to the immense programme pressures a decision was taken to commence with the station CMS installation without IFC drawings. This is not in line with the Works Information.
| 05SY - Systemwide | Cxxx-NCR-000713 | NCR | Westbourne Park Bus Deck CMS installation has commenced without IFC drawings. |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-07-11 | 2018-07-10 11:08 | -1 | 2018-01-29 15:55 | Electrical - Cable Management | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | Due to the immense programme pressure a decision was taken to commence with the station CMS installation without ICF drawings. This is not in line with the works information.
| 05SY - Systemwide | Cxxx-NCR-000714 | NCR | Westbourne Park ITP documentation error. |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-06-28 | 2018-04-16 07:12 | -73 | 2018-01-30 08:57 | Electrical - Cable Management | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | An ITP is in place but an error has been noted in the recommended pull test values. The pull tests carried out successfully but were at a greater value than recommended on the data sheets.
| 05SY - Systemwide | Cxxx-NCR-000715 | NCR | Farringdon East TVF Steel Alignment off 30mm |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-02-21 | 2018-02-20 12:58 | -1 | 2018-01-31 16:01 | Structural Engineering - Structural Engineering - General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | See attached photos showing the fan steel for TVF/B 1202 and TVFC/1203 being laterally mis-aligned by 30mm. Proposal to move the fan steel to suit the installed transitions. The ATD and TTD are concentric.
| 05SY - Systemwide | Cxxx-NCR-000716 | NCR | Damage to Walkway Arm |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-05-01 | 2018-04-30 09:14 | -1 | 2018-02-01 09:02 | Tunnelling - Walkways | 1000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | During a quality site visit to the Westbound trace between Royal Oak Portal and Paddington Station it was noted that one of the walkway arms had been damaged. It is unclear what the cause of the damage is. Please see the attached photos for more information. Damaged walkway arm is located at WB CH548 (Ring 26).
| 05SY - Systemwide | Cxxx-NCR-000717 | NCR | TVS - Whitechapel West - Steelwork - ATD/ASA/FID Steelwork - Fabrication Error - Incorrect Bracket Location |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-05-30 | 2018-06-25 10:22 | 26 | 2018-02-01 15:50 | Systems - Ventilation and Pressure Relief | 3000 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Steelwork Design Drawing Ref: Cxxx-__-M-DDD-D061_WS105_Z-30502 Suppliers Steelwork Drawing Ref: Cxxx-__-H-DWG-D061-50021 During Installation of the ATD/ASA/FID Steelwork at Whitechapel West Station it was identified that the B2 to B3 bracket (Shown in Section D in Cxxx-__-H-DWG-D061-50021) welded to the B2 Beam on the North-western side of the ATD-B / ASA-B Steelwork frame has been welded in the wrong position. The bracket has been welded approximately 400mm along the beam during fabrication. In the current condition Beam B3 can not be installed. Proposed resolution is for __ to cut the bracket off of the steel beam on site and repair the area in accordance with the Galvanising Repair Procedure. __ to design bolted connection for replacement bracket that can be installed on site in the correct location. This shall be accompanied by a report confirming that __ have assessed the remedial works and confirm that it meets the requirements of the design.
| 05SY - Systemwide | Cxxx-NCR-000718 | NCR | Damaged to installed and IRN'd CMS |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-11-30 | 2019-03-06 07:28 | 96 | 2018-02-05 11:35 | Electrical - Cable Management | 5000 |  | Damaged | Rework | 3 (3-6k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | High Level Ladder rack has been damaged at Connaught West in the open route.
| 05SY - Systemwide | Cxxx-NCR-000719 | NCR | Damaged to installed CMS BOS WB |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-10-01 | 2018-11-15 16:11 | 45 | 2018-02-08 11:48 | Electrical - Cable Management | 5000 |  | Damaged | Repair | 3 (3-6k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Low level HV ladder rack has been damaged, the side wall has been squashed/bent out of shape.
| 05SY - Systemwide | Cxxx-NCR-000720 | NCR | Spare Material Stored on IRNed HV Ladder Rack |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-04-07 | 2018-04-10 13:11 | 3 | 2018-02-07 11:29 | Electrical - Cable Management | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | It was noted on 17/11/17 during an IRN inspection that spare cant arms were being stored on top of the HV ladder. This is a recurring issue that has been seen throughout the trace. This specific instance was seen around CH7584. It was requested at the time that the material be removed and teams be re-briefed regarding the storage of materials and protection of installed works. However during a joint inspection with Crossrail on 06/02/18 it was noted that the spare material was still stored on the HV ladder, which has since been accepted via IRN and cables have been pulled. The attached photos are from the inspection on 06/02/18.
| 05SY - Systemwide | Cxxx-NCR-000721 | NCR | PLU separation fence max distance between posts exceeded |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-10-31 | 2019-10-07 12:06 | -24 | 2018-02-09 16:35 | Civil - Civil Engineering General | 10000 |  | Incorrect Installation | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | there is 17 cases where distance between posts exceeds specified maximum of 2.4m as result of greter distances timber rails were extended by joining two pieces of timber rail which led to non compliant connection detail.
| 05SY - Systemwide | Cxxx-NCR-000722 | NCR | Stepney Green Shaft – Level B4 (Eastbound) Type C Door – Core Drill Damage |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-08-08 | 2018-08-08 10:55 | 0 | 2018-02-12 16:28 | Systems - Cross-passage Doors | 3000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Contamination | Completed |  | Due to recent core drilling works in the doorway at STG shaft door type C (EB side), a segment of un-reinforced concrete (approximately 400x250mm in size) has cracked and therefore fallen away from the edge.
| 05SY - Systemwide | Cxxx-NCR-000723 | NCR | Damage to 2 Fibre optic cables (CR088-DAT-0009) & (CR088-DAT-00010) |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-08-31 | 2018-08-03 07:07 | -28 | 2018-06-22 09:31 | Communications and Control Systems - Fibre Optic Network | 3000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | There is damage to two fibre optic cables that have been installed and coiled and tied up in position awaiting installation into cabinets, both cables had previously been tested at both ends. Fortunately the damage to one cable (CR088-DAT-0009) is at the last metre of cable and can still be used, the damage to the other cable (CR088-DAT-00010) has resulted in the cable being unusable.
| 05SY - Systemwide | Cxxx-NCR-000725 | NCR | WOO-E ASA damage on splitter |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-06-27 | 2018-05-22 08:55 | -36 | 2018-02-14 11:59 | Mechanical - Mechanical Engineering General | 5000 |  | Damaged | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following a visit on site, it appears that two of the ASA splitters installed at high level have been bumped into. See picture attached
| 05SY - Systemwide | Cxxx-NCR-000726 | NCR | FAR E TVF Steelwork HSFG M30 Bolts Torquing |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-04-25 | 2018-03-15 08:18 | -41 | 2018-02-14 10:46 | Structural Engineering - Structural Engineering - General | 2500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | See attached drawing East TVF Steel Cxxx-__-H-DWG-M123-50024. There are two M30 HSFG bolts that cannot be accessed for torqueing.
| 05SY - Systemwide | Cxxx-NCR-000727 | NCR | Track- Failed Aluminothermic Weld at ROP |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-05-16 | 2018-03-15 16:13 | -62 | 2018-02-14 15:11 | Track - Welding | 5000 |  | Material | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Royal Oak Portal, S&C C1-C4, WB Ch 0+363.4 C210 weld has failed the inspection due to a hole in the head of the rail. See attached picture and QCR.
| 05SY - Systemwide | Cxxx-NCR-000728 | NCR | Cariboni top tubes received with wrong end caps |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-05-11 | 2018-04-30 09:16 | -11 | 2018-02-16 14:33 | Over Head Line Electrification - Over Head Line Electrification General | 5000 |  | Material | Reject | 3 (3-6k) | Complete | Material/Preservation Problems - Other | Completed |  | __ received 12 top tubes with wrong end caps on 14th Feb 2018. It should have been aluminium cap instead of plastic cap. Please find attached pictures and documentation.
| 05SY - Systemwide | Cxxx-NCR-000729 | NCR | LIS-W - __s LB13002 - Lifting Beams and Gantries |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-06-29 | 2018-05-16 15:26 | -44 | 2018-02-16 15:11 | Structural Engineering - Steel Member | 3000 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Not Defined | Completed |  | LIS-W LB13002 - was subject to a 13mm deflection of the bridge beam during load testing thereby failing the Load Test in accordance with Cxxx-__-E-GPD-CRG03-50005.
| 05SY - Systemwide | Cxxx-NCR-000732 | NCR | Supplier detailed design implemented for Attenuator stiffeners prior to formal CRL acceptance. |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-03-29 | 2018-04-03 10:18 | 5 | 2018-02-16 16:07 | Systems - Ventilation and Pressure Relief | 2000 |  | Planning | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Cxxx-NCR-000532 requested Airflow Stiffeners on TVS Attenuators have been installed prior to formal Crossrail acceptance of the corrective action recommended by the Contractor's lead Designers.
| 05SY - Systemwide | Cxxx-NCR-000733 | NCR | Damaged FID Power Cable - LIS-E SL+0 FID Run |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-04-30 | 2018-05-08 13:52 | 8 | 2018-02-16 16:32 | Electrical - Cable Management | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During a joint inspection between __/CRL a damaged FID Power cable was found at SL+0
| 05SY - Systemwide | Cxxx-NCR-000734 | NCR | TVS - WHI-E - FID / FID Steelwork Hole Mis-Alignment - Steelwork Manufacturing Error |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-04-18 | 2018-04-18 14:18 | 0 | 2018-02-19 09:27 | Systems - Ventilation and Pressure Relief | 3000 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Along one length of the FID steelwork at WHI-E the holes are misaligned with the Fan Isolation Damper. This appears to be a manufacturing error of __’s steelwork, roughly 30 holes are effected.
| 05SY - Systemwide | Cxxx-NCR-000736 | NCR | BZP nuts have been delivered instead of A2 SS |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-05-21 | 2018-07-23 11:34 | 63 | 2018-02-20 15:13 | Over Head Line Electrification - Supports | 10000 |  | Material | Rework | 2 (6-60k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | According to OHLE System Specification-Cxxx-MMD-R6-RSP-CR001-00001, section 8.8 (Fabrication Requirements), stainless nuts must be used in order to prevent corrosion. As per copy of order attached, Yard team have requested to Selkent 10000ud. of these nuts. However, the provider has sent BZP nuts instead with a delivery note that specified that they were stainless nuts. The team didn’t notice this mistake and built approximately 350 cantilevers to be installed in the tunnel. In consequence, all the cantilevers built and installed since November 2017 have the wrong type of nut with an important risk of getting corroded. The areas affected are: Paddington to Bond Street Eastbound, Royal Oak Portal to Whitechapel Westbound, new overlap at Pudding Mill Lane Portal (both bounds)
| 05SY - Systemwide | Cxxx-NCR-000737 | NCR | Earthing and Bonding in Open route not covered by ITP/Method Statement |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-05-21 | 2018-05-22 08:47 | 1 | 2018-02-20 15:49 | Over Head Line Electrification - Earthing & Bonding | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | The Method Statement and Inspection Test Plan has been designed for Earthing and Bonding in tunnels. The ITP mentions the open route in its scope however, does not specified any requirement. In consequence, the route of the cable is not clear and there is not any quality control in place for the installation of spider plates, especially, for the concrete box.
| 05SY - Systemwide | Cxxx-NCR-000738 | NCR | Track: Defective SO Unit on C13 |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-03-09 | 2018-03-26 10:58 | 17 | 2018-02-23 14:44 | Track - Turnouts | 3000 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | NCR raised to record traceability. C13 POE was installed and tested by Cxxx without any issues. However during the Testing of the POE by Cxxx one of the SO unit failed. Subsequent checks by Cxxx confirmed that the SO Unit was faulty (detection in one direction not working)and replaced it with one from C7. Paperwork was revised and resubmitted (including the serial number of the unit).
| 05SY - Systemwide | Cxxx-NCR-000739 | NCR | PAD Atmosphere Side Transition Access Hatch Orientation |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-06-28 | 2018-06-20 09:47 | -8 | 2018-02-22 12:05 | Systems - Ventilation and Pressure Relief | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | It has come to our attention that the access hatch on the Atmosphere Side Transition at PAD-W doesn’t align with the doorway at the upper level for access i.e. orientation of access hatch on the back of transition faces the back wall rather than being on the frontal face of the transition where the doorway at the upper level.
| 05SY - Systemwide | Cxxx-NCR-000740 | NCR | Use of RCD Protection within the Tunnel Lighting & Power Panel Design |  | Crossrail | PDP | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-07-22 | 2018-07-20 12:19 | -2 | 2018-02-22 15:28 | Electrical - Lighting | 10000 |  | Design | Rework | 2 (6-60k) | Complete | Design Problem - Other | Completed |  | The requirements for safety in the works information specifically identify that RCD,s protection on safety critical circuits shall not be used.
| 05SY - Systemwide | Cxxx-NCR-000741 | NCR | Handrail Thread Protrusion |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-06-29 | 2018-07-02 15:12 | 3 | 2018-02-22 16:48 | Tunnelling - Walkways | 6000 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Total 2400m of handrail has been installed in Thames tunnel and between Mile End and Eleanor St. Site inspection has revealed that the rear 2 handrail fixings (connecting the sliding extrusion to the support arm) only have 1 thread protrusion. It is understood that the standard practice is to allow for minimum of 3 rows of thread protrusion. This issue has been relayed back to __s designers. Likely causes are that the design did not factor in the additional thickness of the support arm. __ have advised (in progress meeting 23/01/18) that longer bolts are to be procured and the existing install is to be replaced.
| 05SY - Systemwide | Cxxx-NCR-000742 | NCR | FAR-W TVF-A 1101 JB clash with beam |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-03-16 | 2018-05-01 07:07 | 46 | 2018-02-23 17:34 | Structural Engineering - Structural Engineering - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | See attached photos showing clash between steel beam and fan junction box. The fan has been spun around 180 degrees so the JB is in the front of the shaft and the access door is at the back. There is still man access to the door and it is able to open
| 05SY - Systemwide | Cxxx-NCR-000743 | NCR | Track - HAS - Two cracked HAS sleepers |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-06-28 | 2018-06-05 11:42 | -23 | 2018-02-28 12:16 | Track - Rails and Sleepers | 5000 |  | Damaged | Rework | 3 (3-6k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | Two number HAS sleepers located on westbound track, approximate chainage 5160 (8m from transition with FTS) are cracked in the 4 foot. The cracks are on average 0.8mm wide and at least half of the sleeper deep.
| 05SY - Systemwide | Cxxx-NCR-000745 | NCR | Over torqueing of earth bar connections |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-06-07 | 2018-05-17 08:55 | -21 | 2018-03-06 14:58 | Electrical - Earthing & Bonding | 2000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During a site visit carried out on 05/03/2018 it was noticed that Torque Wrench SN 79108372850 used for Earthing and Bonding connections was set at the wrong value of 25Nm instead of 17Nm as required by ITP ref: Cxxx-__-O4-ITP-CRG03-50189 v2.0 paragraph 6.3.3. Installation witnessed for earth bars ref: TSP-E/B-6990-1b and TSP-E/B-7005-1a in Farringdon Eastbound platform area. An investigation to identify how many connections had been tightened with the torque wrench incorrectly set
| 05SY - Systemwide | Cxxx-NCR-000746 | NCR | No rebar scanning observed prior to drilling for installation of traction spider plate ref: TSP-E/B-7005-1a |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-06-07 | 2018-05-08 06:42 | -30 | 2018-03-06 15:19 | Electrical - Earthing & Bonding | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | During site visit carried out on 05/03/2018 no rebar scanning was observed prior to drilling for installation of traction spider plate ref: TSP-E/B-7005-1a located in Farringdon Eastbound Platform Wall area.
| 05SY - Systemwide | Cxxx-NCR-000747 | NCR | Missing Washers SCL Station |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-04-30 | 2019-04-18 09:43 | -12 | 2018-03-07 19:22 | Electrical - OHLE | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | During a Surveillance carried out by the OHLE Field Quality Manager at Tottenham Court Road Station (SCL station) has been found that the team installing the OHLE drop tubes did not place two of the washers specified in the ITP. These two washers are the ones highlighted in the image attached.
| 05SY - Systemwide | Cxxx-NCR-000748 | NCR | Glanding and Termination Checksheet not completed as per ITP |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-05-30 | 2018-05-14 14:53 | -16 | 2018-03-08 16:59 | Electrical - LV Equipment | 1000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Already installed and glanded TVS damper actuator power and control cables at TCR East did not have completed and signed termination and glanding check sheets as per ITP Cxxx-__-O4-ITP-CRG03-50236 v1.0. Section 6.3.5 of ITP states that check sheets will be completed but this has not been done immediately after the glanding in accordance with the ITP.
| 05SY - Systemwide | Cxxx-NCR-000749 | NCR | WHI-W ASA Steelwork Misallignement |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-07-31 | 2018-07-23 09:54 | -8 | 2018-03-09 16:29 | Systems - Ventilation and Pressure Relief | 2000 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Central beam across Void A for ASA-A/1631 WHI-W Level A appears to be installed incorrectly. The brackets from which this beam are mounted are not centrally located over the void. This has caused the central beam to be installed at an angle, making it impossible to install ASA-A/1631.
| 05SY - Systemwide | Cxxx-NCR-000750 | NCR | ASA Steel pillars realignment on level A - WHI-W |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-06-27 | 2018-04-23 07:14 | -65 | 2018-03-09 17:03 | Systems - Ventilation and Pressure Relief | 2000 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | ASA steel framework pillars are misaligned resulting in minimal or no space for attenuators to be placed and installed on the framework underneath. Steel pillars (two on void for ASA-B/1632 and one on void for ASA-A/1631) have been identified that are installed in incorrect alignment as per drawings - three have been checked, HOWEVER, the rest of the pillars need to be verified as well; please refer to Cxxx-__-H-DWG-D061-50021).
| 05SY - Systemwide | Cxxx-NCR-000752 | NCR | Damage to ROC and OLE Wire during Dymanic Testing |  | Contr | ALC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-06-13 | 2018-10-19 10:04 | 128 | 2018-03-14 11:39 | Over Head Line Electrification - Over Head Line Electrification General | 10000 |  | Testing and Commissioning | Rework | 2 (6-60k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | Damage to ROC and OLE wire at Stepney Green Junction during train testing between VDP to STG (WB Bore) at 7mph.
| 05SY - Systemwide | Cxxx-NCR-000753 | NCR | WHI-E &WHI-W ATD/TVF/TTD Access Hatch Orientation |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-06-27 | 2018-05-08 13:56 | -50 | 2018-03-15 17:59 | Systems - Ventilation and Pressure Relief | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Orientation of ATD-A/1791 and TTD-A/1794 at WHI-E, and ATD-B/1692 and TTD-B/1695 at WHI-W is incorrect as per Tunnel Ventilation System Equipment Specification (Cxxx-MMD-O8-RSP-CR001-00003)
| 05SY - Systemwide | Cxxx-NCR-000754 | NCR | Emergency Walkway Plank - Yellow Edge Tape Peeling off |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-09-01 | 2018-09-11 07:37 | 10 | 2018-03-16 15:29 | Mechanical - Mechanical Engineering General | 5000 |  | Workmanship | Rework | 3 (3-6k) | Complete | Material/Preservation Problems - Other | Completed |  | Emergency Walkway Yellow Edge Tape was seen to be peeling off in some locations in the Thames Tunnel - Eastbound Tunnel - CH21550 area.
| 05SY - Systemwide | Cxxx-NCR-000755 | NCR | WHI-E TSA Steelwork & Acoustic Floor Panel Hole Misalignment |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-04-20 | 2018-04-18 14:19 | -2 | 2018-04-06 15:24 | Systems - Ventilation and Pressure Relief | 2000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | There are 6 no of holes in the south-westerly corner of the steelwork that do not align with the corresponding ones on the steelwork.
| 05SY - Systemwide | Cxxx-NCR-000756 | NCR | Cables installed on non IRN'd CMS ROP-WBP. |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-07-31 | 2018-07-10 11:15 | -21 | 2018-03-20 12:40 | Electrical - Cable Management | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | Due to the immense programme pressure a decision was taken to commence installing cables on non IRN'd CMS between ROP-WBP. The CMS cannot be IRN'd as IFC drawings have not yet been issued.
| 05SY - Systemwide | Cxxx-NCR-000759 | NCR | FBW - Failed Weld 1024 - Damage on running edge |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-06-21 | 2018-05-03 08:58 | -49 | 2018-03-23 17:43 | Track - Welding | 5000 |  | Damaged | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the weld inspection of the Flash Butt weld 1024 located on eastbound track at chainage 7140, damage was discovered on the running edge of the rail next to the weld. The weld has not been accepted by the weld inspector (Jason Negus from McGinley) with such damage.
| 05SY - Systemwide | Cxxx-NCR-000762 | NCR | FBW - Non-compliant graphs for welds 981 & 1040 |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-06-21 | 2018-05-10 14:04 | -42 | 2018-03-23 19:08 | Track - Welding | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The machine graph for weld 981 shows the duration of the unstable phase of the welding process was 72 seconds. This is 2 seconds outside of the maximum of 70 seconds. The machine graph for weld 1040 indicates that the unstable phase of the welding process is non-compliant, despite it meeting the maximum duration of 70 seconds.
| 05SY - Systemwide | Cxxx-NCR-000764 | NCR | Track- FBW missing graphs 1025/979 |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-05-05 | 2018-05-08 13:49 | 3 | 2018-03-26 15:47 | Track - Welding | 500 |  | Software | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | Missing FBW Graphs for Welds no1025 and 979. CHs: 7034EB and 8089WB respectively.
| 05SY - Systemwide | Cxxx-NCR-000765 | NCR | Delivery of MES and ESS shaft doors without manufacturing file |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-05-31 | 2018-06-21 14:57 | 21 | 2018-03-26 16:01 | Systems - Cross-passage Doors | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Non-compliance to __ procedures and ITP Manufacturing files not sent by the subcontractor prior delivery. Cxxx-__-O4-LRC-CRG03-50033 Cxxx Systemwide Main Works Manufacturing & Test Plan Deliverables Pack - Eleanor Street Shaft Cxxx-__-O4-LRC-CRG03-50034 Cxxx Systemwide Main Works Manufacturing & Test Plan Deliverables Pack – Mile End Shaft
| 05SY - Systemwide | Cxxx-NCR-000766 | NCR | Damage to Stepney Green WB Type C door |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-08-31 | 2019-01-09 09:01 | 131 | 2018-03-26 16:30 | Systems - Cross-passage Doors | 3000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper handling of material | Completed |  | The type C door at Stepney Green shaft, Westbound, has been damaged during storage. The shaft side of the Type C door has been dented and the paint removed. Please see the attached photo for further details.
| 05SY - Systemwide | Cxxx-NCR-000767 | NCR | Track- C6 Switch Blade damaged |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-07-12 | 2018-07-10 11:17 | -2 | 2018-04-03 15:46 | Track - Turnouts | 50000 |  | Workmanship | Repair | 2 (6-60k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Right Hand Side, C6 Switch blade damaged, due to a Train accident, running through the points, with the blades placed in the wrong position.
| 05SY - Systemwide | Cxxx-NCR-000768 | NCR | HAS Track - EB Cracked HAS sleeper |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-07-27 | 2018-10-05 13:57 | 70 | 2018-04-03 16:56 | Track - Rails and Sleepers | 6000 |  | Damaged | Rework | 3 (3-6k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | One HAS sleeper located on Eastbound track at chainage 5771 is cracked.
| 05SY - Systemwide | Cxxx-NCR-000769 | NCR | Lockable Access Doors to TVS Fans |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-05-31 | 2019-06-06 09:08 | 6 | 2018-04-05 16:06 | Systems - Ventilation and Pressure Relief | 6000 |  | Manufacturing Defect | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | It was recently noted that none of the fans at Farringdon have a lockable access doors or a provision for locking. This contravenes requirement 6.5 d) in Cxxx-__-H-RSP-CRG03-50006: 'A means of padlocking the access door in the closed position shall be provided.' This is endemic thought the TVS with only a few exceptions. Last March during the FAT test it was agreed between CRL (Michael Zbucki), __ (Sam Panter) and __ that the ends of the locking pins would be pre drilled to enable a padlock to be installed, but this has only been done on very few fans. Also __ agreed to provide some locking device on the small access door to the impeller.
| 05SY - Systemwide | Cxxx-NCR-000770 | NCR | Eleanor St. - TID linkage cover modifications |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-07-31 | 2018-07-23 09:57 | -8 | 2018-04-06 09:36 | Systems - Ventilation and Pressure Relief | 2000 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The TID linkage cover panels provided by TROX for the central modules do not fit onto the dampers when they are coupled together. __ instructed __ to cut 50mm back of the cover plates to fit the existing cover panel as is. New flange bolt holes were required to be drilled into the cover panels to secure them to the damper. Both the cut panels and drilled holes were made good with galvanised paint.
| 05SY - Systemwide | Cxxx-NCR-000771 | NCR | Water leaking out of the HV cable |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-06-14 | 2018-05-18 10:35 | -27 | 2018-04-10 17:32 | Over Head Line Electrification - High Voltage Power Supply | 3000 |  | Manufacturing Defect | Reject | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Water leaking out of the HV cable. The drum the cable come off was 25KV-A-EB 30 and the cable number is CR092-OLE-00004 * • Location: Joint29 ch9535 Ring 3247 • Date: 7th April 2018 • Time Identified: 22:50 • Eastbound • Drum: 25KV-A-EB_30 Is a brand New Drum • Cable Number: CR092-OLE-00004 • Cable Length: 495m • Install Date : 5th April 2018
| 05SY - Systemwide | Cxxx-NCR-000773 | NCR | TVS - TCR-E - Electrical - Damper limit switch cable damage |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-05-18 | 2018-04-30 11:35 | -18 | 2018-04-11 13:07 | Electrical - LV Equipment | 1500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | TCR-E Level +2 Fan Isolation Dampers (FID) - During a site inspection on April 11th 2018, it was found that cable N105-CCC-00028 which runs from junction box N105-LVD-02740 to FID A has been damaged. The outer sheath has been sliced open and the steel wire armour exposed.
| 05SY - Systemwide | Cxxx-NCR-000775 | NCR | Damaged to Fly leads supplied for tunnel luminaires |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-07-31 | 2018-07-20 12:23 | -11 | 2018-04-12 16:12 | Electrical - LV Equipment | 500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | After inspecting Luminaires with fly leads attached to them that had been delivered to Plumstead stores it was noticed that a tear in the cable sheathing at the narrow base end of the plug, after inspecting 2 more fitting the fault was found again. a visit to the manufacturing company was arranged and the same reoccurring fault was found on all of the 54mm connecta plug fly leads.
| 05SY - Systemwide | Cxxx-NCR-000776 | NCR | __ Acoustics Limited Commencing Works without an Accepted Quality Plan |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-05-23 | 2018-06-14 10:32 | 22 | 2018-04-12 08:43 | Systems - Ventilation and Pressure Relief | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | Following the review of Cxxx __ Acoustics TVF Attenuators Quality Plan (ref. Cxxx-__-H-STP-CRG03-50004), Section 11.1 states quite clearly that 'The Project cannot commence until the Quality Plan and ITP have been accepted.' Based on the submission date of the document by __ (23/03/18) and given that the attenuators have long since been manufactured, it is therefore evident that this section of the Quality Plan has not been complied.
| 05SY - Systemwide | Cxxx-NCR-000777 | NCR | WBP - UTX chambers / OHLE cables in the water |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-10-31 | 2019-10-23 09:41 | -8 | 2018-04-13 17:38 | Electrical - General | 10000 |  | Incorrect Installation | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | WBP cables pulled/installed via UTX chambers C1, C27, C2a/C4a, C2/C4, C3, C5, C5a, C6, C7, C8, C9 and C11 are partially (depending on the Chamber location) partially submerged under the water. ever-changing water levels within UTX chambers understood to be caused by variable water table levels in west side (country end) of WBP site, while UTX in East side (city end) are not affected by this issue. The OHLE HV cables are not designed for being pulled in water. Please also refer to Cxxx-EWN-03900 (29/03/2018) - WBP – Risk of cable failure due to water ingress in Cxxx UTX Chambers (Note that on 10/04/2018, between 1m and 2m of water were observed in a few chambers and on 13/04/2018, the water dropped drastically down to below the cables)
| 05SY - Systemwide | Cxxx-NCR-000778 | NCR | Cable joint need to be earthed according to the design |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-07-22 | 2018-08-13 14:58 | 22 | 2018-04-13 15:04 | Over Head Line Electrification - Over Head Line Electrification General | 1000 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | CWS E/B cH 13880 Negative feeder joint is bonded to TSP. There are no joints installed for TFS/NFS (M&E Cxxx scope) so bonding cables are left lose. * There are 3 connections to this TSP: Negative feeder: joint is connected and bonded to TSP TSP-CNW-E/B-2b. TFS and NFS connections: Cable pulled by Cxxx M&E. No joints have been installed at that location so OHLE Cxxx are not able to connect the earthing cable to it. Both bonding cables are connected only to TSP at present. * Similar issue might be at different areas. It has to be double checked by Construction/ Quality.
| 05SY - Systemwide | Cxxx-NCR-000779 | NCR | Failure of M16 bolts connecting TVF flanges and Flexible Sleeve steelwork |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-06-27 | 2018-05-09 12:59 | -49 | 2018-04-18 15:00 | Systems - Ventilation and Pressure Relief | 1000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | At a number of locations (e.g. CWS, LIS) where Tunnel Ventilation Fans have been installed, it has been found that when tightening the M16 bolts that secure the flexible sleeve to the TVF flanges /airflow straighteners / transition ducts, the bolts are failing when torqued to their specified level. The ITP for Installation of Tunnel Ventilation Equipment (Cxxx-__-O4-ITP-CRG03-50084) states, in activity number 6.5.5, that M16 fan securing nuts/bolts should be torqued to 150Nm. Given a number of bolts are failing before they are torqued to this level, the works do not conform to the design requirements. It is suspected that the cause for the failure of the bolts is the misalignment of the holes around the TVF flanges and the flexible sleeves, meaning bolts often have to be pushed into place using force. This potentially leads to the bolt threads being damaged, forming stress concentrations susceptible to fail when the bolts are torqued up. Further to this, if the bolts are forced through at angles, they force likely is not evenly distributed around the bolt head/ TVF flange as they are torqued up. __ are required to confirm the root cause behind the failure of these bolts.
| 05SY - Systemwide | Cxxx-NCR-000780 | NCR | CP1 & CP2 Sump Cover Galvanisation Thickness not as per Fabrication ITP |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-07-31 | 2019-04-11 14:43 | -111 | 2018-04-17 15:27 | Mechanical - Mechanical Engineering General | 30000 |  | Manufacturing Defect | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | The galvanisation thickness on the sump covers in CP1 and CP2 were checked during a quality surveillance and found to be less than stated on the fabrication ITP. Average over 24 readings was 55.6 microns. ITP requirement is 100 microns minimum.
| 05SY - Systemwide | Cxxx-NCR-000782 | NCR | Sump Cover Installation without Decal Code 1 Design Drawing and Method Statement on eB |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-08-30 | 2018-09-18 08:18 | 19 | 2018-04-17 15:48 | Mechanical - Mechanical Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Sump Cover Installed in Cross Passage 1 and Cross Passage 2 without a decal code 1 design drawing and Method Statement on eB.
| 05SY - Systemwide | Cxxx-NCR-000783 | NCR | Traction Earth Wire found damaged in Farringdon at ch5800 Westbound road |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-07-06 | 2018-06-18 11:50 | -18 | 2018-04-18 14:18 | Electrical - Earthing & Bonding | 5000 |  | Damaged | Rework | 3 (3-6k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | During a progress inspection Traction Earth Wire was found damaged at ch5800 Westbound road in Farringdon Station area.
| 05SY - Systemwide | Cxxx-NCR-000784 | NCR | No change control for additional CMS installed above the MCC, and the VSD location change in the FCR. |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-07-31 | 2018-12-05 15:24 | 127 | 2018-04-30 11:33 | Systems - Ventilation and Pressure Relief | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | A planned Crossrail surveillance was undertaken on 18h April 2018. This looked at the TVS (Tunnel Ventilation System) electrical installation. Within the MCC room extra CMS (ladder) has been installed above the cabinet to accommodate extra cabling for the MCC. This has been installed onto existing CMS constructed by the previous contractor with no SOB (Site Observation) being raised, no evidence of extra load calculations has been provided to confirm that the existing CMS can support the additional loads. Within the FCR the locations of the VSD’s do not align with the drawing Cxxx-__-M-DDA-CR143_WS152_4-10004 ‘Canary Wharf Station, Tunnel Ventilation Layout, East Shaft, Level -3’ or sketch submission Cxxx-__-Y-RGN-CRG03-50105 Cxxx – ‘TVS MCC room and FCR layouts equipment setting out Sketches’. There is also no SOB to capture and confirm this change. In addition the drawing and sketches are both at code 1 yet do not align with each other. Section 6 in Cxxx - Procedure for IFC and Management of Drawings on Site Cxxx-__-O4-GPD-CRG03-50054 defines the process required for management of field changes.
| 05SY - Systemwide | Cxxx-NCR-000785 | NCR | BOS-W FID Support Steelwork - Level +3 |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-05-30 | 2018-05-30 14:34 | 0 | 2018-04-20 14:12 | Systems - Ventilation and Pressure Relief | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The NCR is in response to the EWN raised by Cxxx (Cxxx-EWN-03150) regarding the clash at BOS WTH Level +3, between Cxxx's FID support steelwork and the pressure door to be fitted on the wall separating the 2 FV shafts. The NCR is meant to formalise the subject topic discussion and agreement between Cxxx and Cxxx. Issue: Per the FID steelwork GA drawing (Cxxx-__-H-DWG-Cxxx-50042), the PFC and baseplates extend beyond the S/O and occupy the space in front of the doorway in both FV shafts, this introduces a clash with the pressure door swing if installed. Cxxx Technical Review: - Cxxx assessed alterations to the steelwork to resolve the clash however the requirement for hot works, lack of access, and significant impact to programme made this the least preferable option. - After a thorough review Cxxx suggested that it is feasible to eliminate the pressure door and leave the doorway permanently open as this has no impact on the TVS performance. Cxxx advised CRL that this can be easily implement provided Cxxx is in agreement with the proposed solution. - As part of the review, Cxxx checked the noise calculations and expect that the increase in noise levels due to the doorway opening in Level+3 is within the tolerances accounted for in the calculations, therefore the figures presented in the G&G report for Bond street can remain as-is. - Cxxx also checked the A&M strategy and note that the doorway has no impact on the maintenance activities to be carried in either shaft, including major activities such as the fan replacement. The A&M stipulates that the ventilation system must be isolated and locked off prior to fan removal from either shaft, this entails electrically isolating and closing the FID which eliminate impact of the doorway opening on the adjacent operational shaft. As for other maintenance tasks, these are typically done in non operational hours or weekend shutdowns and that's also outlined in the current A&M strategy. With that the A&M document need not be reissued. - CRL advised Cxxx that Cxxx confirmed via email the door removal has little or no significant impact on the TVS noise requirements in all operational modes, and the increase in noise levels due to the opening in the wall is not expected to affect D25 compliance. Other Discussions: 1) In the event that the Infrastructure Maintainer in the future decides to carry out maintenance work in one fan whilst the other is in operation, this is still possible: Works below the FID would require the FID to be closed, whilst works on the FID and above would require a temporary cover of the doorway opening - it would need to be openable as to still provide emergency means of escape. This doesn’t need to be documented at this stage as the A&M strategy assumption is that maintenance works take place when both fans are out. 2) In the event that a door is required in the future, the current door can be modified and installed with no impact to CRL programme, the following can be considered: a. Raised low-headroom door (so that when it opens the under side of the door is above the FID steelwork) or; b. Roller shutter door or; c. Sliding door. Cxxx kindly request CRL to review this NCR and confirm with all parties acceptance of the proposed solution of eliminating the pressure door at Level+3.
| 05SY - Systemwide | Cxxx-NCR-000786 | NCR | LIS Traction E&B cable routed without a CMS tray and with spacing between supports exceeding maximum required |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-08-29 | 2019-02-14 07:47 | 169 | 2018-04-20 13:19 | Electrical - Earthing & Bonding | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | During a joint visit with Cxxx, CRL and __ it was found that Traction E&B cable route within Liverpool Street Station West End Link Route, Eastbound side has not always been supported on cable tray and distance between cable support exceeded maximum 650mm required ADDITIONAL INFORMATION: See new photos attached. This NCR was raised to highlight the TEB earthing cable route in Liverpool Street station was not compliant with standard: - unprotected cable installed on __ and not on cable tray - __ spaced of more than 800mm Considering it is related to earthing cables only, could Crossrail confirm it is acceptable or advise the civil contractor, in charge of the cable route, to correct as per standard. Inspection was carried out with Fitzroy Best, from CRL
| 05SY - Systemwide | Cxxx-NCR-000788 | NCR | FTS Track - Absence of 28 day compressive strength results for concrete __ & LR upstands |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-06-26 | 2018-06-19 12:40 | -7 | 2018-04-27 09:26 | Track - Track General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | The concrete used to cast the upstands of the braking blocks and lateral restraints in slab W9 (pour date 06/06/2017, delivery ticket ref: 74270262) does not have compressive strength results for 28 days. One cube sample was tested at 3 days in order to determine if the concrete strength was sufficient to meet the requirement of 30N/mm2 before preload of the bearings - result: 31.5N/mm2. Following this, no further cubes were crushed and therefore no records of strength at 28 days has been recorded.
| 05SY - Systemwide | Cxxx-NCR-000789 | NCR | Delayed Submission of Method Statements for TVS works to eB |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-07-22 | 2018-07-02 10:06 | -20 | 2018-05-02 14:20 | Information Management | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | On 1st February 2018, it was identified that the following Method Statements for TVS related works have not been added into eB and subsequently transmitted to Crossrail as outlined in the Works Information Volume 2B Parts 12 and 14.7. The documentation below is safety critical. An incomplete Project record has the potential to delay successful completion and handover. Cxxx-__-O1-GMS-C101-50028 – Revision 3.0 - Cxxx - __ Temp Works RAMs for Liverpool Street West -Temporary Works Installation –Decommission E-mail from Paul Baird to Daniel Merryweather 27/11/2017. Not available on eB. Cxxx-__-O1-GMS-Cxxx-50018 – Revision 1.0 – Cxxx - __s - BOS-W - Method Statement – Temporary Works Installation / Decommission (Placeholder) E-mail from Paul Baird to Rishi Wason 08/01/2018. Not available on eB. Cxxx-__-O1-GMS-M123-50076 – Revision 1.0 – Cxxx - Farringdon – Method Statement – Temporary Works Installation (placeholder) E-mail from Paul Baird to Luke Chen 09/01/2018. Not available on eB. Cxxx-__-O1-GMS-B071-50038 - Revision 1.0 - Cxxx - Paddington TVS Cable Installation and Test Method Statement (placeholder) E-mail from Paul Baird to Christos Charidemou 12/01/2018. Not available on eB. Cxxx-__-O1-GMS-Cxxx-50073 – Revision 1.0 - Cxxx - Bond Street TVS Cable Installation Method Statement E-mail from Paul Baird to Rishi Wason 12/01/2018. Not available on eB. Cxxx-__-Z3-DWG-Cxxx-50001 – Revision 1.0 - Cxxx - __s - BOS-W - Lift plan for installation of steel sections and gantry beams in west draught relief area (placeholder) E-mail from Paul Baird to Rishi Wason 12/01/2018. Not available on eB. As a result of various exhaustive e-mail requests, many of the documents have now been uploaded, however there are still 2 Method Statements which are missing from eB. E-mails requests from CRL (Paul Baird) to the __ authors attached, also subsequent e-mails to John Chipman and Vere Peters. Cxxx-__-O1-GMS-C101-50028 – Revision 3.0 - Cxxx - __ Temp Works RAMs for Liverpool Street West -Temporary Works Installation –Decommission E-mail from Paul Baird to Daniel Merryweather 27/11/2017. Not available on eB. Cxxx-__-Z3-DWG-Cxxx-50001 – Revision 1.0 - Cxxx - __s - BOS-W - Lift plan for installation of steel sections and gantry beams in west draught relief area (placeholder) E-mail from Paul Baird to Rishi Wason 19/01/2018. Not available on eB. Following the e-mail requests (detailed above), EWN-03262 was raised on 1st Feb 2018 and now NCR-000789 raised on 1st May 2018.
| 05SY - Systemwide | Cxxx-NCR-000790 | NCR | Force gauge testing not carried out as per ITP |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-06-30 | 2019-03-19 07:46 | -103 | 2019-01-09 09:34 | Electrical - OHLE | 500 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Verification Problems - Not Defined | Completed |  | It has been noted that the force gauge testing of the doors at cross passages and shafts as not been carried out by __s as per the ITP. Force has been measured with the door opened and pushed on the door. However the ITP states an adaptor should be added to the end of the force gauge and force measure from the push bar.
| 05SY - Systemwide | Cxxx-NCR-000791 | NCR | ASA modules are larger than as per drawings on level A - WHI-W |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-07-31 | 2018-07-25 11:33 | -6 | 2018-05-04 11:35 | Systems - Ventilation and Pressure Relief | 2000 |  | Manufacturing Defect | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | ASA modules to be installed at WHI-W are larger than as per drawings. Please refer to WHI-W ASA Installation 37580D 113A where it can be seen that on Void B, the total length of the attenuators is 4745 mm compared to that of 4729mm as per drawing. Similarly on Void A, the total length of the attenuators is 4750mm compared to that of 4729mm as per drawings. An NCR (Cxxx-NCR-000750) was also raised to address the similar issue. However, at the time, it was believed that it was just the steelwork where rework needed to be done in order for these attenuators to be installed correctly. However, following the corrective measures of that NCR, subcontractors were still unable to install the attenuators correctly which is when dimensions were taken and compared to original designs and attenuators were found to be larger than compared to as per drawing.
| 05SY - Systemwide | Cxxx-NCR-000792 | NCR | Commencing Infill Panel Installation Works without an Accepted ITP/Drawing |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-07-05 | 2018-06-20 14:58 | -15 | 2018-05-04 12:47 | Mechanical - Mechanical Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | The TCR-E infill panel installation works were commenced without an accepted ITP (Cxxx-__-O4-ITP-CRG03-50247) and drawings. Whilst an inspection and test plan was in place for the installation process, it is understood that the installation of the infill panels was commenced without first obtaining a Code 1 acceptance of the Inspection and Test Plan from the Crossrail.
| 05SY - Systemwide | Cxxx-NCR-000793 | NCR | Commencing Infill Panel Installation Works without an Accepted Method Statement |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-06-01 | 2018-05-16 15:02 | -16 | 2018-05-04 13:14 | Systems - Ventilation and Pressure Relief | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | The TCR-E infill panel installation works were commenced at TCR-E without an accepted method statement (Cxxx-__-C4-GMS-N105-50001) Whilst method statement was in place for the installation process, it is understood that the installation of the infill panels was commenced without first obtaining a Code 1 acceptance of the method statement from the Crossrail.
| 05SY - Systemwide | Cxxx-NCR-000794 | NCR | No evidence of calculations to verify the additional loading to the existing CMS in the MCC Room. |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-05-01 | 2019-03-27 10:37 | -35 | 2018-05-08 15:23 | Systems - Ventilation and Pressure Relief | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | During the site surveillance it was observed that extra CMS (ladder) has been installed above the MCC to support additional cabling for the MCC. This CMS has also been used to support the MCC from the lifting eyes. The primary CMS route has been installed by another contractor. The additional loading to support the MCC/Cables using the existing CMS has not been forthcoming. Calculations are requested to verify the extra loading to the CMS, due to the additional support needed for the MCC and the additional weight of the cables, are within specifications. Works Information Volume 2B – Part 29 – Contractor’s Design, Assurance, Records and Certification (Systemwide) states: 29.2.1 General These records include documents submitted during the course of the works to verify compliance with the requirements specified in the Works Information. For the purposes of this section records means all drawings, CAD Data, specifications, calculations, software, schedules, reports, consents, approvals, permits, licenses, authorisations and the like that evidence the progress and compliance of the works through to Completion and the correction of Defects notified as outstanding at Completion or notified thereafter up until the defects date. Records shall be sufficiently detailed to provide assurance of compliance with the Works Information and provide support to the Contractor’s self-certification process.
| 05SY - Systemwide | Cxxx-NCR-000795 | NCR | Track-WBPRH_ As-Built Alignment at Westbourne Park Railhead, Ballasted Track |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-07-31 | 2018-07-27 12:59 | -4 | 2018-05-30 15:08 | Track - Turnouts | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | The geometrical and installation tolerances contained within ‘Cxxx-OVE-R4-RSP-CR001-50001 General Trackwork Specification’ for the ballasted tracks at Westbourne Park do not take in to account the line speed variations for the sidings and Turnback roads. As agreed that the tolerances have been brought in line with the NR specification ‘NR/L2/TRK/2102 Design and construction of track’ where tolerances are split into 6 categories based on line speed, we believe that working to this specification is a better fit considering the various lines speeds and the fact that we are connecting to NR tracks already installed to these tolerances. Our proposal based on the individual line speeds (Line Speed), NR specification ‘NR/L2/TRK/2102 (P110) and the Com Lots defined for Westbourne Park (Com Lot Definition and Westbourne Park Com Lot) is as follows: •Speed up to 20mph for TRK-SCB-MRCSD-S1_S4. •Speed between 25 and 40mph for: o TRK-SCB-TURNT-W3_W9 o TRK-BTK-TURNT-ABCE (Except EB branch) •Speed between 40 to 60mph for: o TRK-SCB-TURNT-W1_W2 o EB Branch (TRK-BTK-TURNT-ABCE)
| 05SY - Systemwide | Cxxx-NCR-000796 | NCR | Evacuation walkway planks installed without yelllow edge tape |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-08-30 | 2018-09-05 12:12 | 6 | 2018-05-10 09:58 | Mechanical - Mechanical Engineering General | 2000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | During a quality site visit to the Eastbound trace between Royal Oak Portal and Bond Street, it was noted that some evacuation walkway planks have been installed between CH2200 to CH2530 without the required yellow edge tape. Please see attached photo for more information.
| 05SY - Systemwide | Cxxx-NCR-000797 | NCR | WHI TVS Eastbound UPE Grille (West End of Platform)- Insufficient Fixing Area |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-09-27 | 2018-08-06 10:15 | -52 | 2018-05-16 10:08 | Systems - Ventilation and Pressure Relief | 2500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A standard UPE grille could not be installed under the platform at WHI, at the most westerly grille aperture of eastbound tunnel. This is due due to the aperture's proximity to a perpendicular wall. The perpendicular wall clashes with the right-side flange of the UPE grille that would normally be used to fix/seal the grille in place.
| 05SY - Systemwide | Cxxx-NCR-000799 | NCR | TVS- Specification of Glands Used for Tunnel Ventilation System Control Cables |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-08-31 | 2018-09-24 12:03 | 24 | 2018-05-17 09:45 | Communications and Control Systems - SCADA/Central Management System | 60000 |  | Incorrect Installation | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A portion of the Tunnel Ventilation control cable glands have been specified incorrectly and have not taken into consideration the diameter of the cable armour strands which falls under the range specified by the cable gland manufacturer’s guidelines. This issue applies only to ELV cables and is not applicable to power cabling - 0.75mm 7 core - 0.75mm 12 core - 0.75mm 27 core - 0.75mm 2 pair - 0.75mm 10 pair - 0.75mm 2 triad
| 05SY - Systemwide | Cxxx-NCR-000800 | NCR | TFM Anchor installed within no drill zone. |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-07-16 | 2018-08-07 14:29 | 22 | 2018-05-16 15:48 | Mechanical - Piping | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | At EB CH3039 an anchor bracket has been installed with the top right hand bolt installed with in the drill zone of one of the features within the tunnel ring.
| 05SY - Systemwide | Cxxx-NCR-000801 | NCR | ESS - Damaged LV Power Cables in MCC Room |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-08-30 | 2018-08-03 12:18 | -27 | 2018-05-18 12:47 | Electrical - Cable Management | 1500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | During a joint inspection between __/CRL, 3 x 4mm 3 core LV Power cables that run between the MCC and VSDA/B/C were found to have damaged outer insulation in the MCC room. Cable type: Fire Resistant, SWA, Prysmain FP600S (Class 2); __ Cable tags (CRL asset tags):Cxxx-PC-00000509(CR514-LVD-00017); Cxxx-PC-00000513 (CR514-LVD-00027); Cxxx-PC-00000517 (CR514-LVD-00037);
| 05SY - Systemwide | Cxxx-NCR-000803 | NCR | Whitechapel EB Core Drilling at Risk |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-08-31 | 2019-01-17 08:49 | 139 | 2018-06-20 13:44 | Electrical - Cable Management | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Please be advised that as part of ongoing works, towards completion of the OHLE switch cable routes and LV CMS install at WHI EB WTH, Cxxx __ have had to proceed at risk with core drilling prior to final confirmation of permission from CRL (captured though Cxxx-RFI-001406 & a 2nd RFI is to be raised which will reference this NCR). This is necessary due to having to proceed to meet the key programme Completion Dates for energisation. The response to RFI 1406 was; "in principal this is acceptable, but we need the locations and core diameter and depths confirming. Ideally please could the relevant Cxxx reinforcement drawing be marked up." RFI 1438 was raised to capture this information for the OHLE switch CMS and is waiting acceptance from CRL. An additional RFI to capture locations of core drilling for LV CMS has also been raised (Cxxx-RFI-xxxxxx). Core drilling was carried out prior to CRL response to ensure dates were met for the install. Cxxx-EWN-03463 has been raised to warn CRL of the drilling at risk.
| 05SY - Systemwide | Cxxx-NCR-000808 | NCR | No MCR for installed cable end terminals |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-08-01 | 2018-08-03 12:25 | 2 | 2018-05-29 08:07 | Electrical - Power Distribution | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | It was confirmed with the Crossrail delivery team that an MCR for these ferrules is required. The insulation material is unknown and the volumes for the terminations are large. This is a product that forms part of the permanent installation. __ procedure Cxxx-__-O4-GPD-CRG03-50016 Procedure for Approval and Acceptance of Materials, Products and Plant and Crossrail procedure CRL1-XRL-N2-GPD-CR001-50007 Demonstration of Materials Compliance Procedure state that the eB MCR system is to be used to demonstrate product compliance prior to installation. The product that was witnessed being used was the Kompress End Terminal 4mm2 Conductor Reference KPET 4 F Colour Orange.
| 05SY - Systemwide | Cxxx-NCR-000809 | NCR | __ couplings installed on without approved MCR |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-07-27 | 2018-06-21 08:07 | -36 | 2018-05-23 10:35 | Mechanical - Piping | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | Please be advised that due to an un-foreseen supply issue Cxxx __ can no longer procure Gruvlock couplings used in the installation of both the Tunnel Fire Main and Tunnel Pumped Drainage. To avoid any delay to this installation, our only option is to procure a different brand of the same type of coupling. Accordingly, __ couplings have now started to be installed within the tunnels. this installation has started prior to the MCR being submitted. This issue has been captured previously in Cxxx-EWN-03378.
| 05SY - Systemwide | Cxxx-NCR-000810 | NCR | OHLE Maintenance Plan during Test and Commissioning at Decal Code 3 procedure used for OHLE maintenance |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-11-30 | 2018-11-21 10:27 | -9 | 2018-05-24 11:46 | Electrical - OHLE | 1000 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | During joint __/CRL surveillance to look at Maintenance During Dynamic Testing for OHLE, it was noted that OHLE Maintenance Plan during Test and Commissioning document ref.Cxxx-__-R6-GPD-CRG03-50005 at Decal code 3 - Not Accepted was used for OHLE maintenance since start of Dynamic Testing
| 05SY - Systemwide | Cxxx-NCR-000811 | NCR | Track Geometry Test Report for Zones 1-4 not submitted before full line speed testing |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-07-06 | 2018-07-06 12:12 | 0 | 2018-05-24 12:20 | Track - Track General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | During joint __/CRL surveillance to look at track Maintenance During Dynamic Testing, it was noted that Track Geometry Test Report for Zones 1-4 (doc ref: Cxxx-__-O4-RGN-CRG03-50393) which is required before full line speed test begins has not been submitted and is a ‘Placeholder’ stage. Full line speed has already been achieved at time of surveillance(23/05/2018) Furthermore, Track Geometry Test Report for Zones 1 & 2 (doc ref: Cxxx-__-R4-RGN-CRG03-50081 Rev 1.0) submitted in December 2017 is still at ‘Draft’ stage and has not yet been approved by CRL
| 05SY - Systemwide | Cxxx-NCR-000812 | NCR | No documented evidence that Track Maintenance Inspection frequency has been achieved for high risk areas |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-07-06 | 2018-07-06 11:45 | 0 | 2018-05-24 12:38 | Track - Track General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | During joint __/CRL surveillance to look at track Maintenance During Dynamic Testing, it was noted that Track Maintenance during Dynamic Testing Plan (doc ref: Cxxx-__-K2-STP-CRG03-50027 Rev 3.0) Track Section 7.1.1 requires a Basic Visual Inspection (BVI) for high risk areas at a frequency of 4 weekly. The start date used for managing frequency was considered 26th February 2018 when dynamic testing started; based on this, for High Risk Areas, the surveillance requested 3 x MIF1 Forms (Maintenance Inspection Form) to meet the 13 weeks which had passed. It was stated these inspection had taken place, however no MIF1 form has been produced, as such no documented evidence exists to assure that these inspections have taken place. Furthermore, for plain line BVI with a 8 weekly frequency, MIF1 forms were only available for chainage 17450-16850. No verifiable records have been found for the other chainages within zone 1 and 2. Moreover, Sections 7.1.6, 7.3, 7.4, 7.5, 7.8 and 7.9 of doc ref:Cxxx-__-K2-STP-CRG03-50027 Rev 3.0 all refer to inspection under the BVI. As BVI MIF1 records are not being produced, no evidence exists to confirm that these inspections have been completed.
| 05SY - Systemwide | Cxxx-NCR-000813 | NCR | No documented evidence that Track Maintenance Inspections took place for Switches and Crossings during Dynamic Testing |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-07-31 | 2018-07-06 11:50 | -25 | 2018-05-24 12:45 | Track - Track General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Track Maintenance during Dynamic Testing Plan (Cxxx-__-K2-STP-CRG03-50027) Rev 3 Switches and Crossings Section 7.12.1 requires a weekly inspection. During joint __/CRL surveillance to look at track Maintenance During Dynamic Testing, it was noted that since the start of Dynamic Testing - 26 February 2018 - no records have been produced to evidence and assure that such inspections have been completed at the desired frequency.
| 05SY - Systemwide | Cxxx-NCR-000814 | NCR | No documented evidence that OHLE Maintenance Inspection frequency has been achieved for FOC |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-07-17 | 2018-07-06 11:51 | -11 | 2018-05-24 12:57 | Electrical - OHLE | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | OHLE Maintenance Plan during Test and Commissioning (Cxxx-__-R6-GPD-CRG03-50005 Rev 1.0) Appendix 1 Maintenance Regime for FOC (Flexible Overhead Catenary) requires a Ground Visual Inspection at 4 weekly frequency from the start of Dynamic Testing. The start date used for managing frequency was considered 26th February 2018 when dynamic testing started; During joint __/CRL surveillance to look at OHLE Maintenance During Dynamic Testing 3no. records were requested for Zones 1 & 2. It was stated that the OHLE inspection team had only been resourced early May; as such the 4 weekly frequency has not been met. A regime of inspection is now underway, however a complete Ground Visual Inspection run has yet to be completed.
| 05SY - Systemwide | Cxxx-NCR-000815 | NCR | Test Data Sheets (Page 1 of 2) including CRL Sign Off not available for First Train Run Testing as required by __ Procedure |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-06-21 | 2018-07-02 10:08 | 11 | 2018-05-24 13:14 | Systems - Other | 500 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Management Problem - Other management problem | Completed |  | A planned Crossrail surveillance was undertaken on 11th May 2018 which involved a witness of First Train Run Testing and 23rd May 2018 which involved a desktop review of records to support this testing. On checking, First Train Run Test Procedure Cxxx-__-O4-GPD-CRG03-50122 (Rev 3) Section 8.8.3 states “9) The Test Data Sheet of the testing day is signed-off by the Test Lead Engineer and Crossrail witness”. The Test Data Sheet comprises of 2 pages, the first containing the sign off and the second containing the test runs. Page 2/2 of the Test Data Sheet for testing on 12/05 was provided. It was stated that Page 1/2 has never been completed and could not be made available as defined by the procedure; as such this evidence does not exist as required. It was further stated that there has never been a CRL witness and associated sign off for any First Train Run testing completed to date. This goes against the documented and accepted procedure.
| 05SY - Systemwide | Cxxx-NCR-000816 | NCR | First Train Run Testing being completed by TTL not LTE as defined by __ Procedure |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-07-04 | 2018-06-19 12:48 | -15 | 2018-05-24 13:17 | Systems - Other | 500 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | A planned Crossrail surveillance was undertaken on 11th May 2018 which involved a witness of First Train Run Testing and 23rd May 2018 which involved a desktop review of records to support this testing. On checking, First Train Run Test Procedure Cxxx-__-O4-GPD-CRG03-50122 (Rev 3) Section 8.8.3 states “9) The Test Data Sheet of the testing day is signed-off by the Test Lead Engineer (TLE) and Crossrail witness”. On checking Page 2/2 of the Test Data Sheet for testing on 12/05 it was found the Lead Test Engineer was recorded as ‘Tamas Belluska’. TRD 79 which covered this testing recorded ‘Tamas Belluska’ as the Test Train Leader (TTL). No __ TLE was documented. The procedure clearly defines the TTL and LTE as separate roles in the definition section. Furthermore Section 8.8 defines requirements for both the LTE and TTL. If the TTL is acting as the LTE, undertaking both roles, the procedure should clearly define this to ensure that both roles can be completed by one individual, whilst providing the level of independence required.
| 05SY - Systemwide | Cxxx-NCR-000817 | NCR | Contact wire damaged between Paddington and Bond Street WB |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-08-28 | 2018-09-13 14:07 | 16 | 2018-05-30 14:01 | Electrical - OHLE | 6000 |  | Damaged | Rework | 3 (3-6k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | OHLE team have found that a section of contact wire has been damaged between Paddington and Bond Street Westbound, specifically at chainage 2310
| 05SY - Systemwide | Cxxx-NCR-000819 | NCR | No documented records of cleaning activities for TC1 in zone 1 and 2 |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-09-26 | 2018-08-20 09:50 | -37 | 2018-06-01 13:55 | Systems - Other | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | During surveillance to look at cleaning train TC1 activities it was noted that no documented records have been produced for TC1cleaning activities in zone 1 and 2 have
| 05SY - Systemwide | Cxxx-NCR-000820 | NCR | No documented conditional survey took place to assess the cleaning requirements of the open section |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-08-30 | 2018-08-01 10:42 | -29 | 2018-06-01 13:59 | Systems - Other | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | During __ surveillance to look at cleaning train TC1 activities it was noted that no documented conditional survey took place to assess the cleaning requirements of the open section as required by Method Statement ref: Cxxx-__-O1-GMS-CRG03-50223 rev 3.0 paragraph 1 - Scope of Works
| 05SY - Systemwide | Cxxx-NCR-000822 | NCR | Rusty Sump Cover CP09 |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-08-20 | 2018-07-10 14:08 | -41 | 2018-06-01 16:44 | Mechanical - Mechanical Engineering General | 3000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | During a sump cover inspection in CP09 between Stepney Green and Whitechapel on the 16th of May 2018, water was observed to be leaking from the Cross passage rings. The water had then dripped onto the sump cover and in turn caused a dark discolouration and rust to be formed on the sump cover. Though the covers will be replaced due to the insufficient galvanised thickness, however this could potentially cause damage to the replacement covers and other surrounding installed assets.
| 05SY - Systemwide | Cxxx-NCR-000823 | NCR | Rusty Sump Cover and CMS due to Ingress in CP13 |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-08-20 | 2018-07-10 14:25 | -41 | 2018-06-01 17:25 | Mechanical - Mechanical Engineering General | 1000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | During a quality inspection on the 30th May, water ingress was noticed in Cross passage 13. A pool water was present in the cross passage which was observed to be coming from the cross-passage tunnel rings. Water had dripped onto the sump covers and CMS which caused surface discolouration and rust – See attachment. An NCR (Cxxx-NCR-000822) has been raised for same issue in CP09.
| 05SY - Systemwide | Cxxx-NCR-000824 | NCR | T&C - Geometry Defect L3 – Narrow Gauge – FTS Barbican WB |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-07-18 | 2018-07-20 12:24 | 2 | 2018-06-06 10:43 | Track - Track General | 3000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Section between CH7906 – 8106 WB, FTS Barbican The minimum value recorded by the recording car, with the track under load, is 1427.5mm in that section. This value is outside the installation tolerances and exceeds L3 thresholds (-6/+9mm). L3 thresholds were set by __ as indicative values based on experience and maintenance tolerances.
| 05SY - Systemwide | Cxxx-NCR-000825 | NCR | Support fixing on Fire Proofing layers BOS |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-07-26 | 2018-08-03 12:39 | 8 | 2018-06-07 10:09 | Electrical - OHLE | 5000 |  | Supervision/Management | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | OHLE Fixings are currently installed with a different embedment than the one they are designed for
| 05SY - Systemwide | Cxxx-NCR-000826 | NCR | Support fixing on Fire Proofing layers STG EB |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-06-28 | 2018-08-03 12:44 | 36 | 2018-06-07 10:20 | Electrical - OHLE | 5000 |  | Supervision/Management | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | OHLE Fixings are currently installed with a different embedment than the one they are designed for
| 05SY - Systemwide | Cxxx-NCR-000827 | NCR | Support fixing on Fire Proofing layers STG WB |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-06-22 | 2018-08-03 12:44 | 42 | 2018-06-07 10:24 | Electrical - OHLE | 5000 |  | Supervision/Management | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | OHLE Fixings are currently installed with a different embedment than the one they are designed for
| 05SY - Systemwide | Cxxx-NCR-000828 | NCR | Support fixing on Fire Proofing layers WHI |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-06-22 | 2018-08-03 12:46 | 42 | 2018-06-07 10:28 | Electrical - OHLE | 5000 |  | Supervision/Management | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | OHLE Fixings are currently installed with a different embedment than the one they are designed for
| 05SY - Systemwide | Cxxx-NCR-000829 | NCR | Walkway Gauging Clash |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-10-30 | 2018-10-05 12:29 | -25 | 2018-06-15 08:56 | Tunnelling - Walkways | 5000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | During installation of the walkway (EB&WB) between Canary Wharf and Stepney Green some gauge clashes were raised resulting in sections of the walkway not being installed. Further details of the locations are below; - WB CH12633 to 12669, two panels at rings 1742 & 1754. The support arms were found to be approximately 30mm offset prior to the extrusion being installed. - EB CH12055 to 11880, extrusion was found to be out of gauge about 30m from CP 10 and panels could not be installed. No items were left within the train envelope at the end of shift and the area was made safe for the passage of trains.
| 05SY - Systemwide | Cxxx-NCR-000830 | NCR | Unable to install damper bolts due to actuator cover |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-07-31 | 2018-06-20 12:30 | -41 | 2018-06-08 13:49 | Structural Engineering - Structural Engineering - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | Due to the actuator cover, there is no access to reach behind to install the nut and 2 washer. Therefore, there is one bolt missing next to the actuator. See photos below.
| 05SY - Systemwide | Cxxx-NCR-000831 | NCR | Walkway Gauging Clash - Paddington |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-11-28 | 2018-09-04 06:45 | -85 | 2018-06-08 15:11 | Tunnelling - Walkways | 2000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Previous Construction - Other | Completed |  | Between EB CH1576 and CH1596 it has been found that the installed walkway cannot be fitted within the gauge requirements of 1535mm from TSOP. the extent of the clash is as follows; - Ring 668 = 120mm (1415mm from TSOP) - Ring 671 = 82mm (1453mm...) - Ring 673 = 25mm (1510mm...) - Ring 675 = 27mm (1508mm...) - Ring 677 = 23mm (1512mm...) A scanned survey of the area has been carried out, it is thought that the issue is caused by tapering of the tunnel ring segments. Survey data for the area confirms an offset of tunnel ring by up to 200mm, it would appear that the setting out of the track did not take this into account.
| 05SY - Systemwide | Cxxx-NCR-000832 | NCR | Continuity Clips Damaged |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-08-31 | 2018-09-11 07:21 | 11 | 2018-06-11 08:40 | Mechanical - Piping | 2000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | It has been found that a number of continuity clips have been damaged or broken. This has been an issue on both the TPD and TFM. However is more prevalent on the TPD. Particularly in areas where walkway has been installed. Further to this some broken continuity clips have been discovered after IRN and T&C activities were completed. To replace the continuity clips the integrity of the pipe would be broken and IRN/T&C activities would have to be done again. It is therefore suggested that a method of providing continuity without undoing the couplings is used.
| 05SY - Systemwide | Cxxx-NCR-000833 | NCR | Whitechapel TFM UTX has concrete overspill in it |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-08-31 | 2018-10-29 11:54 | 59 | 2018-06-11 15:30 | Mechanical - Piping | 2500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | it was noted that the EB UTX duct for the TFM at Whitechapel crossover had some concrete overspill at the opening of the pipe, see photo attached. There is a concern that the pipe may be blocked further in.
| 05SY - Systemwide | Cxxx-NCR-000834 | NCR | TFM Hydrant Bungs Stolen/Missing |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-08-31 | 2018-09-04 08:00 | 4 | 2018-06-11 16:19 | Mechanical - Mechanical Engineering General | 1000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | During a Quality inspection of the TFM in Thames Tunnel it was noted that a number of the hydrant bungs were missing. there was evidence that the chain had been tampered with in order to detach the bungs. This is an issue that has occurred before where by people were removing the bungs. the __ security time have been made aware of this issue. Please see attached photos showing where the bungs have been removed.
| 05SY - Systemwide | Cxxx-NCR-000835 | NCR | Non compliant core drilling at Farringdon EB |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-08-31 | 2018-06-15 06:14 | -77 | 2018-06-13 07:22 | Electrical - Cable Management | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | CA drillers have been instructed to core drill at Farringdon EB into reinforced concrete in order to provide CMS support brackets for OHLE switch CMS. The instruction stated a maximum of 15mm of re-bar to be removed to achieve a hole depth of 60mm. However it was confirmed on site that on Saturday 9th that they have drilled through one section of 37mm depth re-bar. It has been confirmed that this is an isolated incident and they are proceeding to only drill through a max of 15mm of re-bar to achieve a depth of 60mm. Permission to drill re-bar was given through Cxxx-RFI-001439.
| 05SY - Systemwide | Cxxx-NCR-000836 | NCR | Cxxx TVS Systemwide - Damper Actuator Thermal Jacket |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-09-12 | 2018-08-30 12:11 | -13 | 2018-06-14 16:16 | Systems - Ventilation and Pressure Relief | 2000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate man -machine interface | Completed |  | The fire protection thermal cover on “Face Mounted” actuator needs to be lifted to be able to close the dampers. The damper blades bite onto the cover if not removed while closing/opening the dampers. This can damage the dampers particularly during the T&C phase when the damper operation is automatic. This issue also compromises the thermal integrity of the fire protection cover.
| 05SY - Systemwide | Cxxx-NCR-000837 | NCR | Cxxx TVS TCR W +2 Fan Isolation Dampers Installation |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-09-12 | 2018-08-22 10:09 | -21 | 2018-06-14 16:21 | Systems - Ventilation and Pressure Relief | 1000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | The actuators for FIDs (Fan Isolation Dampers) on Level +2 are installed such that there may be an issue with the correct functioning of the actuator. This also prevents thermal jackets to be fitted on the actuators. The actuators are too close to the floor which may prevent them functioning as intended. This issue also compromises the thermal integrity of the fire protection cover as they can’t be fitted.
| 05SY - Systemwide | Cxxx-NCR-000838 | NCR | DN200 Pipe Steel Grade |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-08-31 | 2018-07-03 07:04 | -59 | 2018-06-15 09:57 | Mechanical - Piping | 1000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | After a review of the pipe material certificates the Streel Grade used for the DN200 TFM Pipe is not what was requested in the Works information. It is the same grade of Steel used for the smaller pipe sizes which are dual certified to BS EN 10217 and 10255 (Grade P235 and S195). The difference between the grades can be found in BS EN 10217: - P235 pipework is usually used for Heavy Duty M&E Installations. - P265 is used in the Oil and Gas, Power and Process Industries.
| 05SY - Systemwide | Cxxx-NCR-000839 | NCR | C9 points damage due to run through |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-10-30 | 2018-11-21 10:02 | 22 | 2018-06-21 11:02 | Track - Turnouts | 100000 |  | Damaged | Repair | 1 (>60k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | Construction train ran through C9 points and damaged the switches. Extend of damage to be confirmed.
| 05SY - Systemwide | Cxxx-NCR-000840 | NCR | Track Lubricator Cabinets - stainless steel welds cleaning inconsistent |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-08-20 | 2018-07-20 13:17 | -31 | 2018-06-21 12:11 | Track - Track General | 3000 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The supplier of the track lubricators (__) informed __ of an issue with the stainless steel welds cleaning inside the cabinets on items already delivered to site. They raised an internal NCR (SHE-3082) and have recalled the products.
| 05SY - Systemwide | Cxxx-NCR-000841 | NCR | Luminaire installation has commenced without an code 1 approved ITP |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-08-31 | 2018-08-08 10:33 | -23 | 2018-06-22 10:16 | Electrical - Lighting | 1000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | Due to the immense programme pressures a decision was taken to commence with the lighting luminaire installation without an code 1 approved ITP. The ITP was submitted to Crossrail for review and was given positive feed back but also stated that further review was required.
| 05SY - Systemwide | Cxxx-NCR-000843 | NCR | Tunnel Ligthing Luminaires Delivered Damaged |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-10-18 | 2018-10-22 15:11 | 4 | 2018-07-20 13:29 | Electrical - Lighting | 5000 |  | Damaged | Repair | 3 (3-6k) | Complete | Material/Preservation Problems - Improper handling of material | Completed |  | A number of Luminaires have been delivered with damage/surface defects. A box of luminaires was observed during a surveillance to be have been delivered in incorrect packaging. The correct packaging should have a layer of cardboard that separate each luminaire to prevent damage. However this was not the case in the one box and several of the luminaires had surface defects.
| 05SY - Systemwide | Cxxx-NCR-000844 | NCR | Screeding works started without an approved MCR. |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-08-31 | 2018-07-03 08:27 | -59 | 2018-06-22 15:33 | Materials - General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | Screeding activities have started in a number of Cross Passages without an approved MCR for Isocrete and RBS Rapid Concrete.
| 05SY - Systemwide | Cxxx-NCR-000845 | NCR | ACO drains not installed as per design in a number of Cross Passages |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-10-31 | 2018-08-20 10:50 | -72 | 2018-06-26 07:20 | Civil - Drainage | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | ACO drains have not been installed as per Cxxx design in a number of Cross Passages. A typical example is CP15: The design and as-built is seen attached. It clearly shows the 135mm x 250mm deep channel running the full width of the flooring. It appears in some cases that this is not how the drains have been installed. On site the channel does not run full width.
| 05SY - Systemwide | Cxxx-NCR-000846 | NCR | MK couplings installed without approved MCR |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-09-03 | 2018-08-30 12:13 | -4 | 2018-06-26 09:08 | Mechanical - Piping | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | MK couplings have been installed on the pipework without an approved MCR in place.
| 05SY - Systemwide | Cxxx-NCR-000847 | NCR | TUCA - RRAP not properly fitting on the slab |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-10-05 | 2018-11-05 10:53 | 31 | 2018-06-28 13:26 | Track - Track General | 1000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | It has been reported that the 4ft panels were not fitting properly when they were being installed and have not been installed exactly as per the supplier's instruction.
| 05SY - Systemwide | Cxxx-NCR-000848 | NCR | Damaged Walkway Plank |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-08-31 | 2018-08-17 07:16 | -14 | 2018-06-28 08:40 | Mechanical - Mechanical Engineering General | 1000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | During an inspection on 27/6/18 it was noted that the outside walkway plank had been damaged at Ring 281 between ROP and PAD on the EB. The yellow edge tape had been ripped and the grip structure scraped and flattened. Please see the attached photos.
| 05SY - Systemwide | Cxxx-NCR-000849 | NCR | AEW damaged at Farringdon station east end of platform |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-10-04 | 2018-09-13 14:11 | -21 | 2018-06-29 13:54 | Over Head Line Electrification - Over Head Line Electrification General | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | AEW cable has been found damaged at Farringdon station east end of platform. Please see attached picture.
| 05SY - Systemwide | Cxxx-NCR-000850 | NCR | Tunnel Luminaires installation spacings not to design details |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-12-11 | 2018-11-12 12:40 | -29 | 2018-06-29 15:45 | Electrical - Lighting | 5000 |  | Incorrect Installation | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Tunnel Luminaires installation spacing (Mains to UPS) observed during an inspection was not to the 9.5m spacing in design details specified in the Tunnel Lighting Performance Specification. Location is in CH2086 (Ring #986) Paddington to Bond Street Westbound Tunnel. Spacing between two luminaires at the time of inspection was 6.5m Ring 986.
| 05SY - Systemwide | Cxxx-NCR-000851 | NCR | Tunnel Lighting Luminaires - Excessive Fly-Lead Lengths & Coils |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-09-27 | 2018-11-15 16:17 | 49 | 2018-07-04 16:15 | Electrical - Lighting | 3000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | An observation of the tunnel lighting luminaire installation within the trace, has identified that the 3-core fly-leads from the luminaires to the socket joints are being configured and tied in a manner which may introduce a risk by mutual conductance due to the proximity of the 25kV AC OHLE system. It is therefore imperative that an assessment be made in accordance with the requirements contained within BS7671:2008+A3:2015 (Requirement for Electrical Installations), regulations 132.11 and also 332.2 as quoted below. • 132.11 - "The electrical installation shall be arranged in such a way that no mutual detrimental influence will occur between electrical installations and non-electrical installations. electromagnetic interference shall be taken into account" • 332.2 - "Consideration shall be given by the designer of the electrical installation to measures reducing the effect of induced voltage disturbances and electromagnetic interferences (EMI)" In so far as can be ascertained, the excess fly-lead cable is coiled such that this will give rise to an induced voltage that may be stored or give rise to a potential voltage, creating direct risk to the IM after the TLPP has been isolated and locked off. This risk has not been identified in the IHA nor the risk assessed or included on the CDM risk register.
| 05SY - Systemwide | Cxxx-NCR-000854 | NCR | __s carrying out CPD remedial works to out of date Method Statements |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-03-28 | 2019-02-01 15:07 | -55 | 2019-01-08 16:12 | Mechanical - Mechanical Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | __s have been carrying out works on the doors in both the cross passages and the shafts. Cxxx-__-O1-GMS-CRG03-50023 - Cxxx - Method Statement - Risk Assessment Method Statement Installation RAMS - Type A - B and C Cross Passage Door and Cxxx-__-O1-GMS-CRG03-50280 - Cxxx - Risk Assessment Method Statement Installation (RAMS) – MES, ESS, FIS Type A Shaft Doors are both out of date.
| 05SY - Systemwide | Cxxx-NCR-000855 | NCR | CP5 WB Door not opening |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-09-30 | 2019-01-30 14:02 | 122 | 2018-07-10 15:01 | Mechanical - Mechanical Engineering General | 1500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | During surveys of Cross Passage Doors by the O&M team it has been noted that the right hand door at CP5 WB does not open.
| 05SY - Systemwide | Cxxx-NCR-000858 | NCR | Missing Cxxx cable no. M135-TSP-00009 |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-10-26 | 2018-08-30 15:07 | -57 | 2018-07-11 12:26 | Communications and Control Systems | 5000 |  | Material | Rework | 3 (3-6k) | Complete | External Phenomenon - Theft, tampering, sabotage, or vandalism | Completed |  | __s pulled in 400M of cable - M135-TSP-00009, Cxxx have said they arrived to work on the cable but could not locate it. __s supplied a cable installation check sheet, the cable register has it recorded as installed, the IRN cover sheet has been sign by Cxxx which included this cable. As a result Cxxx have had to pull in another cable to replace missing one.
| 05SY - Systemwide | Cxxx-NCR-000859 | NCR | Silvertown Footbridge - Wrong spacing for drilled holes in the main deck |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-11-30 | 2019-08-20 16:14 | -102 | 2018-07-11 15:05 | Civil - Civil Engineering General | 2000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | The holes for the anchors M10x75mm supporting the fins (posts) located on the main deck on both sides of the Silvertown Bridge have been drilled at an incorrect distance. The design indicated 100mm distance between centres as shown on the drawing Cxxx-OVE-S-DDD-CR146_Z-55500, C01, Detail 3. The drilled distances range from 128mm to 142mm.
| 05SY - Systemwide | Cxxx-NCR-000860 | NCR | Damage to RH Switch Rail of C5 caused by Milling Machine |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-10-31 | 2018-10-26 09:35 | -5 | 2018-07-13 13:15 | Track - Turnouts | 50000 |  | Damaged | Repair | 2 (6-60k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | During the milling of C5, the machine created a defect approximately 15cm long and 1cm deep on the RH switch rail. See attached pictures.
| 05SY - Systemwide | Cxxx-NCR-000862 | NCR | Silvertown Footbridge - installation of earthing bonds into bridge prior to consultation with FDC |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-11-30 | 2019-08-20 16:18 | -102 | 2018-07-12 16:43 | Civil - Structural Engineering | 1000 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The installation of bonds to traction for Silvertown Bridge has been completed before the designer (Cxxx) have had the chance to review and approve how the bonds are fixed into the structure, to ensure that its integrity is not compromised. Please provide details for review and approval. The bond to traction on the northern side of the bridge is currently in an unacceptable arrangement (although CRL do understand that at the time images were taken, works were not yet complete). If this arrangement is to remain however, please provide details how the bonds / cables will be secured so that these can't be damaged by the general public (since this side of the bridge is on a public footpath).
| 05SY - Systemwide | Cxxx-NCR-000863 | NCR | Rail damage on HP rail at the back of C11 - Milling machine |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-10-14 | 2018-09-11 07:24 | -33 | 2018-07-16 10:52 | Track - Rails and Sleepers | 20000 |  | Damaged | Repair | 2 (6-60k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | During the milling of C11, the machine created a defect approximately 15cm long and 1cm deep on the RH rail in the plain line after the crossing of C11. See attached picture and sketch.
| 05SY - Systemwide | Cxxx-NCR-000864 | NCR | __ Seaflame 27 Core Cable Quality Issue |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-08-29 | 2018-08-03 12:37 | -26 | 2018-07-18 08:04 | Communications and Control Systems | 500 |  | Manufacturing Defect | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | A manufacturing quality issue has recently been found with some __ Seaflame 27 core control cable used to connect TVS MCC panels with damper control cable junction boxes. The issue is that too few strands of steel wire armour have been wound onto the cable during manufacturing. __ have observed that the affected cable has around 56 strands of steel wire armour, whereas the correctly manufactured cable has around 78 strands. The affected cable has been installed at the Stepney Green, Paddington East and Paddington West sites.
| 05SY - Systemwide | Cxxx-NCR-000865 | NCR | Damage on drum Cxxx-182 (120mm 4C) |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-10-18 | 2018-11-21 10:45 | 34 | 2018-07-18 08:42 | Electrical - General | 5000 |  | Manufacturing Defect | Use As-Is | 3 (3-6k) | Complete | Material/Preservation Problems - Improper handling of material | Completed |  | We have found damage to the cable on drum Cxxx-182 (120mm 4C) approximately 150m into the drum. Cable Number: Cxxx-PC-00000365-1 Bound: West Bound Drum Number: Cxxx-182 Install Date: 13.07.18 Damage found: CH:8624
| 05SY - Systemwide | Cxxx-NCR-000866 | NCR | Commencing works Phase 1 & 2 works for Silvertown Footbridge without an accepted ITP |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-10-31 | 2018-11-14 11:55 | 14 | 2018-07-18 13:41 | Civil - Structural Engineering | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Commencing works Phase 1 & 2 works for Silvertown Footbridge without an code 1 acceptance for the ITP.
| 05SY - Systemwide | Cxxx-NCR-000867 | NCR | Commencing Phase 1 & 2 works for Silvertown Footbridge without all MCRs accepted |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-12-31 | 2019-10-21 11:24 | -71 | 2018-07-18 14:34 | Civil - Structural Engineering | 6000 |  | Documentation and Records | Rework | 3 (3-6k) | Complete | Management Problem - Other | Completed |  | Commencing Phase 1 & 2 works for Silvertown Footbridge without all MCRs accepted. the following MCRs are required as a minimum: 1) Glazing panels, 2) Stainless steel, 3) Stainless steel mesh, 4) Handrails with RAL 5010 (blue coating).
| 05SY - Systemwide | Cxxx-NCR-000868 | NCR | Silvertown Footbridge - Unpolished Bridge Deck Parapet Fins |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-08-31 | 2019-08-18 21:33 | -13 | 2018-07-19 09:04 | Civil - Civil Engineering General | 6000 |  | Material | Rework | 3 (3-6k) | Complete | Material/Preservation Problems - Other | Completed |  | Unpolished deck parapet fins installed with glazing along the Silvertown Footbridge deck.
| 05SY - Systemwide | Cxxx-NCR-000869 | NCR | Silvertown Footbridge - Earthing and Bonding Installation |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-08-31 | 2019-08-20 14:54 | -11 | 2018-07-19 09:14 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Commencement of the earthing and bonding installation to the Silvertown Footbridge strengthening and upgrade elements without an accepted design.
| 05SY - Systemwide | Cxxx-NCR-000870 | NCR | Cable RA 2162 ( CR146-RAD-00092) Has failed its tests |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-10-31 | 2018-08-03 12:48 | -89 | 2018-07-19 15:42 | Communications and Control Systems - Radio | 3000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Cable RA 2162 ( CR146-RAD-00092) was tested and failed its tests. This cable needs to be replaced. Location: Connaught Tunnel
| 05SY - Systemwide | Cxxx-NCR-000871 | NCR | Damage to rail by Milling Machine at CH 22450 WB |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-09-18 | 2018-08-20 10:51 | -29 | 2018-07-20 13:26 | Track - Rails and Sleepers | 20000 |  | Damaged | Repair | 2 (6-60k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | Milling Machine caused a rail damage in Thames Tunnel WB (22450 WB). See attached reports and picture.
| 05SY - Systemwide | Cxxx-NCR-000872 | NCR | Labels peeling away from Craig & derricott isolator front plates. |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-10-31 | 2018-11-21 10:49 | 21 | 2018-07-20 13:04 | Electrical - Switchgear | 3000 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | It has been found in numerous locations in the trace and open routes that the Labels are peeling away from __ isolator front plates.
| 05SY - Systemwide | Cxxx-NCR-000873 | NCR | Silvertwon footbridge - construction with no "F2" drawings being accepted |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-12-31 | 2019-10-07 11:33 | -85 | 2018-07-25 13:00 | Civil - Civil Engineering General | 10000 |  | Documentation and Records | Repair | 2 (6-60k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | Progress of construction and fabrication activities without getting formal acceptance of F2 design.
| 05SY - Systemwide | Cxxx-NCR-000874 | NCR | TVS BOS-E Non compliant bolts used for TVF |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-10-24 | 2018-08-22 10:51 | -63 | 2018-07-26 14:11 | Systems - Ventilation and Pressure Relief | 3000 |  | Material | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Insufficient information made available to the worker. | Completed |  | It was noticed during an inspection on 26.07.2018 that non-compliant bolts (Geomet) were used to connect flexible coupling to fan. These bolts couldn't achieve the required torque values (150Nm +/-15 Nm) as per the ITP Cxxx-__-O4-ITP-CRG03-50084.
| 05SY - Systemwide | Cxxx-NCR-000875 | NCR | Cable has been damaged in ATS Isolator |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-10-31 | 2018-08-03 12:10 | -89 | 2018-07-27 15:53 | Electrical - LV Equipment | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | On inspection of the ATS panel isolators the brown core was noted to have an nick in the insulation approximately 10mm long between the gland entry and the isolator terminals.
| 05SY - Systemwide | Cxxx-NCR-000876 | NCR | Tunnel leaking onto walkway. Thames Tunnel WB. |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-11-29 | 2018-12-13 10:38 | 14 | 2018-07-30 13:54 | Track - Walkways | 3000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | During a site walk it was noticed that there was a leak in one of the tunnel rings in WB Thames Tunnel. this leak had caused a high amount of mineral deposits to form on the walkway plank. The leak was found at ring 309/310. Please see the attached photo's for further information.
| 05SY - Systemwide | Cxxx-NCR-000877 | NCR | Glanding and termination of LV equipment at Westbourne Park without an Accepted Method Statement |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-10-31 | 2018-09-13 14:14 | -48 | 2018-07-31 10:23 | Electrical - LV Equipment | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Glanding and termination of LV equipment carried out at Westbourne Park without an Accepted code 1 Method Statement on Aconex or eB.
| 05SY - Systemwide | Cxxx-NCR-000878 | NCR | Missing Bolts between FID and ATD Skirt |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-10-02 | 2019-01-09 08:57 | 99 | 2018-07-31 14:21 | Systems - Ventilation and Pressure Relief | 5000 |  | Manufacturing Defect | Repair | 3 (3-6k) | Complete | Subcontractor Problems - Interfacing problems | Completed |  | During installation of the ATD skirt between the FID and ATD transition, it was noticed that the top flange holes on the skirt were misaligned with holes on the steelwork and couldn’t be bolted. The proposed solution is to use lindapter fixings to secure the top half of the flange to the FID steelwork. This was confirmed by supplier and installer Hargreaves.
| 05SY - Systemwide | Cxxx-NCR-000879 | NCR | 32mm SWA Glands |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-11-11 | 2018-10-25 09:51 | -17 | 2018-09-12 08:37 | Electrical - General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | 32mm SWA glands are not providing sufficient connection to the armouring of the SWA, a high percentage are coming loose after being installed.
| 05SY - Systemwide | Cxxx-NCR-000880 | NCR | WBP - Rail Lubricator Track Components Damaged |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-09-30 | 2018-10-05 12:13 | 5 | 2018-08-02 10:30 | Track - Track General | 5000 |  | Damaged | Rework | 3 (3-6k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | Rail lubricator application bar (1 no.) and wheel sensor (1 no.) located on the left leg of the Eastbound track CH -240 at Westbourne Park has been damaged by an RRV bucket during ballast profiling works.
| 05SY - Systemwide | Cxxx-NCR-000881 | NCR | PLU Portal - Track Pedestrian Crossing - Absence of brushed concrete finish |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-11-14 | 2018-10-05 12:46 | -40 | 2018-08-02 11:00 | Track - Track General | 3000 |  | Incorrect Installation | Reject | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | The concrete located in the 6 foot for the pedestrian crossing has been finished smooth and does not have a brushed finish as per ITP. Pedestrian Crossing located at Plumstead Portal, chainage 22850 (EB) , 22930 (WB) The area of concrete is approx 1800x3000mm. Concrete depth varies from 60mm to ~250mm as it was cast on top of a ramp running perpendicular to the pedestrian crossing route. Adjacent to the existing ramp, the concrete depth increases further to more than 300mm to tie in with the existing slab and abut the rubber crossing panel (see photo). ********** Update 14/09/2018: Following a site visit by QC on 06/09/2018 to PLU portal pedestrian crossing, the concrete steps adjacent to the rubber panels were found to have a poor finish and voiding underneath the PVC edge beam (photos added)
| 05SY - Systemwide | Cxxx-NCR-000882 | NCR | Milling Damage to Axle Counters x 2 |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-09-21 | 2018-09-26 10:44 | 5 | 2018-08-07 10:50 | Civil - Track | 5000 |  | Damaged | Rework | 3 (3-6k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | The Rail Milling Machine damaged Axle Counters at 2 locaions: 1) 8.060km and 2) 8.181km both on the Eastbound. Cxxx has been notified (see attached email).
| 05SY - Systemwide | Cxxx-NCR-000883 | NCR | TLPP Cable Glanding Checksheet at Plumstead Portal not completed as per ITP |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-10-31 | 2018-11-21 11:09 | 21 | 2018-08-08 10:29 | Electrical - LV Equipment | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Installed TLPP in both Westbound and Eastbound LV Rooms at Plumstead portal did not have cable installation and glanding check sheets completed as per ITP Cxxx-__-O4-ITP-CRG03-50179 v2.0. Section 6.3.4 of ITP and section 6.5 of the method statement states that check sheets will be completed but this has not been done immediately after the glanding in accordance with the ITP.
| 05SY - Systemwide | Cxxx-NCR-000884 | NCR | Incorrect Asset Labels on Tunnel Lighting and Power Panels |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-11-12 | 2019-02-06 08:48 | 86 | 2018-08-14 08:20 | Electrical - LV Equipment | 3000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | During a recent surveillance it was observed that the asset labels on the Tunnel lighting and Power Panel (TLPP) at Plumstead Portal Eastbound and Westbound LV rooms did not match the TLPP schematic and the Roomfuss asset schedule.
| 05SY - Systemwide | Cxxx-NCR-000885 | NCR | Welding documentation and records could not be provided. |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-09-30 | 2019-06-14 14:35 | -108 | 2018-08-09 08:00 | Architectural - General | 6000 |  | Documentation and Records | Rework | 3 (3-6k) | Complete | Management Problem - Other management problem | Completed |  | A planned Surveillance was carried on the Silvertown Way Footbridge-Structural Steelwork (Installation and Offsite Fabrication), fixings and connections on the 1st August 2018. The following documentation was requested from the Contractor; WPS, WPQR, WPQC, FPC, RWC Certificate, munufacturing checksheets and evidence of weld testing . No Weld Documentation had been received, as such could not be provided, and CRL acceptance could be demonstrated.
| 05SY - Systemwide | Cxxx-NCR-000886 | NCR | Evidence of pull testing for Strengthening Ring connections, could not be provided. |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-08-31 | 2019-06-14 14:20 | -78 | 2018-08-09 08:01 | Architectural - General | 6000 |  | Documentation and Records | Use As-Is | 3 (3-6k) | Complete | Procedure Problem - Other | Completed |  | A planned Surveillance was carried on the Silvertown Way Footbridge-Structural Steelwork (Installation and Offsite Fabrication), fixings and connections on the 1st August 2018. The following documentation was requested from the Contractor; Evidence of pull testing for Strengthening Ring connections including; Who carried out the pull testing, Calibration of Equipment and Checksheets . No Documentation had been received, as such could not be provided, and CRL acceptance could be demonstrated.
| 05SY - Systemwide | Cxxx-NCR-000887 | NCR | Installation Records could not be provided |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-08-31 | 2019-10-21 21:23 | 51 | 2018-08-09 08:02 | Architectural - General | 6000 |  | Documentation and Records | Rework | 3 (3-6k) | Complete | Procedure Problem - Other | Completed |  | A planned Surveillance was carried on the Silvertown Way Footbridge-Structural Steelwork (Installation and Offsite Fabrication), fixings and connections on the 1st August 2018. The following documentation was requested from the Contractor; Installation Checksheets in line with ITPs Cxxx-__-O4-ITP-CR146-*50004 and *50009 for the Footbridge strengthening works and Staircase and Bridge Deck works. No Documentation had been received, as such it could not be verified that the installation including the torqueing of fixings had been completed in line with the relevant ITPs
| 05SY - Systemwide | Cxxx-NCR-000888 | NCR | No evidence provided of Sample and Benchmark Acceptance |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-08-31 | 2019-10-22 16:43 | 52 | 2018-08-09 08:02 | Architectural - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | A planned Surveillance was carried on the Silvertown Way Footbridge-Structural Steelwork (Installation and Offsite Fabrication), fixings and connections on the 1st August 2018. On request the Contractor was unable to provide evidence of acceptance for samples and benchmarking for the works carried out on the Footbridge
| 05SY - Systemwide | Cxxx-NCR-000889 | NCR | Non compliant Chemical anchors installed in the Footbridge soffit. |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-10-31 | 2018-11-12 10:16 | 12 | 2018-08-09 08:03 | Architectural - General | 0 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | A planned Surveillance was carried on the Silvertown Way Footbridge-Structural Steelwork (Installation and Offsite Fabrication), fixings and connections on the 1st August 2018. The Contractor has installed Chemical anchors in the soffit of the footbridge as part of the strengthening ring installation. The installation is in line with Cxxx-OVE-S-DDD-CR146_Z-55520 C01, but not with CROSSRAIL CHIEF ENGINEERS GROUP (CEG) REQUIREMENTS.
| 05SY - Systemwide | Cxxx-NCR-000890 | NCR | Contractor has not installed anti-vibration washers or locknuts as specified |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-08-31 | 2019-08-07 13:49 | -24 | 2018-08-09 08:04 | Architectural - General | 6000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A planned Surveillance was carried on the Silvertown Way Footbridge-Structural Steelwork (Installation and Offsite Fabrication), fixings and connections on the 1st August 2018. During the surveillance it was witnessed that the bolts had been installed without anti-vibration washers or locknuts.
| 05SY - Systemwide | Cxxx-NCR-000891 | NCR | Welding not completed in line with the specification |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-09-30 | 2019-06-19 13:53 | -103 | 2018-08-09 08:05 | Architectural - General | 30000 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A planned Surveillance was carried on the Silvertown Way Footbridge-Structural Steelwork (Installation and Offsite Fabrication), fixings and connections on the 1st August 2018. During the surveillance it was witnessed that the welded joints have not been finished inline with the Specification. See attached photo
| 05SY - Systemwide | Cxxx-NCR-000893 | NCR | Cable damaged at WBP as a result of cable pulled by Cxxx |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-06-30 | 2019-03-27 10:40 | -95 | 2018-08-09 16:25 | Communications and Control Systems - General | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | On Monday 06th August 2018, whilst carrying out routing surveys at WBP, F__ noticed the cabling installed by __ has been left in a manner which does not meet with quality or specification to the standard carried throughout the job by FBT, cables have been left un dressed, crossed and also whilst installing these they have burnt through FBT’s installed cables Cxxx-PC-000055-1, Cxxx-PC-000055-2, Cxxx-PC-000055-3, one of these cables has almost penetrated the outer sheath. More details and photos in attached observation report.
| 05SY - Systemwide | Cxxx-NCR-000894 | NCR | No evidence was provided that pull testing had been carried out to the correct values. |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-08-31 | 2019-10-21 11:02 | 51 | 2018-08-15 10:39 | Architectural - General | 6000 |  | Documentation and Records | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A planned Surveillance was carried on the Silvertown Way Footbridge-Structural Steelwork (Installation and Offsite Fabrication), fixings and connections on the 1st August 2018. Pull test records supplied by the Contractor showed that the testing was carried out to a maximum of 8.3kN, this was found to be in line with the ITP *50009 inspection number. The contractor was asked to provide calculations to support the pull test value of 8.3kN. No evidence was provided that pull testing had been carried out to the correct values.
| 05SY - Systemwide | Cxxx-NCR-000895 | NCR | Track - CON West RRAP – Concrete Workability out of tolerance |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-09-16 | 2018-09-13 14:16 | -3 | 2018-08-16 10:41 | Track - Track General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | During the concrete pour of the RRAP infills at Connaught West Compound on 10/08/2018, the second batch (batch time: 09:55, Ticket Ref: 541701) delivered to the Connaught West RRAP for the concrete infill had flow test results of 660mm which exceeds the flow tolerance (540mm - 640mm) by 20mm. This batch was used for WB cess and part of the 6 foot infill.
| 05SY - Systemwide | Cxxx-NCR-000896 | NCR | WBP Track - Supporting Slab for Floor Mounted Lubricator Grease Cabinet not constructed as per design |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-09-27 | 2018-10-16 13:10 | 19 | 2018-08-16 12:53 | Track - Track General | 3000 |  | Supervision/Management | Reject | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | The supporting slabs for Rail Lubricator Grease Cabinets in ballast areas at Westbourne Park have not built as per detail in Cxxx-FCD-000783. The geotextile is not installed as per design; Second layer of A252 steel mesh has been omitted and QC inspection not undertaken prior concreting. These have been constructed in the following locations at Westbourne Park: Ch 0+222, Ch 0+192, Ch 0-217.
| 05SY - Systemwide | Cxxx-NCR-000897 | NCR | Leaky coupling discovered on TFM during filling. |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-10-22 | 2018-09-04 06:48 | -48 | 2018-08-17 12:33 | Mechanical - Piping | 1000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | During filling of the TFM pipe in Sector 16 EB a leak occurred due to an incorrectly fitted rubber under the coupling. This section of pipe had been IRN'ed and was signed off on 26/07/18. The pipe had not been pressurised when the leak occurred.
| 05SY - Systemwide | Cxxx-NCR-000898 | NCR | 40 year design life not guaranteed on additional TVS Attenuator components (factory fitted) |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-01-30 | 2019-02-04 09:49 | 5 | 2018-08-17 16:10 | Systems - Ventilation and Pressure Relief | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | In accordance with the Works Information Volume 2A the Contractor carried out the detailed design of the Tunnel Ventilation Systems. The Contractor carried out specific analysis to demonstrate the performance requirements and smoke control criteria for all modes of operation. This analysis was carried out in compliance with the __ Modelling Design Plan (Cxxx-__-H-GML-CRG03-50001) that satisfied the criteria as set out within WI Vol 2A Section 4.6. Through the detailed design development, the Contractor has expanded upon the modelling criteria as set out within the Works Information to include assessments of the actual flow conditions internally within the Ventilation shafts. This exercise was prompted from concerns raised from the temporary ventilation systems as described in NCR 532. Results of this simulation showed that there is a high frequency oscillating load acting on the attenuators, specifically on the splitter nose cones. The anticipated extent of this oscillating load was determined based on potential contributing factors including open/closed system design, transition duct angle, fan physical size and flow rate, all influencing the degree of flow detachment and oscillation impacting components downstream of fans. It was determined that the attenuator nose cones were not rated to withstand this fatigue inducing load. Therefore the 40 year design life could not be guaranteed or assured. To mitigate, the supplier proposed (Cxxx-NCR-000532) an additional nose cone with bracing channels to improve the attenuator splitter rigidity to withstand the fatigue load for the required 40 years. These additional components were installed at the following locations: • Paddington East (TSA & ASA) • Paddington West (TSA & ASA) • Canary Wharf East (ASA) • Canary Wharf West (ASA) • Eleanor Street (ASA-P) • Farringdon East (TSA & ASA-P) • Whitechapel West (TSA & ASA) • Bond Street East (TSA & ASA) • TCR-W (TSA & ASA) • Bond Street West (ASA-P) • TCR-E (ASA) • LIV-W (ASA) • WHI-E (TSA) • Stepney Green (TSA & ASA) • Farringdon West (TSA)
| 05SY - Systemwide | Cxxx-NCR-000899 | NCR | 40 year design life not guaranteed on additional TVS Attenuator components (In-situ Site Install) |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-06-28 | 2019-03-27 10:50 | -93 | 2018-08-17 16:32 | Systems - Ventilation and Pressure Relief | 50000 |  | Design | Repair | 2 (6-60k) | Complete | Design Problem - Inadequate or defective design | Completed |  | In reference to Cxxx-NCR-000532 the Contractor highlighted the requirement to apply additional components onto the attenuator equipment in order to achieve the Works Information Performance requirements of 40 year design life. In the main, the additional components were added into the product design within the manufacturing facility (__s Acoustics Ltd) prior to delivery to site. In limited locations additional components were installed on site as the attenuators were already constructed into their final positions. This permitted the TVS programme to continue unimpeded. The design of the components that were retro fitted on site differed to those installed within the factory due to the circumstances relating to the shaft environment versus the simplicity of working in a factory. To provide the assurance for the variety of components used the Contractor has completed a series of Finite Element Assessments to validate the structural performance. Early studies have indicated that a specific component applied to the in-situ equipment fails to achieve the 40 year design life. Results of this assessment show signs of fatigue over an extensive period of time when the fan is operated at 100% duty. This issue is limited to the following locations: • Canary Wharf East (TSA) • Canary Wharf West (TSA) • TCR West (TSA) • Bond Street East (TSA and ASA) The 3 metre long ‘splitter angles’ have been studied to show large stress oscillations at the bolted connections to the nose cone cover, owing to the lateral pressure fluctuation on this component. Further assessments have indicated that by removing these components the operational requirements of the attenuators should be met however, a full study of this assumption remains ongoing. The contractor proposes the action to remove the ‘angle splitters’ and to complete a CAT III assessment on the Attenuator Product with these components eliminated from the design. Note that BOS-W was not yet retrofitted on site, and so would not have 3m 'angle splitter' installed.
| 05SY - Systemwide | Cxxx-NCR-000900 | NCR | TF HV Cable Head Insulation Damaged - Liverpool Street W/B |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-09-27 | 2018-11-26 13:41 | 60 | 2018-08-21 10:46 | Electrical - OHLE | 2000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | The insulation on one of the HV cable heads is damaged at Liverpool street WB Ch.8480.918
| 05SY - Systemwide | Cxxx-NCR-000901 | NCR | WOO-W-ASA Splitters Installation |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-02-28 | 2019-02-13 14:47 | -15 | 2018-08-21 12:59 | Systems - Ventilation and Pressure Relief | 5000 |  | Incorrect Installation | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | During installation of the WOO-W-ASA it was noticed that the splitters sitting on the door frame do not align with the adjacent top tier splitters sitting on plinth, meaning the channels supporting the splitters laterally on the atmosphere and tunnel faces would be misaligned. Upon evaluating options to ensure the lateral stability of the splitters is maintained, it was agreed to reposition the door frame splitters and modify the lateral channels to suit the misalignment. Images 0717,0718, & 0720 attached shows the modification adapted on site. The modification has been reviewed by __ and confirmed to maintain the lateral stability of the splitters. Please see attached communication from __.
| 05SY - Systemwide | Cxxx-NCR-000902 | NCR | Incorrect fixings used in the Structrual Coller installation on the Silvertown Way Footbridge. |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-09-30 | 2019-06-19 14:10 | -103 | 2018-08-23 10:17 | Architectural - General | 10000 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A planned Surveillance was carried on the Silvertown Way Footbridge-Structural Steelwork (Installation and Offsite Fabrication), fixings and connections on the 1st August 2018. On review of the installation check sheets for the strengthening collars, submitted post surveillance, it was noted that __ FIS A fixings were referenced as being installed with __ HY200 resin. It is known that __ will not assure nor guarantee any arrangement that uses a mix of __ and non __ products. The installation should be confirmed as acceptable as part of close out to the NCR with the designer Cxxx as the structural calculations had been made using __ software and data.
| 05SY - Systemwide | Cxxx-NCR-000903 | NCR | Track Pedestrian Crossing - Broken Concrete supports |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-11-12 | 2018-10-25 10:11 | -18 | 2018-08-24 09:24 | Track - Track General | 3000 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Pedestrian crossing (PC) located on the westbound cess side at chainage 18907: The PC at this location incorporates a concrete support for the rubber panel which also acts as step access to the crossing. The second concrete step of the support has broken off and separated from the lower step. The design requirement shows 280mm for the first step run from the edge of the existing GRP cover over drainage in the cess, and the next step to be the remaining distance to the RRAP (approx. 80mm). This damage occurred as the rubber panel of the crossing was being lifted out. Pedestrian crossing (PC) located on the eastbound cess side at chainage 18800: Whilst removing the rubber panels of the PC at this location, the concrete upstand supporting the rubber panels shifted as a whole from its fixed position.
| 05SY - Systemwide | Cxxx-NCR-000904 | NCR | Civils Work on Entry Door to Trace not finished by the Cxxx team in Fisher Street Shaft |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-06-28 | 2019-04-26 09:34 | -63 | 2018-08-29 14:42 | Civil - Civil Engineering General | 2000 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | Civils Work on Entry Door to Trace not finished by the Cxxx team in Fisher Street Shaft on both Westbound and Eastbound. This is causing a delay in the removal of Cxxx temporary cable protection to fibre cable and delay in installation of permanent CMS in that area.
| 05SY - Systemwide | Cxxx-NCR-000905 | NCR | TVS TCR East - Steelwork for acoustic enclosure |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-02-27 | 2019-02-04 13:55 | -23 | 2018-09-03 11:53 | Mechanical - Heating Ventilation & Air Conditioning | 1000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | NCR for MBL install of the steelwork in TCR GYB - The fixings securing the steelwork column to the floor are currently not sufficiently embedded into the RC. This is for about 20-30% of the fixings, and requires approx. 10-15mm further embedment to meet standard requirements. __ need to know if due to the minimal load on the column and the fixings in the floor and soffit if these may be deemed acceptable by CRL, as the fixings are now permanent.
| 05SY - Systemwide | Cxxx-NCR-000906 | NCR | WBP Track - Damaged RRAP Panels |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-02-28 | 2019-02-20 09:28 | -8 | 2018-09-03 12:57 | Track - Walkways | 6000 |  | Damaged | Reject | 3 (3-6k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | There are 8 number RRAP rubber panels located at Westbourne Park Discharge Siding between Ch 0-226.78 and 0-239.54 & Eastbound between Ch 0-223.75 and 0-234.55 which have evidence of damage to the panel adjacent to the gauge face of the rail.
| 05SY - Systemwide | Cxxx-NCR-000907 | NCR | Damaged Ladder Extrusion for Walkway |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-10-31 | 2018-10-31 13:48 | 0 | 2018-09-03 15:48 | Track - Walkways | 3000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | A train has struck and caused damage to a walkway bracket arm and ladder extrusion. Minor damage has occured but replacement of the arm is necessary. Please see photos for further information.
| 05SY - Systemwide | Cxxx-NCR-000908 | NCR | CPD at CP19 not Closing Properly |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-10-31 | 2018-12-18 15:42 | 48 | 2018-09-04 13:30 | Mechanical - Mechanical Engineering General | 2000 |  | Equipment Breakdown | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | During a bench marking exercise for the doors at CP19 it was founding that the opening mechanism was working in 2 stages. This meant that the doors were opening before the shoot bolts were locking in place. On the occasions that the shoot bolts were not locking in place the door was not closing automatically due to the bolts dragging on the floor.
| 05SY - Systemwide | Cxxx-NCR-000909 | NCR | __ Lifting Beams Trolly Axel Pin Corrosion |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-10-10 | 2018-12-18 15:44 | 69 | 2018-09-05 15:13 | Materials - General | 3000 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | This NCR has been populated to capture the last remaining non-conforming __s Lifting Beam Axel Pin. The non-conformance is anticorrosion protection that has been applied to the Axel Pins does not meet the accepted specification. A previous NCR (NCR-000483) was populated after a Crossrail QIEP to capture the non-conformance of the Axel Pins installed by __s on 65 gantries.
| 05SY - Systemwide | Cxxx-NCR-000910 | NCR | NCR - Spring Washers on drop tube fixings are too small and migrate into the fixing hole |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-04-30 | 2019-03-21 10:53 | -40 | 2018-09-08 12:16 | Over Head Line Electrification - Supports | 100000 |  | Design | Rework | 1 (>60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | RfL has raised an issue, in the OHLE CIAC 2, regarding the spring washers installed on the drop tube fixings which are too small and migrate into the fixing hole (see picture attached). When this issue was identified during the installation, it has been discussed between the engineering and construction teams that the washer still fulfilled its functions. No formal observation/report has been recorded by the construction/quality teams. This issue may concern a large number of OHLE supports. Investigation/survey needed to identify the supports concerned.
| 05SY - Systemwide | Cxxx-NCR-000911 | NCR | NCR - OHLE Catenary wire support installed too close from the end of the horizontal beam - Support XRA/18/465 at Connaught (South Portal) |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-03-31 | 2019-03-08 15:22 | -23 | 2018-09-08 13:03 | Over Head Line Electrification - Supports | 6000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | RfL has raised an issue, in the OHLE CIAC 2, regarding an OHLE catenary wire support which seems to be installed too close from the end of the top tube (see picture attached). RfL did not precise which cantilever it is but it has been identified by the design team as the XRA/18/465 installed at E/B Ch. 18525.2 (Connaught South Portal). As per the OHLE Mounting Diagram (Cxxx-__-R6-DDD-CR146_ST003_Z-01870), the catenary wire support should be at 0.237m from the end of the top tube. The minimum distance acceptable is 100mm as per the drawing Inspection needed to measure the actual distance between the catenary wire support and the end of the top tube. If less than 100mm, the support has to be moved. Blocking clamp may be needed.
| 05SY - Systemwide | Cxxx-NCR-000912 | NCR | Cxxx HV Ladder Rack damaged |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-01-31 | 2019-01-09 09:09 | -22 | 2018-09-10 13:30 | Electrical - Cable Management | 5000 |  | Damaged | Rework | 3 (3-6k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | A length of ladder rack has been damaged on the EB near Plumstead portal. EB CH22887.
| 05SY - Systemwide | Cxxx-NCR-000913 | NCR | TVS - TCR E - Niko rail causing cracks to concrete |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-11-10 | 2018-10-19 10:08 | -22 | 2018-09-11 10:30 | Mechanical - Heating Ventilation & Air Conditioning | 20000 |  | Damaged | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | __ are using a nico rail system to install the acoustic chamber in the fan room at the east ticket hall of TCR station. The rail is fixed to steel beams which are fixed with mechanical anchors to the station structure. The connections are to the RC soffit beams. In three locations, the mechanical anchors have been installed too close to the edge of the soffit beams. As a result, the concrete has cracked and spalled.
| 05SY - Systemwide | Cxxx-NCR-000914 | NCR | TVS-TCR E-Commencing acoustic enclosure installation works without an accepted ITP and design |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-03-29 | 2019-03-28 11:23 | -1 | 2018-09-12 10:32 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | The TCR-E acoustic enclosure installation works were commenced without an accepted Inspection and Test Plan (Cxxx-__-O4-ITP-N105-50004 Rev1.0). The relevant drawing (Cxxx-__-Y-DWG-N105-50021 Rev 2.0) has also not been accepted by the client. Whilst an Inspection and Test Plan and the drawings were in place for the installation process, it is understood that the installation of the acoustic enclosure was commenced without first obtaining a Code 1.
| 05SY - Systemwide | Cxxx-NCR-000915 | NCR | OHLE E&B - Damaged Bonding Cable - Cross Passage 19 (CP19) |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-11-09 | 2018-09-27 09:26 | -43 | 2018-09-12 13:16 | Electrical - Earthing & Bonding | 1000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | During inspection of non-related M&E works inside Cross Passage 19 I noticed that one of the bar-to-bar bonding cables has had the outer insulation damaged/torn due to interference by others. The photos contained within CRL-OBS-24433 show damage to the cable and also how the cables are now unsupported as they sweep from duct opening to wall. These bar-to-bar bonding cables are routed from the E/B TSP located outside. __ have been notified separately of the damage / non-compliances requiring rectification. It is suggested that the cables are both replaced in order to allow for the modification to the duct opening into the CP.
| 05SY - Systemwide | Cxxx-NCR-000916 | NCR | TFM Pipe Installation Non-Compliant Sector 10 |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-11-30 | 2018-10-16 12:19 | -45 | 2018-09-12 14:25 | Mechanical - Piping | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | An inspection was carried out upon the Tunnel Fire Main (TFM) in the WB running tunnel. This inspection was upon the general install of these assets, as well as a 10% torque check on all the bolts used in the installation. In Sector 10 at Eleanor St shaft the TFM was found to be running directly across the adit faces (see attached photo). Refering to the __ drawing Cxxx-__-M-DDA-CR001_Z-1107- Fire Main Sector 10, Mile End Shaft to Eleanor St sht 07 of 07. The drawing clearly shows the TFM pipework running underneath the adits. The TFM pipework running across the adits was found to be unsupported over a 6m length and could be subject to excessive vibration from passing trains and air flow from the Tunnel Ventilation fans. See attached photos. Additionally several pipe couplings were found to be of the wrong type ie at ring 823 a rigid coupling should be of the flexible type and at ring 823 rigid couplings on a valve should be of the flexible type. Also several small sections of pipe were missing notably at ring 1270. Originally recorded in CRL-OBS-24464. __ originally notified on 30th August 2018.
| 05SY - Systemwide | Cxxx-NCR-000917 | NCR | ESS sump cover install concrete damage |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-11-30 | 2018-10-18 11:02 | -43 | 2018-09-12 16:03 | Civil - Civil Engineering General | 2000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During installation of the sump cover steelwork at ESS sump one of the HILTI M12 HAS-R was hand tightened resulting in the concrete cracking and a large chunk coming away. Please see the attached photos for further details.
| 05SY - Systemwide | Cxxx-NCR-000919 | NCR | Fibre cables running into CP4a have been damaged. |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-12-31 | 2019-02-01 15:10 | 32 | 2018-09-14 12:02 | Electrical - Electrical Engineering General | 5000 |  | Damaged | Rework | 3 (3-6k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | Two fibre cables that run into CP4a have been damaged and will need to be replaced. The cables affected are; - CR084-DAT-00005 (EB) - CR084-DAT-00006 (WB)
| 05SY - Systemwide | Cxxx-NCR-000920 | NCR | Commencing of RCD removal work on Tunnel Lighting and Power Panel without inclusion in method statement |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-11-13 | 2018-10-26 08:40 | -18 | 2018-09-14 14:31 | Electrical - LV Equipment | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Work on the removal of RCDs and associated cables from already installed tunnel lighting and power panels (TLPPs) ongoing without including this aspect of the work in the method statement. The changes are made to address Cxxx-PMI-01444 from CRL.
| 05SY - Systemwide | Cxxx-NCR-000921 | NCR | Damaged lighting cable at Connaught tunnel 4th arch in from the west compound |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-12-31 | 2019-01-14 14:37 | 14 | 2018-09-18 10:35 | Communications and Control Systems - Radio | 3000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On the westbound there is a damaged cable 4th arch in from the west compound. The cable seems to have been cut on the edge of the tray.
| 05SY - Systemwide | Cxxx-NCR-000922 | NCR | Sector 10 EB Hydrant Locations |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-10-31 | 2018-09-20 14:07 | -41 | 2018-09-19 09:09 | Mechanical - Mechanical Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Following a review of the Tunnel Fire Main in Sector 10 Eastbound Tunnel it has been identified a Hydrant (H19) has been installed 4m away from its intended position, this is due to a clash with a walkway bracket and the hydrants fitting neatly at the end of a 6.4m pipe. This means it is 66m away from Hydrant H20 and 53m away from Hydrant H18. It is not in accordance with the Cxxx Works information whereby hydrants should be spaced every 60m.Its original location was 62m away from Hydrant H20 and it still complies with the requirement of the Cxxx Fire Strategy where the maximum distance between the hydrants is 70m.
| 05SY - Systemwide | Cxxx-NCR-000923 | NCR | Silvertown Footbridge - Strengthening Rings Threaded Rod Non-Compliant Embedment Depth |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-10-31 | 2019-06-19 14:20 | -134 | 2018-09-20 15:32 | Civil - Civil Engineering General | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the approved and witnessed extraction of the M24 threaded rod from the northern main pier strengthening ring, it was observed that bolt number 42 (drawing attached) had been installed with an incorrect embedment depth of 60mm. Design embedment depth required is 180mm.
| 05SY - Systemwide | Cxxx-NCR-000924 | NCR | Cables run through wrong penetration |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-10-31 | 2018-11-05 11:03 | 5 | 2018-09-21 15:45 | Electrical - Electrical Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | At Limmo shaft EB TLPP cables have been run through the wrong penetration. As a result they are not supported by proper CMS on the shaft side.
| 05SY - Systemwide | Cxxx-NCR-000925 | NCR | Non-illuminated Signage - Absence of retro-reflective properties |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-12-14 | 2018-10-26 14:36 | -49 | 2018-09-24 10:29 | Architectural - Signage | 5000 |  | Material | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Non-illuminated signage procured for installation in trace do not have retro-reflective properties as per the specification. Circa 200 number of these non-compliant signs have been installed.
| 05SY - Systemwide | Cxxx-NCR-000926 | NCR | WB OHLE HV Joint Blown |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-01-09 | 2018-11-19 08:09 | -51 | 2018-09-25 09:57 | Over Head Line Electrification - Over Head Line Electrification General | 6000 |  | Damaged | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | __ have identified a blown OHLE HV joint (OHLE Joint No 22 - WB CH7210) on the westbound trace near Farringdon Station
| 05SY - Systemwide | Cxxx-NCR-000927 | NCR | Luminaire Asset labels - Not approved glue ( Tape) used |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-02-28 | 2019-02-13 14:55 | -15 | 2018-10-02 10:56 | Electrical - Lighting | 3000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | Luminaires Labels have been attached with the "Double sided Adhesive tape 9088-200" from 3M despite the recommendation of the asset team to use the 3M's " Scotch-Weld, Low Odour Acrylic Adhesives - DP8805NS " which is approved by Crossrail on PMC-03853.
| 05SY - Systemwide | Cxxx-NCR-000928 | NCR | Oscillation of TTD and Support Steelwork at WOO-W |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-10-16 | 2019-09-24 09:01 | -22 | 2018-10-02 12:41 | Systems - Ventilation and Pressure Relief | 10000 |  | Design | Repair | 2 (6-60k) | Complete | Design Problem - Not Defined | Completed |  | During Phase 2.3 Testing and Commissioning of the TVS system at Woolwich WTH, Oscillation of the Tunnel-side Transition Duct and support steelwork was observed when Fan A was run in supply mode. __ are carrying further investigations to deduce the cause of the oscillation and advise the corrective actions required.
| 05SY - Systemwide | Cxxx-NCR-000929 | NCR | LVD Cable Cxxx-PC-00003150 has been damaged by a MEWP |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-03-31 | 2019-02-28 11:30 | -31 | 2019-02-27 16:43 | Electrical - LV Equipment | 1500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | LVD Cable Cxxx-PC-00003150 has been damaged by a MEWP. The cable has been damaged near the nose of the cable, which was laying in troughing. The MEWP has ran onto the troughing causing it to collapse a damaged the cable end.
| 05SY - Systemwide | Cxxx-NCR-000930 | NCR | Fan Vibrations at WHI ETH |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-09-30 | 2019-07-11 13:45 | -81 | 2018-10-02 12:39 | Systems - Ventilation and Pressure Relief | 40000 |  | Design | Use As-Is | 2 (6-60k) | Complete | Design Problem - Other | Completed |  | During Phase 2.3 Testing and Commissioning of the TVS at WHI ETH, excessive vibration levels were observed for Fans A and B. The vibration trends between Fans A and B were not consistent and Fan B appeared to behave more erratically. __ consulted __ and MMD to understand the possible cause of the vibrations and carried on-site vibration testing of the installed steelwork, as well as a site visit with __ representatives to inspect the fans closely. __ await a report from __ on their findings and corrective actions.
| 05SY - Systemwide | Cxxx-NCR-000931 | NCR | External cold shrink tubing not forming correct seal on NF cable - WBP |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-12-20 | 2018-12-18 15:50 | -2 | 2018-10-04 11:12 | Over Head Line Electrification - High Voltage Power Supply | 3000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | CR076-OLE-00003 – Cable Joint 01 EB CR076-OLE-00009 – Cable Joint 01 WB 1. External cold shrink tubing not forming correct seal, self-amalgamating tape visible at one end of joint including abrasion marks to outer sheath of cable. This tape shouldn’t be visible and should be contained and enclosed within the joint itself via the cold shrink tube. This suggests that ether, the manufacturing jointing procedure has been incorrectly followed (i.e. stripping lengths incorrect), or that the exposure of joint material to sunlight has caused UV degradation. Moisture ingress likely. CR076-OLE-00023 – Cable Joint TF 02 WB 1. External cold shrink tubing not forming correct seal, self-amalgamating tape visible at one end of joint. This tape shouldn’t be visible and should be contained and enclosed within the joint itself via the cold shrink tube. This suggests that ether, the manufacturing jointing procedure has been incorrectly followed (i.e. stripping lengths incorrect), or that the exposure of joint material to sunlight has caused UV degradation. Moisture ingress likely. 2. External cold shrink tubing at left hand side of joint appears to have left ‘air-gap’ between outer sheath of cable and tubing wall. Sealing of joint against moisture jeopardised.
| 05SY - Systemwide | Cxxx-NCR-000932 | NCR | Cable cleat splits on NF cables - WBP |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-12-20 | 2019-02-13 14:59 | 55 | 2018-10-04 11:31 | Over Head Line Electrification - High Voltage Power Supply | 2500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Multiple split cable cleats have been captured in WBP.
| 05SY - Systemwide | Cxxx-NCR-000933 | NCR | External cold shrink tubing not forming correct seal on HV cable - CUH |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-12-20 | 2019-01-15 10:14 | 26 | 2018-10-05 09:43 | Over Head Line Electrification - High Voltage Power Supply | 3000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | OHLE Traction Power HV Cable installation at Custom House in the vicinity of OHLE Mast XRA/17/007 CR145-OLE-00021 – Cable Joint Spur TFS 16 EB CR503-OLE-00022 – Cable Joint Spur TFS 15 EB External cold shrink tubing not forming correct seal, self-amalgamating tape visible at one end of joint. This tape shouldn’t be visible and should be contained and enclosed within the joint itself via the cold shrink tube. This suggests that ether, the manufacturing jointing procedure has been incorrectly followed (i.e. stripping lengths incorrect), or that the exposure of joint material to sunlight has caused UV degradation. Another possible cause is cable expansion/contraction from direct sunlight that has caused cable to expand and contract beyond the design range of the cold shrink tubing.
| 05SY - Systemwide | Cxxx-NCR-000934 | NCR | OHLE NF - Asset Labelling of 25KV (NF) Cables |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-03-29 | 2019-03-19 10:45 | -10 | 2018-10-05 13:24 | Over Head Line Electrification - High Voltage Power Supply | 3000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | The labelling of Negative feeder cables has not been done in accordance with the Crossrail Cable Identification Guidance (CRL1-XRL-Z3-GUI-CR001-50029) available on eB: “Each circuit (including 3 single core cables working as one feeder), which may include any joints, will be an individual Asset Tag E.g. Source asset to Destination asset. “ At all locations, an asset tag has been installed per feeder cable Instead of 1 tag/Circuit.
| 05SY - Systemwide | Cxxx-NCR-000935 | NCR | Cable entry stuffing gland back nut loose on luminaire fittings |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-12-31 | 2018-11-21 11:38 | -40 | 2018-10-08 10:28 | Electrical - Lighting | 1000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | On inspection of the luminaires in the trace between Plumstead portal and NWP both bounds it was noted that the back nut of the stuffing gland was loose on three of the luminaires inspected.
| 05SY - Systemwide | Cxxx-NCR-000936 | NCR | Tunnel Pipework Pressure testing carried out without an approved safety pack |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-12-21 | 2018-12-19 11:15 | -2 | 2018-10-17 11:40 | Mechanical - Piping | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Tunnel Pipework (Tunnel Pumped Drainage and Tunnel Fire Main) test and commissioning which includes Filling and Pressure testing carried out without an approved safety pack.
| 05SY - Systemwide | Cxxx-NCR-000937 | NCR | Canary Wharf East Level -4 EB-DRD Room - CMS Brackets Corroded |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-01-30 | 2019-09-09 14:06 | -143 | 2018-10-09 13:36 | Electrical - Cable Management | 6000 |  | Damaged | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During inspection and testing of __s Pressure Doors it was observed that the CMS Brackets showed signed of corrosion. The area was wet full of debris and what looked like a drain in one corner was full of dirt. Please refer to photo's.
| 05SY - Systemwide | Cxxx-NCR-000938 | NCR | Track POE - Fixing down of POE Pump Units to Track Slabs |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-01-08 | 2019-01-09 12:28 | 1 | 2018-10-10 12:21 | Track - Track General | 5000 |  | Design | Reject | 3 (3-6k) | Complete | Design Problem - Not Defined | Completed |  | This NCR is related to the fixing down of POE Pump Units to the slab track, located at the following sites: Westbourne Park C1, C2, C3, C4 – Connaught C15-C16 Prospective locations with a similar issue: C5, C6, C7, C8, C9, C10,C11, C12, C13 & C14 Whilst reinstalling the bolts to fix the POE Pump Units to the track slab to satisfy Cxxx-PMI-01504 (Resolution of Slow Moving Points - Use of Brushed Rather Than Brushless Motors), we are finding that full motion of the HILTI - HUS HR cannot be achieved due to degradation / concrete swarf propagation caused when unscrewing/screwing the bolts. The bolt (HILTI - HUS HR M10 x 130) currently in place is as per detailed in the design response to site observation TRK STW 092 (captured formally in Cxxx-FCD-000397).
| 05SY - Systemwide | Cxxx-NCR-000939 | NCR | Damaged Radio Cable RA2176 |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-12-31 | 2019-02-01 15:15 | 32 | 2018-10-10 11:15 | Communications and Control Systems - Radio | 5000 |  | Damaged | Rework | 3 (3-6k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | Damage to radio cable RA2176 on the westbound between CP17 and Woolwich at ring 1013. Damage reported to __ Cxxx on the 5th of September. Section of cable has got a indentation in it and a piece removed. This cable will not function as required due to damage going into the inner core of the cable and not just the outer sheath.
| 05SY - Systemwide | Cxxx-NCR-000940 | NCR | Cables pulled through incorrect opening in ESS WB adit door |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-04-30 | 2019-02-04 09:29 | -85 | 2018-10-10 16:18 | Electrical - Cable Management | 2000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | . The fibre cables run through the same opening as the LV cables despite there being a divider in this opening. They have raised concerns over potential EMC issues. It would appear the LV cables should run through the bottom opening as this is where the tray lines up to.
| 05SY - Systemwide | Cxxx-NCR-000941 | NCR | OHLE Earthing Switch installation has been done without updated Method Statement |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-12-20 | 2019-01-17 14:18 | 28 | 2018-10-11 10:14 | Over Head Line Electrification - Over Head Line Electrification General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Earthing switches (FIS, WHI X, ROP, PML, VDP, CON, PLU) have been installed without updated Method Statements. Indoor Switch MS, and Outdoor Switch MS don't cover earthing switch installation details.
| 05SY - Systemwide | Cxxx-NCR-000942 | NCR | Tunnel Pumped Drainage Test and Commissioning carried out without an approved test description document |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-12-21 | 2018-12-19 11:39 | -2 | 2018-10-17 11:41 | Mechanical - Piping | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Tunnel Pumped Drainage test and commissioning carried out without an approved test description document. The document sets out all the tests to be carried out on the pipework during phases 2.2, 2.3 and 3 including the respective check sheets to be used.
| 05SY - Systemwide | Cxxx-NCR-000943 | NCR | Damaged FAR-W TID-EB Blades |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-03-08 | 2019-02-05 07:55 | -31 | 2018-10-15 10:50 | Systems - Ventilation and Pressure Relief | 6000 |  | Damaged | Rework | 3 (3-6k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | During testing of the FAR-W TID-EB on Septemeber 25th, 3no. blades were found to be bent. Upon investigation it could not be identified how the damage had been caused. No obstructions were present when the damage was found and the torque switch within the actuator should prevent damage. It is likely that scaffolding may have existed in the adit behind the damper set, leading to damage when the damper was opened. These 3no. blades require replacement. New blades will be ordered from __ and delivery date to be updated; time will be circa 6 weeks. In the interim, the blades have been brought back into position to allow the damper set to function. This is to allow T&C activities to continue and for the FAR-W PTV to be utilised as TTVS.
| 05SY - Systemwide | Cxxx-NCR-000944 | NCR | Failed FAR-W VSD-B Main Isolator |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-12-14 | 2018-12-18 14:49 | 4 | 2018-10-15 11:07 | Systems - Ventilation and Pressure Relief | 2500 |  | Equipment Breakdown | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | The main transfer switch of Unit VSD-B/1152 failed during testing on September 27, 2018. It was apparent that the isolator was no longer functioning, taking the VSD out of service. On 28th September & 1st October, __ engineer attended site to identify the issue and remove the failed component. A new isolator was ordered on warranty and delivered on October 4, 2018. On 4th & 5th of October, the __ engineer fitted the new component bringing the VSD back into service and the transfer switch has been operated a number of times to ensure it is working correctly. The failure and replacement of this component has been captured within the __ SAT.
| 05SY - Systemwide | Cxxx-NCR-000945 | NCR | Earthing of Tunnel Ventilation System Fans |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-10-04 | 2019-09-17 12:54 | -17 | 2018-10-16 12:17 | Electrical - Electro Magnetic Compatibility | 5000 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | The earthing arrangement in and around the Tunnel Ventilation Fan power cable junction boxes does not comply with electromagnetic compatibility best practice.
| 05SY - Systemwide | Cxxx-NCR-000946 | NCR | Walkway Plank Serrations |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-05-31 | 2019-04-10 13:00 | -51 | 2018-10-16 16:12 | Mechanical - Mechanical Engineering General | 6000 |  | Manufacturing Defect | Rework | 3 (3-6k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | During routine walkway inspection approximately 60m of planks around CP5A have been found with incorrect spacings between the extrusion serrations. Between CH.7865 and CH.7927 Westbound the serrations of the outer plank are spaced at approximately 17mm intervals, instead of 10mm.
| 05SY - Systemwide | Cxxx-NCR-000947 | NCR | Track NCR - Damaged Lubricator Cabinet |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-04-30 | 2019-04-09 09:56 | -21 | 2018-10-17 11:55 | Track - Track General | 5000 |  | Damaged | Reject | 3 (3-6k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | On the 16/10/2018, train ME10 was working west of CWS between CP10 and CP11 with the access platforms both extended to allow access to carry out the planned LV Installation/lighting on trays 1 and trays 4-5. The train crew moved the train towards CWS direction and made contact with the lubricator cabinet which is installed at chainage 12311 on the maintenance walkway side of the tunnel. No injuries were sustained – The lubricator cabinet has been damaged and the cover is bent (photos attached). The installation of the cabinet was compliant as per ITP Cxxx-__-R-ITP-CRG03-50001 - the distance between the cabinet and the running edge of the rail was 1520mm (exceeding the 1300mm required). An additional cabinet located on WB ch 5919 has sustained damage to the top right corner of the cabinet, adjacent to the cabinet door. The cabinet door is bent and the cabinet has been scratched. The installation of the cabinet was compliant as per ITP Cxxx-__-R-ITP-CRG03-50001 - the distance between the cabinet and the running edge of the rail was 1640mm (exceeding the 1300mm required).
| 05SY - Systemwide | Cxxx-NCR-000948 | NCR | Injection tubes removed from Crosspassages in the SGI enlargement |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-05-31 | 2019-05-22 15:01 | -9 | 2018-11-01 15:32 | Tunnelling - Linings - SGI Rings | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | Following site inspections carried out on 22/08/2018, 03/09/2018 and 05/09/2018, It was noted that some injection tubes and the grout boxes which should have been present on the concrete face between the SGI rings had been removed in the following locations: CP13: Injections tubes removed in 4no. locations in the SGI enlargement. CP11: Injections tubes removed in 1no. location in the SGI enlargement. CP09: Injections tubes removed in 2no. locations in the SGI enlargement. CP06: Injections tubes removed in 4no. locations in the SGI enlargement. CP5a: Injections tubes removed in 2no. locations in the SGI enlargement. See attached photos for further details.
| 05SY - Systemwide | Cxxx-NCR-000949 | NCR | Damaged screws on OHLE indoor switches Voltage transformers preventing maintenance and secondary cable replacement |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-01-30 | 2019-02-14 12:02 | 15 | 2018-10-22 13:56 | Over Head Line Electrification - Over Head Line Electrification General | 3000 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Damaged screws on OHLE indoor switches Voltage transformers preventing maintenance and secondary cable replacement. Please find attached pictures.
| 05SY - Systemwide | Cxxx-NCR-000950 | NCR | WBP RRAP - Concrete mix used for RRAP not compliant with ITP |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-12-24 | 2018-11-19 08:33 | -35 | 2018-10-25 13:12 | Track - Track General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | The concrete mix poured for the concrete element of the RRAP at Westbourne Park is not compliant with that stated in the ITP for Road Rail Access Points and Level Crossing at Westbourne Park (Cxxx-__-O4-ITP-CR076-50010).
| 05SY - Systemwide | Cxxx-NCR-000951 | NCR | Installation comenced without ITP - TCR -3 Steel Wall |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-11-30 | 2018-11-26 13:44 | -4 | 2018-10-24 13:19 | Systems - Ventilation and Pressure Relief | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | The ITP for the installation of the TVS tunnel pressure Steel wall within Tottenham court rd. east shaft at the level minus 3 (Cxxx-__-O4-ITP-N105-50008) was submitted to Crossrail on 24/10/2018 while the installation has already been completed since April 2018.
| 05SY - Systemwide | Cxxx-NCR-000952 | NCR | Luminaire connecta plugs and collars are not enaging into the sockets |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-01-31 | 2018-12-12 14:16 | -50 | 2018-10-26 14:15 | Electrical - Lighting | 50000 |  | Manufacturing Defect | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Inadequate/insufficient tooling. | Completed |  | On inspection of the luminaires installed between STG-PML Eastbound, a reoccurring issue of Luminaire connecta plugs and collars are not enaging into the sockets were found. Upon further investigation between CRL, __ & the supplier it has been established that the 54mm sockets are affected everywhere on the trace, whilst the 60mm sockets are unaffected.
| 05SY - Systemwide | Cxxx-NCR-000953 | NCR | Cracked Screed in CP02 |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-12-25 | 2018-11-19 08:35 | -36 | 2018-10-25 08:28 | Civil - Civil Engineering General | 5000 |  | Damaged | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | It has been noted during a de-snagging inspection that a crack is present in CP02 on the trace side of the doors.
| 05SY - Systemwide | Cxxx-NCR-000954 | NCR | Rusty Panel Hinges on Track Friction Modifier |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-03-31 | 2019-02-28 07:40 | -31 | 2018-10-25 08:51 | Electrical - LV Equipment | 5000 |  | System Defect | Rework | 3 (3-6k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Corrosion observed on the Track Friction Modifier cabinet hinges and internal bolts in North Woolwich Portal.
| 05SY - Systemwide | Cxxx-NCR-000955 | NCR | Damaged Walkway Ladders - Sector 2 |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-01-31 | 2019-01-15 10:38 | -16 | 2018-10-25 08:58 | Tunnelling - Walkways | 10000 |  | Damaged | Rework | 2 (6-60k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | During an inspection to survey the Cross Passages it was noted that a number of Walkway ladders had been damaged CP3 and CP4. it is unknown how these ladders were damaged as they are within the gauge requirement and no incidents have been reported to the RMC.
| 05SY - Systemwide | Cxxx-NCR-000957 | NCR | AEW damage found around Paddington- E/B at Ch 1967 |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-01-17 | 2018-10-31 15:06 | -78 | 2018-10-30 17:20 | Over Head Line Electrification - Over Head Line Electrification General | 3000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper handling of material | Completed |  | On 29/10/2018 during high level inspection, Aerial Earth Wire was found at Eastbound Chainage 1967.
| 05SY - Systemwide | Cxxx-NCR-000958 | NCR | Tunnel Walkway Surface Finish of Aluminium Planks |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-05-31 | 2019-04-11 13:49 | -50 | 2018-10-31 08:50 | Architectural - Finishes | 250000 |  | Material | Rework | 1 (>60k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | On the 30th August, __ arranged to have 2 sets of Slip resistance tests of the aluminium planks forming the emergency escape walkway to be carried out, Crossrail were invited to witness the tests at SATRA testing facility – Kettering; the witnessed test resulted in a slip resistance Pendulum Test Value (PTV) of 29 (non compliant). The following was agreed in Cxxx-RFI-000009: LUL Standard 1-135 (A3 Premises – Finishes) requires a PTV of 36 or above Additionally, LUL 1-135 also indicates that the slip resistance of the walkways should be as follows: Going of Ramp Max. /Gradient Maximum Rise / Coefficient of friction / SRV Value [m] [-] [mm] [-] [-] Any Level 0 0 36 10 1:20 500 0.05 41 5 1:15 333 0.067 43 2 1:12 166 0.083 45 Based on the tests conducted to date, and under certain conditions the walkway does not achieve the minimum requirement.
| 05SY - Systemwide | Cxxx-NCR-000959 | NCR | Over Tightening of Tunnel Illuminated Pushbutton Terminals |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-01-29 | 2019-02-14 12:09 | 16 | 2018-10-31 16:21 | Electrical - LV Equipment | 10000 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The majority of field wiring terminals within the Tunnel Illuminated Pushbuttons have failed following the torquing element of the installation procedure. Either the terminal screw head has been deformed, meaning that future disconnection would not be possible or the terminal screw has stripped the thread into which it fixes, causing the terminal to not clamp the cable core.
| 05SY - Systemwide | Cxxx-NCR-000960 | NCR | TVS TCR-W Gaps in the sealing of the TSAs |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-06-28 | 2019-05-09 09:33 | -50 | 2018-10-31 15:26 | Systems - Ventilation and Pressure Relief | 5000 |  | Workmanship | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the site visit on 29.10.18, It was identified that there were gaps in the sealing of the TSAs at L-1 on TCR West. These are most severely demonstrated on TSA-C. As seen in the pictures attached, there is a gap between the sealing panels in the L-1 deck. This is critical as it results in the L-1 level not being de-pressurised, and will result in air leakage from L-2.
| 05SY - Systemwide | Cxxx-NCR-000961 | NCR | Asset Labelling Signs breaking |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-02-15 | 2019-02-20 09:48 | 5 | 2018-11-01 13:57 | Track - Track General | 3000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | Some of the asset labels located on the floor are getting broken.
| 05SY - Systemwide | Cxxx-NCR-000962 | NCR | Walkway Plank Manufacture Inconsistencies |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-05-31 | 2019-04-16 09:31 | -45 | 2018-11-05 10:46 | Tunnelling - Walkways | 6000 |  | Manufacturing Defect | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | During a number of inspections some inconsistencies have been found with the manufacture of the walkway planks. This includes serrations at double the design distance along the planks as well as some planks that do not have any serrations at all. There have also been issues with the required slip resistance not being met during slip resistance testing.
| 05SY - Systemwide | Cxxx-NCR-000963 | NCR | Wrong maintenace procedure for POE Covers |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-08-15 | 2019-06-10 07:55 | -66 | 2019-05-17 15:57 | Track - Track General | 500 |  | Incorrect Installation | Reject | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During POE maintenance works, when POE team removes the covers, the fixings __ bolts come away from the bearer. According to __, this would come from the way they are un-torqueing it. Apparently they should do it by holding the top of the __ bolt and take the nut by hand with a spanner.
| 05SY - Systemwide | Cxxx-NCR-000964 | NCR | CMS supports installed on Numbering plates - all Whitechapel Crossover |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-02-14 | 2019-03-27 11:00 | 41 | 2018-11-08 09:56 | Electrical - OHLE | 2500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | During the inspection it is noticed that CMS supports are installed on numbering plates in Whitechapel Crossover.
| 05SY - Systemwide | Cxxx-NCR-000965 | NCR | Incorrect fixings used for walkway posts in Whitechapel crossover |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-12-31 | 2018-12-05 16:38 | -26 | 2018-11-08 11:12 | Tunnelling - Walkways | 2500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Walkway brackets in Whitechapel crossover have been installed using the incorrect fixings. M12 __ HST3-R have been used instead of the required M12 __ HSB-P.
| 05SY - Systemwide | Cxxx-NCR-000966 | NCR | STG TVS __ Panel Enclosure |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-10-18 | 2019-09-23 08:55 | -25 | 2018-11-08 13:14 | Systems - Ventilation and Pressure Relief | 6000 |  | Design | Use As-Is | 3 (3-6k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | During a routing inspection of the TVS works at Stepney Green shaft, it was identified that the gaps on level B2 between atmosphere transitions and the slab are being enclosed by __ with a full height (floor to fan isolation damper) partition made from channel frame and 8mm think durasteel panels. This is recorded under CRL-OBS-25709. This enclosure will block access to the inspection hatch in the transition, maintenance access to the earth bonding terminals, general access to the structural bolts and prevent visual inspection. Furthermore, the enclosure forms a horizontal deck at the damper level which could be give the maintainer the impression that it can used for standing on when working on the dampers. This is a serious safety concern because the 8mm durasteel panel is not a suitable load bearing material. __ has not submitted any designs for gap infill panels except at for the dampers at Canary Wharf. Please see the attached photos which are self-explanatory. Furthermore, the enclosure will result in the fan room becoming pressurised. This is a change to the access and maintenance strategy which CRL have not been notified about (no access to the fans during running) and creates higher differential pressure exerted on the access doors and floor hatches.
| 05SY - Systemwide | Cxxx-NCR-000968 | NCR | Walkway Posts Installed too Close to Track |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-12-31 | 2019-01-03 08:12 | 3 | 2018-11-12 08:31 | Tunnelling - Walkways | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Walkway posts at Liverpool Eastbound East End have been installed 90mm too close to the track.
| 05SY - Systemwide | Cxxx-NCR-000971 | NCR | Cracked clay inlet pipe to CP09 sump. |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-02-28 | 2019-02-04 10:05 | -24 | 2018-11-15 11:58 | Civil - Drainage | 5000 |  | Damaged | Repair | 3 (3-6k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | It has been discovered that the clay inlet pipe in CP09 has cracked where it comes out the sump wall.
| 05SY - Systemwide | Cxxx-NCR-000972 | NCR | Firemain clashes E&B bars and connections at Ch 19609 E/B, Ch 8508 E/B |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-01-31 | 2018-11-26 13:47 | -66 | 2018-11-16 10:12 | Electrical - General | 5000 |  | Planning | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Firemain clashes E&B bars and connections at Ch 19609 E/B, Ch 8508 E/B. Please see attached pictures.
| 05SY - Systemwide | Cxxx-NCR-000973 | NCR | GRP Post and Base - bracing required |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-03-31 | 2019-02-04 10:08 | -55 | 2018-11-16 16:31 | Electrical - Lighting | 5000 |  | Manufacturing Defect | Repair | 3 (3-6k) | Complete | External Phenomenon - Other | Completed |  | The GRP posts used for lighting have arrived from the supplier and are wobbly. Where the post sits in its spigot it has too much movement causing the post to move from side to side with only a small amount of force.
| 05SY - Systemwide | Cxxx-NCR-000974 | NCR | Back of House Screed angles at Whitechapel Galvanisation issues |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-12-31 | 2018-12-05 16:40 | -26 | 2018-11-19 09:38 | Mechanical - Mechanical Engineering General | 2500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A number of galvanised metallic angles for the back of house screeding at Whitechapel have been found to have large deposits of galvanic coating. This is causing the angles to not sit close enough together when installed. See photos attached for further info.
| 05SY - Systemwide | Cxxx-NCR-000975 | NCR | Connaught Hydrant Spool Corrosion |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-01-30 | 2019-02-04 11:40 | 5 | 2018-11-19 14:19 | Mechanical - Piping | 3000 |  | Manufacturing Defect | Reject | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Upon delivery last week it has been noted that a number of hydrant spools for the Connaught Tunnel Fire Main have been delivered with corrosion present.
| 05SY - Systemwide | Cxxx-NCR-000976 | NCR | Platform Pavement Screed work commenced with a code 3 method statement |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-01-30 | 2019-02-04 11:04 | 5 | 2018-11-21 10:49 | Civil - Concrete Pavement | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Platform Pavement Screed work commenced with a code 3 method statement - Cxxx-__-O1-GMS-CRG03-50285 rev 2.0.
| 05SY - Systemwide | Cxxx-NCR-000977 | NCR | Sector 3 EB Walkway Plank Overhang |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-10-02 | 2019-08-27 13:53 | -36 | 2018-11-22 08:45 | Tunnelling - Walkways | 6000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During a post IRN survey it was noted that at 12 no locations the plank overhang from the folded channel was too long. Planks were within gauge however the overhang was larger than 292mm maximum overhang. In addition to this there was a number of locations where the fall was towards the track.
| 05SY - Systemwide | Cxxx-NCR-000978 | NCR | Slotted holes on cantilever SPS at various locations |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-07-26 | 2019-07-25 10:59 | -1 | 2019-01-08 15:54 | Over Head Line Electrification - Supports | 5000 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | In some locations, the design of the angle clamp support does not allow the hanger clamp to be correctly positioned to achieve the design stagger. In consequence there is an error of up to 40mm.
| 05SY - Systemwide | Cxxx-NCR-000981 | NCR | Fisher St EB Door Issues |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-12-23 | 2019-01-09 09:29 | 17 | 2018-11-23 16:23 | Systems - Cross-passage Doors | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | during an IRN inspection re-visit, following a non-successful first one, it was found that the adit door at Fisher St EB still did not meet the IRN criteria. the main issue being that the right hand side door did not open properly. The push bar was stiff to open and the shoot bolt did not lock in place. In addition to this the rubber seal around the damper surround was loose and the upper earth braid was damaged.
| 05SY - Systemwide | Cxxx-NCR-000982 | NCR | Limmo Sump Cover Issues |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-05-15 | 2019-04-29 07:24 | -16 | 2018-11-26 14:05 | Mechanical - Mechanical Engineering General | 5000 |  | Design | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Error by manufacturer in shipping or marking | Completed |  | Two issues have arisen from the sump cover install at Limmo: 1. Clash between grating and pipe – the pipe is not in the same location as the __ drawing. Photo and drawing attached. 2. The middle and split covers are not bearing in the correct direction (6no total. 2 normal 4 split)
| 05SY - Systemwide | Cxxx-NCR-000983 | NCR | Testing of temporary tunnel fire main (TTFM) without an approved method statement |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-05-11 | 2019-01-17 14:49 | -114 | 2019-01-11 10:04 | Mechanical - Mechanical Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | It was noted during a recent surveillance that pressure testing was being carried out as part of the maintenance activity on the temporary tunnel fire main without an approved method statement.
| 05SY - Systemwide | Cxxx-NCR-000984 | NCR | Custom House points heating element positioning |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-02-17 | 2019-01-03 08:19 | -45 | 2018-12-19 15:00 | Electrical - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | At Custom House CH 16711 to CH 17386 EB & WB points end 1342 A&B, 1343 A&B and 1347 A&B the points heating element does not extend to the end of switch rails.
| 05SY - Systemwide | Cxxx-NCR-000985 | NCR | TLPP Earthing and Bonding |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-01-27 | 2019-01-03 08:37 | -24 | 2018-11-28 12:32 | Electrical - Earthing & Bonding | 20000 |  | Incorrect Installation | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The earthing and bonding requirements within Cxxx-__-Y-RGN-CRG03-50054 (Section 8.2 and 8.3) with respect to the Tunnel Lighting Power Panels and outgoing circuits have not been implemented on site 8.3. Tunnel Lighting and Power Cables This CPC shall not be connected to the station earth. The CPC shall be terminated into the earth bar located within the TLPP. Steel wire armoured cables shall be glanded off in the TLPP cable chamber and an earth tag fitted inside the chamber. The earth tag will be connected to the earth bar. 8.4. Tunnel LV Power Cables Cables fed from the Tunnel Lighting and Power Panels shall have an integral or separate CPC connected to the earth bar located within the TLPP.
| 05SY - Systemwide | Cxxx-NCR-000986 | NCR | Code-1 Method Statement has not been revised for replacement spring washer work yet |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-12-12 | 2018-12-05 17:14 | -7 | 2018-11-28 14:23 | Over Head Line Electrification - Supports | 500 |  | Planning | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Method Statement - Installation of Rigid Overhead Conductor System (including cantilevers and Contact wire) in Crossrail Tunnels Cxxx-__-O1-GMS-CRG03-50169 hasn't been revised for replacement of spring washer work yet.
| 05SY - Systemwide | Cxxx-NCR-000987 | NCR | 2 x 16 mm2 cable has been used as main protective bonding at PAD-E sub-platform level dampers, instead of 35 mm2 |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-05-21 | 2019-05-15 06:48 | -6 | 2018-11-30 10:23 | Electrical - Earthing & Bonding | 3000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | At PAD-E sub-platform level, 2 x 16 mm2 cable has been used as main protective bonding at PAD-E sub-platform level dampers, instead of 35 mm2
| 05SY - Systemwide | Cxxx-NCR-000988 | NCR | At LIV-E, for the UPD’s, 2 x 16 mm2 cable has been used as main protective bonding, instead of 35 mm2 |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-05-31 | 2019-06-11 15:48 | 11 | 2019-01-10 08:48 | Electrical - Earthing & Bonding | 2500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | At LIV-E, for the UPD’s, 2 x 16 mm2 cable has been used as main protective bonding, instead of 35 mm2
| 05SY - Systemwide | Cxxx-NCR-000989 | NCR | NF cable external insulation of selaing end is damaged in STG |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-01-10 | 2018-12-10 14:39 | -31 | 2018-12-03 11:23 | Over Head Line Electrification - High Voltage Power Supply | 5000 |  | Damaged | Rework | 3 (3-6k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | In STG - VDP E/B Chainage 11394, external insulation of sealing end was found damaged by maintenance team. CR512-OLE-00001, 1x400mm2, 25kV-A-163, 102K-R5--SEGS-DB-102K-E/B_NF_1.
| 05SY - Systemwide | Cxxx-NCR-000990 | NCR | Tunnel Lighting - Multi Circuit lighting fire rated Junction Boxes |  | Crossrail | PDP | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-02-28 | 2019-01-18 14:17 | -41 | 2018-12-03 13:06 | Electrical - Lighting | 1000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | It has become apparent that the accepted design to use of fire rated Junction boxes where lighting circuits deviate to other section of the tunnels and also cross passages are being replaced by using cable joint kits. The use of cable joint kits on sub circuits will affect the RAMS requirements to the detriment of the MTTR and also it availability which will have serious consequences on the operational railway which rely on the Tunnel lighting to be operational in the event of an incident or planned tunnel evacuation. It has been stated that Cable glands cannot be found which can provide the fire integrity for the cable and therefore maintain the FT120 rating required for fire enhanced cables used in the emergency lighting and also for the tunnel lighting which is required for evacuation purposes the main cables used in the systems are __ FP. these are manufactured and should be available from the market and the supply chain. The accepted design identifies in the design that Junction boxes are required for provision of sub circuit distribution. A specification for these junction boxes was provided in the accepted design and the additionally the tunnel lighting system performance requires design assurance that faults can be traced easily and rectified within 4 hrs to enable operation the railway safely. It is unlikely that without sub circuit distribution being provided as per the accepted design that the system would be acceptable to the IM.
| 05SY - Systemwide | Cxxx-NCR-000991 | NCR | TCR-E Acoustic Enclosure - acoustic performance not achieved |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-10-30 | 2019-10-16 06:52 | -14 | 2018-12-11 14:00 | Systems - Ventilation and Pressure Relief | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Following the installation of TCR-E Enclosure Acoustic at FAN room Noise Tests were carried out and the acoustic performance of the system was not achieved on high frequencies 1 - 8kHz range.
| 05SY - Systemwide | Cxxx-NCR-000992 | NCR | Fire stopping install issues at MES, ESS and FSS |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-02-15 | 2019-02-14 12:00 | -1 | 2018-12-05 17:17 | Fire - Compartmentation | 5000 |  | Manufacturing Defect | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | The bulkhead around the Roxtec transit bracket encroaches on the space required for the Roxtec stay plates to be installed upright. Please see photos attached. It seems as if there was not enough allowance in the manufacture of bulkhead face plate to incorporate these stay plates.
| 05SY - Systemwide | Cxxx-NCR-000993 | NCR | Single external cable sheath crack on HV cable - 25kV 400mm2 LSOH (Systemwide) |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-06-28 | 2019-06-24 13:34 | -4 | 2018-12-12 16:15 | Over Head Line Electrification - High Voltage Power Supply | 10000 |  | Damaged | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Error by manufacturer in shipping or marking | Completed |  | Single external cable sheath crack evident on a cable run of LSOH HV cable -25kV, 400mm2. Please find attached pdf tracker which refers previous NCRs for cable sheath external crack.
| 05SY - Systemwide | Cxxx-NCR-000994 | NCR | 2 or more external sheath cracks on HV cable - 25kV 400mm2 LSOH (Systemwide) |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-06-30 | 2019-05-22 13:51 | -39 | 2018-12-12 16:15 | Over Head Line Electrification - High Voltage Power Supply | 150000 |  | Damaged | Rework | 1 (>60k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | 2 or more external sheath cracks are evident on the same cable run of LSOH HV cable -25kV, 400mm2. Please find attached pdf tracker which refers previous NCRs for cable sheath external crack.
| 05SY - Systemwide | Cxxx-NCR-000995 | NCR | Track POE - PLU Portal - 1376B POE Break Out Device Activated |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-04-12 | 2019-02-28 07:41 | -43 | 2018-12-12 18:02 | Track - Turnouts | 5000 |  | Damaged | Repair | 3 (3-6k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | Two break out devices (BOD) of points 1376B at PLU were activated by an unknown RRV on Friday 7th December 2018. An Emergency Speed Restriction was put into place for dynamic testing, with the points scotched, clipped and returned to use. The BOD activated, preventing a points run through.
| 05SY - Systemwide | Cxxx-NCR-000996 | NCR | TWS at Crossovers installed without IFC drawings. |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-02-13 | 2018-12-18 16:05 | -57 | 2018-12-13 10:28 | Tunnelling - Walkways | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | The walkway system at the crossovers, Stepney Green, Whitechapel and Fisher Street, has been installed without IFC drawings.
| 05SY - Systemwide | Cxxx-NCR-000997 | NCR | Silvertown Footbridge - Strengthening Collar Defective M20 Anchor |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-09-30 | 2019-06-19 14:14 | -103 | 2018-12-14 11:02 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the removal of the steel strengthening collars, on the South Main Pier the M20 anchor denoted as S10 was found to have an extension piece added between the nut and locknut. The bolt appeared to have been shortened by cutting and subsequently an additional threaded bar section had been screwed onto the M20 anchor by one of the nuts making it appear as a solid single bar. The shortened bar does not appear have achieved the required full 200mm embedment. __ are carrying out an investigation to determine the root cause of this NCR.
| 05SY - Systemwide | Cxxx-NCR-000998 | NCR | Tunnel Lighting and Power Panel Outgoing Cable Cut Short |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-02-28 | 2019-02-13 15:46 | -15 | 2018-12-20 08:20 | Electrical - Lighting | 2500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | A technician glanding cables into the Liverpool Street Station West, Eastbound Tunnel Lighting and Power Panel (TLPP) mistook the un-armoured FP PLUS Flex Cable for a Steel Wire Armoured (SWA) cable. The technician started to gland the cable as if it had SWA, by cutting a ring around it at the point of entry to the TLPP using a hacksaw. In doing the conductive cores of the cable were cut and so irreparably damaged
| 05SY - Systemwide | Cxxx-NCR-000999 | NCR | TVS VSD Damage - TCR East |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-04-04 | 2019-04-04 09:29 | 0 | 2019-01-04 10:58 | Systems - Ventilation and Pressure Relief | 5000 |  | Damaged | Rework | 3 (3-6k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | On the 17th November 2018, one of the three Tunnel Vent VSD's installed at TCR East overheated causing irreparable damage, necessitating replacement.
| 05SY - Systemwide | Cxxx-NCR-001000 | NCR | Cross Passage Fire Alarm System not meeting electrical system specification |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-05-31 | 2019-02-25 09:31 | -95 | 2019-01-09 10:06 | Electrical - LV Equipment | 3000 |  | Material | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | When carrying out an inspection on site of the fire alarm systems, it has been noticed the beacon mounting arrangement was not sufficient to prevent dust and water ingress. __ did review all components of the fire alarm system and identify that the following components do not comply with the electrical specifications - Fire alarm panel IP30 - Sounder / beacon IP21 - Manual Call point IP24
| 05SY - Systemwide | Cxxx-NCR-001003 | NCR | Commencement of Phase 3 TVS Testing without an accepted Commissioning Test Plan |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-01-31 | 2019-02-11 13:15 | 11 | 2019-01-10 12:48 | Systems - Ventilation and Pressure Relief | 500 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Phase 3 Airfow tests have commenced and were conducted in the tunnel between FAR and TCR without first obtaining an accepted Commissioning Test Plan Tunnel Ventilation System - Phase 3 (reference Cxxx-__-E-STP-CRG03-50011 currently at Code 3 dated 28th November 2018).
| 05SY - Systemwide | Cxxx-NCR-001004 | NCR | Damaged Insulators |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-03-20 | 2019-03-21 16:15 | 1 | 2019-01-15 10:55 | Over Head Line Electrification - Over Head Line Electrification General | 10000 |  | Damaged | Reject | 2 (6-60k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | Several numbers of OHLE insulators have been found damaged after installation in different locations. EB Ch 2201, Ch 2240, Ch 2481, Ch 3467 - WB Ch 4637, Ch 4657, Ch 5873
| 05SY - Systemwide | Cxxx-NCR-001005 | NCR | IRN inspection of the TFM in Sector 15 Connaught Tunnel |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-03-28 | 2019-03-28 07:37 | 0 | 2019-01-14 15:05 | Mechanical - Piping | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | On 11th January 2019 CRL were invited to conduct an IRN inspection of the TFM in Sector 15 at Connaught Tunnel. There were several concerns after the IRN inspection of the Tunnel Fire Main:- • Many of the fire hydrants had not been installed, and many of the pipe couplings required re-torqueing. • There are several places where water is leaking through the tunnel walls and pouring directly onto the pipework. Has this been considered as part of the design review? • It was noticeable that no anchor points on the pipework, which was a concern. Confirmation required that the design thrust on the 150dia pipe can be accommodated. • After the inspection, further investigation revealed that there was no IFC drawings for this pipework. Considering the above points the IRN for the TFM pipework could not be signed off.
| 05SY - Systemwide | Cxxx-NCR-001006 | NCR | Damaged hydrant at WOO EB West End |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-03-28 | 2019-02-13 09:48 | -43 | 2019-01-21 11:21 | Mechanical - Piping | 1000 |  | Damaged | Reject | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | During the installation of the interface at WOO EB West End on 17/01/19 it was noted that the first hydrant turn wheel had sheered off. See photos attached for further info.
| 05SY - Systemwide | Cxxx-NCR-001007 | NCR | TVS Cabling over Fan Flooring |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-09-30 | 2019-09-24 09:07 | -6 | 2019-01-21 16:40 | Mechanical - Heating Ventilation & Air Conditioning | 5000 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | The installed tunnel ventilation fan flooring at TCR West & East does not allow for cabling to freely pass through the installed slot in the flooring. The CMS and cabling feeding the fan connection boxes requires lidding and checker plating to enable safe access for maintenance of the equipment. This suggests the design of the fan flooring and the electrical installations have not been thoughtfully aligned to consider the end user maintenance activities. Presently there is a tripping hazard and could reduce the life expectancy of the cables if used for maintenance access without mechanical protection. Photographs can be seen in the attached document as noted during a recent observation visit.
| 05SY - Systemwide | Cxxx-NCR-001008 | NCR | PLU OHLE Switch (both bounds-near the portal eye) does not allow sufficient clearance for fire evacuation |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-04-26 | 2019-03-06 07:47 | -51 | 2019-01-22 11:21 | Over Head Line Electrification - High Voltage Power Supply | 6000 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | The OHLE switch located at PLU (both bounds-near the portal eye) does not allow sufficient clearance. The space required is 850mm that is not achieved in either bound.
| 05SY - Systemwide | Cxxx-NCR-001009 | NCR | TVS FAR-E infill panel torque test fail |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-04-23 | 2019-03-11 07:42 | -43 | 2019-01-23 16:22 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | No evidence of torque of M8 bolts on a __ installation of an infill panel on the 2nd floor of the east shaft (ASA) at Farringdon Crossrail station
| 05SY - Systemwide | Cxxx-NCR-001010 | NCR | Paddington Sump Cover Design/Fabrication issues |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-05-15 | 2019-04-18 10:07 | -27 | 2019-01-24 13:22 | Mechanical - Mechanical Engineering General | 6000 |  | Design | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | 5 number panels have been fabricated as per design. However the finished sumpo does not match the design drawings. These 5 panels are too be refabricated as per the panels at Limmo captured via Cxxx-NCR-000982.
| 05SY - Systemwide | Cxxx-NCR-001011 | NCR | Walkway prost grout failed cube test |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-04-24 | 2019-03-19 09:03 | -36 | 2019-01-24 13:35 | Tunnelling - Walkways | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | Cube tests for the walkway post grouting at Fisher Street have failed the 28 day cube crush result. Results attached.
| 05SY - Systemwide | Cxxx-NCR-001012 | NCR | STG WB Walkway Handrail Return |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-03-24 | 2019-02-13 09:53 | -39 | 2019-01-24 13:57 | Tunnelling - Walkways | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Walkway handrail return has been installed into the fireproofing at STG using the standard M10 __ HST3-R fixings. As the fireproofing is not load bearing longer fixings are required.
| 05SY - Systemwide | Cxxx-NCR-001013 | NCR | Leaking couplings during filling of TFM |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-04-12 | 2019-03-06 07:49 | -37 | 2019-01-25 13:39 | Mechanical - Piping | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | During the filling of the TFM at STG EB (Sector 8/12) 13 couplings sprung a leak. 8 of these couplings were in a 20m area under the GRP scaffolding.
| 05SY - Systemwide | Cxxx-NCR-001014 | NCR | Surface Lighting Earth Connection Damaged |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-05-31 | 2019-02-14 08:28 | -106 | 2019-01-28 07:31 | Electrical - Lighting | 5000 |  | Damaged | Rework | 3 (3-6k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | During a Quality Walk through from PAD-WBP, it was noted that the earthing pins on the posts for the surface lights in Westbourne Park had been damaged after the installation. One was bend and the other completely sheared off (refer to photo). Although the rework might be minimal, an NCR has been raised to ensure that a solution can be agreed with CRL through the NCR route.
| 05SY - Systemwide | Cxxx-NCR-001016 | NCR | TVS - Paddington Unistruct Impact on Fan Removal |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-08-28 | 2019-08-05 12:44 | -23 | 2019-01-29 12:21 | Systems - Ventilation and Pressure Relief | 5000 |  | Incorrect Installation | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | It was observed at Paddington west ventilation shaft that the unsitruct that supports the fan cables are concreted into the slab. This will require this to be broken out during fan removal which will prolong the maintenance activity. This show's the access and maintenance of the tunnel ventilation fans have not been fully considered and this requires rework. The east shaft was not surveyed during the site survey and this should be checked if the same issue occurs.
| 05SY - Systemwide | Cxxx-NCR-001017 | NCR | STG EB Walkway Ramp Post Span |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-04-30 | 2019-02-13 09:35 | -76 | 2019-01-30 09:09 | Tunnelling - Walkways | 3000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Span between bottom of ramp and first walkway post is approximately 3.385m.
| 05SY - Systemwide | Cxxx-NCR-001018 | NCR | Walkway Post Grout Cubes |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-03-31 | 2019-03-11 07:51 | -20 | 2019-01-30 10:43 | Tunnelling - Walkways | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Grout cubes for the walkway posts have not been taken and tested as per the agreed ITP. 1. Grout cubes for Fisher St EB pour (17/12/18) have not been taken. 2. Fisher St WB & WHI EB batches: 2 cubes have been crushed after 7 days, instead of leaving 1 cube spare incase further testing is required.
| 05SY - Systemwide | Cxxx-NCR-001019 | NCR | Cxxx SCADA Monitoring of TLPP Mode Selector Switch |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-09-30 | 2019-09-06 10:25 | -24 | 2019-01-30 11:35 | Electrical - Lighting | 25000 |  | Design | Rework | 2 (6-60k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | During the commissioning of the monitoring and control interface between the Cxxx TLPPs and the Cxxx SCADA system, it has become apparent that the Cxxx SCADA system has been configured to accept the inverse of the Mode Selector Switch monitoring signals provided by the TLPPs. This is a systemwide issue affecting the 58 TLPPs installed at stations, shafts and portals, plus the training panel installed at TUCA.
| 05SY - Systemwide | Cxxx-NCR-001020 | NCR | Liverpool Street East Sump Covers |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-06-27 | 2019-04-11 12:50 | -77 | 2019-02-04 11:11 | Mechanical - Mechanical Engineering General | 3000 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Rebar has been struck in 24 out of 30no HD bolt locations. Targetted embedment depth is 110mm and rebar is struck between 40 and 55mm. See sketch pon attached SOB.
| 05SY - Systemwide | Cxxx-NCR-001021 | NCR | STG Type C Door |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-06-30 | 2019-06-17 09:09 | -13 | 2019-02-05 13:20 | Systems - Cross-passage Doors | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The contact limit switch at STG Type C door does not make contact with the door it self. To remedy this __s have added a screw onto the door skin to ensure contact has been made. This was installed with out acceptance from __. In addition it is also causing damage to the limit switch. See photos attached.
| 05SY - Systemwide | Cxxx-NCR-001022 | NCR | Stepney Green Door Push Bolt |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-04-30 | 2019-04-04 09:08 | -26 | 2019-02-05 13:34 | Systems - Cross-passage Doors | 2000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Interfacing problems | Completed |  | Push bolts at Stepney Green not locking in position when handle is pushed.
| 05SY - Systemwide | Cxxx-NCR-001023 | NCR | CP17 Door Push Bolt |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-04-30 | 2019-03-06 07:52 | -55 | 2019-02-05 13:38 | Systems - Cross-passage Doors | 2000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | Push bolts on CP17 door are not locking in place when push bar fully engaged.
| 05SY - Systemwide | Cxxx-NCR-001024 | NCR | Cracked track bearer at VDP S&C C16 |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-06-18 | 2019-06-10 08:42 | -8 | 2019-02-07 10:38 | Track - Rails and Sleepers | 5000 |  | Damaged | Rework | 3 (3-6k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | After a Quality Inspection from MTCE team carried out on the open section between Victoria Dock Portal and Connaught West compound, it was noticed that there were a crack through the bearer 1314B points, on bearer 1624. post installation and IRN process approved in the above detailed location.
| 05SY - Systemwide | Cxxx-NCR-001025 | NCR | Clip impossible to install due the insulated fishplate at scissors crossover in Westbourne Park W3-W6. |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-08-10 | 2019-08-19 10:41 | 9 | 2019-05-17 09:14 | Track - Rails and Sleepers | 5000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | The IBJ’s have a thin insulated plate on one side, but an normal plate on the other, and this is where it has become impossible to install the clips. It affects bearer W333 and W633.
| 05SY - Systemwide | Cxxx-NCR-001026 | NCR | Handrail Heights |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-05-12 | 2019-02-19 09:47 | -82 | 2019-02-12 14:55 | Tunnelling - Walkways | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | Walkway handrail fixed to the shaft wall at Limmo shaft WB has been installed at a height of approximately 1040mm above the top of walkway plank. This effects one bracket at both the west and east ends of the shaft.
| 05SY - Systemwide | Cxxx-NCR-001027 | NCR | Damage on OHLE Negative Feeder 102B at WBP ATS |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-04-14 | 2019-02-28 12:12 | -45 | 2019-02-13 10:53 | Over Head Line Electrification - High Voltage Power Supply | 5000 |  | Damaged | Rework | 3 (3-6k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | We captured a damage on OHLE Negative Feeder cable 102B at WBP ATS.
| 05SY - Systemwide | Cxxx-NCR-001028 | NCR | Design drawing for E&B at Plumstead Portal TEB needs to be corrected |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-07-01 | 2019-07-05 08:08 | 4 | 2019-02-14 09:03 | Over Head Line Electrification - Earthing & Bonding | 2000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | • Incorrect Design of Plumstead Earthing & Bonding connections from TSP to TEB and inconsistency with CEG’s Earthing & Bonding Strategy. • According to the Earthing & Bonding Strategy, our design should have two connections between: - TSP-PLUP-W/B-1a and TEB-PLUP-W/B, - TSP-PLUP-E/B-1a and TEB-PLUP-E/B,
| 05SY - Systemwide | Cxxx-NCR-001029 | NCR | Incorrect Cable Orientation at MES, ESS and FIS |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-08-31 | 2019-06-26 11:56 | -66 | 2019-02-14 09:44 | Fire - Compartmentation | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The orientation of the cable install at MES, ESS & FIS adit door cable transit bracket is causing a problem with the Roxtec module installation. The main issue is the cables do not pass through the transit bracket horizontally. The LV cables in the trace are on the bottom CMS tray, while they are on the top tray within the shafts. This is repeated by the coms and control cables, but the opposite direction. This means that the cables pass through the module installation zone diagonally, which prevents the modules being installed.
| 05SY - Systemwide | Cxxx-NCR-001030 | NCR | TVS - Earthing & bonding of the TVS Platform and UPE dampers at Liverpool street West Shaft |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-07-24 | 2019-05-03 07:45 | -82 | 2019-02-14 13:40 | Electrical - Earthing & Bonding | 5000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The installed earthing and bonding at Liverpool street west shaft on tunnel isolation damper west bound and both under platform extract dampers requires the following works as instructed under Cxxx-PMI-01367. • To install gap glands to the control cablings on the actuators • To remove crossbonds from the damper assembly • To disconnect and sleeve the CPC within the actuator housing • To coordinate with Cxxx to ensure CMS gapping is carried out. The installed inspected works only account for the power supplies to each actuator only. The above will need to be carried out to satisfy the requirement of Cxxx-PMI-01367 to ensure the installation and compliant to earthing zones.
| 05SY - Systemwide | Cxxx-NCR-001031 | NCR | Cxxx-TVS-TCR West, Infill Panel-Torque Test Failure |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-05-20 | 2019-04-15 11:47 | -35 | 2019-02-19 13:56 | Systems - Ventilation and Pressure Relief | 2000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | The purpose of the inspection on Monday, the 18th of February at TCR-W was to torque test/final inspection of MITE infill UPED @ floor -5. During a planned ITP hold point a test / inspection of the fixings (HST3 anchors) securing CRC track to connect to soffit & slab using M10 bolts at 500mm max centres failed to maintain their integrity. All of the chosen fixings allowed the nut to turn over 90 degrees before the torque wrench indicated that 45Nm had been achieved. This rendered the fixings as Non-compliant.
| 05SY - Systemwide | Cxxx-NCR-001032 | NCR | Materials installed without an approved MCR |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-05-31 | 2019-04-10 13:11 | -51 | 2019-02-19 14:50 | Systems - Drainage/Pumping Systems | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Installation has been carried out in a number of Cross Passages with materials that have not yet been approved via the MCR process.
| 05SY - Systemwide | Cxxx-NCR-001033 | NCR | Cable routing and installation of LV power cables at Eleanor Street, Mile End and Fisher St. shafts |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-09-30 | 2019-07-04 13:25 | -88 | 2019-02-20 13:30 | Electrical - LV Equipment | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Due to installing the Comms and power cables prior to the door and bulk head installation at Eleanor St, Mile End and Fisher St. the routing for the cables through the doors and the interface with the shafts have caused the LV power cables and comms cables to cross when transitioning into the shafts. At Mile End WB the quantity of cables transitioning through the transit frame has prevented the transit frame from being fire stopped - this is due to all power cables to Niche 3 being through this frame NCR-940 previously raised for ESS
| 05SY - Systemwide | Cxxx-NCR-001034 | NCR | Radio comunications system Repeater Motorola DR3000 |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-05-28 | 2019-03-28 15:32 | -61 | 2019-02-27 12:47 | Communications and Control Systems - Radio | 6000 |  | Damaged | Rework | 3 (3-6k) | Complete | External Phenomenon - Other | Completed |  | For approximately 3 months channels 1 and 2 have been severely affected by a high level of interference courtesy of a ‘rogue frequency’ that was located on 14th February by the regulator, OFCOM. DR3000 repeater are the oldest equipment in the project, most of them were installed during the civil works phase in 2012-2015 period.
| 05SY - Systemwide | Cxxx-NCR-001035 | NCR | Liverpool St Cracked Concrete |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-08-31 | 2019-07-11 14:01 | -51 | 2019-03-05 09:45 | Civil - Civil Engineering General | 5000 |  | Damaged | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On 02/03/19 walkway tie in works were undertaken from ME15 at Liverpool St station Eastbound West End, including installation of the evacuation walkway platform end bracket Cxxx-__-E-DWG-CRG03-50017. The bracket was set out to adhere to the required edge distance specified by the manufacturer. However, whilst torqueing the __ HST3-R M12 fixings, cracks were observed to propagate at the corner of the concrete station platform. Works were stopped immediately until a resolution is agreed. __ note that the same works have been undertaken at the Eastbound East end of the platform with no issues observed.
| 05SY - Systemwide | Cxxx-NCR-001036 | NCR | Failure to Perform a Training Workshop for Installation of Asset Labels |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-06-06 | 2019-05-16 13:26 | -21 | 2019-03-05 16:28 | Information Management - Asset Information | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | __ Document Cxxx-__-K2-RGN-CRG03-50053 LVD Asset Labelling Scope Definition Section 7.1 states: Prior to any installation works, the Cxxx M&E Asset Information Engineer will run a workshop covering a summary of • Cxxx Labelling Strategy/Scope • Asset Tag and Serialised Equipment Label Fixings • Instructions on Asset Tags Label positioning for open and closed sections. Following a Surveillance of the LVD Asset Label installations it has been identified that this has not been performed
| 05SY - Systemwide | Cxxx-NCR-001037 | NCR | Pudding Mill Lane Walkway Lighting |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-07-31 | 2019-07-11 13:50 | -20 | 2019-03-06 16:39 | Electrical - Lighting | 5000 |  | Design | Repair | 3 (3-6k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | The existing lighting installation is to remain in situ and modified inline with Cxxx-FCD-000987 where the lighting will be extended by use of joint to the correct chainage at the end of the portal. Cxxx-PMI-01655 will be incorporated into the close out of this NCR as it is to be provided from the UPS circuit in both bounds.
| 05SY - Systemwide | Cxxx-NCR-001038 | NCR | Liv St cracked concrete platform WB EE |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-07-31 | 2019-07-31 11:32 | 0 | 2019-03-11 16:10 | Civil - Civil Engineering General | 5000 |  | Damaged | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During install of evacuation walkway platform end bracket Cxxx-__-E-DWG-CRG03-50017 on Sat 9th March 2019 the East end corner of Liv St W/B platform was damaged. See attached photos for detail of the damage to the corner of the platform. Works at the W/B West end were completed with no issues.
| 05SY - Systemwide | Cxxx-NCR-001039 | NCR | Cable damaged captured on CR144-OLE-00021 in VDP |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-06-27 | 2019-03-28 15:47 | -91 | 2019-03-11 15:21 | Over Head Line Electrification - Over Head Line Electrification General | 1500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Cable damage has been found in VDP. CR144-OLE-00021 , 26/45kV LSOH/CWS/XLPE/A , 1x240 mm2, length 249m, Eastbound. From Spur no:14 (ch 16389) To Spur no:15 (ch 16626) ----- Damage Chainage 16,580 in VDP area Eastbound. The cable was installed: 08/02/17 The cable was tested on the: 15/08/17
| 05SY - Systemwide | Cxxx-NCR-001040 | NCR | ESS failed BCU-02 control unit on VSD-C |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-04-30 | 2019-04-08 07:21 | -22 | 2019-03-11 15:40 | Electrical - Switchgear | 1500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | On 29/11/18 the __ engineer investigated a failure preventing the operation of VSD-C at ESS; serial no. 1170504919. The engineer had found that the BCU-02 control unit had failed. Physical & environmental conditions within the room had not caused the failure. The likely cause of failure was early life component failure. On 03/12/18 the new component arrived and was fitted by the __ engineer. The VSD was brought back into service. As of 11/03/19 the VSD is still operational, having been used as temporary tunnel ventilation for a number of months.
| 05SY - Systemwide | Cxxx-NCR-001041 | NCR | QS610-48 Commissioning & Testing Plan not available for Tunnel Fire Main |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-06-25 | 2019-06-06 09:15 | -19 | 2019-03-12 17:50 | Fire - Fire Systems & General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Lack of procedure | Completed |  | During a Crossrail surveillance carried out at Finsbury Circus on Tunnel Fire Main commissioning documentation it was found that a Commissioning & Testing Plan (CTP) was not available at the time. It is a requirement of the works information that a CTP is produced and in use at the time of commissioning taking place. Works Information Volume 2B - Part 28 - Testing and Commissioning Process 21.1.3 States: "The Contractor shall produce a Testing and Commissioning Plan to describe the Testing and Commissioning activities to be undertaken."
| 05SY - Systemwide | Cxxx-NCR-001042 | NCR | TVS - Rust on Roof Dampers TCR WTH |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-09-02 | 2019-07-11 13:38 | -53 | 2019-03-14 10:41 | Mechanical - Mechanical Engineering General | 5000 |  | Manufacturing Defect | Rework | 3 (3-6k) | Complete | Material/Preservation Problems - Other | Completed |  | Suspected corrosion has been noticed on the completed roof draught relief dampers at the western ticket hall at TCR. Also there are large gaps around the support brackets which are not sealed. Photos attached.
| 05SY - Systemwide | Cxxx-NCR-001043 | NCR | Silvertown Footbridge - Deck anchors damaged during dismantling of deck fins |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-11-30 | 2019-08-19 16:24 | -103 | 2019-03-14 13:20 | Architectural - General | 15000 |  | Damaged | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Main deck parapet arrangement of the Silvertown Bridge had been temporarily installed to accommodate a temporary opening of the footbridge. The installation then had to be dismantled due to its temporary nature. During the removal process, some anchors which secured the deck fins into place were damaged when nuts were ground off. Damaged anchors in their vast majority have to be remediated as these are no longer usable (see attached spreadsheet noting which 14 anchors are damaged beyond repair)
| 05SY - Systemwide | Cxxx-NCR-001044 | NCR | Incorectly Drilled Holes in Makrolon Busbar Covers |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-05-30 | 2019-05-22 13:52 | -8 | 2019-03-18 10:05 | Electrical - LV Equipment | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | The holes drilled in the Makrolon bus bar covers for cable entry are too large and so it would be possible to touch the live side of the panel with the covers in place. Attached are photos of the covers.
| 05SY - Systemwide | Cxxx-NCR-001045 | NCR | 28 day cube test result does not meet requirements |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-07-31 | 2019-06-17 11:44 | -44 | 2019-03-14 16:11 | Civil - Civil Engineering General | 2000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Not Defined | Completed |  | 28 day cube test for Woolwich WB BoH screeding does not meet the 30N/mm2 requirement. See results attached.
| 05SY - Systemwide | Cxxx-NCR-001046 | NCR | TFM Sector 05 EB - Pipe Defect at Ring no. 3803 |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-05-14 | 2019-04-18 10:14 | -26 | 2019-03-18 14:56 | Fire - Fire Systems & General | 5000 |  | Damaged | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the pressure testing on the 15th of March a pipe defect was discovered on the TFM pipe in Sector 05 EB Tunnel ring no. 3803. A pin sized hole found off seem; pipe to be replaced and the pipeline tested.
| 05SY - Systemwide | Cxxx-NCR-001047 | NCR | Cross Passage Sump MCC Outgoing Circuits - Lack of F2 Design |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-05-31 | 2019-03-29 10:47 | -63 | 2019-03-18 15:25 | Electrical - Electrical Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | Lack of approved F2 design for the outgoing circuits from the Cross passage pumps MCCs.
| 05SY - Systemwide | Cxxx-NCR-001048 | NCR | CWS Non-Pressure doors install - Site Changes Made without acceptance |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-06-28 | 2019-05-16 13:40 | -43 | 2019-03-20 16:53 | Systems - Ventilation and Pressure Relief | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | The Contractors Door Supplier proceeded to carry out unauthorised changes to the surrounding civil structure due to possible design / manufacturing errors in the non pressure doors on level -3 at canary wharf ventilation shaft. Such changes were not assessed as per the Contractors Design Change process. Subsequent unauthorised alterations may have compromised the civil structural requirements.
| 05SY - Systemwide | Cxxx-NCR-001050 | NCR | Site change process not followed for CP sump ventillation |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-05-20 | 2019-04-11 11:25 | -39 | 2019-03-20 16:46 | Mechanical - Mechanical Engineering General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | A number of site changes have been made to CP ventilation system without being captured through the SOB/FCD process. Item 1. Drawing Cxxx-__-M-DDD-CR001_Z-17101 shows the arrange for the fan support structure. This is not what has been installed on site. Item 2. CP Mechanical ventilation layout drawings Cxxx-__-M-DDD-CR001_Z-220XX shows rectangular ductwork to be used on the fan side (forced ventilation). Circular ductwork has been installed on site.
| 05SY - Systemwide | Cxxx-NCR-001051 | NCR | Pumped Drainage MCC Panel Damage |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-09-30 | 2019-08-06 12:28 | -55 | 2019-03-21 13:21 | Electrical - LV Equipment | 2000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper handling of material | Completed |  | Pumped Drainage MCC panel has been damaged in transit to site. Damage was discovered when the packaging was removed, following positioning on site. The damage is to a panel foot, pump status lamps, control buttons and a VSD control keypad. Attached are photos of the damage.
| 05SY - Systemwide | Cxxx-NCR-001052 | NCR | Pumped Drainage MCC Panel Damage |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-10-30 | 2019-10-01 14:10 | -29 | 2019-03-21 14:18 | Electrical - LV Equipment | 3000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper handling of material | Completed |  | Pumped Drainage MCC panel has been damaged in transit to site. Damage was discovered when the packaging was removed, following positioning on site. The damage is to a panel foot, pump status lamps, control buttons and a VSD control keypad. Attached are photos of the damage.
| 05SY - Systemwide | Cxxx-NCR-001053 | NCR | Discolouration of Lumnaire & CMS Rust in CP09 due to water leaks from cross passage metallic rings |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-08-30 | 2019-05-03 13:22 | -119 | 2019-03-21 15:58 | Electrical - LV Equipment | 3000 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | Water leaks from the cross-passage rings had dripped onto the CMS and in turn caused a dark discolouration on the installed luminaires. The outer covering has been stained and what looks like rust has been formed on the surface of the CMS. Water was also observed to be leaking onto the luminaire flyleads. See attached photos.
| 05SY - Systemwide | Cxxx-NCR-001055 | NCR | TVS Damper Actuators - LED Colour |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-10-11 | 2019-10-14 15:28 | 3 | 2019-03-22 11:23 | Systems - Ventilation and Pressure Relief | 10000 |  | Manufacturing Defect | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Post IRN during Testing and Commissioning activities on the Dampers it has been noticed that the damper actuator LEDs either had faint or no lights, also inconsistent colours for the open/closed function with some showing close (Red), open (Green) and vice versa. The extent of this issue needs to be clarified by TVS T&C. Ensure added to DRACAS.
| 05SY - Systemwide | Cxxx-NCR-001056 | NCR | Woolwich Station WTH EB Pump Supply CP 17 |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-04-08 | 2019-04-10 13:21 | 2 | 2019-03-25 12:11 | Electrical - Power Distribution | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | The supply cable from the Cxxx CP17 MCC isolator cannot be terminated into the Isolator without straining the terminals within the isolator. The affected cable is CR147-LVD-00034/Cxxx-PC-00000802-1 BS6724 SWA 240sq. mm 4 core.
| 05SY - Systemwide | Cxxx-NCR-001057 | NCR | TVS - CWS East - Damaged bolts due to over torqueing |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-06-27 | 2019-05-14 07:09 | -44 | 2019-03-25 14:05 | Architectural - Doors | 3000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | Inspection of the finished non pressurised doors was carried out on Thursday 27/02/19, the bolts securing the door leafs to the hinges was found to be rounded/damaged(photos attached ) due to over torqueing. The bolts was previously torqued to a value of 80Nm and was supposed to be 33Nm.
| 05SY - Systemwide | Cxxx-NCR-001059 | NCR | Use of __ LFHU Metallic Conduit for Critical Sump Electrical Install is not MCR approved |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-09-30 | 2019-05-15 11:49 | -138 | 2019-04-02 12:14 | Electrical - Cable Management | 3000 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | Cxxx have installed __ LFHU Metallic Conduit without an approved Cxxx MCR. The product has been used to provide mechanical protection for the control cables in the Cross Passages (CP), and Station Shafts and Portals (SSP) Motor Control Centre (MCC) installation works. The use of this metallic conduit was identified during an IRN inspection. The __ LFHU Metallic Conduit has been LU APR approved for "Limited and Dispersed Use" - giving a limit of 500g to each application to preserve its fire performance. This product has been MCR approved at Cxxx: Cxxx-__M-E-LRC-D061-50010.
| 05SY - Systemwide | Cxxx-NCR-001060 | NCR | Canary Wharf UPS Routes |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-08-28 | 2019-07-03 14:11 | -56 | 2019-04-08 09:01 | Electrical - Electrical Engineering General | 5000 |  | Design | Repair | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Cxxx designed and installed a new sub mains cable routing through Canary Wharf Station as no adequate route had been provided by the station designers. Cxxx-FCD-000834 was signed and agreed to cover the cable routing and CMS installation with Crossrail for this purpose. Between the FCD sign off and cable pulling, the existing CMS planned to be used for the cable pull had been reworked in both the Fan Exhaust Rooms by a third party, meaning that the route had to change last minute.
| 05SY - Systemwide | Cxxx-NCR-001061 | NCR | Cxxx SCADA Monitoring of TLPP Tunnel Lighting Status Signal |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-09-27 | 2019-09-06 10:33 | -21 | 2019-04-05 10:01 | Communications and Control Systems - SCADA/Central Management System | 6000 |  | Design | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | During the commissioning of the Cxxx SCADA monitoring and control interface with the Cxxx TLPPs, it has become apparent that the TLPPs are not providing the monitoring of the tunnel lighting status required by the SCADA control algorithms. The design intent of the TLPP outputs used to drive the "Switched Mains Tunnel Lighting/Status" and "Switched UPS Tunnel Lighting/Status" SCADA inputs is to monitor the availability of the circuit breakers that feed tunnel Lighting when the lights are "OFF" and when the lights are "ON", the combined availability of the circuit breakers and the status of the lighting current switches. As a result, when all monitored components are heathy the outputs to the SCADA is logic 1 / ON, irrespective of whether the tunnel lights are "ON" or "OFF". The design intent of these SCADA inputs is solely to monitor whether the tunnel lights are "ON" or "OFF. A signal is available from the TLPP to monitor if tunnel lights are "ON" or "OFF, however the SCADA does not provide an input for this.
| 05SY - Systemwide | Cxxx-NCR-001062 | NCR | CMS Lidding Expansion Joints |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-09-30 | 2019-10-18 07:58 | 18 | 2019-04-08 15:35 | Electrical - Cable Management | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The CMS lidding installed at Connaught West Compound has been installed without expansion joints and is expanding in hot weather
| 05SY - Systemwide | Cxxx-NCR-001063 | NCR | Leaking Hydrants at Connaught Tunnel TFM During Filling/Pressure Test |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-06-30 | 2019-06-20 06:58 | -10 | 2019-04-10 16:07 | Mechanical - Piping | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Issue is that the two threads between the hydrant and the welded pipe do not marry up and the joint is leaking.
| 05SY - Systemwide | Cxxx-NCR-001064 | NCR | BUCF - Works started without an approved method statement |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-07-10 | 2019-05-16 13:27 | -55 | 2019-04-11 14:26 | Systems - Ventilation and Pressure Relief | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | At the BUCF in Ilford, with works near to completion, Cxxx - BUCF VCS Equipment Installation and Testing and Commissioning Method Statement document reference Cxxx-__-O1-GMS-CRG03-50261 still a placeholder
| 05SY - Systemwide | Cxxx-NCR-001065 | NCR | Cxxx-TVS-TCR-W: water present within the casing of the roof mounted E/B DRD actuators |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-10-10 | 2019-09-18 10:10 | -22 | 2019-04-15 12:04 | Electrical - General | 3000 |  | Design | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During a quality inspection on TCR West ventilation shaft Roof damper on 5th April 2019, water ingress or condensation build up was noticed on all 3no actuators located on the roof. See Photos attached.
| 05SY - Systemwide | Cxxx-NCR-001066 | NCR | Connaught Pump MCC Generator Panel |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-08-31 | 2019-06-06 10:28 | -86 | 2019-04-15 15:42 | Electrical - LV Equipment | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | RE: Cxxx-RFI-001618, Following the recent submission of the Pump MCC Specification (Cxxx-__-D-RSP-CRG03-50005) the form of construction of the Connaught Pump Generator Panel is specified as Form 4 Type 6; all Pumps MCC Panels have been constructed to Form 4 Type 2A. The reason for the change is the due to the classification of the panel; it has been classified as an emergency power supply panel. This is true for large panels which multiple feeders (ie, Station and Shaft Switchgear); however, the Connaught Generator Panel only has 2 outgoing feeders and any maintenance of the incoming supply, busbars or component replacement will require a full panel shutdown whether it is Form 4 Type 2A or Type 6. The only maintenance activities which will be carried out when the panel is in operation are checking the settings on the MCCB or Thermostat. The panel will be provided with internal shrouding to IP4X will be provided for all exposed busbars and connections. For these reasons, there is no benefit to constructing the panel to Form 4 Type 6 and __ proposes to constructe the panel to Form 4 Type 2A with internal shrouding to IP4X. External IP rating will be IP66 which is the same as the Surface Lighting Power Panels. __ Propose Use As Is disposition as Form 4 Type 2A with internal shrouding to IP4X. External IP rating will be IP66.
| 05SY - Systemwide | Cxxx-NCR-001067 | NCR | TFS termination at Plumstead ATS was damaged |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-07-30 | 2019-05-16 13:30 | -75 | 2019-04-24 06:54 | Electrical - OHLE | 5000 |  | Damaged | Repair | 3 (3-6k) | Complete | Material/Preservation Problems - Other | Completed |  | During NFS TFS pressure test, the damaged was found at HV termination at Plumstead ATS.
| 05SY - Systemwide | Cxxx-NCR-001068 | NCR | IP rating not maintained on LV assets during glanding works |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-07-01 | 2019-06-07 08:05 | -24 | 2019-05-02 11:06 | Electrical - LV Equipment | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | IP washers have not been installed on all Cxxx LV assets to maintain the asset IP rating detailed in the Cxxx equipment specifications. Without IP washers, CMP Solo glands (A2 and CW) provide an IP 54 rating rather than that specified in the equipment specifications. The following assets now achieve a minimum IP rating of IP54 Platform End Spaces Rooms - TLPP - IP washers not installed - C&C isolators - IP washers not installed - CP MCC Isolators - IP washers not installed Platform End Space - Not Enclosed (Victoria Dock Portal and Liverpool St.) - TLPP - IP washers not installed - C&C Isolator - IP washers not installed - CP MCC Isolators - IP washers not installed - MVSO - IP washers not installed Cross Passages - Distribution Boards - IP washers not installed - Auto Changeover Switches - IP washers not installed - Multi Voltage Socket Outlets - IP washers not installed Assets in the running tunnels and open route areas are not affected by this NCR where IP washers have been installed meeting the Cxxx Equipment Specification requirements - Multi Voltage Socket Outlets (installed on SSP back walls) - Isolators - Pushbuttons (including Cross Passages) - Surface Lighting Panels - PHCCs - Junction Boxes - Fire Alarms - refer to Cxxx-NCR-001000
| 05SY - Systemwide | Cxxx-NCR-001069 | NCR | Damaged STS sleepers due ME4 derailment at the tunnel CP 17 area |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-08-15 | 2019-08-05 13:13 | -10 | 2019-05-17 08:34 | Track - Rails and Sleepers | 8000 |  | Damaged | Repair | 2 (6-60k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | An incident happened at the tunnel from EB Ch 20477 up to Ch 20490 RHS, The Unimog road-railer, used for shunting, maintenance and cleaning tasks, has derailed producing damage on the STS sleepers. Not rails, no concrete slab or tie bars have been damaged.
| 05SY - Systemwide | Cxxx-NCR-001070 | NCR | Incorrect Size cable used for Hyrdo-carbon panel supply from MCC in Cross passages |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-07-31 | 2019-05-16 13:37 | -76 | 2019-05-07 15:29 | Electrical - LV Equipment | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Cxxx have installed a incorrect cable size to supply the Hydro carbon controller panels within the Cross passages that include a MCC, (CP1, CP2, CP4A, CP5A, CP6, CP9, CP11, CP13, CP17, CP18 and also including Niche 03. 1.5mm __ 0HLS Saffire BS6724 3c has been installed instead of 2.5mm. The designer MMD have now confirmed via SOB the use of 1.5mm is suitable and this will be captured in FCD 1000.
| 05SY - Systemwide | Cxxx-NCR-001071 | NCR | CEG Decision to Remove PRV's from SSP TFM. |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-10-23 | 2019-09-12 10:40 | -41 | 2019-05-07 08:19 | Mechanical - Piping | 10000 |  | Design | Use As-Is | 2 (6-60k) | Complete | Design Problem - Other | Completed |  | As per Cxxx-EWN-03000 and Cxxx-RFI-000919. The Works Information Mechanical Equipment Specification requires Station, Shaft and Portal Contractors to provide pressure relief valves at breeching inlets for the Central and Thames tunnels. The Employer’s Chief Engineers’ Group has advised that these are not required and as a result they have not been installed by Others. The PRV’s are critical components in the Contractor’s design of the TFM and failure to provide these protective devices would put the system at risk. The Contractor cannot therefore accept responsibility for the performance of the system if the design is compromised by Others. • Where PRVs have not been fitted at the stations, shafts and portals then these should now be fitted. The fire brigade appliance relief valves may offer no protection to the fire main system. • The pressure relief offered by the devices fitted to the fire appliances is unknown but is designed to protect the fire appliance equipment NOT the connected system. The pressure setting may be set too high and the relief flowrate may be too low. • If CEG deem PRVs not necessary, then their accompanying design justification would need to be submitted and accepted by CRL’s Assurance Team and other Stakeholders. • It would not be beneficial for __ to carry out additional analysis to justify the removal of PRVs as previous studies indicate that they are required.
| 05SY - Systemwide | Cxxx-NCR-001072 | NCR | Commissioning Test Plan not available for LVD Test & Commissioning Activities |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-08-16 | 2019-06-07 08:00 | -70 | 2019-05-08 15:57 | Electrical - LV Equipment | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Lack of procedure | Completed |  | It was found that a Commissioning & Testing Plan (CTP) was not available during a recent surveillance on LVD Test & Commissioning activities.
| 05SY - Systemwide | Cxxx-NCR-001073 | NCR | Connaught Drainage Covers slip resistance |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-08-28 | 2019-08-12 08:26 | -16 | 2019-05-13 16:55 | Track - Walkways | 6000 |  | System Defect | Repair | 3 (3-6k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Laboratory and in-situ pendulum testing of the drainage covers installed within Connaught tunnel indicates that the covers failed to meet the slip resistance value required in the specification. The failed results occur when the sample is tested at a 45 degree orientation, in the wet only. Results in the 0 and 90 degree orientations were above the required value of 40 SRV. The slip resistance of the metallic side strip adjacent to the cover was also found to be below the 40SRV when tested in-situ.
| 05SY - Systemwide | Cxxx-NCR-001075 | NCR | Damaged CMS and Post at NWP |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-09-30 | 2019-10-01 14:16 | 1 | 2019-05-28 12:41 | Electrical - Cable Management | 6000 |  | Damaged | Rework | 3 (3-6k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | At North Woolwich Portal a piece of plant has come into contact with a 3 meter section of CMS causing it to become buckled. As well as the CMS being damaged a 4.8m post that holds up the CMS has also been bent causing it to lean over by approximately 10degrees. The exact location of the damage is WB - ch19490.
| 05SY - Systemwide | Cxxx-NCR-001076 | NCR | Surface Lighting Junction Box Warning Labels - CON |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-08-31 | 2019-07-16 06:34 | -46 | 2019-05-28 12:35 | Electrical - LV Equipment | 5000 |  | Design | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Due to the constraints within Connaught we have ended up having to mount junction boxes the opposite way round from the position we had originally intended to install them. This has meant that the labels that were purchased stuck to the boxes are now upside down in some cases.
| 05SY - Systemwide | Cxxx-NCR-001079 | NCR | TVS - CWS - Commencing work without an approved MCR. |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-08-19 | 2019-06-17 12:28 | -63 | 2019-05-21 15:45 | Mechanical - Mechanical Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | The non-pressurised doors at CWS installation works were commenced without a Code 1 approved MCR: Cxxx-__-M-MCR-CR143-50001 via the MCR process.
| 05SY - Systemwide | Cxxx-NCR-001080 | NCR | Asset Labelling - Isolators |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-09-27 | 2019-08-21 09:59 | -37 | 2019-05-28 11:35 | Information Management - Asset Information | 3000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | For the following LV asset - L746155 Isolator The Cxxx LVD Asset Labelling Scope Definition Cxxx-__-K2-RGN-CRG03-50053 was not followed for all isolator installations due to 1. site constraints preventing installation of labels adjacent to isolators 2. multiple isolators in a same location making the label unambiguous to the asset difficult/impossible 3. incorrect installation
| 05SY - Systemwide | Cxxx-NCR-001081 | NCR | IRN 28 CON TLPP E/B LV TDS checksheets have been Photocopied |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-08-31 | 2019-06-17 05:23 | -75 | 2019-06-07 09:21 | Electrical - LV Equipment | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | TDS checksheets have bee photocopied to produce the same tick box checks throughout the paperwork, although each sheet has been signed and dated individually the photocopying does not give assurance that the inspections have been carried out on each item/equipment individually and progressively.
| 05SY - Systemwide | Cxxx-NCR-001082 | NCR | IRN 29 CON TLPP W/B LV TDS checksheets have been Photocopied |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-08-31 | 2019-06-17 05:24 | -75 | 2019-06-07 09:22 | Electrical - LV Equipment | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | TDS checksheets have bee photocopied to produce the same tick box checks throughout the paperwork, although each sheet has been signed and dated individually the photocopying does not give assurance that the inspections have been carried out on each item/equipment individually and progressively.
| 05SY - Systemwide | Cxxx-NCR-001083 | NCR | Royal Oak Portal (ROP) Drainage Covers slip resistance |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-09-30 | 2019-08-29 14:13 | -32 | 2019-06-05 15:02 | Track - Walkways | 6000 |  | System Defect | Repair | 3 (3-6k) | Complete | Material/Preservation Problems - Other | Completed |  | At Royal Oak Portal approx. 0.5km of aluminium track drainage covers have been installed in the open route towards Westbourne Park. In-situ slip testing of the covers has indicated that the slip resistance of the covers in the worst case direction is below the 40 PTV required by the spec. Full test report with all measured values will be issued shortly.
| 05SY - Systemwide | Cxxx-NCR-001085 | NCR | Victoria Dock Portal (VDP) Drainage cover slip resistance |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-09-30 | 2019-08-16 13:22 | -45 | 2019-06-05 15:09 | Track - Walkways | 6000 |  | System Defect | Repair | 3 (3-6k) | Complete | Material/Preservation Problems - Other | Completed |  | At Victoria Dock Portal approx. 0.2km of aluminium track drainage covers have been installed in the open route towards Custom House Station. In-situ slip testing of the covers has indicated that the slip resistance of the covers in the worst case direction is below the 40 PTV required by the spec. Full test report with all measured values will be issued shortly.
| 05SY - Systemwide | Cxxx-NCR-001086 | NCR | CAW-CP11 MCC LV System has been energised by T&C before completion of an IRN. |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-08-31 | 2019-06-20 07:06 | -72 | 2019-06-15 08:11 | Electrical - LV Equipment | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | It became apparent on 7/06/19 that T&C have not followed procedure and a section of the MCC installation in CP 11 has been energised and tested before completion of the IRN.
| 05SY - Systemwide | Cxxx-NCR-001087 | NCR | Water condensation in the lubricator cabinets |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-09-10 | 2019-09-27 10:29 | 17 | 2019-06-12 13:24 | Track - Track General | 6000 |  | Manufacturing Defect | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | We have noted water condensation on the top lid lubricators cabinets, They have been investigated layering up gaskets and reducing depth of bolt engagement (simulate shoulder bolts) to improve seal and re-evaluated the seal visually after each additional layer. The result was that increasing the seal has negligible effect and water would easily penetrate. With the addition of wind/turbulent air, water ingress is inevitable. Increasing the depth of seal also raises the height of the Perspex from the tank by the same amount, i.e. gap never really gets smaller.
| 05SY - Systemwide | Cxxx-NCR-001088 | NCR | BOS cracked concrete |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-10-31 | 2019-07-31 11:34 | -92 | 2019-06-17 10:38 | Civil - Civil Engineering General | 3000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | At BOS, there are cracks in the screeding on the westbound east end. Please see image attached for this item.
| 05SY - Systemwide | Cxxx-NCR-001089 | NCR | TCR Concrete crack |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-10-31 | 2019-07-31 11:35 | -92 | 2019-06-17 10:46 | Civil - Civil Engineering General | 3000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | At TCR, There is damage to the screeding on the westbound east. Please see attached images for more details
| 05SY - Systemwide | Cxxx-NCR-001090 | NCR | LIS cracked concrete |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-10-31 | 2019-07-31 11:37 | -92 | 2019-06-17 10:53 | Civil - Civil Engineering General | 3000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | At LIS the screed appears to be damaged and in bad condition due poor workmanship. Please see attached photo.
| 05SY - Systemwide | Cxxx-NCR-001091 | NCR | OHLE - some intermediate drop tubes have potential weakness |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-01-24 | 2019-11-01 13:18 | -84 | 2019-06-21 08:28 | Over Head Line Electrification - Supports | 550000 |  | Design | Repair | 1 (>60k) | Complete | Design Problem - Other | Completed |  | OHLE Intermediate drop tube, the pivot link between the cantilever and the vertical drop tube has been visually identified as deflecting. Preliminary investigations lead __ to believe that in instances deflecting has occurred past the elastic point on the yield curve. No short term risks have been identified however it is believed that during maintenance or additional loading of these supports future operations could be effected. Type A, B & C are the most likely to be effected due to their geometry. A(s) -->2553 AE-->0 B-->1800 C-->348 D-->46 E-->35 F-->38 G-->254 H-->582 I-->0 J-->1 M-->43 M4-->0
| 05SY - Systemwide | Cxxx-NCR-001093 | NCR | TVS BOS-E Damaged field ethernet cable |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-09-27 | 2019-07-31 11:38 | -58 | 2019-06-19 10:01 | Communications and Control Systems - SCADA/Central Management System | 1000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | When setting up the profinet between the VSD A and the MCC there was an issue with the field Ethernet cables. From testing it the failure is one of the twisted pairs is an open circuit, this stops the two devices communicating...Ethernet field cable for VSD A is damaged
| 05SY - Systemwide | Cxxx-NCR-001094 | NCR | Connaught Shaft Pipe Support Steelwork |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-10-31 | 2019-07-15 09:13 | -108 | 2019-06-19 12:24 | Mechanical - Piping | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The original Cxxx drawings (Cxxx-OVE-S-DDA-CR001_Z-22360 and Cxxx-OVE-S-DDA-CR001_Z-22361) and the calculation document Cxxx-OVE-C4-XCL-CR146_WS158-50001 note the inclusion of 356*171*51 UKB that are to be used to support the Cxxx pipework at intermediate levels -0.2, -2.5, -4.5, -6 and -7.5. The Cxxx drawing (Cxxx-__-P-DDD-CR001_Z-13103) and SOB-622 show pipework supports on the 203*133*30 UKB installed by Cxxx that form the walkway supports. Cxxx pipework has been connected onto the secondary support steelwork instead of the designated pipework support steelwork. Connections were made as per SOB622 and the Cxxx drawings attached this is a MM design issue. they were either not aware of or followed the principles of the Cxxx and Cxxx designs and installations looking at the Cxxx drawings listed below it is obvious what has been designated for pipework supports – this directly contradicts the drawings and SOBs received by the Cxxx mechanical team.
| 05SY - Systemwide | Cxxx-NCR-001097 | NCR | BOS-E Fan-A Vibration Compliance |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-12-17 | 2019-10-23 10:10 | -55 | 2019-06-20 13:49 | Systems - Ventilation and Pressure Relief | 10000 |  | System Defect | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | On 13th June 2019 the commissioning of the BOS-E fans took place. The commissioning was performed by the Fans manufacturer, __. Prior to this day __ had performed static maintenance on the fan to check the installation and condition of the fan. During commissioning the fan was inspected, greased and run in stepped speeds to full speed in both directions. It was found that the vibration of Fan-A exceeded the commissionable level of 4.5mm/sec RMS for the design duty point of 75% and 76%, as per the TVS mode tables. It was noted that no excessive vibration was found at the fans casing or anti-vibration mounts. At the time of raising this NCR, data has been collected by __ for analysis. The outcome of this investigation will be the proposal to rectify this issue.
| 05SY - Systemwide | Cxxx-NCR-001099 | NCR | WHI Back of house angle fitting |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-07-26 | 2019-07-15 13:43 | -11 | 2019-06-26 08:19 | Mechanical - Mechanical Engineering General | 3000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | At WHI, the identified scope of work for Cxxx is the installation of metallic angles at the face of the platform to provide horizontal extension since the platform is already at Final Floor Level vertically. The extension angles are 150mm wide and 1m long. As shown in the attached photos the designed gap between plates is 2mm but due to the concrete platform imperfections a larger gap is created (see attached), nominally 4mm.
| 05SY - Systemwide | Cxxx-NCR-001101 | NCR | Incoming Pipe Connections - Tunnel Drainage System |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-10-20 | 2019-09-19 07:50 | -31 | 2019-06-26 15:36 | Civil - Drainage | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | After reviewing the CCTV surveys conducted for tunnel drainage in Zone 2, that pipe connections were not as per the agreed FCD and expanding foam was found in drainage pipes at several locations (CP's 11 and 13 and Niche 3). See attached for further examples and locations.
| 05SY - Systemwide | Cxxx-NCR-001102 | NCR | Pedestrian crossing Fhisher Street, rivet nut coming out |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-11-01 | 2019-12-24 08:24 | 53 | 2019-07-01 15:29 | Track - Track General | 5000 |  | Manufacturing Defect | Reject | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The rivet nuts are not holding into the frames. It looks like they haven’t been riveted enough to hold in. See pictures attached.
| 05SY - Systemwide | Cxxx-NCR-001103 | NCR | TFM ID Banding |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-11-30 | 2019-07-26 10:25 | -127 | 2019-07-10 13:17 | Mechanical - Piping | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | ID banding on the TFM has not been installed as per BS1710_2014.
| 05SY - Systemwide | Cxxx-NCR-001104 | NCR | Manufacture of Whitechapel Pod Door Commenced without Approved ITP in Place |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-10-31 | 2019-08-21 07:44 | -71 | 2019-07-10 13:12 | Mechanical - Mechanical Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | The manufacture of the Rhino Door for Whitechapel Maintenance Pod has proceeded without an approved manufacturing ITP in place, Cxxx-__-O4-ITP-CR092-50001 has not yet been transmitted to CRL for acceptance.. In addition to this a number of Hold points with in the manufacturing ITP have been passed without the verifying documents in place.
| 05SY - Systemwide | Cxxx-NCR-001105 | NCR | Manufacture and Installation of coping support angles carried out without an approved manufacturing ITP |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-10-08 | 2019-08-27 13:57 | -42 | 2019-07-10 15:15 | Mechanical - Mechanical Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Metallic coping support angles have been manufactured and installed without an approved manufacturing ITP
| 05SY - Systemwide | Cxxx-NCR-001106 | NCR | Back of house work commenced without a completed gate review documentation |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-10-31 | 2019-10-14 15:33 | -17 | 2019-07-10 15:29 | Mechanical - Mechanical Engineering General | 1000 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Back of house works including the installation of metallic angles commenced without a completed design gate review documentation.
| 05SY - Systemwide | Cxxx-NCR-001107 | NCR | No Commissioning Test Plan (CTP) for LVD Test & Commissioning Activities Phase 2.3 to 3 |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-10-09 | 2019-10-16 06:59 | 7 | 2019-07-11 16:17 | Electrical - LV Equipment | 1000 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Commissioning & Testing Plan (CTP) was not available on LVD Test & Commissioning activities (phase 2.3 onwards) in accordance with Works Information Volume 2B - Part 28 - Testing and Commissioning Process
| 05SY - Systemwide | Cxxx-NCR-001108 | NCR | Works carried out not following ITP procedure |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-10-14 | 2019-10-28 14:30 | 14 | 2019-07-16 12:42 | Civil - Civil Engineering General | 0 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | According to the __ quality process and the ITP for the surface preparation and protection works of the White Hart Bridge. The works must be controlled by the __ quality team and by CRL after an invitation sent by the construction team. Some of this controls are formalized by the signature of a QCR. Works were not controlled by the __ quality team and no QCRs have been signed by CRL and __ Quality team. We precise that all the works were controlled by the sub agent and the site engineer and also by a CRL representative.
| 05SY - Systemwide | Cxxx-NCR-001109 | NCR | Cxxx TVS limit switches IP & fire rating |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-10-14 | 2019-10-23 09:55 | 9 | 2019-07-16 15:28 | Systems - Ventilation and Pressure Relief | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | On the 5/7/2019 during works planned at Bond Street Crossrail station it was brought to the attention by one of the __ technicians that only one of the two entry points of the limit switches is used having a cable through a gland, while the other one is blanked off with a standard red plug (cap), which after discussing that with the product supplier and the manufacturer (see e-mail trail attached) isn't fire compliant or IP67 rated
| 05SY - Systemwide | Cxxx-NCR-001110 | NCR | 70mm2 catenary wire is used instead of 65.4mm2 in WBP |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-01-31 | 2019-12-24 08:14 | -38 | 2019-07-16 15:50 | Over Head Line Electrification - Catenary Masts | 6000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | 70mm2 catenary wire was installed between the West side of the neutral section at location XR00+012 and the anchor at location J01/19A a distance of around 187.5m.
| 05SY - Systemwide | Cxxx-NCR-001112 | NCR | TPD Liner Pressure Test CP04A WB - Calibration Certificate Unavailable |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-09-27 | 2019-08-05 13:14 | -53 | 2019-07-24 10:03 | Mechanical - Public Health Engineering | 1000 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | The Calibration Certificate used for the Test of the CP04A Test is unavailable and a copy cannot be sourced (the manufacturer and supplier have both been approached but cannot assist). In order to validate the test results an internal assurance calibration of the data logger will be conducted. We will test the Gauge (SN21990) against a calibrated logger and gauge. This internal assurance check will be used to verify the performance of the data logger and test results.
| 05SY - Systemwide | Cxxx-NCR-001113 | NCR | BS-W Damaged control cable |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-12-10 | 2019-12-17 08:42 | 7 | 2019-07-24 12:26 | Systems - Ventilation and Pressure Relief | 3000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | during commissioning shift, it was discovered that the cable from FPP to vibration sensor Cxxx-CC-00000162-1.2 has a large part of insulation damaged (see attached photo)
| 05SY - Systemwide | Cxxx-NCR-001115 | NCR | Bended OHLE anchor bolts in FAR W/B |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-01-31 | 2020-01-10 09:40 | -21 | 2019-09-17 10:29 | Over Head Line Electrification - Over Head Line Electrification General | 5000 |  | Damaged | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In FAR W/B trace, it was noticed that the anchor bolts have deflection issue. The location was around XRA7/01
| 05SY - Systemwide | Cxxx-NCR-001116 | NCR | Works carried out without code 1 ITP, MS, MCRs and drawings approved by CRL |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-10-23 | 2019-09-19 12:04 | -34 | 2019-07-25 15:50 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | The last weekend some works were done without code 1 ITP, MS, MCRs and drawings. The only works done are the next: - Setting out of the west foundation - Excavation of the west foundation - Installation of the rebar anchors for the west foundation The next works were started but not finished and required to be modified and finished: - Installation reinforcement for the west foundation - Installation of formworks for the west foundation Works were done without code 1 for the below documents: -Materials Compliance Record - White Hart Road Bridge - Stainless Steel Rebar Anchor / Cxxx-__-O4-MCR-CRG03-50046 -Materials Compliance Record - White Hart Road Bridge – Grout / Cxxx-__-O4-MCR-CRG03-50049 -Method Statement for White Hart Bridge - Remediation works / Cxxx-__-O1-GMS-CR148-50086 -Inspection and Test Plan - White Hart Road Bridge - Walkway foundation / Cxxx-__-C-ITP-CRG03-50005 - White Hart Bridge – New footbridge foundation detail – Cxxx-__-C-DDD-CR148_SD013_Z-30007 The works were covered by both a WPP (within the sidings team) and RAMS signed off. ITP and MCR’s were submitted to CRL. These MCR’s are duplicates of the Cxxx ones which have been code 1. The ITP was based on an approved Cxxx ITP for the RC Works. The documents were agreed with the exception of the lack of specification from __ (the team used the Cxxx specifications in lieu of a __ specifications)– an issue raised on Friday afternoon by CRL. __/CRL/ __ had a conference call on Friday and all parties agreed to proceed on the basis that __ provided a statement that they were satisfied with the MCR’s, which was done. There was no IFC drawing in place but it was agreed between that we would proceed using the by exception process. Whilst CRL verbally accepted the works could proceed a formal agreement was not formalised on eB.
| 05SY - Systemwide | Cxxx-NCR-001117 | NCR | Vent Testing - Leak Test |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-09-30 | 2019-08-08 07:24 | -53 | 2019-07-31 14:48 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | __’s CTP Cxxx-__-O4-ITP-CRG03-50268 specifies a Class C leakage test on line number 6.3.2 and was QAD-150 prepared for this work. Once testing commenced it was noted that the ductwork would not pass the Class C test set out in DW144 at any pressure in the range between 1100Pa and 2000Pa. __ continued tests on several locations with two different test rigs (a PANDA 341 and ALF 150) to confirm that the equipment was not the root cause of the issue. The equipment was shown to be working within acceptable levels.
| 05SY - Systemwide | Cxxx-NCR-001118 | NCR | Sheath of SWA Cable has been drilled whilst Installing lidding - CON |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-11-27 | 2019-10-10 14:38 | -48 | 2019-08-02 07:10 | Electrical - Cable Management | 3000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | Whilst reworking the CMS lidding at Connaught open route a SWA cable was found to have its PVC sheathing damaged where its has been drilled through hitting the metal armouring.
| 05SY - Systemwide | Cxxx-NCR-001119 | NCR | Surface lighting luminaire fuse |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-10-31 | 2019-09-12 10:47 | -49 | 2019-08-02 12:00 | Electrical - LV Equipment | 3000 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | During commissioning we have had a number of issues with faulty light fittings causing the whole circuit to trip instead of the single luminaire which makes faulty finding difficult.
| 05SY - Systemwide | Cxxx-NCR-001120 | NCR | CP 2 & 3 Lighting cables short of TLPP |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-10-31 | 2019-11-01 12:08 | 1 | 2019-08-02 12:03 | Electrical - LV Equipment | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The lighting cable Cxxx-PC-000141-1 has ended up short of the TLPP at Paddington.
| 05SY - Systemwide | Cxxx-NCR-001121 | NCR | Bond Street Station Back of House Lighting |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-11-29 | 2019-09-24 09:03 | -66 | 2019-08-02 12:09 | Electrical - Lighting | 3000 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Following the installation of the lighting system in accordance with the MMD designs, it was observed that the survey information provided to MMD to complete their designs were not considered in MMD designs. This has resulted in the lights not sufficiently illuminating the walkway and trace and a non-conformance to the lux requirements in the WI Electrical Performance Specification. Please find attached site images for reference.
| 05SY - Systemwide | Cxxx-NCR-001122 | NCR | Scratch and marks in 8 deck parapet fins |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-11-14 | 2019-12-11 15:32 | 27 | 2019-08-16 08:48 | Civil - Civil Engineering General | 3000 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Some marks and scratches are presents in 8 deck parapet fins, as indicated in the report Cxxx-__-O4-RGN-CRG03-50539.
| 05SY - Systemwide | Cxxx-NCR-001123 | NCR | TVS-Cxxx-Damper blades misalignment |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-12-17 | 2019-12-13 15:09 | -4 | 2019-08-16 15:16 | Mechanical - Heating Ventilation & Air Conditioning | 5000 |  | Manufacturing Defect | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the recent inspection at FAR-W, it was noticed that some damper blades do not close completely. The issue was then further investigated on other sites and similar occurrences were noted including gaps between blades, clashing of blades and linkages not closing completely.
| 05SY - Systemwide | Cxxx-NCR-001124 | NCR | Use of expanding foam for TPD sump inlet pipes |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-01-30 | 2020-01-15 13:59 | -15 | 2019-08-21 10:24 | Mechanical - Piping | 1500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | Expanding foam has been used as a backing for the screed that seals the inlet pipe connection. This NCR supersedes Cxxx-NCR-001101.
| 05SY - Systemwide | Cxxx-NCR-001125 | NCR | FAR-E DRDE-1223-A1 damaged cable |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-11-19 | 2019-10-30 16:19 | -20 | 2019-08-21 10:45 | Electrical - LV Equipment | 5000 |  | Damaged | Rework | 3 (3-6k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | FAR-E DRDE-1223-A1 damaged cable's insulation
| 05SY - Systemwide | Cxxx-NCR-001126 | NCR | Non Return Valves in Sumps |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-01-31 | 2019-12-20 09:39 | -42 | 2019-08-27 13:27 | Mechanical - Piping | 5000 |  | Material | Repair | 3 (3-6k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Non Return Valves in sumps have been found to be collecting/catching debris. A number of changes were made to the design. These are listed out chronologically below; 1) Cxxx-MMD-M-RSP-CR001-00002 Rev 6.0 states "Non-return valves with bores 80mm and larger shall be recoil check pattern with non-slam closing characteristics. Recoil and swing check non-return valves shall normally be mounted in the horizontal plane." Cxxx-MMD-M-RSP-CR001-00001 Rev 9.0 state "Each pump discharge branch shall be fitted with a recoil type check valve and isolating gate valve." 2) Cxxx-RFI-000282 was raised to an alternative non-slam type non-return valve (nozzle, wafer or other) was to be considered. 3) Hattersley Water Check Valves, as per CRL-MCR-004805, have been installed on site. After discussions with the designer they have advised that these valves are better for use in potable water systems.
| 05SY - Systemwide | Cxxx-NCR-001127 | NCR | Embedment of anchors not as the manufacturer's requirement |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-11-30 | 2019-10-21 13:06 | -40 | 2019-08-28 16:01 | Civil - Civil Engineering General | 15000 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | As per the NCRs Cxxx-NCR-000861, Cxxx-NCR-1077 and Cxxx-NCR-1078, the embedment of the anchors for the stringer and the coping was not as per the manufacture's requirements.
| 05SY - Systemwide | Cxxx-NCR-001128 | NCR | Bending of the pre-fabricated stainless steel coping upstand |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-12-03 | 2019-10-25 16:12 | -39 | 2019-09-04 12:55 | Civil - Civil Engineering General | 6000 |  | Damaged | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the installation of the Silvertown Footbridge coping, the __ construction team realised that the coping upstand was higher than required. In order to install the top part of the coping to the correct level, the coping upstand was tilted with an angle to ensure that the top piece can be installed to the correct level. In the design drawings, the coping upstand is upright and welded to the botton piece.
| 05SY - Systemwide | Cxxx-NCR-001130 | NCR | Length of spans |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-12-20 | 2019-12-10 08:58 | -10 | 2019-09-11 12:39 | Over Head Line Electrification - Supports | 6000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | The length of the span between the supports is bigger than the permitted one(10.10m)
| 05SY - Systemwide | Cxxx-NCR-001131 | NCR | Fin bowed in the North/South direction at the top of it |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-12-31 | 2019-10-11 21:19 | -81 | 2019-09-17 09:38 | Civil - Civil Engineering General | 1000 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The bridge deck fins fabricated previously by JLE have now been installed on-site by __. It has come to light after the fins have been lined and levelled that some are slightly bowed in the North/South direction at the top of the fin (over the length where the glazing will sit). The allowable fabrication tolerance for a rolled stainless steel sheet over 1 metre is +/- 9mm. All fins fall within this tolerance bar one which has a deviation of 12mm over this distance. The concerned fin is the E9.
| 05SY - Systemwide | Cxxx-NCR-001133 | NCR | Cxxx-TVS-BOS-W: pilot holes drilled for anchor points in RC walls at Level -2 and Level -4 WTH |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-12-18 | 2019-12-05 14:59 | -13 | 2019-09-18 15:10 | Systems - Ventilation and Pressure Relief | 5000 |  | Incomplete Works | Repair | 3 (3-6k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | As part of its access and maintenance obligations for the tunnel ventilation system (TVS), Cxxx is required to install anchor points which will be used to protect operatives from leading edges during the removal of TVS equipment. Anchor points have been installed throughout the system including around the tunnel isolation dampers at Level -2 and Level -4 at BOS-W. While installing the anchor points at Level -2 and -4 BOS-W, Cxxx's sub-contractor hit rebar in a number of locations and could not achieve the required embedment depth. Alternative locations were chosen until satisfactory embedment was achieved. The 'pilot' holes have not been repaired. Please see the attached photos for the extent of the pilot holes - a total of 8no. holes must be repaired.
| 05SY - Systemwide | Cxxx-NCR-001134 | NCR | OHLE- missing slotted washers against the wall (Systemwide) |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-01-31 | 2019-12-20 12:14 | -42 | 2019-09-20 12:05 | Over Head Line Electrification - Supports | 6000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | During site survey, it was noticed that slotted washers are missing between nut and the wall. It is approximately 800 areas which including soffit fixing areas too.
| 05SY - Systemwide | Cxxx-NCR-001135 | NCR | Ball fitting has been double-drilled, holes at 1347B (C16) Right Hand switch rail |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-02-19 | 2020-01-06 13:13 | -44 | 2019-09-20 14:21 | Track - Rails and Sleepers | 10000 |  | Manufacturing Defect | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | During Ultrasonic testing (U15/U1) of the bolt holes at 1347B (C16) Right Hand switch rail identified the rail ‘untestable’ on the 28/08/19. Further investigative work undertaken on the 29/08/19 (loosening and inspection of the anti-creep device ‘Ball and Claw’) highlighted that the one of the bolts on the ‘Ball’ fitting has been double-drilled.
| 05SY - Systemwide | Cxxx-NCR-001136 | NCR | Cxxx-TVS-LIS-W: damage to cable terminations in junction box |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-11-20 | 2019-11-20 11:41 | 0 | 2019-09-27 14:29 | Systems - Ventilation and Pressure Relief | 5000 |  | Workmanship | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | On Wednesday 18th September 2019, it was noticed that VSD A at LIS-W was unresponsive. A fault finding exercise took place over the preceding 3 days. The fault was found in the fan power cable junction box (M135-LVD-02910) where it was discovered that arcing had caused damage to the internal components of the junction box.
| 05SY - Systemwide | Cxxx-NCR-001137 | NCR | Pump MCC Power Supply Unit EMC Compliance |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-12-12 | 2019-11-07 11:35 | -35 | 2019-10-01 09:37 | Electrical - Electro Magnetic Compatibility | 5000 |  | Documentation and Records | Repair | 3 (3-6k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | During the development of the Mechanical EMC Compliance Report, it was discovered the __ Power Supply Units (ABL8REM24030 and BL8REM24050) installed in the Pump Motor Control Centres (CRL-MCR-004980 and CRL-MCR-004981) were not compliant with the Crossrail EMC requirements. These have been replaced with PULS Power Supply units (cs3e241 and cs5e241) which are compliant; these units are referenced in the EMC Report Cxxx-__-E-RGN-CRG03-50092.
| 05SY - Systemwide | Cxxx-NCR-001138 | NCR | PAC & PCC Documentation errors |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-12-31 | 2019-11-29 08:21 | -32 | 2019-10-01 10:32 | Electrical - LV Equipment | 5000 |  | Documentation and Records | Rework | 3 (3-6k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | It has been identified that the PCC folder for the CUH OHLE and the PAC for FAR have been uploaded without the front cover that has been signed by CRL. In addition the NIC/EIC sheets uploaded for the CUH OHLE folder had old copies where the design signatures were missing mixed in with the fully signed off version. Following initial review these appear to be document control errors, however, investigation is required to establish exactly how this has occurred.
| 05SY - Systemwide | Cxxx-NCR-001139 | NCR | Anchor Depth for the NR2 Upper stringer |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-12-30 | 2019-10-21 13:09 | -70 | 2019-10-01 16:52 | Civil - Civil Engineering General | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 1no. anchor that supports NR2 (upper) stringer was installed but to less than the required embedment depth of 90mm. As it was installed directly into the resin packet that was pre-set in the hole, it could not be removed.
| 05SY - Systemwide | Cxxx-NCR-001140 | NCR | Whitechapel EB CH 10014-10157 Non conforment Lighting Design |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-12-31 | 2019-11-20 11:35 | -41 | 2019-10-02 10:28 | Electrical - Lighting | 6000 |  | Design | Repair | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | Whitechapel EB CH 10014 - 10157 Lighting design does not conform to the works Information, following Lux level testing the minimum requirements have not been achieved.
| 05SY - Systemwide | Cxxx-NCR-001141 | NCR | Whitechapel Pod Door drawing/installaion mismatch |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-12-31 | 2019-10-07 13:04 | -85 | 2019-10-03 08:51 | Systems - Cross-passage Doors | 1000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | During an inspection with CRL on Friday 27th September it was found the installation of the Whitechapel pod door did not match what was shown on the drawing. Drawing Cxxx-__-Y-DWG-CR092-50001 shows the doors to have 3 hinges however on site the doors have been installed with 2 hinges.
| 05SY - Systemwide | Cxxx-NCR-001142 | NCR | __ fire stopping to the firemain at shafts |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-02-29 | 2019-12-20 09:29 | -71 | 2019-10-14 08:49 | Fire - Fire Systems & General | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | __ CFS-IS has been installed at the cross passages and shafts to provide fire protection for all penetrations where RoxTec has not been used. It has been found that this product has only been tested for penetrations where the cable/pipe has a maximum diameter of 36mm. The maximum size of pipe that has been installed has an outside diameter of 219mm. It has been confirmed by both __ and Western Thermal that the __ CFS-IS product is not rated for this situation. Therefore we regard the installation as non conforming.
| 05SY - Systemwide | Cxxx-NCR-001143 | NCR | Stringer anchor embedment |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-01-06 | 2019-10-21 12:38 | -77 | 2019-10-08 10:51 | Civil - Civil Engineering General | 2000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A number of M10 __ HAS-R-TZ anchors that support the stringers have been installed both above and below the agreed acceptable embedment depth of 90mm. __ gave us an official dispensation to embed +6/-0mm from the original design embedment of 90mm. However, given the on-site tolerances of actually measuring the anchors (~1mm) and the lengths of the anchors varying by ~1mm, __ feel that an additional +/-2mm tolerance is necessary. This gives an allowable range of 88-98mm embedment. Based on this there are 8no. anchors under-embedded and 12no. over-embedded.
| 05SY - Systemwide | Cxxx-NCR-001144 | NCR | ROP Platform extensions |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-12-10 | 2019-11-11 10:16 | -29 | 2019-10-09 12:44 | Mechanical - Mechanical Engineering General | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | __ was instructed to carry out a Category 2 check on the Back of House & Portal Walkway Platform Edge extension brackets produced by __ Ltd. During this activity it was identified that incorrect assumptions were made by __ in relation to the concrete types resulting in an overutilization of the designed anchors. This failure was identified at Royal Oak Portal(ROP) only where the cantilever is 600mm. The installation went ahead for program reasons on the initial design that was deemed acceptable for VDP. For ROP, __ have therefore developed an additional bracket design (see attached 174-F3246-CS-0005_C3.pdf) which would be added to each bracket in order to account for a cracked concrete calculation. The design is to support an in situ fix avoiding the need of removing already installed brackets. This has also been confirmed as structurally acceptable by MMD. Additional bracket designs to be included on the redline drawings to form part for the As-Built works.
| 05SY - Systemwide | Cxxx-NCR-001145 | NCR | Sheared anchor NR2 Upper |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-01-07 | 2019-10-21 13:12 | -78 | 2019-10-09 12:55 | Civil - Civil Engineering General | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 1no. anchor that supports NR2 (upper) stringer was installed but to less than the required embedment depth of 90mm. As it was installed directly into the resin packet that was pre-set in the hole, when McNeally Brown attempted to remove the anchor it sheared at a point inside the hole and has left behind some of the anchor. The anchor remaining in the hole cannot now be removed.
| 05SY - Systemwide | Cxxx-NCR-001146 | NCR | Tunnel Fire Main (TFM) Thrust Brackets |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-07-31 | 2020-06-12 10:26 | -49 | 2019-10-09 14:46 | Mechanical - Mechanical Engineering General | 165000 |  | System Defect | Repair | 1 (>60k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Further to Cxxx-NCR-001095, Cxxx have experienced a number of deformed thrust brackets at various locations of the TFM. (see attached diagram showing locations) Approx. 20 No. bent brackets have been identified as being affected. The thrust brackets installation providing restraint, consists of 3 No. M20 threaded bars connecting a section of the pipe to the anchor bracket which is then attached to the wall with 6 No. bolts. It has been observed that the M20 threaded bar providing longitudinal restraint is showing signs of deformation, (see attached photographs) the most likely cause is that this happened during pressure testing against a closed valve or blanked off pipe end, however this requires further investigation.
| 05SY - Systemwide | Cxxx-NCR-001147 | NCR | LIV-E FID access works started without an approved ITP and coded drawings |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-12-10 | 2019-11-29 08:23 | -11 | 2019-10-11 14:57 | Systems - Ventilation and Pressure Relief | 1000 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | On the 9th of October during a planned inspection of FID access steelwork torque inspection, it was noted that the installation has started without an approved ITP, also the steelwork drawings 'Cxxx-__-Y-DWG-C101-50057' were not coded
| 05SY - Systemwide | Cxxx-NCR-001148 | NCR | Reduced gap between stringer and stair |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-01-12 | 2019-10-22 16:13 | -82 | 2019-10-14 07:50 | Civil - Civil Engineering General | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | There are 4no. steps on the South-right stairs whereby the line of the stringers installed has left a gap at the tread of less than the specified 5mm between the face of the concrete stair and the stringer. This has made it very difficult to pour grout into the gap.
| 05SY - Systemwide | Cxxx-NCR-001150 | NCR | No MCR for Rhino door at Whitechapel Pod |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-12-17 | 2019-11-20 11:43 | -27 | 2019-10-17 11:57 | Mechanical - Mechanical Engineering General | 1000 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | During production of the IRN RPL for Whitechapel pod door it has been found that no MCR is in place. MCR number has been created but no document provided.
| 05SY - Systemwide | Cxxx-NCR-001151 | NCR | Cross Passage Lux Levels on Equipment |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-12-31 | 2019-12-19 08:15 | -12 | 2019-10-23 08:25 | Electrical - Lighting | 6000 |  | Design | Use As-Is | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Whilst carrying out LUX testing within the Cross Passages, Niche03 and WHI maint POD we have found that we are failing to meet the lighting levels set out in the works information on some electrical panels. When testing the lighting we have found that in a number of locations The lighting on electrical panels is falling below the 150lux required and on the internal side of the door the lux level is falling below 50lux. The affected areas/equipment and lux levels achieved are shown on the attached Excel sheet (lux levels results were taken with both mains and UPS lights on)
| 05SY - Systemwide | Cxxx-NCR-001152 | NCR | Silvertown Footbridge – Stringer Grout Voids |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-01-19 | 2019-11-18 11:38 | -62 | 2019-10-21 13:44 | Civil - Civil Engineering General | 3000 |  | Material | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | After striking the temporary works shutters on the Silvertown footbridge, there are areas noted where the grout did not fill the underside/chamfer area on the SL2 and SR2 stringers. This is likely due to pinch points along the stringer/concrete alignment which did not allow the grout to flow sufficiently to the underside of the stairs. This was not discovered or verifiable until the works were completed and the shuttering removed. See attached mark-up of the areas where grout voids are found.
| 05SY - Systemwide | Cxxx-NCR-001153 | NCR | Connaught Tunnel Pumped Drainage Generator Connection Panel Cable Cabling |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-11-28 | 2019-11-18 08:17 | -10 | 2019-10-22 10:10 | Electrical - LV Equipment | 2000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | The Connaught Tunnel Pumped Drainage Generator Connection Panel is separated into various compartments. As is detailed on the attachment titled "Connaught Pumped Drainage Generator Panel IP Rated Sections.pdf ", the 3 compartments at the bottom of the panel are not IP rated, whereas those containing electrical switchgear are rated to IP66. As is detailed on the attachment titled "Connaught Pumped Drainage Generator Panel Power Cable Entry NCR.pdf" power cable cores have been transited into the IP66 rated compartments on the panel without any method of sealing as they pass through the gland plate, therefore compromising the IP rating.
| 05SY - Systemwide | Cxxx-NCR-001154 | NCR | Silvertown Footbridge – Handrail Bracket Welding |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-01-20 | 2019-11-20 21:58 | -61 | 2019-10-22 08:16 | Civil - Civil Engineering General | 0 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | There is a clash between the drilled holes and the welding on the back of the handrail brackets which has meant that the weld cannot be along the full length of the plate. The holes have to be drilled prior to welding as the heat affected zone around the weld area would make the steel too hard to adequately tap. The weld cannot be completed over the full length after drilling because the heat input would warp the tapped threads. Therefore __’s fabricator have not completed the welding along the full length of the plate.
| 05SY - Systemwide | Cxxx-NCR-001155 | NCR | Silvertown Footbridge – Handrail Bracket Drilled Holes |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-01-21 | 2019-11-12 14:55 | -70 | 2019-10-23 13:59 | Civil - Civil Engineering General | 3000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The drilled holes to the balustrades on the Silvertown Footbridge have been drilled 15mm out of position for 22 bracket (12 on the South Right, and 10 on the South left). This means that there is a clash between the handrail bracket and the mesh panels which sit circa 11mm proud of the balustrade.
| 05SY - Systemwide | Cxxx-NCR-001156 | NCR | Silvertown Footbridge – North Retaining Wall Bracket |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-01-22 | 2020-01-07 13:22 | -15 | 2019-10-24 09:12 | Civil - Civil Engineering General | 6000 |  | Planning | Repair | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | The North Left stringer is supported from the retaining wall and not off the bridge like the rest of the structure, for this there are retaining wall brackets which cantilever off the wall, these hold the balustrades post, which hold the stringer. The brackets on the retaining wall are roughly 40mm too short, so we are outside of the design allowance for 10mm packing.
| 05SY - Systemwide | Cxxx-NCR-001157 | NCR | OCS - Cracked splice over the covered catenary wire end - WBP |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-02-06 | 2019-12-30 15:38 | -38 | 2019-10-24 13:28 | Over Head Line Electrification - Over Head Line Electrification General | 6000 |  | Damaged | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Maintenance team has captured crack at the covered catenary wire end in WBP. Please see attached Diagram and Pictures.
| 05SY - Systemwide | Cxxx-NCR-001158 | NCR | Bond Street East Fan Performance Compliance |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-12-14 | 2019-12-10 10:49 | -4 | 2019-10-25 11:44 | Systems - Ventilation and Pressure Relief | 5000 |  | System Defect | Repair | 3 (3-6k) | Complete | Verification Problems - Other | Completed |  | On 23rd October 2019, vibration levels above the 4.5mm/sec commissionable level were observed whilst running both Bond Street East Shaft fans at their duty speed of 91% (900rpm). Investigations were undertaken on the 24th October 2019 by __ and __, to collect data on the vibration performance. It was found that vibration levels had grown in magnitude since results were collected on the fan performance following the incorporation of a stiffening 'collar' into the fans. In addition to increased magnitude, it was found that for the 91% (900rpm) fan speed the vibration grew with time, whilst running the fan under steady-state conditions. At the time of raising this NCR (25th October 2019) investigations are underway by __ and the fan manufacturer, __, to identify the cause and bring the fan back into compliance.
| 05SY - Systemwide | Cxxx-NCR-001159 | NCR | OHLE- Z brackets' traceability needs to be resolved |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-02-28 | 2019-12-12 09:52 | -78 | 2019-11-05 13:42 | Over Head Line Electrification - Supports | 3000 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Not Defined | Completed |  | Hard stamp information on manufactured Z brackets includes the drawing numbers too for traceability purpose. When hard stamps were applied on Z brackets in Transforge, they were done according to "intermediate drop tube drawing numbers" instead of new "Z bracket drawing numbers". Forexample; 00035 instead of 99035. Cxxx-__-R6-DDD-CRG03-00035 (P05) Intermediate Drop Tube Fixing, Length = 0.147m Cxxx-__-R6-DDD-CRG03-99035 (P01) Intermediate Drop Tube Fixing, Length = 0.147m, Z-bracket & Eyebolt-side packing Details, This traceability issue on Z brackets need to be resolved.
| 05SY - Systemwide | Cxxx-NCR-001160 | NCR | Stepney Green Exit Sign Installation |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-12-16 | 2019-12-05 15:01 | -11 | 2019-11-12 10:03 | Electrical - Lighting | 1500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | At Stepney Green Shaft, the illuminated directional exit signs required at Stepney Green Shaft in line with the revised __ design and PMI for evacuation routes from the tunnel have not been installed as required. Cxxx-FCD-001210 details the revised installation requirements to meet the design. The attached SOB details the solution to implement the installation of the missing exit sign and pushbutton on the existing circuits at STG. The cable calculations previously completed allow for the load of the exit signs and missing pushbuttons as they are already incorporated into the design but not installed. the use of junction boxes mitigates the need to install long run of cables in the tunnel and termination works in multiple assets.
| 05SY - Systemwide | Cxxx-NCR-001161 | NCR | TVS Cxxx -Deterioration of actuator thermal jackets |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-04-01 | 2019-12-19 08:21 | -104 | 2019-11-14 13:54 | Mechanical - Heating Ventilation & Air Conditioning | 5000 |  | Damaged | Rework | 3 (3-6k) | Complete | Material/Preservation Problems - Improper handling of material | Completed |  | During one of the inspections at Woolwich and Farringdon, it was noted that the damper actuator thermal jackets had deteriorated. In some cases, the sewed seams were burst, and fixing straps had become detached (see attached photo). There is a danger that loose jacket material could interfere with the damper operation. Also, the heat resisting integrity could be compromised. During the initial investigation it was noted that the thermal jacket deterioration has possibly occurred due to but not limited to the below mentioned reasons: 1) Water ingress impinging on the jackets e.g. ELS 2) Damage due to works carried out by other sub-contractors 3) Vermin infestation 4) Thermal jackets strapped too tight at some locations and hence one of the TVS teams is out on site fixing this issue This issue requires investigation on other sites and remedial action.
| 05SY - Systemwide | Cxxx-NCR-001162 | NCR | Silvertown Footbridge – Mesh Panel – Fin Gaps |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-04-30 | 2020-04-02 11:40 | -28 | 2019-11-26 10:57 | Civil - Civil Engineering General | 6000 |  | Design | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Further to RFI-1776 & RFI-1812, the designed gap within the F2 drawings either side of the mesh panel is a nominal 10mm. The fabrication and installation tolerances within the structure increase the maximum permissible installed gap to 12mm. The contractor has identified areas where the installed structure exceeds this tolerance. These areas are indicated in the attached document "Distances"
| 05SY - Systemwide | Cxxx-NCR-001163 | NCR | Silvertown Footbridge – North Handrail Alignment |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-05-31 | 2020-04-07 08:58 | -54 | 2019-11-15 10:37 | Civil - Civil Engineering General | 6000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The North Left handrail appears to bend/bow along the stairs by up to 15-20mm due to the brackets being mounted too high or low. This was discussed in the snagging walkout and PTR meeting on 6/11/19.
| 05SY - Systemwide | Cxxx-NCR-001164 | NCR | Silvertown Footbridge – Mesh Panel Alignment |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-02-13 | 2020-01-23 14:24 | -21 | 2019-11-15 10:44 | Civil - Civil Engineering General | 3000 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Alignment of South Right Mesh at Mid Landing (ME13) is not as per design. The mesh panel is taller than designed that therefore is higher than in other areas of the bridge.
| 05SY - Systemwide | Cxxx-NCR-001165 | NCR | STG Green Intervention/Evacuation Doors Opening Swing |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-12-20 | 2019-12-06 07:39 | -14 | 2019-11-15 13:45 | Systems - Cross-passage Doors | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | Following a site visit by Crossrail on 13/11/19 it has been raised that there is some confusion over the opening direction of the intervention and evacuation doors. Drawing Cxxx-__-M-DDL-CR001_Z-17120 shows the both the EB intervention and evacuation door opening away from the trace. However shows the WB evacuation door opening away from the trace and the intervention door opening into the trace. However the Tunnel Mechanical Equipment Specification, Cxxx-MMD-M-RSP-CR001-00002, section 5.4 states "the doors shall be hinged so as to open away from the tunnel". The door sets at Stepney Green have been installed as per the drawing.
| 05SY - Systemwide | Cxxx-NCR-001166 | NCR | OHLE Feeder cable installation bracketry spacing requirements at Woolwich Station |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-01-31 | 2020-01-15 14:14 | -16 | 2019-11-29 10:38 | Electrical - Cable Management | 3000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | The OHLE feeder cable installation at Woolwich Station do not correspond to the requirements indicated on the drawings to limit the distance between Fixing to 1000mm. FCD 1159 has been rejected.
| 05SY - Systemwide | Cxxx-NCR-001167 | NCR | CMS at __ B4 restricts the evacuation route. |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-05-31 | 2020-05-27 07:18 | -4 | 2019-12-05 16:07 | Electrical - Cable Management | 6000 |  | Design | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | This CMS located in front of the emergency escape and intervention doors at STG B4 restricts the minimum width for evacuation/ intervention and needs to be modified.
| 05SY - Systemwide | Cxxx-NCR-001168 | NCR | TFM Hydrant Signage |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-01-16 | 2019-12-19 13:55 | -28 | 2019-12-04 15:47 | Mechanical - Mechanical Engineering General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | The signs for the TFM Hydrants have been ordered as per the design Cxxx-__-E-RGN-CRG03-50014 Revision 3.0, However this document is now up to Revision 6.0 and shows a different design for the hydrant signs.
| 05SY - Systemwide | Cxxx-NCR-001169 | NCR | Cxxx __ Systemwide Track Labelling Non-Compliance : Sleepers (L21322) |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-01-30 | 2020-02-28 10:08 | 29 | 2019-12-09 17:51 | Information Management - Asset Information | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Lack or improper material identification and traceability | Completed |  | During Asset Verification Surveys we have identified that close to 11km (1694 Nos.) of L21322 - Sleepers are incorrectly labeled with the Lclass denoted as L21321. Examples of these can be found in the issued VAP reports This is non compliant with RFL / CRL Asset information requirements. Please see Crossrail Asset Naming & Labeling Convention and Sleeper Lclass definition document. The asset data in AIMS is correct.
| 05SY - Systemwide | Cxxx-NCR-001170 | NCR | OHLE VT in LIV Street Station Switch 101/2 picks up signal of wrong section |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-03-02 | 2020-01-15 14:34 | -47 | 2019-12-10 11:08 | Over Head Line Electrification - Over Head Line Electrification General | 5000 |  | Design | Repair | 3 (3-6k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | In Liverpool St station, the OHLE switch 101/2 has been installed as per Design drawings. However, the voltage transformers on switches in LIV St and Whitechapel are picking up the signal of the same section (101C). The voltage transformer in LIV St Switch should pick up 101D section through the correct cable. Cxxx-__-R6-DDA-C101_8-00153 Cxxx-__-R6-DDA-C101_Z-10555 Cxxx-__-R6-DDA-C101_8-00153 Cxxx-__-R6-DDB-C101_8-00151 Cxxx-__-R6-DDB-C101_8-00153
| 05SY - Systemwide | Cxxx-NCR-001171 | NCR | Silvertown Footbridge – __ Mesh Notches |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-04-30 | 2020-04-15 12:35 | -15 | 2019-12-11 16:25 | Civil - Civil Engineering General | 6000 |  | Manufacturing Defect | Repair | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | The new mesh panels by McNealy brown have small notches cut into the mesh which allows the M6 fixings to be installed around the frame. It has been advised by the Clients Designer that this is not acceptable and the intention is to have the M6 fixing pass through the mesh in order to secure the mesh into the frame, therefore this is not acceptable.
| 05SY - Systemwide | Cxxx-NCR-001172 | NCR | Track Geometry Signage |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-01-30 | 2019-12-30 15:17 | -31 | 2019-12-16 10:55 | Track - Track General | 3000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Following a number of track signage inspections it has been found that the information presented on track geometry (horizontal and vertical alignment) signage is incorrect. For the vertical alignment the chainage displayed on the sign is that of the centre point of the curve not the beginning of the curve. The current sign is installed at the centre point chainage displayed on the sign. However the requirement is for the signs to be installed at the beginning and end of the curve. Please see attachment Cxxx-OVE-R4-DDA-CR001_Z-11106_C03_MU_JC_191210-01 for an example of the issue.
| 05SY - Systemwide | Cxxx-NCR-001173 | NCR | Silvertown Footbridge - Mesh Panels - Inadequate fixity of mesh within its frame |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-04-30 | 2020-04-15 12:25 | -15 | 2019-12-16 17:04 | Architectural - Balustrade | 6000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The mesh panel fixings at the Silvertown Footbridge are not compliant to the Cxxx issued Silvertown Footbridge – Material and Workmanship Specification (Cxxx-OVE-A-RSP-CR146_WS159-50001) due to the loose installation of the elements of the panels (i.e excessive gaps between the mesh,frame and typical packer dimension) without providing the required fixity. The typical packer dimension (provided by the contractor) should have been adjusted on site during installation to require the necessary fixity of the mesh into the frame. Packers currently retaining the mesh in the frames are too small to provide adequate fixity, hence the mesh bows in the frames (even when there is no pressure exerted on it).
| 05SY - Systemwide | Cxxx-NCR-001174 | NCR | Traction Power Earthing & Bonding Cables (Daisy chaining cabling) |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-02-28 | 2020-02-06 12:22 | -22 | 2020-01-06 15:25 | Information Management - Asset Information | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | During Asset Validation process within Systemwide Trace , it has been identified that the Tunnel Systems Traction Bonding Earth wiring that "Daisy chains" between Earth bars to create a bonding circuit are incorrectly labeled as per CRL requirements. This issue has been identified throughout the Central Section and seems to be systemic.
| 05SY - Systemwide | Cxxx-NCR-001175 | NCR | Incorrect labelling and data records for Traction side Earthing & Bonding connection cables |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-02-28 | 2020-08-17 09:42 | 171 | 2020-01-06 15:25 | Information Management - Asset Information | 3000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | During Asset Validation process within Systemwide Trace , it has been identified that the Earthing & Bonding cabling (specifically the Earth bar connections) are incorrectly labeled. The Asset Information (AIMS) data contains duplicate records for each of these cables. CRL requirements for Earth cables stipulates that the cables must be labeled at each end. This has been carried out but the label at each end of the cable is different. (probably due to the duplicate AIMS data) The cable itself passes through the track Cable UTX. This issue has been identified throughout the Central Section and seems to be systemic.
| 05SY - Systemwide | Cxxx-NCR-001176 | NCR | Drop tube installed with insufficient electrical clearance |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-06-30 | 2020-06-25 11:45 | -5 | 2020-01-08 16:28 | Over Head Line Electrification - Supports | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Electrical or instrument noise | Completed |  | Drop tube at westbound at north Woolwich portal adjacent to XRA-19-505 does not have sufficient electrical clearance. Distance between drop tube and the ROC less than 270mm in the horizontal direction and less than 270mm from the pantograph in the vertical direction.
| 05SY - Systemwide | Cxxx-NCR-001177 | NCR | TVS - BOS W - SOR Cable Pull |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-03-20 | 2020-03-19 13:10 | -1 | 2020-01-09 15:03 | Mechanical - Heating Ventilation & Air Conditioning | 7500 |  | Incomplete Works | Repair | 2 (6-60k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | The issue was raised as part of the Punchworks list (reference - Cxxx-PWK-00070) explaining the need of SOR cable pull, gland and terminate at Bond Street West. The cable was found to be short during the final stage of the original pull (approx. 50m of panel). It was agreed on site to join the cable in the interim. __ installed a purpose splice box to join cable and commissioned. All results were found to be satisfactory.
| 05SY - Systemwide | Cxxx-NCR-001178 | NCR | Tunnel Fire Main (TFM) Fire Hydrants in Trace Open Sections around Connaught Tunnel Approach & Exit Ramps |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-02-28 | 2020-03-20 05:47 | 21 | 2020-01-15 11:10 | Information Management - Asset Information | 3000 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | During Crossrail Asset Validation Process it was identified that __ have a Fire Hydrant arrangement that is identified by __ as a single Fire Hydrant Asset that is in fact two Fire Hydrants. Please see attached photograph. For clarity this was raised internally by Crossrail asset team into the Query Log process for RFL to comment. 22/08/19 QLG CQ2123 RFL have agreed that this arrangement should be captured as two Fire Hydrant assets. As yet there has been no change to the current asset information regarding this issue. The change should increase the number of Hydrant assets and also any associated Signage. This will increase asset data and also labeling. We estimate that there are circa 30 affected Hydrants.
| 05SY - Systemwide | Cxxx-NCR-001179 | NCR | Defective TVS Actuator LED Boards at TCR-W |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-09-20 | 2020-06-18 11:35 | -94 | 2020-01-23 09:54 | Systems - Ventilation and Pressure Relief | 500 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Following the replacement of TVS actuator LED board (as detailed within NCR-1055), it has been found that some LED boards are failing prematurely; namely: TCR-W FID-B A1&A2 and TCR-W FID-A A1.
| 05SY - Systemwide | Cxxx-NCR-001180 | NCR | Silvertown Footbridge - Redundant Hole in Glazing Steel Splice Plate |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-05-31 | 2020-02-13 15:32 | -108 | 2020-01-23 16:29 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On the Horizontal steel spice plate for the glazing steel trim, there is an additional redundant unused hole at each fin location (circa 20 location across the bridge). These were drilled on site in the incorrect position and was therefore not used, and correctly placed holes were drilled instead.
| 05SY - Systemwide | Cxxx-NCR-001181 | NCR | Silvertown Footbridge - Northern Streetworks - Pavings/Concrete Fill |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-08-31 | 2020-04-15 14:21 | -138 | 2020-01-23 16:42 | Civil - Civil Engineering General | 6000 |  | Incorrect Installation | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the installation of the bollards as part of the Streetworks at the Northern side of Silvertown Footbridge, a mass concrete foundation was cast to the FGL instead of having paving slabs. REV 2 See attached markup and email which details the levels and extent of the concrete infill as requested. Levels pasted below for information; Point ID Easting Northing Height 1 92365.9338 34587.2804 101.9138 2 92366.1018 34589.2138 101.9137 3 92364.5405 34590.2255 101.9513 4 92362.7685 34590.5389 101.9926 5 92360.7587 34591.7189 102.0573 6 92358.1727 34592.9578 102.0549 7 92357.2229 34592.3155 101.9773 8 92358.4406 34593.8161 102.0406 9 92356.3549 34594.8155 102.0093 10 92355.0631 34593.7844 101.9703 11 92353.6094 34595.2539 101.9633 12 92352.6501 34593.8326 101.9826 13 92351.369 34594.6651 101.9475 14 92352.2752 34596.4966 101.9497 15 92354.353 34594.1187 101.9857
| 05SY - Systemwide | Cxxx-NCR-001182 | NCR | Silvertown Footbridge - Inconsistent Use of Fixings |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-05-31 | 2020-05-28 16:27 | -3 | 2020-01-23 16:52 | Civil - Civil Engineering General | 6000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following the opening of the Footbridge, it is noted that the use of fixings across the bridge is inconsistent. Areas included are; Stringer-Balustrade connection Handrail bracket - balustrade connection Mesh Panel Bracket - balustrade connection Types of inconsistencies include; Use of Nordlock washers where not required nut + shear nut combination where not required missing double nut where required
| 05SY - Systemwide | Cxxx-NCR-001183 | NCR | TVS Cyber Penetration (Route Control Centre Romford) |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-03-31 | 2020-04-01 13:54 | 1 | 2020-02-03 12:41 | Systems - Ventilation and Pressure Relief | 500 |  | Software | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | Following an independent Cyber Penetration Test of the VCS network and subsequent report a number of issues have been identified that require improvement measures to be implemented within the software. A mitigation review meeting held on 21st January 2020 between __ / AIS, __, CRL & RFL agreed that all issues will be rectified within the report apart from two, which are; - AISL-002-1-4 No Anti-Virus – This will remain and instead White Listing will be used in preference to the maintenance effort required to keep anti-virus packages up to date. - AISL-002-3-7 No Network segmentation - This is a single, distributed application that would make segmentation extremely challenging. In addition it should be noted that physical access to equipment is restricted. The RCC and BUCF control rooms have strict controlled entry. At a station or shaft access requires access to the non-public areas of a station, access with a key into the MCC room and access with a key into the MCC panel. Access to the network then requires the intruder to fake a MAC address. The remaining issues being rectified will result in making improvements to the security within the software. Rather than retesting after making the improvements it has been agreed that a report will be produced detailing the changes that have been made and how they have been implemented. This will be issued to CRL and RFL for review.
| 05SY - Systemwide | Cxxx-NCR-001184 | NCR | Silvertown Footbridge - Nordlock Washer Discolouration |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-05-15 | 2020-04-15 12:30 | -30 | 2020-02-05 17:08 | Civil - Civil Engineering General | 6000 |  | Material | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | It has been noted that the Nord Lock anti-vibration washers used on the Silvertown footbridge are showing signs of discolouration. The specification of the washers are compliant to the requirements in the Silvertown Footbridge Materials and Workmanship specification in regards to both Material Grade (1.4404) and corrosion resistance and has an accepted Code 1 MCR.
| 05SY - Systemwide | Cxxx-NCR-001187 | NCR | Asset Labeling and Naming of Lclass L21321 - Baseplate |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-03-31 | 2020-03-23 07:02 | -8 | 2020-02-11 09:23 | Information Management - Asset Information | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Cxxx have incorrectly named and labeled the L21321-Baseplates at Pudding Mill Lane Portal Bridge. The required naming convention stipulates the name to be BASEPLATE [nnnnn] (BASEPLATE 00001). The Baseplates at PML are individually labeled, the baseplates elsewhere are labeled in sets of 10 pairs.
| 05SY - Systemwide | Cxxx-NCR-001188 | NCR | Asset Information - Cxxx Track Baseplates (Heel Plates) Unlabeled. |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-06-26 | 2020-06-11 10:07 | -15 | 2020-02-11 09:24 | Information Management - Asset Information | 500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Heel Plates were identified by __ and originally collected as Slide Chairs ( as they are very similar). After the question was raised into CRL Query Log, RFL requested that the Heel Plates be identified under the Baseplate lclass L21321 classification. Due to the space constraints around the location of the Heel Plates within the Switch Half Set and the conditional labeling requirements for Baseplates (every 10th pair unless installed on a skew where each Baseplate to be labeled, this is the case at PML bridge. There would also have been
| 05SY - Systemwide | Cxxx-NCR-001189 | NCR | Asset Information Track Assets - Lclass 21322 Sleepers |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-03-16 | 2020-03-23 06:56 | 7 | 2020-02-11 09:52 | Information Management - Asset Information | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Some of the installed Sleeper Assets (classification L21322) have been incorrectly named. The Crossrail requirement is for Sleepers to have a 5 Digit (SLEEPER [nnnnn] ) name. The sleepers in question are missing a leading zero (SLEEPER 0001). The affected sleepers are only in the Royal Oak Portal area.
| 05SY - Systemwide | Cxxx-NCR-001190 | NCR | Asset Information - GERB Spring Housings - L213662 |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-03-24 | 2020-03-23 07:04 | -1 | 2020-02-11 10:36 | Information Management - Asset Information | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | GERB Spring Housings are incorrectly named and labeled by __. The Asset naming convention stipulates GERB Spring Housing [nnn]. __ have named and labeled as Spring Housing [nnn]. This issue has also been raised on CRL QLG as RFLi may accept a change to the AIMS naming pattern
| 05SY - Systemwide | Cxxx-NCR-001191 | NCR | Asset Information Asset Naming and labelling of L213661 Shear Key |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-03-17 | 2020-03-23 06:59 | 6 | 2020-02-11 10:40 | Information Management - Asset Information | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Shear Keys have been incorrectly named using a 3 digit identifier instead of the required 4 digit. Although the number of assets is 188, due to the labeling requirement that stipulates "One Asset Tag Label to be fixed on a group of 4 shear keys (each key to be an asset tag) adjacent to the Slab Label in the 4' ; the amount of labeled assets is actually only 47.
| 05SY - Systemwide | Cxxx-NCR-001192 | NCR | Capping of ducts for UTX's works started without an approved ITP |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-07-17 | 2020-05-29 07:46 | -49 | 2020-02-27 10:23 | Electrical - General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Lack of approval Code 1 procedures excessive | Completed |  | Capping of ducts for UTX's throughout the trace has commenced without an approved code 1 ITP in place.
| 05SY - Systemwide | Cxxx-NCR-001193 | NCR | Capping of duct for UTX works started without an MCR submission for materials used |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-04-30 | 2020-04-29 11:12 | -1 | 2020-02-27 10:46 | Electrical - General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Lack of approval Code 1 procedures excessive | Completed |  | The material used for capping of the ducts for UTX's has not been MCR approved.
| 05SY - Systemwide | Cxxx-NCR-001194 | NCR | Shaft Walkway Handrail Extensions |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-06-30 | 2020-08-05 08:26 | 36 | 2020-02-24 15:13 | Track - Walkways | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The walkway handrail at Mile End, Eleanor Street and Fisher Street Shafts does not extend far enough into the shaft adits. Additionally the Tunnel Fire Main is further out than where the handrail ends.
| 05SY - Systemwide | Cxxx-NCR-001195 | NCR | TVS-FAR WTH,Level -4 - Cables not installed correctly |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-09-20 | 2020-08-07 09:56 | -44 | 2020-03-05 10:47 | Systems - Ventilation and Pressure Relief | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The TVS cables at FAR WTH Level -4 have been installed with inadequate mechanical support/protection. It seems that this is due to installed CMS by the Principle Contractor doesn't serve the purpose of supporting these cables. The CMS require to be alerted to accommodate this and cables will require adjusting.
| 05SY - Systemwide | Cxxx-NCR-001196 | NCR | Fisher Street & CP01- The fixings to the support brackets to the walkway are loose |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-08-31 | 2020-07-29 07:55 | -33 | 2020-03-06 13:24 | Tunnelling - Walkways | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Whilst we were conducting the VAP last week it was observed that there were a few areas where the fixings to the support brackets to the walkway were loose at Fisher Street and CP01
| 05SY - Systemwide | Cxxx-NCR-001197 | NCR | Walkway at CP11 Resonating During Pump Operation |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-06-30 | 2020-07-15 09:54 | 15 | 2020-03-06 13:33 | Materials - General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | During the VAP with CRL CEG on the 13th February we witnessed the walkway resonating when the Pump at CP11 operated.
| 05SY - Systemwide | Cxxx-NCR-001198 | NCR | Automatic Air Valves not located at high points around Fisher Street Crossover |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-06-26 | 2020-03-30 11:29 | -88 | 2020-03-11 14:43 | Mechanical - Mechanical Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | On the VAP on the 25th February it was noted that there was no means to release air from the Tunnel Fire Main at high points around the Fisher Street Crossover
| 05SY - Systemwide | Cxxx-NCR-001199 | NCR | Torque Wrench Calibration Cert Missing |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-06-17 | 2020-05-28 15:14 | -20 | 2020-03-17 10:30 | Mechanical - Mechanical Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Verification Problems - Unavailability or inadequate M&TE | Completed |  | The torque wrench that has been used on Quality Inspections does not have a calibration certificate. The wrenches that have been used for the install do have in date certificates, these are attached for information.
| 05SY - Systemwide | Cxxx-NCR-001200 | NCR | TVS Outlet D25 Noise Exceedance at FAR-E |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-09-20 | 2020-09-04 04:16 | -16 | 2020-04-07 15:04 | Systems - Ventilation and Pressure Relief | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | As per the WI requirements CRL1-XRL-T1-RSP-CR001-50004, the contractor shall demonstrate compliance against the D25 agreed noise design criteria for each Tunnel Ventilation System (TVS) shafts and comply with the cumulative design target of 5 dB below background. The noise measurement completed on the night of 13/02/2020, recorded a TVS outlets rating noise levels of 1.7 dB above background at the __ residential receptor in Normal (UPE) mode. This mode is exceeding the TVS forecasted noise level by 8.7 dB and is also contributing to a cumulative exceedance of the 5 dB below background criteria. A summary of the results are presented in the attached report 1871m-SEC-00262-05. This survey was carried out after all the TVS and station contractor infrastructure remedial works were completed.
| 05SY - Systemwide | Cxxx-NCR-001201 | NCR | TVS D25 Outlet Noise Exceedance at WOO-E |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-05-29 | 2020-08-21 09:12 | 84 | 2020-05-15 01:05 | Systems - Ventilation and Pressure Relief | 500 |  | Testing and Commissioning | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | As per the WI requirements CRL1-XRL-T1-RSP-CR001-50004, the contractor shall demonstrate compliance against the D25 agreed noise design criteria for each Tunnel Ventilation System (TVS) shafts to comply with the cumulative design target of 5 dB below background. The noise measurement completed on the night of 06/01/2020 results in a TVS outlets rating noise levels of 4.0 dB and 4.6 dB below background at both receptors respectively ‘__’ and ‘Crossrail OSD-NE’ in Congested Extract mode. This mode is exceeding the TVS forecasted noise levels which is causing a cumulative exceedance of the D25 cumulative criteria. This survey was carried out after all the TVS and station contractor infrastructure remedial works were completed.
| 05SY - Systemwide | Cxxx-NCR-001202 | NCR | MCR has not been submitted for the REB __le at WBP |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-06-30 | 2020-07-03 13:42 | 3 | 2020-05-06 12:58 | Electrical - General | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | The material used for the REB building has not been submitted to CRL and MCR approved.
| 05SY - Systemwide | Cxxx-NCR-001203 | NCR | The wiring of the CPD limit switches was not carried out in line with the Code 1 drawing |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-08-31 | 2020-06-29 13:52 | -63 | 2020-05-07 14:11 | Systems - Cross-passage Doors | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | During discussions in the Autumn of 2018 between __, __s and __ a wiring diagram was agreed by all parties. __s were requested to submit this wiring diagram as v 3.0 of the CP Fire Status Monitoring Wiring Diagram Dual Leaf drawing, Cxxx __-Y-DWG-CRG03-50126. Unfortunately __s submitted the wrong diagram as v 3.0.
| 05SY - Systemwide | Cxxx-NCR-001204 | NCR | Installation of Pipes and NRVs in Connaught with out Approved MCR's |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-08-31 | 2020-06-15 11:33 | -77 | 2020-05-11 14:30 | Systems - Drainage/Pumping Systems | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | Pumped drainage system has been installed in Connaught Sump without a number of materials approved via MCR. These are: - Larger Pipe Diameter and Thicker Wall Galvanised Pipework - Stainless Steel Grooved Pipework - Larger Non-Return Valves - Stainless Steel Grooved Couplings This issue was found during an assurance check of the RPL for the relevant IRN. The RPL had listed the MCR's for the materials in the Cross Passage and other SSP Sumps. However the design for Conanught Shaft is different and the pipework is of a different size and valves of a different type.
| 05SY - Systemwide | Cxxx-NCR-001205 | NCR | Fire Risk Assessment Code 3 for installed MF775 Silicone Membrane |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-09-24 | 2020-05-28 08:02 | -119 | 2020-05-18 14:02 | Track - Track General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | The Fire Risk Assessment for the Application of MF775 Silicone Membrane in Connaught Tunnel is not accepted by CEG however this product is installed onsite. Cxxx-__-R4-__-CR146-50001 - 'Cxxx - Fire Risk Assessment for the Application of MF775 Silicone Membrane in Connaught Tunnel' rev 2 was given a code 3 on 16/12/2016. It was then resubmitted on 02/04/2020 and again given code 3.
| 05SY - Systemwide | Cxxx-NCR-001206 | NCR | TVS Cxxx - Inoperable Actuators - Systemwide |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-10-01 | 2020-09-04 04:27 | -27 | 2020-06-01 13:15 | Systems - Ventilation and Pressure Relief | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | __ reported issues with several non-functioning actuators (as listed below) installed within the Tunnel Ventilation systems on the Crossrail Systemwide Cxxx Contract. FAR-E DRDW A1 TCR-W FID A A2 TCR-E FID A A1 TCR E FID A A2 WOO-E FID A A1 WOO-E FID C A2 WOO-E TIDW A4 LIV-E DRDE A1 LIV-E DRDE A2 LIV-E FIDB A2 LIV-E DRDW A1 LIV-E DRDW A1 STG FID B A2 FAR-W TIDE A2
| 05SY - Systemwide | Cxxx-NCR-001209 | NCR | Cxxx TVS - Eleanor St Fan Performance |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-09-19 | 2020-08-21 10:37 | -29 | 2020-06-11 15:15 | Systems - Ventilation and Pressure Relief | 500 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The Tunnel Ventilation System - Performance Specification specifies in Section 5.5 that "The tunnel ventilation system shall meet performance requirements after loss (due either to failure or removal for maintenance) of any single fan, single damper module or single item of control equipment." The TVS has been designed to meet this criterion by ensuring each ventilation damper consists of more than one damper module. This is documented in the following documents: Tunnel Ventilation System - Operating Strategy (Cxxx-__-H-STP-CRG03-50001 v3.0) Section 8.10.3 "Ventilation dampers will be constructed of multiple modules, so that single module failures will allow partial operation to continue. The number of modules will be selected so that failure of a single module (either failure to close on demand or failure to open on demand) will not prevent functional performance of the system." Tunnel Ventilation System Mode Tables (Cxxx-__-H-RSP-CRG03-50009 v9.0) Sections 5.2 and 6.4.1 No change to Ventilation Configuration with up to one actuator within a FID failing RAM Demonstration (90% Design) Tunnel Ventilation System (Cxxx-__-H-RGN-CRG03-50019 v6.0) TVS RAM demonstration forms - Fan Isolation Dampers Each damper will be made up of multiple damper modules driven by sufficient number of actuators such that the failure of one actuator does not constitute a single point failure. This might be seen as a safety related failure; however, this is negated by the fact that there is sufficient in-built resilience at the equipment level as well as the system level whereby the functional performance of the system will not be affected. The Tunnel Ventilation Control logic includes the requirements of a partial damper failure, however the primary instruction in this event (as per Mode table 8 and earlier) is to direct the operation of the system to move from one fan to another (within the same shaft). Following a meeting with the CEG team it was established that this logic was not in accordance with the strategy set out in the RAMS assessments. As such the direction was given to amend the VCS to suit the RAMS modelling, whereby the primary instruction is for a fan to continue to operate with a partially failed damper. During this meeting it was highlighted that a risk had been identified (subsequently recorded in Cxxx-EWN-04453) that changes in the shaft civil infrastructure may have fostered a change in the air flow resistance which may therefore have a negative impact on the performance of the TVS fans thus resulting in a stalling affect. The Contractor has now implemented the changes in the VCS (Mode Table Revision 9) and carried out additional performance testing of the fans at the sites assumed to hold the most risk of stall failure.
| 05SY - Systemwide | Cxxx-NCR-001220 | NCR | Incomplete Stressing works at WBP |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-10-05 | 2020-09-17 11:55 | -18 | 2020-07-07 17:48 | Track - Rails and Sleepers | 20000 |  | Planning | Rework | 2 (6-60k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | During the planning of the Stressing works at WBP, we failed to identify the requirement to stress the 4no rails between the Switch Heels and Xing Legs commonly known as the ‘Belly’ or ‘Internal’ rails.
| 05SY - Systemwide | Cxxx-NCR-001221 | NCR | TVS Cxxx - Burnt damper actuator sited at Canary Wharf East shaft |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-01-15 | 2020-11-10 15:47 | -66 | 2020-07-09 12:23 | Systems - Ventilation and Pressure Relief | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | During an inspection at Canary Wharf East on 05th of February, it was noticed that one of the Damper Actuator (CWS-E FID A A2) was burnt from inside. Upon initial assessment, it was noticed that this was due to a wiring fault. The agreement was to replace this actuator which has been done now. The faulty actuator has been sent back to __ for their investigation. __ to complete investigation with __/Rotork and identify any underlying issues with manufacture which could result in further failures of this or other similar components. Final report and recommendations to be linked to this NCR. This issue was initially covered as part of the NCR 1186 which was cancelled by mistake. There is also an open punchwork item (PWK 400) specific to CWS-E FID A A2 which will be closed in coming days as the listed actuator at CW has been replaced now. The other systemwide issue with actuators is that individual actuator components have worn out because of the clutch issue. This issue is covered separately as part of the NCR 1206.
| 05SY - Systemwide | Cxxx-NCR-001222 | NCR | TVS - Mode Reconfiguration Timings |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-12-18 | 2020-10-30 11:19 | -49 | 2020-07-17 11:51 | Systems - Ventilation and Pressure Relief | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Section 5 of the Tunnel Ventilation System – Performance Specification Cxxx-MMD-O8-RSP-CR001-00002 Which forms part of the Works Information states The Tunnel Ventilation System shall be designed so that the time taken for any one shaft to undergo a re-configuration from any operating mode to any other operating mode does not exceed 90 seconds, unless the Project Manager’s acceptance has been obtained otherwise. It has recently been observed that for some specific modes that this timing is exceeded with a maximum of 120 seconds.
| 05SY - Systemwide | Cxxx-NCR-001223 | NCR | LULCS1 Code used |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-08-04 | 2020-08-10 08:45 | 6 | 2020-07-21 17:23 | Information Management - Asset Information | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | The Earth BAR CR144-ENB-00139 was created under LULCS1 CR144 - Canary Wharf Station to Custom House Station. The earth bar is situated in a room (LIP-S-0086) in Limmo shaft. Limmo Shaft is between Canary Warf and Custom House station, therefore using Cr144 is not incorrect. However, Crossrail automatic check tool is picking this as an error.
| 05SY - Systemwide | Cxxx-NCR-001224 | NCR | Drop tube installed with insufficient electrical clearance |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-09-18 | 2020-09-10 13:38 | -8 | 2020-07-23 10:45 | Over Head Line Electrification - Supports | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Drop tube at westbound at North Woolwich Portal adjacent to XRA-19-505 does not have sufficient electrical clearance. Distance between drop tube and the ROC less than 270mmin the horizontal direction and less than 270mm from the pantograph in the vertical direction.
| 05SY - Systemwide | Cxxx-NCR-001225 | NCR | Fire alarm cables in CP19 junction box have been Kinked. |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-10-31 | 2020-08-24 08:40 | -68 | 2020-07-24 07:05 | Electrical - LV Equipment | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Fire alarm cables have been twisted/kinked in the 100x100mm junction box above the fire alarm panel.
| 05SY - Systemwide | Cxxx-NCR-001226 | NCR | TVS Cxxx - Misplaced SAFs for Woolwich FIDs and TIDs |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-09-22 | 2020-09-08 09:37 | -14 | 2020-07-24 12:08 | Systems - Ventilation and Pressure Relief | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | This NCR is being raised to notify the client that TVS Cxxx team have misplaced two SAFs 1. Fan Isolation Dampers (FIDs), Cxxx-__-O4-LRC-CR147-50090 and 2. Tunnel Isolation Dampers (TID-EB and TID-WB, Cxxx-__-O4-LRC-CR147-50091. These two SAFs were planned to be submitted on eB to support the IRN ‘Cxxx Installation Release Notice (IRN) - Woolwich West Damper, Cxxx-__-O4-NOX-CR147-50025’. The above mentioned IRN was signed on 29.06.2018 after completing a site inspection of the dampers related to the missing SAFs in presence of CRL (__ and Navid Hojjati) and __ (Alex Hedger, Jim Lawes, Dinesh Hansla and Will Chow). As per the usual IRN procedure, hard copies of these two missing SAFs were reviewed and signed/Coded 1 by all parties involved on the day including CRL and __.
| 05SY - Systemwide | Cxxx-NCR-001227 | NCR | Cross Passage Fire Alarms Zoning |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-10-31 | 2020-09-04 11:18 | -57 | 2020-07-24 15:29 | Electrical - LV Equipment | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The Cross passage Fire alarm Zone arrangement does not align across the Protect schedule, redlines and as built drawings.
| 05SY - Systemwide | Cxxx-NCR-001228 | NCR | Cross Passage Sump Covers - Valve Access Hatches |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-10-31 | 2020-12-03 12:51 | 33 | 2020-07-31 08:16 | Mechanical - Mechanical Engineering General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | It has been found that at a number of locations the access hatches in the Cross Passage sump covers do not align with the TPD valves in the valve pit. A full survey of the Cross Passages is required. This is in relation to CRL-OBS-32859.
| 05SY - Systemwide | Cxxx-NCR-001229 | NCR | Cxxx __ Auto changeover Unit Factory certificates unavailable for Cross Passage 5 and 6 |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-09-05 | 2020-09-02 09:23 | -3 | 2020-08-22 11:07 | Electrical - LV Equipment | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | The factory certificates issued with the Auto changeover Unit (ATS) for Cross Passage 5 and 6 are unavailable from the manufacturer. These units are covered under Certificate of Conformities included in Cxxx-__-O4-RGN-CRG03-50580 CP5 - CR086-LVD-00001 (Cxxx-EE-02240) - Serial Number - 204991 CofC ref - COC11774 CP6 - CR092-LVD-00001 (Cxxx-EE-00857) - Serial Number - 204997 CofC ref - COC16446
| 05SY - Systemwide | Cxxx-NCR-001230 | NCR | Lack of __ Assurance - __ Fire Stopping |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-11-30 | 2020-11-24 12:00 | -6 | 2020-09-17 14:27 | Fire - Compartmentation | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | __ have not been providing progressive assurance for the Fire Stopping works in Cross Passages and at Shafts. Completion photographs and site diary's have been completed.
| 05SY - Systemwide | Cxxx-NCR-001231 | NCR | Cxxx TVS - Missing calibration certificates, post IRN electrical work SAFs |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-10-24 | 2020-10-06 11:34 | -18 | 2020-09-24 14:11 | Systems - Ventilation and Pressure Relief | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | __ recently submitted 18 SAFs to CRL covering each shaft capturing all electrical works carried out post IRN. These SAFs contained QADs capturing installed works which required changing/alerting to suit the needs of individual shaft environmental changes as SSP complete their scope of works. This NCR is being raised to notify the client that TVS Cxxx team have included assurance packages that are missing calibration certificates for calibrated testing equipment noted on respective check and test data sheets. It is important to note that some of the work was inspected by CRL representative (e.g. tunnels work led by Vim was inspected by __). CRL representative have signed some of these QADs and hence it is fair to say that these missing calibration certificates were checked by CRL representative at the time of inspection. All QADs are signed by __ representative and hence we expect that these missing calibration certificates were checked by __ representative at the time of installation/inspection. It is also important to note that these works and inspections related to missing calibration certificates were carried out a long time ago The contractor (__) did not maintain suitable controls to prevent the loss of these certificates as agreed as per the ‘Works Information Volume 2B (Systems) CRL1-XRL-V3-XWI-CR001-50131, clause 29.2’
| 05SY - Systemwide | Cxxx-NCR-001232 | NCR | Calibration Certificates and Tool Serial Numbers |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-12-31 | 2020-10-08 11:51 | -84 | 2020-09-24 15:39 | Over Head Line Electrification - Over Head Line Electrification General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Revision 1 of the ROC SAF documentation was submitted for review by CRL on 15/01/2018 , however that review did not identify numerous instances where calibration certificates and tool serial numbers had either been omitted from the files or, in a few cases where calibration certificates were out of date. This was subsequently identified in a deep-dive review of the Revision 2 SAF documents. As the subcontractor has now been been demobilised these certificates and tool serial numbers are unavailable, this is further compounded by the restrictions of Covid.
| 05SY - Systemwide | Cxxx-NCR-001233 | NCR | Torque Wrench Calibration documentation |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-11-30 | 2020-10-06 16:42 | -55 | 2020-10-05 11:29 | Electrical - General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | During a deep-dive review of revision 2.0 documents its has been identified that calibration documentation for a Magnusson torque wrench Serial no 3663602813934 has been deemed unsatisfactory/missing. This has been used across various Revision 1.0 SAF's including Cxxx-__-O4-LRC-CR094-50170, Cxxx-__-O4-LRC-CR094-50171, Cxxx-__-O4-LRC-CR094-50169 & Cxxx-__-O4-LRC-CR140-50001 all dating back to approx. 08/03/2019.
| 05SY - Systemwide | Cxxx-NCR-001234 | NCR | Tunnel Mechanical Pipe Couplings (2575 Nos.) |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-10-28 | 2021-04-27 14:59 | 181 | 2020-10-14 16:33 | Information Management - Asset Information | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | 2575 Pipe Couplings within __ Tunnel Mechanical Asset data have been incorrectly assigned to Cross passage spaces and assigned asnon track assets. CRL believe that these assets should have LRS code and chainage data. An example at the Niche Sump Adit N3 space is showing 161 Pipe couplings within this space.
| 05SY - Systemwide | Cxxx-NCR-001236 | NCR | Cxxx-PWK-00421 Liquid Level Switches |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-11-18 | 2021-03-30 05:46 | 132 | 2020-11-04 14:28 | Mechanical - Pumps | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | FAO __/__ (__ please forward) With regards to Cxxx-PWK-00421, the liquid level switches asset information data has been identified as having the incorrect spatial information and naming of the assets as not being unique in a single space. The liquid level switches have been identified uniquely by the following characteristics; • Liquid Level Switch 001 – High High • Liquid Level Switch 002 – High • Liquid Level Switch 003 – Low • Liquid Level Switch 004 – Low Low • Liquid Level Switch 005 – Earth Contractors proposal is to 'use as is' to prevent further cost and time in relabelling and access to facilitate. Equipment numbers affected; EQ00004969 EQ00004970
| 05SY - Systemwide | Cxxx-NCR-001237 | NCR | Fire Stopping Install with Rope Penetration |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-12-31 | 2020-12-16 11:05 | -15 | 2020-11-12 15:39 | Fire - Compartmentation | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Supervision - Supervisor not familiar with the work | Completed |  | At a number of Cross Passage locations Nylon rope has been found to be penetrating through completed fire stopping at low level. This nylon rope compromises the integrity of the __ CFS-IS intumescent fire sealant so must be removed.
| 05SY - Systemwide | Cxxx-NCR-001238 | NCR | Church Manor Way Points Heating and Lighting Panels modification assurance |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-01-31 | 2020-12-03 11:26 | -59 | 2020-11-26 08:27 | Electrical - LV Equipment | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Verification Problems - Not Defined | Completed |  | __ have carried out modification works on the Points heating panel (Cxxx-EE-20229) and Distribution panel (Cxxx-EE-20228) without Issuing all the required assurance documentation. Although a job sheet for the works carried out and a Certificate of conformity have been supplied for both panels upon completion of the modifications, outstanding still is check sheets and calibration certificates for the busbar mods and torqueing values.
| 05SY - Systemwide | Cxxx-NCR-001239 | NCR | Connaught Tunnel Compounds - Factory road compound - Missing Filler Board Between ACO and PV1 Slab |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-12-22 | 2020-12-21 09:04 | -1 | 2020-11-24 17:57 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | Installation of the ACO channel was not carried out as per manufacturer/supplier specification – no filler board between the slab and the concrete surround.
| 05SY - Systemwide | Cxxx-NCR-001240 | NCR | WBP - Termination bolt broken for M&E Points Heating (TSP-WBP-277) |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-01-29 | 2020-12-03 12:18 | -57 | 2020-11-25 12:41 | Electrical - Earthing & Bonding | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | WBP - Termination bolt broken for M&E Points Heating TCB; bonding conductor no longer connected to Traction Spider Plate (TSP-WBP-277).
| 05SY - Systemwide | Cxxx-NCR-001241 | NCR | Connaught Tunnel Compounds - concrete slab repairs |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-12-23 | 2020-12-21 09:07 | -2 | 2020-11-25 12:08 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | CRL/__ joint inspection was carried out on the 09-11-2020 where several defects of concrete slabs were observed - see attached "Structural Inspection of PV1 at Factory Road" with report of defects.
| 05SY - Systemwide | Cxxx-NCR-001242 | NCR | Drop 6 - TP - Traction Power and Overhead Lining Equipment (ES-SYS-04-TP) - Asset Description and Asset DAAID fields needs to be consistent |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-12-22 | 2021-05-28 06:36 | 157 | 2020-12-08 12:06 | Information Management - Asset Information | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | As per comment number 16 on RFL comment sheet CRL1-RFL-Z3-XCS-CR001-50125 R1. Check consistency between description and DAAID. RFL preference is for slashes to be used instead of dashes. Ultimately asset data has to reflect design information. Asset Data has been updated to reflect dashes being changed to slashes as per the RFL request. Some labelling is now non conformant with the associated labelling as labels still contain dashes however, the are still uniquely identifiable and the proposed actions, to save both cost and time, is to use as is.
| 05SY - Systemwide | Cxxx-NCR-001243 | NCR | Copping stones on Newham wall |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-04-30 | 2021-07-12 09:40 | 73 | 2020-12-10 12:07 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | An exercise was undertaken removing coping stones in order to implement Cxxx-PMI-01919 - "Additional Protection for OHLE Masts along Newham Floodwall". At the locations XRA 19 007 & XRA 19 015 coping stones were mistakenly removed as no OHLE mast protection was prescribed at these locations.
| 05SY - Systemwide | Cxxx-NCR-001244 | NCR | Cxxx-PWK-00408 - Drop 6 - TP - Traction Power and Overhead Lining Equipment - C108_Asset_Name_Space_Duplicates |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-12-24 | 2021-09-07 14:59 | 257 | 2020-12-10 12:43 | Information Management - Asset Information | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Duplicate asset names assigned to a same space. 47 tags affected. CR076-ENB-00083 000 EARTH BAR 010 Earth Bar-EBC-6 Not Approved Operational CR076-ENB-00088 000 EARTH BAR 015 Earth Bar-EBC-6 Not Approved Operational CR076-ENB-00099 000 EARTH BAR 010 Earth Bar-EBC-10 Not Approved Operational CR076-ENB-00120 000 EARTH BAR 015 Earth Bar-EBC-4 Not Approved Operational CR082-ENB-00132 000 EARTH BAR 008 Earth Bar-EBC-8 Not Approved Operational CR082-ENB-00133 000 EARTH BAR 009 Earth Bar-EBC-10 Not Approved Operational CR082-ENB-00137 000 EARTH BAR 013 Earth Bar-EBC-6 Not Approved Operational CR082-ENB-00159 000 EARTH BAR 008 Earth Bar-EBC-8 Not Approved Operational CR082-ENB-00160 000 EARTH BAR 009 Earth Bar-EBC-10 Not Approved Operational CR082-ENB-00164 000 EARTH BAR 013 Earth Bar-EBC-12 Not Approved Operational CR084-ENB-00017 000 EARTH BAR 003 Earth Bar-EBC-6 Not Approved Operational CR084-ENB-00027 000 EARTH BAR 003 Earth Bar-EBC-10 Not Approved Operational CR086-ENB-00071 000 EARTH BAR 017 Earth Bar-EBC-6 Not Approved Operational CR086-ENB-00072 000 EARTH BAR 018 Earth Bar-EBC-6 Not Approved Operational CR086-ENB-00074 000 EARTH BAR 020 Earth Bar-EBC-8 Not Approved Operational CR086-ENB-00102 000 EARTH BAR 017 Earth Bar-EBC-14 Not Approved Operational CR086-ENB-00103 000 EARTH BAR 018 Earth Bar-EBC-4 Not Approved Operational CR086-ENB-00124 000 EARTH BAR 020 Earth Bar-EBC-12 Not Approved Operational CR086-ENB-00125 000 EARTH BAR 018 Earth Bar-EBC-12 Not Approved Operational CR088-ENB-00015 000 EARTH BAR 007 Earth Bar-EBC-10 Not Approved Operational CR088-ENB-00016 000 EARTH BAR 008 Earth Bar-EBC-20 Not Approved Operational CR088-ENB-00025 000 EARTH BAR 007 Earth Bar-EBC-8 Not Approved Operational CR088-ENB-00026 000 EARTH BAR 008 Earth Bar-EBC-10 Not Approved Operational CR092-ENB-00092 000 EARTH BAR 035 Earth Bar-EBC-6 Not Approved Operational CR092-ENB-00123 000 EARTH BAR 029 Earth Bar-EBC-4 Not Approved Operational CR092-ENB-00143 000 EARTH BAR 035 Earth Bar-EBC-12 Not Approved Operational CR092-ENB-00144 000 EARTH BAR 029 Earth Bar-EBC-12 Not Approved Operational CR144-ENB-00123 000 EARTH BAR 009 Earth Bar-EBC-20 Not Approved Operational CR144-ENB-00131 000 EARTH BAR 017 Earth Bar-EBC-8 Not Approved Operational CR144-ENB-00132 000 EARTH BAR 018 Earth Bar-EBC-20 Not Approved Operational CR144-ENB-00161 000 EARTH BAR 009 Earth Bar-EBC-8 Not Approved Operational CR144-ENB-00169 000 EARTH BAR 017 Earth Bar-EBC-8 Not Approved Operational CR144-ENB-00170 000 EARTH BAR 018 Earth Bar-EBC-8 Not Approved Operational CR146-ENB-00610 000 EARTH BAR 035 Earth Bar-EBC-4 Not Approved Operational CR146-ENB-00647 000 EARTH BAR 035 Earth Bar-EBC-8 Not Approved Operational CR147-ENB-00500 000 EARTH BAR 003 Earth Bar-EBC-12 Not Approved Operational CR147-ENB-00508 000 EARTH BAR 003 Earth Bar-EBC-12 Not Approved Operational CR148-ENB-00099 000 EARTH BAR 009 Earth Bar-EBC-20 Not Approved Operational CR148-ENB-00105 000 EARTH BAR 015 Earth Bar-EBC-8 Not Approved Operational CR148-ENB-00106 000 EARTH BAR 016 Earth Bar-EBC-20 Not Approved Operational CR148-ENB-00117 000 EARTH BAR 009 Earth Bar-EBC-8 Not Approved Operational CR148-ENB-00123 000 EARTH BAR 015 Earth Bar-EBC-6 Not Approved Operational CR148-ENB-00124 000 EARTH BAR 016 Earth Bar-EBC-8 Not Approved Operational CR512-ENB-00459 000 EARTH BAR 005 Earth Bar-EBC-8 Not Approved Operational CR512-ENB-00775 000 EARTH BAR 005 Room 4 Floor 4 - earth bar TEB-4 Not Approved Planned CR514-ENB-00202 000 EARTH BAR 004 Earth Bar-EBC-14 Not Approved Operational CR514-ENB-00206 000 EARTH BAR 004 Earth Bar-EBC-12 Not Approved Operational
| 05SY - Systemwide | Cxxx-NCR-001245 | NCR | Connaught Tunnel Compounds - Not accepted MCRs in place |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-03-31 | 2021-03-09 07:52 | -22 | 2020-12-11 17:27 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Several permanent materials(see reference documents section) were incorporated into the works prior to formal acceptance by Client.
| 05SY - Systemwide | Cxxx-NCR-001246 | NCR | Connaught Tunnel Compounds - Starting of works without accepted ITP in place |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-01-08 | 2020-12-22 11:23 | -17 | 2020-12-11 17:11 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Works on installation of bollards within both compounds were started without accepted ITP in place (Cxxx-__-O4-ITP-CR146-50030 Rev 1.0 Cxxx - Connaught Compounds - Street furniture installation )
| 05SY - Systemwide | Cxxx-NCR-001247 | NCR | Walkway Access Ladder (Ladder-Ups) - Channel Nuts Becoming Loose |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-03-31 | 2021-01-18 08:23 | -72 | 2020-12-24 14:59 | Tunnelling - Walkways | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following checks by the __ Compliance Team, it was discovered that the Ladder-Ups on the Walkway Access Ladders at CP4a and PAD have come loose. The incident was reported to the RMC and was promptly rectified by the Maintenance Team. No issues were reported on the other fasteners and fixings.
| 05SY - Systemwide | Cxxx-NCR-001249 | NCR | L892 - Cabinet Around PHP - Related to Cxxx-PWK-00455 |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-02-05 | 2021-06-16 07:35 | 131 | 2021-01-22 12:24 | Information Management - Asset Information | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | The contractor has named the following tags as shown below. A mitigation, for use as is, is recommended as these Tag Descriptions correctly identify the function of the Asset. __ are aware that current investigation pending and action with regards to this naming convention is underway with CRL. The asset is not a help point frame as shown on the AIMS AD4 and this should be reviewed. CR146-FPA-00006 CR146-FPA-00007 CR146-FPA-00007 __ECHING CABINET 002 CR146-FPA-00006 __ECHING CABINET 001
| 05SY - Systemwide | Cxxx-NCR-001250 | NCR | Connaught Tunnel Compounds - VDR concrete slab repairs |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-02-25 | 2021-02-01 15:38 | -24 | 2021-01-25 15:44 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | CRL/__ joint inspection carried out on the 27-11-2020 has identified several defects of concrete slabs in Victoria Dock Road compound - see attached email with report of defects "RE Slab inspection VDR". Remedial works were implemented prior to next activity (asphalt works) taking place (see "Completed concrete slab repairs in VDR") as per agreed with CRL/Cxxx methodology - see proposed remedial works highlighted in red colour on attached report ("Structural Inspection of PV1 at VDR v2 (Cxxx Remedial Proposals)" Find attached as-built surveys after completion of remedial works in VDR.
| 05SY - Systemwide | Cxxx-NCR-001251 | NCR | Missing Fencing and Gates Records for WBP |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-04-28 | 2021-04-14 08:59 | -14 | 2021-01-28 13:50 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Missing install records and redlines relating to the following PMI'd fencing and gate works • 2 x Swinging gates (one at the entrance to site & one further down the access ramp near the tracks) • 1 x Sliding gate (beyond the EB tracks to gain access to the WB tracks) To allow 3 padlock’s (NR, RFL & Lafarge) • All fencing extends sufficiently to effectively provide a continuous barrier with the adjacent walls to the East and West., & palisade fence to provide separation between the LUL pumping chamber and the __ Sidings. This includes a missing ITP, MCR, listed below • Cxxx-__-C-ITP-CRG03-50006 - Title : WBP OHLE protection fences and gates. • Cxxx-__-O4-MCR-CR526-50006 rev 1.0 - 40N Concrete • Cxxx-__-O4-MCR-CR076-50007 rev 1.0 -Security Palisade Fence • Cxxx-__-O4-MCR-CR076-50005 rev 1.0 -HST-3 Expansion Anchor • Cxxx-__-O4-MCR-CR076-50006 rev 1.0 -R-XPT Through bolts • Cxxx-__-O4-MCR-CR076-50009 rev 1.0 - Sliding Gate • Cxxx-__-O4-MCR-CR076-50010 rev 1.0 - Swing Gates • Cxxx-__-O4-MCR-CR076-50008 rev 1.0 – concrete C32/40
| 05SY - Systemwide | Cxxx-NCR-001253 | NCR | Connaught Tunnel Compounds - minor displacement in some drainage pipe runs |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-03-08 | 2021-02-26 07:36 | -10 | 2021-02-08 21:55 | Civil - Drainage | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Following the CCTV survey following pipe runs were identified as category 1 i.e. medium joint displacement in: East Compound (Factory Road) pipe runs: 8.000, 7.000, 3.002, 3.001, 4.000, 5.000 have displayed medium displacement. West Compound (Victoria Dock Road) the following pipe run 4.000 has medium displacement. __ propose to air test these runs again with as per Cxxx-__-O4-ITP-CR146-50026.
| 05SY - Systemwide | Cxxx-NCR-001254 | NCR | Alignment Failure between DB schedules & circuit protective devices installed |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-05-30 | 2021-05-04 08:46 | -26 | 2021-03-01 11:20 | Electrical - LV Equipment | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | TLPPs and MVSOs noted to contain circuit charts (NICEIC schedule of tests) that do not always align with site installation. For example, Station room designations (SID codes) that are incorrect; and/ or __ types and ratings that don’t match configuration used within distribution panel. This was highlighted at both TLPPs surveyed at TCR, as well as the majority of the MVSOs.
| 05SY - Systemwide | Cxxx-NCR-001255 | NCR | Connaught Tunnel Compounds - Drainage - Non return valve |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-04-12 | 2021-05-12 06:09 | 30 | 2021-03-15 15:40 | Civil - Drainage | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | Following Cxxx-RFI-001912 a "flap valve" was installed in outlets towards Thame Water sewers rather than "in-line valve" as per answer in RFI 1912. Following Cxxx-FCD-001415 - Rectification to this issue is to remove flap valve and install inline valve (CRL-MCR-09246)
| 05SY - Systemwide | Cxxx-NCR-001256 | NCR | Points Heating __le Internal panel crack |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-04-05 | 2021-06-10 10:07 | 66 | 2021-03-22 11:04 | Electrical - LV Equipment | 500 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | External Phenomenon - Weather or ambient condition | Completed |  | It has been found during maintenance activities that cracks have occured on the fixing point of internal termination boxes within the Points Heating cubicles
| 05SY - Systemwide | Cxxx-NCR-001257 | NCR | Connaught tunnel access platforms not installed in line with manufactures guidance |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-08-31 | 2021-07-16 07:02 | -46 | 2021-05-21 10:32 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Connaught tunnel access platforms not installed in line with manufactures guidance. Access platforms have been supported at less than 50mm from the edge of track slab. The GRP panel works were installed without an approved code 1 ITP in place.
| 05SY - Systemwide | Cxxx-NCR-001258 | NCR | Galvanising coating thickness of the brackets for Connaught Airshaft's Abseil System |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-09-30 | 2021-07-14 08:49 | -78 | 2021-06-14 13:51 | Shafts - Shafts General | 500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Not Defined | Completed |  | The abseil and ladder support system brackets have had an galvanised coating applied to 80 Microns. The project specification requires a minimum of 120 Microns to be applied.
| 05SY - Systemwide | Cxxx-NCR-001259 | NCR | WBP REB SCADA Interface Incomplete |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-10-31 | 2021-12-01 10:03 | 31 | 2021-06-14 13:19 | Electrical - LV Equipment | 500 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | No SCADA interface installed between the REB and the RCC via the Cxxx SCADA network.
| 05SY - Systemwide | Cxxx-NCR-001260 | NCR | L2186 - Portal Frame asset labelling Cxxx OHLE |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-06-28 | 2021-06-18 11:20 | -10 | 2021-06-14 16:51 | Information Management - Asset Information | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | L2186 - Portal Frame asset labels Cxxx OHLE have been printed and installed with PORTAL STRUCTURE in the line two instead of PORTAL FRAME as per asset naming convention. The information on the below 20 nb affected tags is correct on ADCS 080 and ADCS 093: Tag code- label line one Tag name-line two CR525-OLE-00235 PORTAL FRAME 001 CR525-OLE-00236 PORTAL FRAME 002 CR525-OLE-00237 PORTAL FRAME 003 CR525-OLE-00238 PORTAL FRAME 004 CR525-OLE-00239 PORTAL FRAME 005 CR525-OLE-00240 PORTAL FRAME 006 CR525-OLE-00241 PORTAL FRAME 007 CR525-OLE-00242 PORTAL FRAME 008 CR525-OLE-00243 PORTAL FRAME 009 CR525-OLE-00244 PORTAL FRAME 010 CR525-OLE-00245 PORTAL FRAME 011 CR525-OLE-00246 PORTAL FRAME 012 CR525-OLE-00247 PORTAL FRAME 013 CR525-OLE-00248 PORTAL FRAME 014 CR501-OLE-00104 PORTAL FRAME 001 CR502-OLE-00163 PORTAL FRAME 001 CR502-OLE-00164 PORTAL FRAME 002 CR144-OLE-02461 PORTAL FRAME 001 CR144-OLE-02462 PORTAL FRAME 002 CR146-OLE-02337 PORTAL FRAME 001 NCR is to use currently installed labels as it is. The correct asset names are available within asset data and upon scanning the QR bar codes of these assets on site. Photo sample of affected asset attached. Due to limited access to site relabelling will have time and cost implications and it will further delay handover.
| 05SY - Systemwide | Cxxx-NCR-001261 | NCR | Graybar Points Heating Strips - MCR documentation not issued "for acceptance" |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-06-30 | 2021-06-18 07:49 | -12 | 2021-06-16 07:04 | Electrical - LV Equipment | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Electronic eB MCR raised for points heating strips and supporting documentation issued For Information followin Cxxx-PMI-00136. The response from CEG review is that an electronic MCR is not required, but the supporting document was not re-submitted For Acceptance
| 05SY - Systemwide | Cxxx-NCR-001262 | NCR | Connaught Tunnel Compounds - Factory Road - No concrete strength test result for PV1 concrete cast on 12/11/2021 |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-08-10 | 2021-07-08 10:24 | -33 | 2021-07-01 16:42 | Civil - Concrete Pavement | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Contractor cannot locate concrete cubes for PV1 slab pour completed on 12/11/2020 therefore no test result available for this 18.8m3 concrete pour in FR. Contractor have installed 271.3 M3 of concrete in PV1 slabs in the Factory Road Compound and c. 315m3 in VDR, all test cubes made for these pours have passed their compressive strength tests of min 40Mpa see attached "FR concrete strength test results.pdf " Concrete cast on 12/11/2020 represents approximately 3% of all PV1 slabs concrete cast in both compounds.
| 05SY - Systemwide | Cxxx-NCR-001263 | NCR | Asset labelling missprint for 2 control cables - CR512 |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-07-19 | 2021-07-14 06:26 | -5 | 2021-07-05 16:02 | Information Management - Asset Information | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | FOA: __ Labels for 2 control cables tags listed below have been misprinted in label line 2, not following control cables naming convention. Information printed on both labels is correct and indicates source, destination and desing asset ID as required. 1. Asset data reads: CR512-CCC-00842 Label line 2: C-Cxxx-EE-02135-Cxxx-EE-01008 Label line 3: Cxxx-CC-00001569 Label reads: CR512-CCC-00842 Label line 2: Cxxx-EE-02135 link to Cxxx-EE-01008 Label line 3: Cxxx-CC-00001569 2. Asset data reads: CR512-CCC-00843 Label line 2: C-Cxxx-EE-02136-Cxxx-EE-01009 Label line 3: Cxxx-CC-00001570 Label reads: CR512-CCC-00843 Label line 2: Cxxx-EE-02136 link to Cxxx-EE-01009 Label line 3: Cxxx-CC-00001570 NCR is to use currently installed labels as it is. Correct format of asset naming is available within asset data and upon scanning of QR bar codes of these assets on site. Photos of affected asset labels attached. Due to limited access to site, relabelling will have time and cost implications and it will further delay handover.
| 05SY - Systemwide | Cxxx-NCR-001264 | NCR | Signage at STG shaft omitted from original signage strategy |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-12-31 | 2021-11-30 08:22 | -31 | 2021-08-23 11:45 | Architectural - Signage | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | RFLi identified that there were incorrect telephone numbers on the shaft side of STG doors. CRL identified that the STG signs were omitted from the original signage schedule.
| 05SY - Systemwide | Cxxx-NCR-001265 | NCR | Connaught Tunnel Compounds - FR - Edging stones location (P22, P23, P24) |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-08-17 | 2021-10-19 09:17 | 63 | 2021-07-20 09:20 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Contractor identified that coordinates of Edging stones between points P22, P23 and P24 were set out incorrectly. Current position does not allow compliant access to future SR3 fence on north side of walkway due to small gap between fence and edging stones.
| 05SY - Systemwide | Cxxx-NCR-001266 | NCR | Cantilever Asset Label on Approach to Whitechapel Station Captured under D061 LULCS |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-08-05 | 2021-08-31 08:44 | 26 | 2021-07-22 14:45 | Information Management - Asset Information | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | FOA: __ ************* This NCR is generated in relation to negative observation "OBS_26_LCS Tag ID non-compliance" within OHLE Asset Data VAP Report Cxxx-XRL-Z3-RGN-CR001-50013. Cantilevers on approach to Whitechapel Station have been generated and labelled under LULCS "D061 - Whitechapel Station" instead of "CR092 - Liverpool Street to Whitechapel". Currently, all these D061 asset data tags are referred within CODE 1 accepted documents below: 1. Mounting Data Book; Cxxx-__-R6-XDS-CR094-50004 2. OHLE T5X; Cxxx-__-K2-OMT07-CR001-50002 Updating the affected asset data tags to "CR092 - Liverpool Street to Whitechapel" require updates to all of documentation above and also require asset relabelling on site. Therefore __'s proposal is to leave the affected asset tags listed below as is. Changes would have impact on time and cost which will further delay the handover. Eastbound Tags ************** D061-OLE-00251 D061-OLE-00252 D061-OLE-00253 D061-OLE-00254 D061-OLE-00255 D061-OLE-00256 D061-OLE-00257 D061-OLE-00258 D061-OLE-00259 D061-OLE-00260 D061-OLE-00265 D061-OLE-00266 D061-OLE-00267 D061-OLE-00268 D061-OLE-00269 D061-OLE-00270 D061-OLE-00271 D061-OLE-00272 D061-OLE-00273 D061-OLE-00274 D061-OLE-00275 D061-OLE-00276 D061-OLE-00277 D061-OLE-00278 D061-OLE-00280 D061-OLE-00282 Westbound Tags ************** D061-OLE-00316 D061-OLE-00317 D061-OLE-00318 D061-OLE-00319 D061-OLE-00320 D061-OLE-00321 D061-OLE-00322 D061-OLE-00323 D061-OLE-00324 D061-OLE-00325
| 05SY - Systemwide | Cxxx-NCR-001267 | NCR | Voltage Transformer Failures |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2022-03-31 | 2022-01-12 11:59 | -78 | 2021-07-28 11:48 | Over Head Line Electrification - Over Head Line Electrification General | 500 |  | Equipment Breakdown | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | 3 no. of the outdoor voltage transformers on the OHLE switches have catastrophically failed. As reported on the 21/7/21 - A transient trip was experienced on the circuit breakers at PMLA with a critical alarm being triggered on motorised switch 102/15, no trains reported any issues. Upon investigation it was established that there was a voltage transformer on OHLE structure at Plumstead, damaged and hanging loose with the VT insulator 102Q becoming detached from the VT base. The location is PLUMSTEAD Structure Nr. XRA/23/06L. As reported on the 3/8/21 - A second VT was reported as failing at VT 102R. A third failed at 101L – WBP on the 07/10/21.
| 05SY - Systemwide | Cxxx-NCR-001268 | NCR | OHLE Asset Labelling Quality Issues |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-12-31 | 2021-09-16 10:49 | -106 | 2021-08-02 08:59 | Information Management - Asset Information | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Asset labels were found to be misaligned at abbey wood. Upon further review it was found that the ITP being used for these works was not fit for purpose, as it was not specific to OHLE works and did not cover application of labels in wet conditions.
| 05SY - Systemwide | Cxxx-NCR-001269 | NCR | OHLE assets on Plumstead Reception Road captured under CR505 LULCS code instead of CR526 LULCS code |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-08-26 | 2021-08-31 08:52 | 5 | 2021-08-12 11:23 | Information Management - Asset Information | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | FOA. __ The following OHLE assets listed below have been captured under CR505 LULCS code instead CR526 LULCS code and are flagged on CRL Quality Report under M16 Asset-System LULCS1 Mismatch: - 1nb Mast - 2nb Disconnectors - 91nb Droppers All this assets are allocated to FU-2-007731 - Overhead Catenary System (OCS) 009 at Plumstead Depot Facility (PL3) - under LULCS CR526 - Plumsted Depot & Sidings. Updating the affected asset tags to CR526 requires relabelling on site for mast and disconnectors and due to access planning duration, cost and further delay to the asset data handover __ 's proposal is to leave affected asset tags as is under CR505 LULCS code.
| 05SY - Systemwide | Cxxx-NCR-001270 | NCR | Connaught Tunnel Compounds - both compounds - out of tolerance concrete slabs surface levels |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-10-11 | 2021-09-01 07:00 | -40 | 2021-08-24 10:59 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In several areas of both compounds there is a variation of finish surface levels from the design levels. In some cases, it is greater than 10mm tolerance, hence This NCR is raised to record this issue..
| 05SY - Systemwide | Cxxx-NCR-001271 | NCR | Connaught airshaft coping stone mortar batching |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-12-31 | 2021-12-13 09:15 | -18 | 2021-09-08 12:51 | Civil - Civil Engineering General | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | M12 Mortar batching for the coping stones at Connaught airshaft has not met the required compressive minimum strength of 12MPa tested at 28 days.
| 05SY - Systemwide | Cxxx-NCR-001272 | NCR | Rail Defects on Switch Rails at Custom House |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2022-10-04 | 2022-05-24 07:29 | -133 | 2021-10-04 08:06 | Track - Welding | 500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | The rail defects have been discovered in both the LH and RH switch rails of turnout 1343A a.k.a. C13 and the LH switch rail of turnout 1347A a.k.a. C15. The defects were discovered during routine Ultrasonic Testing by RfL. The nature of the failure is similar in all cases where a horizontal crack in the web of the switch rail is present in the vicinity of the flash butt weld adjacent to the forged transition. The forged transition exists where the asymmetric tongue rail section of the switch blade transitions back to the conventional 60E2 rail section. The two defects on 1343A points were discovered on the night of 2-3 August 2021. The L/H switch defect is 55mm long, and the R/H switch defect is 95mm long. Both defects emanate from the flash butt weld joining the shallow depth transition rail to the belly rails, both at a depth of 105mm from the rail head. The defect on 1347A points was discovered on the night of 3-4 August 2021. The L/H Switch rail (through route) defect has a horizontal length of 50mm and a depth of 102mm and transverse cracks one turning upwards and one downwards both picked up by the 37 degree angle UT probes and roughly are 80mm (upwards) & 130mm (downwards) deep.
| 05SY - Systemwide | Cxxx-NCR-001273 | NCR | Voltage transformers not compliant with BS EN 50152-3-3:2001 |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2022-03-31 | 2022-02-03 05:41 | -56 | 2021-10-21 08:21 | Over Head Line Electrification - Over Head Line Electrification General | 500 |  | Material | Reject | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | As part of the root cause investigations for Cxxx-NCR-001267, a damaged Voltage Transformer was sent back to the supplier, Ritz, for Investigations. In Ritz Investigation report UQP10781 dated 14.10.2021, it was identified that the Voltage transformers supplied do not meet the standard BS EN 50152-3-3:2001, which is a requirement of the technical specification. Further to this, it was identified that the Indoor Voltage transformers do not conform with BS EN 50152-3-3:2001, which is also a requirement of their technical specification.
| 05SY - Systemwide | Cxxx-NCR-001274 | NCR | TVS VSD MCC Panel UPS Wiring and Control Logic |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2022-04-30 | 2022-01-26 13:23 | -94 | 2021-11-23 10:58 | Systems - Ventilation and Pressure Relief | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | During a Bismark test at STG it was discovered that when the A or B supply is lost to a shaft the control side of the VSD which feedbacks to the VCS is also lost, meaning there are no feedback signals from the VSD to the VCS as to why the fan has stopped operating. Further investigation found a clause in the Works Information that requires the VCS to ignore short drops in power to allow a changeover of LV supplies to take place in a shaft so that the ventilation response carries on as before as soon as the LV changeover has occurred. At present the VCS does not do that and simply sets the shaft to Out of Service and moves to the next shaft. This causes a potential delay of 90 seconds whilst the next shaft is configured for ventilation.
| 05SY - Systemwide | Cxxx-NCR-001275 | NCR | Asset labelling - Formatting issue on TVS labels |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2022-02-28 | 2022-01-12 14:37 | -47 | 2021-11-26 13:13 | Information Management - Asset Information | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following the TVS VAP Observations, __ have identified that a number of asset (white) and equipment (yellow) labels have been installed on site with minor text formatting issues. 17 no. white asset labels are missing the LClass code from the third text line of the label. (see attachment CR512-TVS-00290). 18 no. yellow EQ labels have a repeat of the Crossrail 'SN' serial number code within text line one of the label, where it should only appear within line three. (see attachment TCR-E EQ LABLES 2). As neither issue results in incorrect information being present, and the ability to clearly identify the asset/equipment via the label remains, __ request that these labels remain installed as they are. With any replacement occurring during standard maintenance regimes in the future as necessary.
| 05SY - Systemwide | Cxxx-NCR-001276 | NCR | Missing Joint Plate Bolt - XRA/16/402. EB |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2022-03-14 | 2022-03-08 18:22 | -6 | 2021-12-14 12:14 | Over Head Line Electrification - Supports | 500 |  | Incomplete Works | Repair | 4 (0.5-3k) | Complete | Supervision - Other | Completed |  | ROC Joint plate at XRA/16/402. EB has only 7 bolts rather than the 8 prescribed by the design. There is no record available to account for this omission.
| 05SY - Systemwide | Cxxx-NCR-001277 | NCR | TVS Fan Stalling during Congested Operation |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2022-07-15 | 2022-07-01 08:34 | -14 | 2022-01-07 09:44 | Systems - Ventilation and Pressure Relief | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Following the switch on of the Congested Mode functionality of the TVS system during Trial Running it was observed that fans at Eleanor Street were stalling in certain circumstances. An investigation was carried out in late December 2021 which concluded that when a train is stopped near to Eleanor Street Shaft and the fans are running to ventilate the stopped train, when another train approaches to pull up behind the first train the pressure generated by that train causes the fans to stall at Eleanor Street. The system reacts to the stalled fan by putting them out of service which makes the shaft unavailable on the Ventilation Control System. A further investigation will be carried out on the 21st of January using specialist equipment from our fan supplier __ to ascertain the level of stall (pressure) and duration at various duty point fan speeds.
| 05SY - Systemwide | Cxxx-NCR-001278 | NCR | Asset labelling - Formatting issue on TM Pump labels |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2022-03-09 | 2022-01-11 15:14 | -57 | 2022-01-10 10:11 | Information Management - Asset Information | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Following Tunnel Mechanical VAP Observations, __ have identified that a number of Pump asset labels have been installed on site with minor text formatting issues. Line 2 only contains the word 'Pump xxx', where it should also contain 'Pumped Drainage' which is missing. Please see attachments. As neither issue results in incorrect information being present, and the ability to clearly identify the asset/equipment via the label remains, __ request that these labels remain installed as they are. With any replacement occurring during standard maintenance regimes in the future as necessary.
| 05SY - Systemwide | Cxxx-NCR-001279 | NCR | Mast Asset Labels Installed with Incorrect L-class Printed |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2022-02-02 | 2022-01-25 15:53 | -8 | 2022-01-12 09:27 | Over Head Line Electrification - Over Head Line Electrification General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | FOA: __ ************** The NCR is raised to accomodate close out of OHLE VAP Cxxx-XRL-Z3-RGN-CR001-50013 Revision 4.0, OBS_05 Asset Tag label contains incorrect data. L21831 Complete Mast asset labels have been printed and installed with "L21834" or "L21832" instead of "L21831" in label text line three. The printing error affecting the following asset tag IDs: CR145-OLE-00047 at site installed as "L21832" CR145-OLE-00048 at site installed as "L21834" CR145-OLE-00049 at site installed as "L21834" It can be confirmed that the information are correct on ADCS, only error at site. NCR is to use currently installed labels as it is. The correct asset information are available within asset data and upon scanning the QR bar codes of these assets on site. Due to limited access to site relabelling will have time and cost implications and it will further delay handover.
| 05SY - Systemwide | Cxxx-NCR-001280 | NCR | Earth Bar Asset Labels Installed with No L-Class Information Printed |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2022-02-02 | 2022-01-24 11:37 | -9 | 2022-01-12 09:54 | Over Head Line Electrification - Earthing & Bonding | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | FOA: __ ************** The NCR is raised to accomodate close out of OHLE VAP Cxxx-XRL-Z3-RGN-CR001-50013 Revision 4.0, OBS_05 Asset Tag label contains incorrect data. L74341 Earth Bar asset labels have been printed and installed with no L-class "L74341" in label text line three. The printing error affecting the following asset tag IDs: CR145-ENB-00465 CR145-ENB-00466 CR146-ENB-00758 It can be confirmed that the information are correct on ADCS, only error at site. NCR is to use currently installed labels as it is. The correct asset information are available within asset data and upon scanning the QR bar codes of these assets on site. Due to limited access to site relabelling will have time and cost implications and it will further delay handover.
| 05SY - Systemwide | Cxxx-NCR-001281 | NCR | Aerial Earth Wire Asset Labels Installed Containing Area Acronyms in Label Text Lines Two and Four |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2022-01-26 | 2022-01-24 11:35 | -2 | 2022-01-12 11:24 | Over Head Line Electrification - Earthing & Bonding | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | FOA: __ ************* This NCR is generated in relation to negative observation "OBS_05 Asset Tag label contains incorrect data" within OHLE Asset Data VAP Report Cxxx-XRL-Z3-RGN-CR001-50013 Rev 4.0. VAP walkout observed aerial earth wire asset labels printed and installed containing area acronyms in label text lines two and four. For example WBP, ROP, LIS etc.. These area acronyms do not appears on the latest version of OHLE ADCS 080 and 093. It is believed that these labels were correctly installed sometime in 2019 based on older version of ADCS generated in 2019 which contains area acronyms. These information since then removed from ADCS 080-UF-063 which generated in July 2020. As example please compare between ADCS Cxxx-080-UF-042 and Cxxx-080-UF-063. Actual quantities of labels affected at site have been not established. The additional information such as CUH, ROP etc indicating area of the source or destination of the aerial earth wire. For that reason, the proposal is to use the labels as is. Due to limited access to site relabelling will have time and cost implications and it will further delay handover.
| 05SY - Systemwide | Cxxx-NCR-001282 | NCR | TVS Fan Vibration – TCR-E Fan C |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2022-07-20 | 2022-07-19 07:59 | -1 | 2022-02-04 13:13 | Systems - Ventilation and Pressure Relief | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Following routine maintenance of fans at Tottenham Court Road by the fan manufacturer __ they discovered a fan casing vibration issue at a Duty Point of 75% on Fan C at Tottenham Court Road East Shaft. The vibration level is above the manufacturers guidelines and could cause damage to the fan were it to be used at that speed for standard ventilation responses. The 75% duty point is used for Incident, congested and maintenance responses for that fan. Further investigation found that the vibration only occurs between 73% to 77% speeds.
| 05SY - Systemwide | Cxxx-NCR-001283 | NCR | Asset data - Request to keep cable labelling 'as is' |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2022-03-31 | 2022-02-22 09:54 | -37 | 2022-02-11 12:36 | Information Management - Asset Information | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Following the tunnel electrical VAP exercise, cable CR146-LVD-00545 was identified as having two labels with different content along its route, one scenario reflected that AIMS data name attribute whilst the other scenario reflected the AIMS label line text attribute. Therefore, the information on the labels was correct in terms of cable source and destination on both instances but obviously one scenario was incorrect when comparing to the data. Actions taken by __ - completion of holistic data check against the latest cable schedule to identify what the correct information on the labels should be, along with holistic check comparing discrepancies within the AIMS data where the cable names did not match a cable label text attribute. Is was identified that the label text content in AIMS matched that of the cable schedule and therefore the AIMS data has been updated so that the cable name attribute is consistent. This NCR is therefore to cover any further label content discrepancies that may exist on-site for any of the assets associated with this NCR. IT SHOULD BE NOTED THAT THE KEY DATA UPON THESE LABELS HAS ALWAYS BEEN CORRECT i.e. THE ASSET ID AND DESIGN ID, ALLOWING FOR TRACEABILITY BETWEEN AIMS AND THE DESIGN.
| 05SY - Systemwide | Cxxx-NCR-001284 | NCR | TVS Damper Linkage Pin |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2022-04-24 | 2022-05-16 07:35 | 22 | 2022-02-11 14:16 | Systems - Ventilation and Pressure Relief | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Insufficient information made available to the worker. | Completed |  | RFLI’s maintainer __ have put a report together showing an issue they are experiencing with the TVS Dampers. The issue is a pin that holds the actuator drive shaft together with the linkage mechanism that drives the damper. This pin is pushed in using friction and has started to drop out at five locations causing these dampers to stop working.
| 05SY - Systemwide | Cxxx-NCR-001285 | NCR | TVS Actuator Contacts |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2022-07-31 | 2022-07-08 13:29 | -23 | 2022-02-11 14:21 | Systems - Ventilation and Pressure Relief | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | External Phenomenon - Not Defined | Completed |  | RFLI’s maintainer __ have put a report together showing an issue they are experiencing with the TVS Actuators. The issue is that the two contactors inside the actuators that drive the actuator open or closed are getting stuck. This prevents the actuator from opening or closing. Hitting the actuator with a tool frees up the contactor allowing the actuator to function as designed.
| 05SY - Systemwide | Cxxx-NCR-001286 | NCR | Cxxx WBP REB FAP Isolator is non-compliant to BS5839 |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2022-03-24 | 2022-02-22 09:21 | -30 | 2022-02-17 09:14 | Electrical - LV Equipment | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | The current fire alarm isolator is to regulation 93/68/EEC (European regulation) and is noted as a deviation from BS5839 and needs to be replaced to meet BS standards. This does not affect the operation of the fire alarm system and is commissioned into service.
| 05SY - Systemwide | Cxxx-NCR-001287 | NCR | VT 101/9 - Jumper Installation Incorrect |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2023-02-22 | 2022-03-29 10:14 | -330 | 2022-02-22 14:36 | Over Head Line Electrification - High Voltage Power Supply | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The RCC have identified that electrical section 101K at Westbourne Park on Turnback B (Highlighted yellow in Diagram 1.1 below), is showing live when Switch 101/9 is operated to the open position. When 101/9 Disconnector Switch is in the open position, Electrical Section 101K should read 0 volts in the RCC. After investigation it has been identified that the Jumper Cable from Voltage Transformer (VT) 101K is connected incorrectly to Electrical Section 101J (please see diagram 1.2 Below). This gives a false indication to the RCC that Electrical Section 101K is still live as it is unmonitored by the Voltage Transformer.
| 05SY - Systemwide | Cxxx-NCR-001288 | NCR | ROP SOUTH - Vanguard rotating spinners on top of diaphragm wall |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2022-04-01 | 2022-03-14 07:49 | -18 | 2022-03-11 12:10 | Civil - Civil Engineering General | 500 |  | Incomplete Works | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Insufficient quantity of material to do the job | Completed |  | Due to constructability issues (supply chain issues) at the time of installation, only two (instead of three) rotating spinners were installed on top of lower part of diaphragm wall in ROP south walkway area and none of the spinners were installed at higher level diaphragm wall - see extracts from the drw Cxxx-__-C-DDL-CR076_PT001_Z-32154 P01
| 05SY - Systemwide | Cxxx-NCR-001289 | NCR | Shallow embedment depth for SR3 fence post |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2022-05-31 | 2022-05-19 13:54 | -12 | 2022-03-29 17:33 | Civil - Civil Engineering General | 3000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Not Defined | Completed |  | The fence posts for Plumstead head shunt fence works that have been delivered to site are 300m too short, this means that only 900m embedment, compared to the specified embedment of 1200mm, can be achieved. Materials were supposed to arrive to site from supplier on the 25th of March however were delayed due to a powder coating issue, they did not arrive until 28th of March, with the works scheduled to commence the following day. However, upon arrival a material inspection was conducted and it was found they were the wrong length. This was notified to CRL soon after on Monday via email.
| 05SY - Systemwide | Cxxx-NCR-001292 | NCR | Segregation of fire alarm cables |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2022-07-22 | 2022-07-21 14:15 | -1 | 2022-04-27 12:45 | Fire - Fire Systems & General | 500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | As part of an inspection by __ for their Verification Certificate works, it was discovered that the LV Fire Alarm System cables in the REB do not conform with the BS 5839 and BS 7671 requirements for mechanical and electrical segregation. These cables are currently not segregated running along the horizontal section of CMS and are bunched with 230V cables.
| 05SY - Systemwide | Cxxx-NCR-001293 | NCR | E&B Installation started without approved MCR's - PLU Portal |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2022-09-30 | 2022-07-21 14:19 | -71 | 2022-07-19 13:14 | Electrical - Earthing & Bonding | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Insufficient quantity of material to do the job | Completed |  | The installation of the earthing and bonding of the TSI walkway handrails at Plumstead Portal has started without and approved MCR in place for the 35/70 mm single core cable and lugs being used.
| 05SY - Systemwide | Cxxx-NCR-001294 | NCR | The calibration certificate for the __ crimper was not supplied by __ hire company |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2022-09-30 | 2022-09-01 08:54 | -29 | 2022-08-25 12:43 | Electrical - Earthing & Bonding | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | The crimper hired from __s to carryout the earthing and bonding for the handrail install at Plumstead did not have a calibration certificate. We proceeded to use the crimper under the presumption __s would have the certificate in their system. The original would usually be with the machine and a copy should be stored in __s document handling system. When we subsequently chased __s for the certificate they were unable to produce it.
| 05SY - Systemwide | Cxxx-NCR-001295 | NCR | BOS Fan fail during a mode change |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2022-12-02 | 2022-11-04 08:56 | -28 | 2022-09-21 16:54 | Systems - Ventilation and Pressure Relief | 500 |  | Testing and Commissioning | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | There have recently been two instances of a fan failing during a mode change between UPE and congestion:  BDS-W TVFB 17/08/2022 07:51:18  BDS-W TVFA 01/09/2022 12:46:17 In both instances, the shaft was running UPE mode 102. Congestion was turned on in VS03W and mode 213 requested at BDS-W. A short time later, the train began to move and UPE mode 102 was requested again. At this point, the fan failed and was set out of service due to ‘Running speed out of tolerance’.
| 05SY - Systemwide | Cxxx-NCR-000001 | NCR | Design Management Plan review |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-07-01 | 2016-09-19 09:41 | 80 | 2016-01-25 11:23 | Systems - Other | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | NCR has been raised to ensure that the following finding on the Design Management Plan will be addressed by the contractor is a timely manner: • The document has not been revisited for over 600 days now. According the WIv2B Part 29.1.4.3. ‘… revisions and submissions will be made within the period for reply’ which is deemed to be 12 months for DMP. • The referenced programme ref. no. Cxxx-SIC-R2-TSC-CR001-50004 is for years 2013/2014 and is out of date. This should be updated in the new revision of DMP • A reference is made to Consents Management Plan but there is no reference number for this document. This should be updated in the new revision of DMP • There are no details of the required category checks for the system. The checking process should have been known by now. This should be updated in the new revision of DMP. For details refer to surveillance report ref. no. Cxxx-XRL-O4-RGN-CR001-50007.
| 05SY - Systemwide | Cxxx-NCR-000002 | NCR | Interlocking Data |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-06-25 | 2016-06-24 15:01 | -1 | 2016-05-04 15:55 | Systems - Other | 500 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | Principles testing has commenced on Westrace Interlocking data at Chippenham
| 05SY - Systemwide | Cxxx-NCR-000003 | NCR | Design |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-08-02 | 2016-09-29 15:33 | 58 | 2016-06-21 12:31 | Surveying - Rail Infrastructure Surveys | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Setting out of signalling is proceeding without an approved design
| 05SY - Systemwide | Cxxx-NCR-000004 | NCR | ITP |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-07-15 | 2016-07-15 14:37 | 0 | 2016-07-01 11:39 | Systems - Signalling | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | Work commenced on manufacturing of Access points without an accepted ITP
| 05SY - Systemwide | Cxxx-NCR-000005 | NCR | Cable Sheath |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-07-29 | 2016-09-07 14:36 | 40 | 2016-07-07 12:53 | Systems - Signalling | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Cable Number: CR146-SCC-00058 2c x 4mm XLPE/SWA/LSOH – Drum Number Cxxx/033. Excessive LZOH sheath noticed at 1072 Ring Number, on Tray 4 in the East Bound Tunnel Bore.
| 05SY - Systemwide | Cxxx-NCR-000006 | NCR | Cable damage |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-08-05 | 2016-09-07 14:19 | 33 | 2016-07-08 08:53 | Systems - Signalling | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 2c 6mm2 steel wire armoured Cable from drum no: 106033M8/L./ F__ Drum No: Cxxx-038 has been wrapped with tape 1920m into a drum of 2060m, confirmation required if the tape is concealing damage or a joint.
| 05SY - Systemwide | Cxxx-NCR-000007 | NCR | Cable Drum Schedule |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-07-25 | 2016-08-22 13:58 | 28 | 2016-07-11 15:44 | Systems - Signalling | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Works Information 2A states; The Contractor shall provide appropriate cable drum schedules identifying which drum all S&CS cables came from and in which locations they were installed. This information shall also be used by the Contactor during the preparation of as built drawings for the works. This information has been requested however no detail has been provided on the understanding that it is a Cxxx deliverable.
| 05SY - Systemwide | Cxxx-NCR-000008 | NCR | ITP |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-09-08 | 2016-09-26 12:31 | 18 | 2016-08-11 09:00 | Systems - Signalling | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | Manufacturing commenced on Westrace B1, B2 and RCS cabinets before ITP accepted between the parties to mitigate programme delays
| 05SY - Systemwide | Cxxx-NCR-000009 | NCR | Cable damage |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-11-04 | 2016-11-01 10:57 | -3 | 2016-09-09 09:26 | Systems - Signalling | 500 |  | Manufacturing Defect | Reject | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | whilst installing cables for Cxxx in the West Bound Thames Tunnel, between Woolwich and NWP Cable number CR146-SCC-0021 was being installed from Drum Cxxx-017. After approx. 400m of installing this cable, the following marks were noticed on the left picture, and then further in, the outer sheathing had split, exposing the SWA armouring. This was at meter mark 4238 We had already pulled 2 cables off this drum earlier measuring 957mts as a new 2,000m drum.
| 05SY - Systemwide | Cxxx-NCR-000010 | NCR | Cable drum danage |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-10-17 | 2016-10-25 09:06 | 8 | 2016-09-19 14:02 | Systems - Signalling | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper handling of material | Completed |  | Cable drum number __ reference Cxxx-008. __ drum serial number Cxxx1534/L has been inspected and damage to the drum has been located on the drum flange by the core and has been deemed not fit for purpose. See attached photographic evidence
| 05SY - Systemwide | Cxxx-NCR-000011 | NCR | Independent Checking of ABX Control table |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-11-25 | 2017-03-14 17:08 | 109 | 2016-10-17 14:47 | Systems - Systems Engineering General | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Management Problem - Improper resource allocation | Completed |  | Abbey Wood Control tables page 17 in the pdf (Cxxx-SIC-R2-DWG-CR001-50035) shows DES :- RA CHD NR for version 005 and the reverse for version 006 which shows a lack of independence and does not meet the extracts from the design handbook 6.6 and 8.3. This undermines the independent checking process which would in turn undermine any design safety justification, given that the safety critical design process relies on the independence of the checker.
| 05SY - Systemwide | Cxxx-NCR-000012 | NCR | Material Compliance Records |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-12-28 | 2017-02-28 10:29 | 62 | 2016-10-31 14:16 | Systems - Signalling | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | No MCR acceptance for the following Ethernet cables for RCS build. Cxxx-SIC-R2-LRC-CR001-50078 (A6Z00039457458) __ Group Ethernet Cables Cxxx-SIC-R2-LRC-CR001-50106 (A6Z00039936749) __ FO Ethernet Cables
| 05SY - Systemwide | Cxxx-NCR-000015 | NCR | Cleveland Cable delivery to site with red tape and cable scuff marks on cable sheath |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-01-15 | 2017-01-05 11:03 | -10 | 2016-12-01 08:36 | Systems - Signalling | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | During a site surveillance at Plumstead cable compound, it was noted that a recent delivery of 4 drums (cable drum no's Cxxx-060, 061, 062 & 063) to site by __ was noted to have red tape and scuff marks on the cable sheath whilst partially battened.
| 05SY - Systemwide | Cxxx-NCR-000016 | NCR | Dual Splitter has been supplied with incorrect connectors |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-01-20 | 2016-12-23 09:43 | -28 | 2016-12-01 08:38 | Systems - Signalling | 500 |  | Material | Reject | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | The Plumstead Stores Manager has reported that a Dual Splitter (part no. A2V00082051478) has been supplied with incorrect connectors and cannot be used.
| 05SY - Systemwide | Cxxx-NCR-000017 | NCR | Custom House B2 __le - Poorly trimmed cable ties contained within cabinets |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-01-31 | 2017-02-20 10:14 | 20 | 2016-12-08 15:06 | Systems - Signalling | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | Site surveillance highlighted that B2 cabinet contains poorly trimmed cable ties within
| 05SY - Systemwide | Cxxx-NCR-000018 | NCR | Work commenced with a code 2 ITP |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-02-09 | 2017-02-14 11:46 | 5 | 2016-12-15 12:43 | Systems - Signalling | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | The contractor wishes to inform the project manager that cable running work has progressed in the RCC with a code 2 ITP Cxxx-SIC-R2-ITP-CR001-50011. The following cables were run 17 x Cat 6 cables and 10 X DVI cables
| 05SY - Systemwide | Cxxx-NCR-000019 | NCR | O & M manuals |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-02-14 | 2017-10-18 13:40 | -119 | 2017-02-14 11:25 | Systems - Signalling | 3000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | The contractor wishes to inform the project manager that the work has progressed without Operations and Maintenance Manuals being submitted prior to the work commencing.
| 05SY - Systemwide | Cxxx-NCR-000020 | NCR | Book Wiring |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-04-24 | 2017-07-04 13:15 | 71 | 2017-03-07 14:33 | Systems - Signalling | 500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | The contractor wishes to inform the project manager that the work has progressed on the installation at the RCC and there was no caveat on the PMC allowing the work to commence. • IRC for RCC (Cxxx-PMC-01998) is accepted at code 1 – it mentions LWOD installation but only references the book wiring (Cxxx-SIC-R2-DWG-CR001-50036) • Barco LWOD drawings were submitted under Cxxx-CCM-02617 on 09/01/2017. W/O: CRL-REV-00137292 stakeholder review was due for completion on: 20/01/2017 . • Cxxx-NCR-000018 was raised 15/12/2016 for work commencing with a code 2 design • Cxxx-NCR-000025 was raised 23/01/2017 for work commencing without an approved design @ RCC.
| 05SY - Systemwide | Cxxx-NCR-000021 | NCR | CIF Earth Wiring |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-01-19 | 2017-03-16 09:39 | 56 | 2017-01-05 10:47 | Systems - Signalling | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | During a routine observation of the Integration Facility earth wiring has been found to be loose or not connected presenting a potential safety hazard. (See attahced photos) Further investigation has revealed that the installation has proceeded at risk prior to the CIF Earthing and Bonding Plan Cxxx-SIC-R2-STP-CR001-50123 (1.0) being accepted by CRL (document submitted 23/12/16, Installation signed as complete 16/12/16).
| 05SY - Systemwide | Cxxx-NCR-000022 | NCR | Damaged AP Cabinet |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-03-18 | 2017-02-14 16:25 | -32 | 2017-01-13 12:39 | Systems - Signalling | 500 |  | Damaged | Reject | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper handling of material | Completed |  | AP cabinet found to have a large scratch on front cover.
| 05SY - Systemwide | Cxxx-NCR-000023 | NCR | Cable scuff marks on cable sheath |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-02-22 | 2017-02-21 11:40 | -1 | 2017-01-23 15:42 | Systems - Signalling | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper storage of material | Completed |  | During a supplier surveillance at __, visual inspection across the drums checked, various types of marks were noted i.e. scuff marks, white marks/ smudges/ streaking to an inconsistent witness line on various drums. Note Cxxx-NCR-000015 refers.
| 05SY - Systemwide | Cxxx-NCR-000024 | NCR | Work has commenced without an approved MCR at RCC |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-04-15 | 2017-02-21 11:42 | -53 | 2017-02-14 15:18 | Systems - Signalling | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | Work has commenced without an approved MCR (Cxxx-SIC-R2-LRC-CR001-50120) for __ CAT 6 S/FTP Cable at the RCC. MCR's has now been returned and accepted by CRL under Cxxx-PMC-02004 and is code 1
| 05SY - Systemwide | Cxxx-NCR-000025 | NCR | Work has commenced without an approved design at RCC |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-05-07 | 2017-04-27 14:39 | -10 | 2017-01-23 15:52 | Systems - Signalling | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | Work has commenced without an approved design (eb ref xxxxxxx) at the RCC
| 05SY - Systemwide | Cxxx-NCR-000026 | NCR | Work commenced on manufacturing of UPS for Custom House without an accepted ITP |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-04-19 | 2017-04-27 14:29 | 8 | 2017-02-14 15:20 | Systems - Signalling | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | Work commenced on manufacturing of UPS for Custom House without an accepted ITP
| 05SY - Systemwide | Cxxx-NCR-000027 | NCR | Work commenced on manufacturing of Fabrications without an accepted ITP |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-04-19 | 2017-04-28 15:18 | 9 | 2017-02-14 15:22 | Systems - Signalling | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | Work commenced on manufacturing of Fabrications without an accepted ITP
| 05SY - Systemwide | Cxxx-NCR-000028 | NCR | Cable abrasion to interface cable within B1 cubicle |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-05-07 | 2017-05-25 16:19 | 18 | 2017-02-14 15:26 | Systems - Signalling | 500 |  | Manufacturing Defect | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Not Defined | Completed |  | While stripping the 25c PIM (p/no. B26649/1) cable it was noted that when removing the outer (grey) insulation, it sometimes sticks to the inner (black) cores and in some cases, takes off slitters of insulation from the cores.
| 05SY - Systemwide | Cxxx-NCR-000030 | NCR | Asset Labels |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-05-07 | 2017-05-01 08:44 | -6 | 2017-02-23 10:08 | Systems - Signalling | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Not Defined | Completed |  | No assets in the SER have asset labels affixed.
| 05SY - Systemwide | Cxxx-NCR-000031 | NCR | Asset Labels |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-05-07 | 2017-05-01 08:46 | -6 | 2017-02-23 10:05 | Systems - Signalling | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Not Defined | Completed |  | No assets in the SER have asset labels affixed.
| 05SY - Systemwide | Cxxx-NCR-000032 | NCR | Asset Labels |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-05-07 | 2017-05-01 08:49 | -6 | 2017-02-23 10:25 | Systems - Signalling | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Not Defined | Completed |  | No assets in the SER have asset labels affixed.
| 05SY - Systemwide | Cxxx-NCR-000033 | NCR | Asset Labels |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-05-07 | 2017-05-01 08:50 | -6 | 2017-02-23 10:24 | Systems - Signalling | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Not Defined | Completed |  | No assets in the SER have asset labels affixed.
| 05SY - Systemwide | Cxxx-NCR-000034 | NCR | Cable Installation Changes |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-05-07 | 2017-10-17 15:02 | 163 | 2017-02-27 17:10 | Systems - Signalling | 3000 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | Cables have been identified in Thames Tunnel as requiring change following a change in the AP/IP allocation plan. It is unclear if the impact of this change has been fully considered as per the __ Quality Plan.
| 05SY - Systemwide | Cxxx-NCR-000035 | NCR | Consideration of Design Impacts |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-05-07 | 2017-10-17 15:00 | 163 | 2017-03-02 09:39 | Systems - Signalling | 6000 |  | Supervision/Management | Rework | 3 (3-6k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | The contractor is not following the accepted Change Management Plan ref Cxxx-SIC-R2-GPS-CR001-50011. Example 1; As part of the development of the Signalling Principles __ are required to produce technical rules for operation of Crossrail S&CS including an NNTR which is the standard that defines the interface between the CBTC and ETCS. The NNTR was updated from versions 07 to 08 and then 09. Versions 07 to 08 changed the design in STM Isolated Mode to give DA. This was rejected by Bombardier and changed in version 09 to reflect comments changing DA to CS. Version 9 of the document was submitted by CCM 02486, 23-11-17. The IHA was submitted (expecting it to be final as per the meeting in December) on 07-02-17 via CCM 02742, however this did not reflect the latest version of the NNTTR and had DA not CS for the isolated mode in a specific failure analysis. Crossrail consider 2 months to be enough for the safety team to be aware of a design change and to include it in the subsequent safety analysis. Example 2; __ have been unable to demonstrate that their change management plan has been followed when assessing the impact of design changes e.g. Radio Access point numbering and consequential design changes. Cxxx- EWN-00276 refers which also requests evidence of Change board activities via meeting minutes.
| 05SY - Systemwide | Cxxx-NCR-000036 | NCR | SAG test specifications not submitted to CRL to support manufacturing ITP ‘s for __ & ATS products |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-04-20 | 2017-05-09 10:46 | 19 | 2017-03-17 15:25 | Systems - Signalling | 500 |  | Planning | Rework | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | __ Germany have not submitted test specifications to CRL for __ and ATS Test plans.
| 05SY - Systemwide | Cxxx-NCR-000037 | NCR | CWX __-R Materials not accepted by PM |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-05-07 | 2017-08-09 12:56 | 94 | 2017-03-21 10:10 | Systems - Signalling | 3000 |  | Material | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Lack of procedure | Completed |  | Installation works have commenced at Canary Wharf without accepted cable MCR. MCR Cxxx-SIC-R2-LRC-CR001-50125 submitted in CCM 0284 (28/02/17) details cables to be used however submission is unacceptable due to lack of product information and relevant certification . MCR submitted for acceptance to PM 28/02/17, __-R works commenced 08/03/17 7 days after submission.
| 05SY - Systemwide | Cxxx-NCR-000038 | NCR | Damaged surge arrestors screws |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-05-15 | 2017-08-17 14:17 | 94 | 2017-03-31 13:15 | Systems - Signalling | 500 |  | Damaged | Reject | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | The screw heads in surge arrestor base (part no. 2178030-1) has been damaged
| 05SY - Systemwide | Cxxx-NCR-000039 | NCR | Bookwiring Design Specification Rev. 5 requires updating |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-08-31 | 2017-08-31 12:12 | 0 | 2017-05-03 11:30 | Systems - Signalling | 500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | The Cxxx Book wiring Design Specification (Cxxx-SIC-R2-RSP-CR001-50081 Rev. 5) section 7.1.2 wording, needs to be updated to reflect crossrail's requirements to the relevant terminology within this section of the document.
| 05SY - Systemwide | Cxxx-NCR-000040 | NCR | CWX __-R - Failure to provide IRN prior to Energisation |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-05-29 | 2017-06-30 09:47 | 32 | 2017-05-15 09:10 | Systems - Signalling | 3000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | Further to Cxxx-SMC-0004, this NCR records the failure to provide an IRN prior to energising the __-R power systems as mandated in the contractors Work Information Volume 2B Section 28.6.3.1. The contractor is reminded that under Works Information Vol 2B Part 20.9 the contractor is obliged to demonstrate the works have been completed in accordance with the Works Information and shall produce records that provide clear evidence of conformance.
| 05SY - Systemwide | Cxxx-NCR-000041 | NCR | Canary Wharf UTX |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-06-06 | 2017-06-30 09:23 | 24 | 2017-05-23 14:56 | Systems - Signalling | 1000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | Access Point Cables and Axle counter cables have been run through UTX 18 on Westbound track and UTX 4 on East bound track prior to handover. Cables in question have no IRN and as such have not been handover to Cxxx. UTXs 4 and 18 have not been proved and therefore have not been handed over to Cxxx.
| 05SY - Systemwide | Cxxx-NCR-000042 | NCR | Canary Wharf Station cable dressing |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-06-06 | 2017-07-14 15:03 | 38 | 2017-05-23 16:04 | Systems - Signalling | 1000 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | Access Point cables and axle counter cables left unsupported and undressed at end of shift (see attached photo).
| 05SY - Systemwide | Cxxx-NCR-000043 | NCR | Work has commenced without an approved MCR in place |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-06-20 | 2017-10-10 13:54 | 112 | 2017-05-31 13:07 | Systems - Signalling | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Other management problem | Completed |  | Cxxx have raised concern that cable clips (12mm Fastway Flange clip) have been used without an approved MCR prior to installation at site.
| 05SY - Systemwide | Cxxx-NCR-000044 | NCR | Design Submissions not in the CMDL |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-06-22 | 2017-07-05 14:55 | 13 | 2017-06-08 16:01 | Systems - Signalling | 0 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | The following designs have recently been submitted without inclusion in the CMDL. Submission of Detailed Power Design - Abbeywood SER and __R v1.0 Submission of Cxxx Crossrail Signalling Power GRIP 5-8 Scheme Detailed Design - Whitechapel (Three Phase) V1.0 Submission of Cxxx Crossrail Power GRIP 5-8 Scheme Detailed Design - Farringdon (Single Phase) V1.0 Submission of Cxxx Crossrail Signalling Power GRIP 5-8 Scheme Detailed Design - Bond Street (Single Phase) V1.0 Submission of Cxxx Crossrail Signalling Power GRIP 5-8 Scheme Detailed Design - Paddington (Single Phase) V1.0
| 05SY - Systemwide | Cxxx-NCR-000045 | NCR | Cables run through none IRN'd UTX |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-06-29 | 2017-06-30 10:41 | 1 | 2017-06-15 09:52 | Systems - Signalling | 1000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | Cables shown run through E/B UTX, the UTX has not been proved and handover to Cxxx to use S09S08- EASTBOUND- PSC02 (AP0837- WWC_SER)  S09S10- EASTBOUND- PSC02 (WWC_SER- AP0903)  S09S08- EASTBOUND- PSC01 (AP0835- WWC_SER)  S09S10- EASTBOUND- PSC01 (WWC_SER- AP0901)  WWC_SER- OEA/OEB  WWC_SER-OEB/OEC  WWC_SER- OEC/OED  WWC_SER- OED/OEE  WWC_SER- OEE/OEF
| 05SY - Systemwide | Cxxx-NCR-000046 | NCR | No documented agreement in place with Cxxx to attach Antenna's to Stanchions |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-07-07 | 2017-10-10 15:18 | 95 | 2017-06-16 14:20 | Systems - Signalling | 1000 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | An antenna has been attached to the stanchion between Victoria Dock Portal and Connaught tunnel without a documented agreement with Cxxx
| 05SY - Systemwide | Cxxx-NCR-000047 | NCR | Termination of earth cables onto un IRN'd star plates |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-06-30 | 2017-08-18 15:01 | 49 | 2017-06-16 14:49 | Systems - Signalling | 2500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Earth cables have been run to and terminated onto un IRN'd star plates
| 05SY - Systemwide | Cxxx-NCR-000048 | NCR | The CMDL does not contain realistic document deliverable dates |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-09-14 | 2019-07-19 14:14 | 673 | 2017-06-16 14:51 | Systems - Signalling | 3000 |  | Planning | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Recent review of version 17 of the CMDL has highlighted that the document does not contain realistic document deliverable dates, to allow documents to be submitted in a timely manner and causes them to go overdue.
| 05SY - Systemwide | Cxxx-NCR-000049 | NCR | Installation of AP3319 and anntena |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-06-30 | 2017-07-14 15:11 | 14 | 2017-06-16 15:00 | Systems - Signalling | 2000 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Not Defined | Completed |  | AP3319 has been installed into a position which clashes with a LV power route. This had previously been identified 6 months prior to install. As such the AP now needs to be removed and reinstalled. In addition the antenna has been installed with no agreement in place between Cxxx and Cxxx.
| 05SY - Systemwide | Cxxx-NCR-000051 | NCR | Work has commenced without an approved design for Bond Street __R |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-07-25 | 2017-10-10 14:53 | 77 | 2017-06-23 09:07 | Systems - Signalling | 3000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Work has commenced at Bond street __R without an approved design (Cxxx-SIC-R2-RGN-Cxxx-50001) being in place.
| 05SY - Systemwide | Cxxx-NCR-000052 | NCR | Work has commenced without an approved design for Paddington __R |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-07-25 | 2017-10-11 13:19 | 78 | 2017-06-23 09:35 | Systems - Signalling | 3000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Work has commenced at Paddington without an approved design (Cxxx-SIC-R2-RGN-B071-50001) being in place.
| 05SY - Systemwide | Cxxx-NCR-000053 | NCR | Work has commenced without an approved design for Woolwich __R |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-07-25 | 2017-10-10 15:02 | 77 | 2017-06-23 09:45 | Systems - Signalling | 3000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Work has commenced at Woolwich __R without an approved design (Cxxx-SIC-R2-RGN-CR147-50001) being in place.
| 05SY - Systemwide | Cxxx-NCR-000055 | NCR | Work has commenced with Code 2 ITP on NR infastructure at Abbey Wood (NKL) |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-07-31 | 2017-09-25 12:57 | 56 | 2017-06-30 10:11 | Systems - Signalling | 3000 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | Work has commenced on NR infrastructure (NKL) at Abbey Wood with code 2 accepted Cable Installation (Crossrail Infrastructure) ITP and does include NR infrastructure cable details.
| 05SY - Systemwide | Cxxx-NCR-000056 | NCR | Installed Metal tie wraps with no MCR |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-08-18 | 2017-11-07 15:42 | 81 | 2017-07-21 10:56 | Systems - LV distributable/Aux Power | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | Surveillance was held in the __R at Canary Wharf Station and it was found that Sub main SWA cables had been installed and held in place via metal tie wraps. The Contractor confirmed that there was no MCR in place for the metal tie wraps.
| 05SY - Systemwide | Cxxx-NCR-000060 | NCR | Metal ty-wraps used in __R without an approved MCR at Woolwich |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-08-24 | 2017-10-23 12:49 | 60 | 2017-07-21 12:30 | Systems - Signalling | 1000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | Metal ty-wraps have been used to secure cables without an approved MCR in place.
| 05SY - Systemwide | Cxxx-NCR-000061 | NCR | 40A fuses fitted in UPS panel at Canary Wharf |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-08-24 | 2017-10-11 13:38 | 48 | 2017-07-25 09:37 | Systems - Signalling | 1000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | 40A fuses have been fitted in the non maintained UPS panel (sections A3 and A4), the current design show 32A fuses in these positions
| 05SY - Systemwide | Cxxx-NCR-000062 | NCR | Document update / checking |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-10-25 | 2017-11-10 11:23 | 16 | 2017-07-25 12:57 | Systems - Signalling | 6000 |  | Design | Repair | 3 (3-6k) | Complete | Management Problem - Inadequate administrative control | Completed |  | There is an increasing number of submissions that have not been checked / updated in accordance with the Cxxx Quality Plan. This includes: References not being updated to the correct versions in particular for design / safety documentation where the version number is important. E.G. the __ SSRS only references design freeze 1 drawings. Documents submitted with obvious quality failings eg 2 front pages.
| 05SY - Systemwide | Cxxx-NCR-000063 | NCR | Substandard Bracketry received from __. |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-09-04 | 2017-10-09 07:42 | 35 | 2017-08-01 10:22 | Systems - Signalling | 3000 |  | Damaged | Reject | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper handling of material | Completed |  | Recent delivery from __ of Bracketry was found to contain three substandard brackets: 1) 1 off E26612/1 (AP Housing Roller Block Mounting) - Exposed area of base material, no galvanisation protection. 2) 1 off E26612/1 (AP Housing Roller Block Mounting) - The base mounting plate appears to be damaged. 3) 1 off E26636/1 Marker Board Tunnel Wall Bracket) - The base mounting plate appears to be damaged.
| 05SY - Systemwide | Cxxx-NCR-000064 | NCR | Overdue IRN documentation at Code 2 for Woolwich and Paddington __Rs |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-10-24 | 2018-01-05 16:06 | 73 | 2017-10-03 12:37 | Systems - Signalling | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Both Woolwich (S-10 Woolwich __R IRN - Cxxx-SIC-R2-RGN-B071-50003) and Paddington (S-2 PDX __R - Cxxx-SIC-R2-RGN-B071-50003) IRN’s are currently Code 2 and passed their acceptance date in eB.
| 05SY - Systemwide | Cxxx-NCR-000065 | NCR | Design |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-10-19 | 2017-11-20 10:31 | 32 | 2017-09-07 13:34 | Systems - Signalling | 3000 |  | Design | Repair | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | RCC Bookwiring Cxxx-SIC-R2-DDE-CR001-17001 rev CC on site not accepted by CRL
| 05SY - Systemwide | Cxxx-NCR-000066 | NCR | Design |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-10-19 | 2019-06-28 10:47 | 617 | 2017-09-07 13:41 | Systems - Signalling | 10000 |  | Design | Repair | 2 (6-60k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | Concern over signatures for SAG elements of the Design incorporated into book wiring.
| 05SY - Systemwide | Cxxx-NCR-000067 | NCR | Design |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-10-19 | 2019-06-20 13:59 | 609 | 2017-09-07 13:45 | Systems - Signalling | 3000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Book of circuits document (ATS and DCS should not exist and needs to be incorporated within the book wiring.
| 05SY - Systemwide | Cxxx-NCR-000068 | NCR | NKL DESJ non conformance with Quality Plan |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-10-30 | 2017-11-16 10:06 | 17 | 2017-09-18 09:12 | Systems - Signalling | 30000 |  | System Defect | Rework | 2 (6-60k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | Further to the Contractor’s resubmission of the Re-submission of Design Engineering Safety Justification (DESJ) NKL Fringe V2 under the cover of Cxxx-CCM-03462 on 26th July 2017. The Project Manager has undertaken a technical review of the document and concluded the following: Not all hazards identified are applicable to the North __ Line, The description of the NKL is out of context and does not refer to the correct drawing, it refers to the Crossrail PWHR and not the Cxxx Hazard Record, Section 4 refers to Westbourne Park and it does not describe all the work done by your design team in conjunction with __ to ensure the interface is safe. The level of inconsistencies detailed above indicates that the document has clearly not been produced in line with the Quality Plan. The document has either not been reviewed or not been produced by competent resources, or both. Further to the Project Manager’s findings detailed above the RAB-C chairman stated “Of the 105 pages, I would say around 5 are specific to the NKL interface and these are quite badly written and confusing. There is also a spurious section referring to Westbourne Park
| 05SY - Systemwide | Cxxx-NCR-000070 | NCR | Material Type for Disconnection Boxes Installed Between PLU-ABW Not In Alignment With Accepted Drawing Pack, Causing Potential for Bi-metallic Corrosion. |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-11-30 | 2019-05-07 15:50 | 523 | 2017-09-21 10:55 | Systems - Signalling | 10000 |  | Material | Use As-Is | 2 (6-60k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | A planned Crossrail surveillance was undertaken on 8th August 2017 to look at onsite installation of Trackside Equipment between Plumstead Portal and Abbey Wood Station. During the site visit the Radio Access Point (RAP) cabinets and disconnection boxes were inspected. On review it was found that both the disconnection boxes and cabinets were manufactured of stainless steel whilst the supporting steelwork installed by Cxxx was of galvanised steel. The contact surfaces between the dis-similar metals contained no insulating washer (photos attached). This is a cause for concern and a potential for bi-metallic corrosion. On checking the mounting drawing pack, Cxxx-SIC-R2-DWG-CR001-50059 (Rev 1), which is referenced in the current RIR, it was found that the disconnection boxes are required to be of galvanised material not stainless steel (E26610). The drawings do not note the metal type for the RAP cabinets. Based on this, the current installation of the boxes does not align with that detailed in the current and accepted drawing pack. Furthermore, following multiple post surveillance requests, no information was provided concerning the dis-similar metal contact; this being acceptance of such contact surfaces, considerations concerning corrosivity environment categories and the stainless steel interface with Cxxx galvanised installation (what is the galvanised thickness and will it meet design life?). Moreover, the material type for the RAP cabinets was not provided.
| 05SY - Systemwide | Cxxx-NCR-000071 | NCR | GRP trunking supports connected to the existing Ductwork system in the SER at CWS |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-07-12 | 2019-07-04 10:17 | -8 | 2017-10-02 08:53 | Systems - Other | 6000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | A planned Crossrail surveillance was carried out to look at installation of CMS and Signalling Equipment in the SER and __R at Canary Wharf Station (CWS). On inspection of the installation in the SER it was found that GRP trunking supports had been connected to the existing ductwork system (see photos). __ were requested to provide evidence of co-ordination with Cxxx (responsible for CWS) and design load calculations to assure that the ductwork fixings and supports would be sufficient to hold the additional loads being parted by the Cxxx CMS and cables. No evidence was provided to confirm this installation. This poses a potential risk of failure until verified otherwise. The Design Coordination Report for SER/__R at Canary Wharf Station (Cxxx-SIC-R2-RGN-CR143-50002) mentions the design coordination of CMS in the SER, however does not detail that it is to be supported from the existing ductwork system. It refers to routes being provided.
| 05SY - Systemwide | Cxxx-NCR-000072 | NCR | Engineering Safety Justification (ESJ) |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-10-31 | 2018-02-21 16:02 | 113 | 2017-10-05 16:05 | Systems - Systems Engineering General | 3000 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | Further to the Contractor’s submission of the Engineering Safety Justification (ESJ) V1 under the cover of Cxxx-CCM-03741 on 7th September 2017. The Project Manager has undertaken a technical review of the document and concluded the following: 1) This ESJ shall cover the right hand side of the V lifecycle as well as parts of the design not cover by the DESJ. The scope is not clear eg if Plumstead or Yellow plant are covered, or if the design specifics for westbound park have been considered. 2) The conditions are not aligned with the design The issues detailed above indicate that the document does not match the design and has not had a sufficient review from the design team despite the requirements of the quality plan.
| 05SY - Systemwide | Cxxx-NCR-000073 | NCR | Pull Testing of fixings installed in the SER and __R and CWS |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-12-15 | 2018-09-13 09:57 | 272 | 2017-10-06 04:17 | Systems - Signalling | 3000 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | A planned Crossrail surveillance was carried out to look at installation of CMS and Signalling Equipment in the SER and __R at Canary Wharf Station (CWS). Testing of the __ chemical anchors was discussed for both the SER and __R. Pull test records were requested for fixings installed in both the SER and __R. It was stated that testing had been completed in the SER, however may not have been completed in the __R. Records were requested as evidence however were not made available. The accepted Method Statement ‘E&P Installation Works SER, __R Canary Wharf’ Cxxx-SIC-R2-GMS-CR143-50002 defines a requirement for Pull Testing, in particular the Risk Assessment section ‘L COSHH’ which requires 25% pull testing of fixings for each asset covering both the SER and __R as a control measure to mitigate the risk of working with the injectable resin. After further discussions with __ and multiple requests for records as evidence to show that this requirement had been met, none could be provided. It is not known how many fixings have been installed and how many results exist; including information on those who have undertaken this testing and their associated competences. It was agreed that the NCR be raised to capture and reference appropriately the non-conformance to ensure that either a) the records are sourced to confirm acceptable testing and compliance with the load calculations, b) the required testing is completed at the set frequency if not done so, or c) justification is made for the installation use as is.
| 05SY - Systemwide | Cxxx-NCR-000074 | NCR | PCC for WWC __R not submitted prior to SER energistaion |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-12-25 | 2018-05-02 15:24 | 128 | 2017-10-06 08:58 | Systems - Signalling | 3000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Following site inspection of WWC __-R and subsequent agreement of outstanding items __ have not submitted the PCC for this installation. __ have since energised the SER which should be conditional on acceptance off the PCC for __R.
| 05SY - Systemwide | Cxxx-NCR-000076 | NCR | Disconnection boxes have been installed that are not reflected in the book-wiring |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-11-09 | 2018-08-01 12:37 | 265 | 2017-10-12 12:35 | Systems - Signalling | 3000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | disconnection boxes being installed that are not reflected in the book-wiring Cxxx-SIC-R2-DWG-CR001-50022 . These are for 2 x axle counters installed in the Woolwich area HEL/OEA and OWA/HWK that are not reflected in the book-wiring Cxxx-SIC-R2-DWG-CR001-50022. The two DBs are required to bond the XQZ cable screen to Earth at 2Km intervals.
| 05SY - Systemwide | Cxxx-NCR-000078 | NCR | 2 PIN sockets in Equipment cubicles |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-12-31 | 2018-10-15 10:10 | 288 | 2017-11-03 09:53 | Systems - Signalling | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | Equipment cubicles at the RCC, CWX contain power sockets for use by the maintainer of the equipment. These sockets have been provided as a European style 2 PIN socket.
| 05SY - Systemwide | Cxxx-NCR-000079 | NCR | Rooms and the Trace energised without approved EMC Control Plan |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-02-01 | 2018-02-12 15:51 | 11 | 2017-11-03 16:06 | Systems - Signalling | 3000 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | Crossrail have advised that the EMC Control Plan (Cxxx-SIC-R2-STP-CR001-50107) is currently Code 3 and rooms and the Trace have been energised without approved EMC plan in place.
| 05SY - Systemwide | Cxxx-NCR-000080 | NCR | Abbeywood Antenna mast brackets installed without approved design for mechanical fixing for the bracket |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-12-15 | 2019-05-01 09:56 | 502 | 2017-11-03 16:04 | Systems - Signalling | 3000 |  | Design | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Crossrail have reported that AP antenna mast brackets installed without approved design for mechanical fixing for the bracket.
| 05SY - Systemwide | Cxxx-NCR-000081 | NCR | Custom House Cables into SER not adequately supported below WTR |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-11-17 | 2019-02-17 16:44 | 457 | 2017-11-03 16:05 | Systems - Signalling | 3000 |  | Incomplete Works | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | During site visit at Custom House it was noted that the cable at the bottom of the WTR (LHS rack, incoming cables from the floor below to the left) has been ty-wrapped on to existing cable and should have been supported from below as it has not been fixed on to the tray.
| 05SY - Systemwide | Cxxx-NCR-000082 | NCR | Equipment damage to Disconnextion Box cables |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-12-25 | 2018-03-16 16:12 | 81 | 2017-11-07 15:32 | Systems - Signalling | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Not Defined | Completed |  | Various terminated cables in Disconnection Boxes (1347A WM/WC DB, 1347A (SO) WC (F), 1347A (SO) WC (R), 1347A WM/WC DB, 1347A(SO) WC (F), 1347A (SO) WC (R)) have been found to have been bent back beyond the permitted bending radius on the trace, this is believed to have occurred during concrete infilling activities.
| 05SY - Systemwide | Cxxx-NCR-000083 | NCR | Damaged Balise |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-12-25 | 2018-01-03 10:47 | 9 | 2017-11-07 15:35 | Systems - Signalling | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | A Balise (FBCUS 032) has been found impaired by contamination of concrete and has had the shuttering placed around the Balise. This is believed to have occurred during concrete infilling activities.
| 05SY - Systemwide | Cxxx-NCR-000084 | NCR | Equipment damage to Axle Counter hoses |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-12-25 | 2018-03-16 16:14 | 81 | 2017-11-07 15:38 | Systems - Signalling | 3000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Various Axle counter (North Woolwich Portal to Victoria Dock Portal, East Bound SE17150 to SE17775 - HEE/HEF, HEF/HEG, HEG/ HEH) hose cables have been crushed by the concrete shuttering timber; this is believed to have occurred during concrete infilling activities.
| 05SY - Systemwide | Cxxx-NCR-000085 | NCR | Custom House Antenna mast brackets installed without approved design for mechanical fixing for the bracket |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-12-14 | 2019-05-01 10:00 | 138 | 2017-11-09 10:17 | Systems - Signalling | 3000 |  | Design | Repair | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Crossrail have reported that AP antenna mast brackets installed without approved design for mechanical fixing for the bracket.
| 05SY - Systemwide | Cxxx-NCR-000086 | NCR | Cables not installed in line with __ guidelines |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-12-19 | 2018-08-01 12:47 | 225 | 2017-12-05 11:38 | Electrical - Cable Management | 3000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Insufficient information made available to the worker. | Completed |  | it was picked up on a site visit to Custom House trackside area that cables have not been run in accordance within __ own guidelines, in that separation between cables does meet defined requirements . Cxxx-SIC-R2-RSP-CR001-50136 Scope Transfer Cabling Activities Cxxx-SIC-R2-STP-CR001-50017 EMC Management Plan Cxxx-SIC-R2-STP-CR001-50018 EMC Management Plan
| 05SY - Systemwide | Cxxx-NCR-000088 | NCR | AP Power cable installation does not match design |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-04-13 | 2018-04-03 14:38 | -10 | 2018-01-23 16:37 | Systems - Signalling | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Design States: IP allocation plan 2.1.4 states diverse routing of cable “This section provides the rationale for the selected diverse routing of cables.” Cxxx-CCM-02285 states “Diversity of route We wish to record that route diversity has also been considered in our design but choice is limited due to the framework design of CMS and physical restrictions in the Connaught Tunnel and SE Spur. __ have diversified the routes as far as reasonably practicable. “ Both AP Power cables in Zones 1 and 2 are installed in tray 4 and not the diverse tray by installation in tray 4 and 7.
| 05SY - Systemwide | Cxxx-NCR-000089 | NCR | Whitechapel cable damage outside SER |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-02-10 | 2018-09-13 10:10 | 215 | 2018-01-26 10:54 | Systems - Signalling | 2000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper handling of material | Completed |  | Cable damage to SWA armoured cable sheath has been found during the cable pulling activity along the cable route, prior to entering the SER.
| 05SY - Systemwide | Cxxx-NCR-000090 | NCR | Westbourne Park PSP paint damage |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-02-09 | 2018-06-28 12:29 | 139 | 2018-01-26 11:29 | Systems - Signalling | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Not Defined | Completed |  | Paint damage has been noted to the bottom of the door frame and around the lifting eye points.
| 05SY - Systemwide | Cxxx-NCR-000091 | NCR | An E&P power cable incorrect MCR documented |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-03-16 | 2019-03-20 14:53 | 369 | 2018-01-26 12:14 | Systems - Signalling | 1000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | An E&P power cable MCR needs to be updated to reflect the current supplied cable used, i.e. Drakka vs. AEI
| 05SY - Systemwide | Cxxx-NCR-000092 | NCR | No MCR for Point Lock Dectection Cable |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-03-02 | 2018-12-03 09:21 | 276 | 2018-01-31 11:32 | Systems - Signalling | 3000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | No MCR in place for use of Point Lock detection cables (part no. 088/002455)
| 05SY - Systemwide | Cxxx-NCR-000093 | NCR | Westrace I/O Issues - New PM Data Upgrade |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-03-16 | 2018-03-13 15:14 | -3 | 2018-02-05 15:14 | Systems - Signalling | 1000 |  | Testing and Commissioning | Repair | 4 (0.5-3k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | The new PM data at Romford RCC did not work as planned highlighting a requirement to upgrade the Westrace PM. According to the ICS 10.3 PM installation details; PM version should be: CED 6/4 PDI E26131/3 version G or higher. PMs at RCC are E26131/3 version D. When carrying out ICS 10.3 download/upload the PM Installation Check form came through ok but the comparison report showed the “Installation Comparison Complete: Differences Found” error. The upgraded Westrace PM (version G) are required to be installed and all I/Os in zone 1 will need to be tested.
| 05SY - Systemwide | Cxxx-NCR-000094 | NCR | Water Ingress Found in AP3328 in Connaught tunnel |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-04-30 | 2019-07-17 14:16 | 78 | 2018-02-14 10:39 | Systems - Signalling | 6000 |  | Damaged | Repair | 3 (3-6k) | Complete | External Phenomenon - Weather or ambient condition | Completed |  | It was reported via email on 30/01/18 by __ (Site Engineer, Signalling Systemwide Cxxx) that water ingress was found in the Access Point cabinet AP 3328 show in Connaught tunnel. Also, the cabinet’s lock was reported to be sticking and rusting. A copy of the email and the pictures are attached.
| 05SY - Systemwide | Cxxx-NCR-000095 | NCR | Abbeywood BSI not secure on WTR within SER |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-03-15 | 2018-12-03 09:29 | 263 | 2018-02-09 15:06 | Systems - Signalling | 3000 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | Test log CFX00364719 (attached) has been raised to highlight that some surge arrestor bases are not secure to the WTR DIN rail (position A2C-46,47; A3C-19,20; A3D-5, 6,14,15) and there seems to be no pattern as to why this is occurring.
| 05SY - Systemwide | Cxxx-NCR-000096 | NCR | WBP PSP Battery Room Comms Battery Stand fixed partially blocking the HVAC Vent; no change control for room changes |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-03-21 | 2018-05-03 13:35 | 43 | 2018-02-21 05:37 | Systems - Systems Engineering General | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | A planned Crossrail surveillance was undertaken on 19th February 2018. This looked at installation of the PSP and REB at Westbourne Park. During the site visit the Battery Room was checked. On review the following was found: - Equipment in the room had been installed differently to that shown in the ‘WBP PSP Equipment Layout Drawing’ (AGHE-728-WBP-6.7-EL-LAY-001) located in ‘Detailed Design – WBP PSP’ Cxxx-SIC-R2-RGN-CR076-50001 at Rev 1 Code 2. This had been done so with no documented evidence of change control coordination with KPHK designer AGHE or coordination with __. - A Comms Battery Stand had been positioned and fixed covering approx. 1/3rd of the HVAC Vent (see photo) where __ Design Drawing 14784-1-1 Issue B shows a min 50mm gap between the HVAC system and any equipment. Blocking the HVAC vent will restrict its operational capabilities which could potentially affect the equipment inside the room. Installation in its current state will need design validation, or the cabinets will require reworking to provide the minimum distance from the HVAC system (to be confirmed by AGHE).
| 05SY - Systemwide | Cxxx-NCR-000098 | NCR | Split duct with the cables in it from the PSP to the REB were found to have been put in on the wrong side of the stansion at Westbourne Park |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-04-13 | 2018-06-20 10:12 | 68 | 2018-03-02 10:50 | Systems - Signalling | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Insufficient information made available to the worker. | Completed |  | It was reported by CRL Site Engineer Nigel Denyer on 27/02/18 that split duct with the cables in it from the PSP to the REB were found to have been put in on the wrong side of the stansion at Westbourne Park.
| 05SY - Systemwide | Cxxx-NCR-000099 | NCR | Damaged cable found at Abbey Wood on 21/02/18 |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-04-05 | 2018-07-26 08:26 | 112 | 2018-03-06 14:48 | Systems - Signalling | 3000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | It was reported by Crossrail on 21/02/18 via Observation no. CRL-OBS-20849: "A previously reported significantly damaged Cxxx __ signal cable that was coiled damaged at the EB westend UTX has now been installed through the UTX along the CRL platform and across to the SER, attached pictures show the damaged cable from pit to first westend EB CRL platform cable pit and cable number, the problem being that this cable could cause damage to other system cables. "
| 05SY - Systemwide | Cxxx-NCR-000100 | NCR | Bond Street __R - Failure to provide accepted IRN prior to conducting SAT |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-04-22 | 2018-07-19 08:56 | 88 | 2018-03-19 15:33 | Systems - Signalling | 3000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate resources | Completed |  | This NCR has been raised to capture that the submitted IRN for Bond Street __R to CRL has not been accepted prior to conducting the Site Acceptance Testing.
| 05SY - Systemwide | Cxxx-NCR-000101 | NCR | Radio APs failed in Zone 1 during Dynamic Testing |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-07-27 | 2019-04-03 12:49 | 250 | 2018-03-27 10:25 | Systems - Signalling | 10000 |  | Testing and Commissioning | Repair | 2 (6-60k) | Complete | Verification Problems - Inspection points not adequate | Completed |  | It was reported by __ via email on 26/03/18 that Test have reported that 8 off radio APs in Zone 1 are faulty or failed.
| 05SY - Systemwide | Cxxx-NCR-000102 | NCR | No evidence provided to confirm compliance for WBP PSP/REB HVAC Units grey coating which has been installed against the PSP/REB olive green coating |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-04-26 | 2018-12-03 15:45 | 221 | 2018-03-29 13:51 | Systems - Signalling | 3000 |  | Design | Repair | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | A planned Crossrail surveillance was undertaken on 19th February 2018. This looked at installation of the PSP and REB at Westbourne Park, including the HVAC Units. During the site visit it was observed that the PSP/REB __ Containers had an external olive green paint coating colour. This aligned with __ Design Drawing 14784-1-1. In addition it was observed that the HVAC Units had an external grey paint coating colour. __ were requested (within the Exit Note) to provide the design specification which referred to this grey colour for the HVAC Units, with particular reference made to the grey on green arrangement. Following email communication, no design or specification evidence could be provided which documented the HVAC colour requirements, in order for the installation to be confirmed as compliant as part of the surveillance. Informal email correspondence from __ noted to a requirement for the HVAC Units to be green in colour not grey, however no design requirement could be provided to confirm this. Until this is produced, this installation of grey coated HVAC Units installed on olive green __ Containers (PSP/REB) cannot be confirmed as compliant. Works Information Part 29 defines the requirements for Contractor design, including requirements for the control of records to provide evidence of conformity, which in this case has been omitted.
| 05SY - Systemwide | Cxxx-NCR-000104 | NCR | The Contractor has not been able to demonstrate a robust RF design and test regime for the __ Radio System |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-05-03 | 2019-11-15 13:34 | 561 | 2018-04-19 09:28 | Systems - Signalling | 5000 |  | Design | Use As-Is | 3 (3-6k) | Complete | Design Problem - Not Defined | Completed |  | Further to Cxxx-EWN-00453, dated 08/01/18; Cxxx-PMC-3064, dated 18/12/17 and Cxxx-PMC-03752 dated 22/03/18 the Supervisor is concerned that the Contractor has not been able to demonstrate a robust RF design and test regime for the __ Radio System.
| 05SY - Systemwide | Cxxx-NCR-000105 | NCR | FBCUS040 Rmoved from site post IRN |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-12-21 | 2019-06-11 15:05 | 172 | 2018-04-25 11:45 | Systems - Signalling | 5000 |  | Testing and Commissioning | Repair | 3 (3-6k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | FBCUS040 Removed from site post IRN
| 05SY - Systemwide | Cxxx-NCR-000106 | NCR | GE Fibre cable damage on drum |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-05-31 | 2018-08-21 14:01 | 82 | 2018-04-27 14:28 | Systems - Signalling | 3000 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Site team have reported that during a fibre cable pulling activity on the GEML (@ 4.5mp on the down main LTN1), a drum nail head was found to have damaged the cable sheath with about 600m left on the drum (R388349/ 002) remaining to pulled off, see attached photo's.
| 05SY - Systemwide | Cxxx-NCR-000107 | NCR | NR Interface wiring system tested at RCC SER without an IRN |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-07-13 | 2019-03-08 12:46 | 238 | 2018-04-26 13:27 | Systems - Signalling | 3000 |  | Testing and Commissioning | Repair | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | IRN for RCC SER Part A was signed off on 07/09/17. At that time there were there were three exclusions agreed with the IRN, which were: 1> NR Interface wiring. 2> Emergency Alarm System. 3> Connections NR business systems. These three items were to be included in IRN part B for RCC SER. However IRN part B was not signed off and testing was carried out on NR Interface wiring system in April-18.
| 05SY - Systemwide | Cxxx-NCR-000108 | NCR | __ Cxxx have not been using the DRCAS eB database to recorded any product failures |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-07-06 | 2018-07-12 12:41 | 6 | 2018-05-01 11:04 | Systems - Signalling | 3000 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | __ Cxxx have not been using the DRCAS eB database to recorded any product failures as of 01/05/18; when there is evidence of certain product failures which should have been reported and recorded in DRCAS database. This is a non-adherence to the requi
| 05SY - Systemwide | Cxxx-NCR-000109 | NCR | High Impedance at __R MCCB ( WHX and others) |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-02-28 | 2019-08-08 15:48 | 526 | 2018-05-21 15:00 | Systems - Signalling | 60000 |  | System Defect | Repair | 2 (6-60k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Testing carried out by __ as Duty Holder at Whitechapel Station has revealed high impedance values which has indicated that the MCCB in the __-R power distribution panel may not rated correctly. Subsequently all radio access point feeds have been isolated and the radio system APs are not communicating. The __ testing regime has not identified this issue and it has been brought to their attention by a third party. (Cable testing at 2.1 completed prior to IRN was either incomplete or did not adequately verify/ validate the design.)
| 05SY - Systemwide | Cxxx-NCR-000110 | NCR | Westbourne Park Damaged Battery Stand Panel |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-06-08 | 2018-11-22 11:20 | 167 | 2018-05-25 10:20 | Systems - Signalling | 2000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper handling of material | Completed |  | The battery stand panel in the Westbourne Park PSP has a dent in it.
| 05SY - Systemwide | Cxxx-NCR-000111 | NCR | Damaged Axle Counter BEA/BEB |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-07-11 | 2018-10-03 11:55 | 84 | 2018-06-07 10:43 | Systems - Signalling | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | External Phenomenon - Not Defined | Completed |  | Test team report that axle counter BEA/BEB has been damaged.
| 05SY - Systemwide | Cxxx-NCR-000112 | NCR | Zone 3 AP0612 requires remedial work |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-09-14 | 2018-09-18 09:37 | 4 | 2018-06-07 10:43 | Systems - Signalling | 1000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | External Phenomenon - Not Defined | Completed |  | Test team have reported that AP 0612 (WB chainage 4162) will require remedial work to address fibre cables which appear to have been fixed down and potentially exceeds the bend radius
| 05SY - Systemwide | Cxxx-NCR-000114 | NCR | Cable pulling at Bonmd Street station revealed that some access point power cables were short |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-08-31 | 2019-06-28 12:21 | 301 | 2018-06-07 11:47 | Systems - Signalling | 6000 |  | Design | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | Installation identified short access point power cables while pulling cables from trackside UTX to the SER at Bond Street station.
| 05SY - Systemwide | Cxxx-NCR-000115 | NCR | Cable pulling at Paddington station revealed that some axle counter cables were short |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-08-31 | 2018-10-03 11:58 | 33 | 2018-06-07 12:07 | Systems - Signalling | 3000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Cable pulling at Paddington station revealed that some axle counter cables were short.
| 05SY - Systemwide | Cxxx-NCR-000116 | NCR | Bracketary has been manufactured without an approved MCR in place |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-09-21 | 2018-12-03 13:09 | 73 | 2018-06-07 13:39 | Systems - Signalling | 2000 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | New mounting brackets for NR fringes (GEML & GWML) have been produced, however the current MCR (Cxxx-SIC-R2-LRC-CR001-50153) is code 3.
| 05SY - Systemwide | Cxxx-NCR-000117 | NCR | Bracketary has been produced without an approved ITP |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-10-31 | 2018-11-07 12:50 | 7 | 2018-06-07 13:56 | Systems - Signalling | 1500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | New mounting brackets for NR fringes (GEML & GWML) have been produced, however the current ITP (Cxxx-SIC-R2-ITP-CR001-50049, Rev. 2, code 1) does not include the new parts E26685/1, E26685/2, E26684/1 manufactured
| 05SY - Systemwide | Cxxx-NCR-000118 | NCR | Plumstead PSP Panel has been produced without an approved ITP |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-10-31 | 2018-11-22 14:40 | 22 | 2018-06-07 14:09 | Systems - Signalling | 1000 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Work has commenced on manufacturing of Plumstead PSP Panel with a code 2 ITP (Cxxx-SIC-R2-ITP-CR148-50001, Rev. 3) in place.
| 05SY - Systemwide | Cxxx-NCR-000119 | NCR | Two MCRs were assigned code 2 in May-17 and Sep-17 by CRL, but the responses were found to be still outstanding by CRL in Jun-18 |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-07-08 | 2019-05-08 14:06 | 304 | 2018-06-08 09:45 | Systems - Signalling | 3000 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | Following a review of the MCRS, triggered by another NCR (NCR-91), CRL identified that there were outstanding responses on eB for the following MCRs: __ GLRE Fibre Optic Cable - Cxxx-SIC-R2-LRC-CR001-50038; code 2 on 19/05/17 Electrical Ancillary Equipment Cxxx-SIC-R2-LRC-CR001-50140 code 2 on 19/09/17 Given responses were approaching or over 12 months old, this NCR has been raised to capture the use on unaccepted materials.
| 05SY - Systemwide | Cxxx-NCR-000120 | NCR | Cable pulling at Westbourne Park highlighted a cable defect |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-08-10 | 2018-08-21 13:54 | 11 | 2018-06-14 07:58 | Systems - Signalling | 3000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Installation team have reported that during cable pulling activity at Westbourne Park on a drum of 2core 10mm SWA, a cable defect (see attached photo) was discovered and prevented the activity from being completed.
| 05SY - Systemwide | Cxxx-NCR-000121 | NCR | Incorrectly dressed cable in FOSE at Whitechapel |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-09-19 | 2019-02-06 15:56 | 140 | 2018-07-17 14:41 | Systems - Signalling | 3000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Installation team have reported that Fibre cable S14S92-Eastbound Track-FOC01 has been incorrectly spliced in FOSE 1401 and needs to be replaced with the correct cable (Fibre cable S31S90-Eastbound Track-FOC01) which requires to be spliced in FOSE 1401 instead.
| 05SY - Systemwide | Cxxx-NCR-000122 | NCR | Cxxx-EWN-03563 - Exposed Earth Cable Bond |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-08-31 | 2018-10-15 10:12 | 45 | 2018-07-30 16:07 | Systems - Signalling | 1000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | __jv's has issued Cxxx-EWN-03563 (attached) in relation to the following issue. During Cxxx (__jv's) daily inspections __jv’s Quality Team have noticed non-compliant Earthing and Bonding (E&B) works completed by other CXXX contracts to __jv assets that have already under gone the IRN process. __jv provide the following record of location where unauthorised E&B have been discovered: Cxxx - AP Cabinet ch5667 TCR to FIS WB - exposed earth cable bond. Photo 1 and 2
| 05SY - Systemwide | Cxxx-NCR-000123 | NCR | Damaged cables were found by CRL on CMS pre IRN at east end of Farringdon on west bound. |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-12-21 | 2019-06-20 14:32 | 181 | 2018-07-27 09:34 | Systems - Signalling | 3000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | It was notified by __ (CRL) via email on 27/07/18, that he found damaged cable (26,7,18) on CMS pre IRN. Location was east end of FAR on west bound (photos attached). John also reported that there was no 2nd CMS and the use of wrong trays (see attached email). Later, on 02/08, further issues were reported by __, which are detailed below: - Eastbound FEA/FEB cable is damaged, photo suggest CMS has been crushed. - Eastbound THE/TEA needs to be re-dressed ( its in the wrong tray). - West bound FWC/FWD cable needs to be replaced ( damaged area has been taped). - AP1016 power cable has been damaged. - Another AP and fibre cable have been damaged but are not labeled. (All photos are attached to the NCR)
| 05SY - Systemwide | Cxxx-NCR-000124 | NCR | Plumstead PSP HVAC units grey coating which has been installed against the PSP olive green coating, no evidence provided to confirm colour compliance |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-09-05 | 2018-12-07 14:33 | 93 | 2018-08-02 13:18 | Systems - Signalling | 3000 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | During site visit to __'s PHK to witness in XPG PSP integration test, it was noted that PSP __ container had an external olive green paint coating colour. It was observed that the HVAC Units had an external grey paint coating colour. No design or specification evidence could be provided which documented the HVAC colour requirements, in order for the installation to be confirmed as compliant as part of the visit. Until this is produced, this installation of grey coated HVAC Units installed on olive green __ Containers (PSP/REB) cannot be confirmed as compliant. Similar issue has been found on XWN PSP and raised on NCR Cxxx-NCR-102 which is currently open at the time of the above finding.
| 05SY - Systemwide | Cxxx-NCR-000125 | NCR | NR GEML - Acess Points have been powered up without IRN sign-off |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-09-08 | 2018-12-18 14:06 | 101 | 2018-08-05 16:08 | Systems - Signalling | 3000 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | Site visit (from Pudding Mill Lane to Stratford NR fringe) highlighted that the AP's appear to have been powered up and without an IRN in place to support energisation of assets.
| 05SY - Systemwide | Cxxx-NCR-000126 | NCR | Unmitiagted use of FGT cable in Tunnel sections |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-11-23 | 2018-12-18 13:40 | 25 | 2018-08-06 10:27 | Systems - Signalling | 3000 |  | Incorrect Installation | Reject | 4 (0.5-3k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | Agreed temporary solution at the __ interface at Pudding Mill Lane has been installed with the agreed mitigation.( see attached photos) FGT cable is not accepted or approved for use in tunnel sections and therefore any risks associated with using this cable, even in a temporary arrangement, need to managed. The accepted mitigation of Fire fly Blanket has not been provided. ( see attached email) In the event of fire the FGT cable presents a significant risk to the health and safety of those required to access the tunnel.
| 05SY - Systemwide | Cxxx-NCR-000127 | NCR | Cable running at Transition from NR to Abbey Wood SER and also at Abbey Wood SER was found to be not to the required standard |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-09-15 | 2019-10-22 10:02 | 402 | 2018-08-16 10:06 | Systems - Signalling | 10000 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During a site inspection on 14/08/18, __ (CRL Site Engineer) found below issues: Transition from NR to ABW SER: Cables were found to be inadequately supported and the weight of cables had buckled the __ fence.
| 05SY - Systemwide | Cxxx-NCR-000128 | NCR | Work commenced and signals were sighted ahead of the signal sighting committee being in place on GEML and GWML NR fringes |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-11-30 | 2018-11-07 12:54 | -23 | 2018-09-25 13:04 | Systems - Signalling | 3000 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | Signal sighting took place outside the SSC on GEML and GWML NR fringes. This process was undertaken independently to push forward the programme. Notwithstanding this, __ did not undertake a competency check and the whole process did not include all the necessary stakeholders i.e. NR, Operation etc.
| 05SY - Systemwide | Cxxx-NCR-000129 | NCR | Fibre optic cables was found to have been raised to the above tray and secured with a strained loop above the AP assets, at Westbound from Farringdon to Tottenham Court Road |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-09-28 | 2018-10-01 15:07 | 3 | 2018-08-22 12:01 | Systems - Signalling | 1000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | External Phenomenon - Theft, tampering, sabotage, or vandalism | Completed |  | It was reported by __ (Cxxx Construction team member) that On 09/08/18, during works on installing cards and dongles in Access Points, __ Cxxx Construction team came across a 2nd incident regarding the fibre optic cables being raised to the above tray and secured with a strained loop above the Access Points assets, near the fibre optic joint muffler. This had been done recently as the Fibre Optic test and repair team had been present in this zone on 18/07/18, where the cables were secured on the tray correctly after testing and repair works carried out. Loops were present at the following Access Points: 0840 - 0832 - 0828 – 0824. A similar issue has previously been found at Westbound from Bond street Station to Tottenham Court Road; which was captured in NCR-112.
| 05SY - Systemwide | Cxxx-NCR-000130 | NCR | DITA equipment has been manufactured without an approved ITP |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-11-30 | 2019-02-19 13:32 | 81 | 2018-09-06 13:20 | Systems - Signalling | 3000 |  | Documentation and Records | Reject | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Work has commenced on manufacture of DITA equipment for NR fringes (GEML) without an approved ITP in place
| 05SY - Systemwide | Cxxx-NCR-000131 | NCR | DITA equipment has been manufactured without an approved Design |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-11-30 | 2020-02-10 13:30 | 437 | 2018-09-11 11:26 | Systems - Signalling | 3000 |  | Documentation and Records | Reject | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | Work has commenced on manufacture of DITA equipment for NR fringes (GEML) without an approved design in place
| 05SY - Systemwide | Cxxx-NCR-000132 | NCR | DITA equipment has been manufactured without an approved MCR |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-11-30 | 2019-06-17 15:00 | 199 | 2018-09-11 11:26 | Systems - Signage | 3000 |  | Documentation and Records | Reject | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Work has commenced on manufacture of DITA equipment for NR fringes (GEML) without an approved MCR in place
| 05SY - Systemwide | Cxxx-NCR-000133 | NCR | CRL-OBS-23091 - axle counters installed as per the Scheme Plan but the Scheme Plan did not take account of the position of the permanat RRAP |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-12-21 | 2019-10-10 14:41 | 293 | 2018-09-11 12:22 | Systems - Signalling | 6000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | CRL raised observation CRL-OBS-23091 on 21/06/18 stating: As part of Sign Sighting exercise undertaken on 21/06/18. It was noticed that axle counters HWK/OWA and HEL/OEA are installed in the location of the RRAP adjacent to Connaught East compound. These axle counters will need to be relocated outside of the RRAP area. This clash was also identified on a joint site visit (Cxxx and CRL) in January 18. No CFX log has been raised to capture the clash and remedial work has not been undertaken in the last 6 months.
| 05SY - Systemwide | Cxxx-NCR-000134 | NCR | CRL-OBS-22495 - Axle counters at the GEML interface at PML are not in the correct place leaving up to a 20m gap in train detection |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-10-11 | 2019-05-13 13:51 | 214 | 2018-09-11 12:30 | Systems - Signalling | 6000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | CRL raised observation CRL-OBS-22495 on 15/05/18, stating: Axle counters at the GEML interface at PML are not in the correct place leaving up to a 20m gap in train detection. This was originally identified in November 2017. CMS transitions to NR need to be completed.
| 05SY - Systemwide | Cxxx-NCR-000135 | NCR | XWN REB WRACE RCA designed contrary to application rules |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-09-27 | 2019-02-06 16:03 | 132 | 2018-09-13 09:07 | Systems - Signalling | 10000 |  | Design | Repair | 2 (6-60k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Number of modules designed exceeds __ own application rules
| 05SY - Systemwide | Cxxx-NCR-000136 | NCR | IXL Network Capacity issues |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-10-31 | 2020-11-12 09:48 | 12 | 2018-09-13 09:23 | Systems - Signalling | 10000 |  | System Defect | Repair | 2 (6-60k) | Complete | Design Problem - Not Defined | Completed |  | Persistent loss of point detection Emergency stop plungers and other functions inhibiting train running.
| 05SY - Systemwide | Cxxx-NCR-000137 | NCR | Damaged AP3319 at Custom House |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-12-14 | 2019-03-18 16:24 | 94 | 2018-09-14 11:30 | Systems - Signalling | 3000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Installation team have discovered a damaged AP (AP3319) on the trace which has been covered by ballast (photo attached) Previous discussions relating to AP3319 when installed and which has been moved on multiple occasions at the request of __ and has also been IRN'd. The works have been done without consultation with Cxxx Installation and without a WAD in place and this __ asset has not been adequately protected and has subsequently been covered it in ballast.
| 05SY - Systemwide | Cxxx-NCR-000138 | NCR | Non compliance related to limitation to 2 trains in a Ventilation section |  | Crossrail | PDP | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-06-28 | 2019-08-15 13:35 | 48 | 2018-09-20 16:13 | Systems - Signalling | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The Works information requires that the S&CS does not allow more than 2 trains in a Ventilation Section in the COS. Through tests and deeper understanding how the TGMT is design, it appears that there are a number of plausible scenarios the TGMT Design is non compliant with the requirement. See Reference document for details
| 05SY - Systemwide | Cxxx-NCR-000139 | NCR | Axle counter cables were found to be burst/split at VDP-CUS (Victoria Dock Portal - Custom House) Eastbound |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-11-27 | 2019-08-02 12:01 | 248 | 2018-09-28 13:46 | Systems - Signalling | 5000 |  | Damaged | Rework | 3 (3-6k) | Complete | External Phenomenon - Not Defined | Completed |  | It was reported by __ (CRL Field Engineer) on 28/09/18 that the outer sheaths of the axle counter cables were found to be burst/split at VDP-CUS (Victoria Dock Portal - Custom House) Eastbound. Cable appears to be the same one according to label scheme visible. The approximate locations was: CH.16765 Cable CR10m west of OHLE Mast XRA-16-661 The degradation of cables due to UV exposure was also observed, as a lot of them appear to have faded in the sun.
| 05SY - Systemwide | Cxxx-NCR-000140 | NCR | Balises were found to have been installed contrary to __ install manual, as they clashed with metal. |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-12-21 | 2019-09-10 09:25 | 263 | 2018-10-08 12:39 | Systems - Signalling | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | It was reported by __ (CRL Site Engineer) on 28/09/18 that balises were found to have been installed incorrectly, as they clashed with metal, at below locations at Tottenham Court and Paddington: WB - TCR-FBTCR06-CH4799.146 WB - PAD-FBPDX22-CH1530.799
| 05SY - Systemwide | Cxxx-NCR-000141 | NCR | AP earth bars bonded to incorrect traction earth bar |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-11-14 | 2019-07-15 08:57 | 243 | 2018-10-11 10:52 | Systems - Signalling | 3000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Previous Construction - Problems based on previous construction errors | Completed |  | Cxxx have advised (as per attachment) that the following AP earth bars have been bonded to the wrong traction earth bars and need to be addressed: Eastbound: Reference Chainage W/B Location Actual connection Connection Status DDA-10103/DDE-00007 -188 Westbourne Park TSP-WBP_178 1XT OK / Cxxx to confirm if connection at TSP-WBP_211 still needed DDA-10104/DDE-00011 276 Westbourne Park TSP-WBP-286 1XT OK if disconnection box bond DDA-10104/DDE-00012 403 Westbourne Park TSP-WBP-403-L 2XT OK if disconnection box bonds DDA-10121 6045 Tunnel (TOT - FAR) TSP-E/B- 6045-1b 2+1xT OK if disconnection box bond DDA-10123 6990 Farrington Station TSP-E/B-6990-1b 1XT Connection allocated changed on TSP-FDN-E/B-2b (Ch. 6921, closer to AP1103), Cxxx to confirm if they keep connection on TSP at ch. 6990. DDA-10133 9960 Tunnel (LIV - WHI) TSP-E/B-9960-1b 2XT Ok if disconnection box bonds DDA-10137 11335 Tunnel (WHI - STG) TSP-E/B-11335-1b 3xT Ok if disconnection box bonds Westbound: Reference Chainage W/B Location Actual connection Connection Status DDA-10103/DDE-00009 42 Westbourne Park TSP-WBP-45-R 2XT OK /Cxxx to confirm if connections from TSP-WBP-60 still needed (earth bar for Cxxx only) DDA-10103/DDE-00010 190 Westbourne Park TSP-WBP-190-R 2XT OK if disconnection box bonds DDA-10104/DDE-00011 277 Westbourne Park TSP-WBP-277 2XT OK if disconnection box bonds DDA-10104/DDE-00011 336 Westbourne Park TSP-WBP-336-R 2XT OK if disconnection box bonds DDA-10104/DDE-00012 403 Westbourne Park TSP-WBP-403-R 2XT OK if disconnection box bonds DDA-10621 5005 Tottenham Court Road Station TSP-TCR-W/B-2b 1XT To move on TSP-W/B-4993-1b as designed and in the SOB DDA-10624 7364 Farrington Station TSP-FDN-W/B-2b 1XT Ok. TSP-W/B-7329-1b installed for Cxxx, Cxxx to confirm if still needed DDA-10625 8187 Liverpool Street Station TSP-LIV-W/B-1b 1XT To move on TSP-W/B-8169-1b added due to change of AP’s position (see SOB) DDA-10129 8540 Liverpool Street Station TSP-LIV-W/B-3b 1XT To move on TSP-LIV-W/B-2b as per design DDA-10133 10209 Whitechapel Crossover TSP-W/B-10209-1b 1XT OK / Cxxx to confirm if earth bar at Ch10240 still needed DDA-10134 10250 By-Pass Tunnel TSP-BPT-W/B-1b 2XT OK if disconnection box bonds DDA-10134 10568 Whitechapel Station TSP-WCL-W/B-3b 1XT OK / Cxxx to onfirm if TSP-W/B-10550-1b still needed DDA-10137 11420 Tunne ( WHI - STG) TSP-W/B-11420-1b 2+2XT OK if disconnection box bonds
| 05SY - Systemwide | Cxxx-NCR-000142 | NCR | Cable Damage to Cxxx Cables at Westbourne Park |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-12-14 | 2018-12-21 12:58 | 7 | 2018-10-22 08:22 | Systems - Signalling | 2000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Cxxx have reported by issuing Cxxx-EWN-03650 (attached) which reports the following issue: "The cables installed by Cxxx at Westbourne Park in the Westbound (Chainage 210) have been left undressed and crossing. As per Cxxx-NCR-000893, Cxxx have already advised that a Cxxx cable sheath was damaged as a result of Cxxx’s cable pulling. In addition, these cables are currently blocking Cxxx cable routes and extra care and time will be required to avoid Cxxx assets during the Cxxx cable pulling activity. It has introduced an additional quality risk (potential to damage Cxxx cables) which will need to be carefully monitored and managed. Both will incur additional cost and will result in a delay to the current programme." Cxxx-NCR-000893 and investigation report attached for reference.
| 05SY - Systemwide | Cxxx-NCR-000143 | NCR | Route Marker Board and Sign Mounting Arrangement |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-12-21 | 2019-07-17 14:15 | 208 | 2018-10-26 08:57 | Systems - Signalling | 6000 |  | Design | Repair | 3 (3-6k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | Further to Cxxx-PMC-04475 and CRL-OBS-25289 it has become clear that the controls around the RMB design and install are defective. Install has commenced without a design being submitted to CR Land continues to proceed with a rejected design (Cxxx-PMC-04475). The design does not demonstrate adequate structural assessment or loading which has necessitated additional supports being added to the RMB contrary to the design submitted. See attached photographs. The design also fails to address CRL concerns in regards to equipotential earthing either through design, an obligation through CDM regulations or by ALARP argument ( obligation under CSM).
| 05SY - Systemwide | Cxxx-NCR-000144 | NCR | Unauthorised disconnection of track circuits at Westbourne Park |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-12-21 | 2018-12-21 12:51 | 0 | 2018-10-31 13:21 | Systems - Signalling | 6000 |  | Planning | Repair | 3 (3-6k) | Complete | External Phenomenon - Other | Completed |  | Cxxx Test team have reported that works (by Cxxx) were being carried out on track that involved the removal of tight joint in the crossing area S&C 1004A/B and 1005A/B (see attached), which has impacted signalling assets.
| 05SY - Systemwide | Cxxx-NCR-000145 | NCR | Cxxx Test & Commissioning team started loading the software drop PD Plus 3, without an accepted Test Plan in place |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-12-28 | 2019-02-17 16:41 | 51 | 2018-11-12 13:52 | Systems - Signage | 3000 |  | Testing and Commissioning | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Cxxx Test & Commissioning team started loading the software drop PD Plus 3, without an accepted Test Plan in place. Test Plan was not made available in a timely manner.
| 05SY - Systemwide | Cxxx-NCR-000146 | NCR | Damaged Points Cable at Whitechapel |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-01-05 | 2019-06-17 14:59 | 528 | 2018-11-16 15:36 | Systems - Signalling | 5000 |  | Damaged | Repair | 3 (3-6k) | Complete | External Phenomenon - Other | Completed |  | Installation team have identified a damaged cable at Whitechapel (see attached photo's). The cable is a 2c 35mm SWA and is therefore a 120v DC points motor power cable for 1154 points (WHX_SER-1154 (Power- Motor (SER to DB, 2 pairs), located in the invert of the EB.
| 05SY - Systemwide | Cxxx-NCR-000147 | NCR | Identification of testing and commissioning spares |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-12-10 | 2019-10-10 14:21 | 304 | 2018-11-26 11:16 | Systems - Signalling | 3000 |  | Planning | Repair | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | Further to: EWN-00517 PMC-03833 PMC-04536 The contractor has not defined the testing and commissioning spares holding as per the requirements of clause 20.4 of volume 2A of the Works Information.
| 05SY - Systemwide | Cxxx-NCR-000148 | NCR | Route Marker Boards XR085 and XR095 were found to be damaged on 25/11/18 at Tottenham Court Road station |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-12-24 | 2019-04-02 08:28 | 99 | 2018-11-26 12:37 | Systems - Signalling | 2000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Not Defined | Completed |  | On 25/11/18, Test team reported that Route Marker Boards XR085 and XR095 were found to be damaged at Tottenham Court Road station. Test completed the Sign Sighting Forms for both RMBs, which showed that both RMBs had exceeded the lateral clearance from track, as a result of the damage. See attached Sign Sighting Forms.
| 05SY - Systemwide | Cxxx-NCR-000149 | NCR | Work has commenced without an approved MCR in place for EMKA cable |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-02-22 | 2019-04-16 09:21 | 53 | 2018-12-06 12:33 | Systems - Signalling | 1500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Work has commenced without an approved MCR in place for EMKA cable which is used on the Plumstead REB
| 05SY - Systemwide | Cxxx-NCR-000150 | NCR | Incorrect cable type installed |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-02-27 | 2019-03-08 12:56 | 9 | 2018-12-17 13:33 | Systems - Signalling | 5000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Management Problem - Inadequate administrative control | Completed |  | 1 sq.mm cable has been installed for points at custom house, contrary to the book wiring specifying 1.85mm. This was not identified by installation team or verification testing and not captured on the OWL for IRN or PCC
| 05SY - Systemwide | Cxxx-NCR-000151 | NCR | Balise NID_ C values incorrect |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-03-22 | 2019-12-02 13:49 | 255 | 2019-02-01 16:13 | Systems - Signalling | 6000 |  | Software | Repair | 3 (3-6k) | Complete | Management Problem - Inadequate supervision | Completed |  | Balise installed do not contain the coorect NID_C header. Design states a the UK national value of 4 shall be used for Crossrail balises however60% of the balises have been found to contain the NID_C value of 888. The result of this error means that incorrect speeds could be applied to CRL infrastructure.
| 05SY - Systemwide | Cxxx-NCR-000152 | NCR | Installation without Design of Chevron Board at CUS |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-03-22 | 2019-06-21 15:25 | 91 | 2019-02-13 10:56 | Systems - Signage | 5000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Management Problem - Inadequate supervision | Completed |  | Chevron board at custom house has been installed without an accepted design
| 05SY - Systemwide | Cxxx-NCR-000153 | NCR | Cables installed without an approved MCR |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-02-25 | 2019-06-04 11:55 | 99 | 2019-02-18 13:49 | Systems - Signalling | 3000 |  | Material | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Cables installed in Bond Street between the SER and __-R do not have an approved materials compliance record for Cxxx.
| 05SY - Systemwide | Cxxx-NCR-000155 | NCR | Incorrect cable type installed and not found by contractor in T&C process |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-06-28 | 2020-11-30 15:29 | 521 | 2019-02-18 14:28 | Systems - Signalling | 3000 |  | Testing and Commissioning | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Incorrect cable was installed in BDS SER - G6724 vice G4724 as specified by design. This was not railed to the client as an item of outstanding work awaiting completion prior to handover. Client unaware if this was raised by contractor internally as either a test log by signalling testers, or captured by E&P installation contractor
| 05SY - Systemwide | Cxxx-NCR-000156 | NCR | Cable joints ABX |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-06-30 | 2020-05-06 09:20 | -55 | 2019-02-25 13:54 | Systems - Signalling | 50000 |  | Incorrect Installation | Reject | 2 (6-60k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | The following Power & Multicore cables at ABX have been jointed contrary to the issued design. • 2c 70mm2 C2 ABX SER to 1375A WM/WC DB (1) – 1 x Joint • 2c 70mm2 C2 ABX SER to 1375A WM/WC DB (2) – 1 x Joint • 2c 70mm2 C2 ABX SER to 1375B WM/WC DB (1) – 2 x Joints • 2c 70mm2 C2 ABX SER to 1375B WM/WC DB (2) – 2 x Joints • 27c 1.85mm D2 ABX SER to 1376B (SO) WC (F) • 27c 1.85mm D2 ABX SER to 1376B (SO) WC (R)
| 05SY - Systemwide | Cxxx-NCR-000157 | NCR | CFX00418857 - WSF during Transition from TPWS to CBTC |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-06-28 | 2019-09-26 09:54 | 90 | 2019-02-26 10:00 | Systems - Signalling | 60000 |  | Software | Repair | 2 (6-60k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Crossrail have identified a WSF of the signalling system during dynamic testing in which the train unit under test failed to emergency break during a transition move on the GWML. (NCR raised to formally record, on EB, issue and outcomes from analysis of CFX00418857.)
| 05SY - Systemwide | Cxxx-NCR-000158 | NCR | Work commenced on installation of RMBs at Westbourne Park without an accepted CRL design |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-04-04 | 2019-06-21 15:27 | 78 | 2019-03-01 11:16 | Systems - Signage | 3000 |  | Design | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | The project has highlighted that RMBs XR17, XR25 AND XR27 appear to have been installed without a CRL accepted design in place.
| 05SY - Systemwide | Cxxx-NCR-000159 | NCR | Damaged Fibre Optic Cable at Custom House Eastbound |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-04-30 | 2019-05-20 08:42 | 20 | 2019-03-11 11:33 | Systems - Signalling | 3000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | It was reported by __(Cxxx Construction team member) that on 10/03/2019 his fibre team was at CUH-NWP to close out a FO log, where they noticed on the Eastbound that the portal entrance AP pigtail cable ties had all been removed so it was loose. Whilst checking it, they noticed that the 32c fibre cable running from CUH FOSE to the portal had been damaged on the low level cms in 4 locations. Please see the photos attached. Temporary measurements were put in place to protect the cable from water ingress, due to the damage that water can cause. The high-level cable could not be checked to see if that had been damaged, so the team still need to go back and check it further along into the tunnel. The cable S31S39 was installed on the Eastbound and runs from FOSE 3301-ch 16880 to CWX SER (chainage 13700). At least 3.5 km will be required. Also required are: APs x 13, Pigtails x 13, Heat shrinks kits x 13. A location for a new FOSE has been detailed in the photos but is dependent upon checking the high level.
| 05SY - Systemwide | Cxxx-NCR-000160 | NCR | ATO Overspeed |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-05-31 | 2019-09-11 15:17 | 103 | 2019-03-11 13:12 | Systems - Signalling | 3000 |  | Software | Repair | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | NCR raised to capture COL00316 - ATO Overspeed and EB applied.
| 05SY - Systemwide | Cxxx-NCR-000161 | NCR | IP66 Polyester Enclosure was installed without a code 1 accepted MCR in place |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-04-24 | 2019-05-16 15:54 | 22 | 2019-03-27 12:52 | Systems - Signalling | 3000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | To address NCR-94, IP66 Polyester Enclosure was installed over AP3328 at Connaught Tunnell. However, the relevant MCR was not produced, submitted & received code 1 acceptance from CRL, prior to the installation.
| 05SY - Systemwide | Cxxx-NCR-000162 | NCR | Emergency Braking applied due to loss of radio, approaching at Liverpool Strreet station |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-10-31 | 2019-09-13 11:48 | -48 | 2019-04-04 13:52 | Systems - Signalling | 10000 |  | Software | Repair | 2 (6-60k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Date, Time: 20.03.2019; 01:25 Submitter: __ Train ID: 36 Train in integrated Mode: Yes Active cab: B OBCUs powered: A Location of Defect: Train Test performed: 72 Expected result: Train to run from XR044 to XR398 in AM stopping at all stations and virtual platforms. Test result: Emergency brake at 01:20 approaching LSX. Deviation observed: RCC reported that the EB was applied due to 'radio WLAN not ok' further info 'TU3601.545106 radio wlan 1 not ok. however no loss of radio icon shown on DMI. Additional information: __ OBCU mod in place. Recovered by acknowledging and continuing into LSX.
| 05SY - Systemwide | Cxxx-NCR-000163 | NCR | System Processing Timer Calculation |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-06-30 | 2019-07-17 14:48 | 17 | 2019-04-02 10:53 | Systems - Signalling | 10000 |  | Software | Repair | 2 (6-60k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The Safe Braking Model of TGMT assumes that the OBCU-ATP outputs a safe reaction after no more that 550ms delay after the inputs reveal the condition. The value of 550ms is set as a configuration parameter in [TGMT_R3_CONF_DATA_OBCU_ATP] TP_SAFE_BRAKING_MODEL_AC_DELAY and is used to calculate the braking curves. The time is made up of, • the computation cycle of the Odometry tasks. • the output of the Emergency Break by SRAUS5A. • the Output of the EB through the final EB Relay. Based on the times required for the above the remaining for the OBCU-ATPs tasks is calculated to be lower or equal to 304 ms. From this calculation the current execution timer value has been set to 295 ms inside the OBCU_ATP application (hard coded). Analysis has identified that there are potential scenarios where it may be required that 2 x execution timer sessions are needed (caused by an synchronicity), plus an additional Time for Loglo processing equalling a total of 1046ms. (500ms OVER the currently applied values) Actions Taken / To Be Taken: Within the PD+7 baseline the engineering data has been modified to extend the system time to 1146ms which is the worst case theoretical scenario which will be loaded in April 2019. Within PD+8 baseline new software and engineering data will aim to reduce the timer to 850ms (exact figure TBC) in June 2019. Hence why we would like to propose an NCR close out date of 30/06/19.
| 05SY - Systemwide | Cxxx-NCR-000165 | NCR | A non Cxxx cable has been installed to close to Balise FBCUS23 which impacts clearance requirements |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-09-30 | 2019-09-09 14:27 | -21 | 2019-04-05 12:32 | Systems - Signalling | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | Test team have reported that post installation of Balise FBCU23 (chainage 17,170 436 EB), a non Cxxx cable has been installed in close proximity which fouls the clearance requirements. See attached photo.
| 05SY - Systemwide | Cxxx-NCR-000166 | NCR | Non Cxxx cables have been installed in front of AP3331 at Connaught obstructing access |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-05-09 | 2019-07-08 14:53 | 60 | 2019-04-05 13:35 | Systems - Signalling | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | Non Cxxx cables have been installed in front of AP3331 at Connaught (EB Connaught SE17863) obstructing access to signalling operational equipment.
| 05SY - Systemwide | Cxxx-NCR-000167 | NCR | Liverpool Street Bookwiring Red Lines drawings submitted to CRL for acceptance did not fully report the changes as per the Testing copy provided with the corresponding PCC |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-10-25 | 2019-10-07 12:54 | -18 | 2019-08-19 10:55 | Systems - Signalling | 1000 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | It was reported by __ (CRL Signalling Engineer, CEG) on 28/03/19 that while reviewing the ‘Red Line’ LSX bookwiring (Cxxx-SIC-R2-DWG-CR001-50017 V7), against the Liverpool Street Book Wiring Test Records at PCC Cxxx-SIC-R2-RGN-C101-50011 V1.0 Part 1, he noted that Sheet 07051 __R Layout had not been updated in accordance with the test record. This implied that Liverpool Street Bookwiring Red Lines drawings did not fully report the changes as per the Testing copy provided with the corresponding PCC. Upendra also noted that some of the Power distribution cubical __s were incorrectly numbered and not cross referenced against the Power Supply bookwiring 50V & 24V DC outgoing circuit detail design sheet.
| 05SY - Systemwide | Cxxx-NCR-000168 | NCR | RCBOs (Residual Current Circuit Breakers) tripping at Custom House and Canary Wharf |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-06-06 | 2019-07-26 13:02 | 50 | 2019-05-03 09:47 | Systems - Signalling | 50000 |  | Design | Repair | 2 (6-60k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | It was reported by __ (CRL Supervisor) on 11/04/19 that Dynamic testing had been disrupted by Radio APs losing power in the last 48 hours, and he requested to raise an NCR to capture this issue and the subsequent remedial works.
| 05SY - Systemwide | Cxxx-NCR-000169 | NCR | Route Marker Board XR105 found to be damaged |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-05-21 | 2019-05-20 08:28 | -1 | 2019-04-17 18:08 | Systems - Signalling | 800 |  | Damaged | Repair | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | Test team have reported that XR105 RMB has been found damaged when testing other equipment in that area at Farringdon, see attached photos. This board was sighted and corresponded by test on 3/12/18 and the RMB was not damaged at that time so this has occurred post Cxxx installation and test.
| 05SY - Systemwide | Cxxx-NCR-000170 | NCR | Damaged fibre optic cables at Farringdon SER |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-07-26 | 2019-07-19 12:40 | -7 | 2019-04-23 14:21 | Systems - Signalling | 3000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | It was reported by __ (T&C Manager - Knorr-Bremse Cxxx) in his email of 13/03/19 to Nick Franklin (TIC Cxxx) that prior to works within the splice tray in the Farringdon Eastbound PSD panel, the Cxxx splice team did a preliminary check on the Westrace fibre cables and noticed that one of the cores was damaged. Jeremy also provided a picture of the damaged cable (highlighted with a light source in the attached picture).
| 05SY - Systemwide | Cxxx-NCR-000171 | NCR | Use of non-calibrated test equipment at Farringdon SER on 18/04/19 |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-05-31 | 2019-06-27 11:55 | 27 | 2019-04-23 14:18 | Systems - Signalling | 1000 |  | Testing and Commissioning | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Lack or improper material identification and traceability | Completed |  | It was reported by __ (CRL) in the Daily Site Report dated 18/04/19: "The work undertaken today was to repair damaged fibre cables from the SER to the EB & WB PSD cubicles. Both of the cables were tested last year but have since been damaged, possibly when other cables had been installed within the cubicles. All the test equipment used today was not in calibration. Kit CRFT03 & 11485 was due last year according to the calibration stickers on the equipment. I’ve since spoken to __, they are now aware of the issue and the cables will be re-tested once the kit is calibrated. The faults on both cables are fixed so there should be no more disruption to the PSD but the cables will require testing again." Please note, NCR-170 has been raised to capture the damaged fibre optic cables.
| 05SY - Systemwide | Cxxx-NCR-000172 | NCR | Damaged RMBs XR412, XR095 & XR337 at Woolwich - Custom House |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-06-14 | 2019-06-17 15:12 | 3 | 2019-05-17 09:57 | Systems - Signalling | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | Cxxx Construction team found the below damaged RMBs at Woolwich - Custom House: XR412 Co-Acting XR095 Co-Acting XR337
| 05SY - Systemwide | Cxxx-NCR-000173 | NCR | SA Speed Not Consistent |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-10-31 | 2019-09-13 11:51 | -48 | 2019-05-20 13:28 | Systems - Signalling | 10000 |  | Testing and Commissioning | Repair | 2 (6-60k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | __ (CRL Testing & Commissioning Engineer) observed during testing that the SA speed appeared to be changing. This happened a few times, with the speed ranging from 19mph to 23mph. (Note: The SA speed was never observed higher than 23mph). See COL00893 for further details and pictures. See COL00893 for further details and pics.
| 05SY - Systemwide | Cxxx-NCR-000174 | NCR | Cables installed on site at RCC did not align with the formally issued design |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-06-30 | 2020-06-30 13:41 | 0 | 2019-06-12 09:33 | Systems - Signalling | 3000 |  | Design | Repair | 4 (0.5-3k) | Complete | Verification Problems - Not Defined | Completed |  | Works were planned in to recover the cat 6 cables at the RCC, as per the scope. On commencement of the shift, the test team undertook a correlation exercise between the installation and design. However, this activity identified that the cables installed on site, did not align with the formally issued design. For this reason, the works were cancelled, as there were no means of confirming which cables fed what.
| 05SY - Systemwide | Cxxx-NCR-000175 | NCR | Damaged RMB XR374 at PLP - ABX |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-07-26 | 2019-07-17 15:18 | -9 | 2019-06-20 10:50 | Systems - Signalling | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | RMB XR374 was found to be damaged by __ Cxxx Construction team at PLP - ABX on 23/05/19.
| 05SY - Systemwide | Cxxx-NCR-000176 | NCR | 620/660 SCADA Interface |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-07-31 | 2020-09-07 13:19 | 38 | 2019-06-28 14:06 | Systems - Signalling | 10000 |  | Software | Repair | 2 (6-60k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | As part of the 620/660 interface works the Cxxx SER/__R and other alarms are required to be transmitted via the 660 SCADA system. A difference in requirements from rev 6.0 to 7.0 of the relevant 660/620 CMS IRS, acknowledged and identified during interface meetings , has not been accounted for in the latest __ design that has been installed on site. As a result this interface will not work until __ Cxxx review their design in line with the latest 660/620 CMS IRS.(660 FOR 2893 refers) The result of this mismatch is a risk to trail running a as no TM1 alarm testing can take place until the change is made.
| 05SY - Systemwide | Cxxx-NCR-000177 | NCR | Plumstead REB's faulty door lock |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-08-13 | 2019-07-19 14:18 | -25 | 2019-07-16 12:47 | Systems - Signalling | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Plumstead REB was delivered with faulty lock on the door, so the REB required retesting due to unauthorised entry
| 05SY - Systemwide | Cxxx-NCR-000179 | NCR | GWML Balises were found to have incorrect packet data |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-10-19 | 2019-10-30 15:30 | 11 | 2019-08-20 10:40 | Systems - Signalling | 5000 |  | Software | Repair | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Please refer to the attached email from David Sherrin (RfL) to Eckhard Leucke (__ Cxxx Project Director - Delivery), for the details of the issue. Also see below the main extract from the email I am not sure how to approach this. I am keen to keep this issue in context and not start a snowball (forgive me – not sure how that translates into German). As you are aware we are now running Integrated Class 345 on the GWML. On two occasions there have been incidents where a Class 345 Driver at Paddington High Level station has been offered CBTC SA mode when the driver does Start of Mission in the west cab in preparation for departure. In one of these cases the Driver appears to have selected CBTC-SA and been offered the CBTC DMI, complete with 28mph limit. Jack has done the analysis, but we believe the following balise is the cause. NID_C=3, BG_903. Approximate grid reference: 51.52131652832031, -0.20118333399295807 Google Maps shows this as Westbourne Park area (ie not the depot) It appears that when the train is travelling east, from OOC the trailing cab, reads balise group NID_C=3, BG_903. This is programmed with a conditional level transition, if the trailing cab is already in CBTC it has no effect. The Level is “known” as CBTC, so it is prompted during the Start of Mission at Paddington. __ believe that from an ETCS perspective the system is performing to standard. It is my understanding – and I am not an expert in Transitions – that there should be no conditional level transitions for trains travelling to Paddington High Level (source: GWML DIR document, but doesn’t show what BG_903 should have programmed). This is achieved by having switchable balise, linked the interlocking, so that when the route is set to Paddington High Level there is no Transition, but when the route is set to the COS a Conditional Level Transition is offered. I think there are two questions here:- 1, Can someone check that there are no balise on the GWML Operational routes that are programmed to give an Conditional Level Transition. This is not allowed, as there are ETCS fitted trains operating into Paddington (not just Class 345), unless these assets are suitable commissioned. 2, Irrespective of if the balise should be there or not, did the design of the Transition consider the impact a Conditional Level Transition balise might have on the trailing cab, which for whatever reason had previously been in L-CBTC ? Ultimately, the answer might be some additional balise to ensure that both cabs previous mode is AWS/TPWS, before the units approach the Westbourne Park area, but as I said earlier I am not Transition Expert. I am guessing that instead of an email exchange the simplest solution would be to schedule some form of call to discuss. Do you need any information before that call and how long do you believe you will need to look at the issue before you can support a discussion.
| 05SY - Systemwide | Cxxx-NCR-000180 | NCR | Multiple rollbacks issues with eb applied reported |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-07-31 | 2022-02-23 17:26 | 572 | 2019-08-20 10:25 | Systems - Signalling | 6000 |  | Software | Repair | 3 (3-6k) | Complete | Management Problem - Other | Completed |  | On 17/07/19, __ reported multiple rollbacks issues with eb applied. Below Go-Canvas log numbers were provided: COL01286, COL01307, COL01344. Below CFX logs have been raised for rollbacks issues: CFX00411415: Headline: Dyn-Test: EB because of reported Rollback (Maximum rollback exceeded) Submit Date: 08/12/2018 Submitter: __ CFX00440165 Headline: Dyn-Test: M__R_18_19: Roll back Submit Date: 01/08/2019 Submitter: __
| 05SY - Systemwide | Cxxx-NCR-000181 | NCR | Lack of checking for Control Tables. |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-12-27 | 2020-01-16 17:39 | 20 | 2019-09-26 07:50 | Systems - Signalling | 6000 |  | Design | Repair | 3 (3-6k) | Complete | Personnel Error - Other human error | Completed |  | The Whitechapel control tables delivered under Cxxx-CCM-06496 have clearly not been checked in accordance with the quality plan
| 05SY - Systemwide | Cxxx-NCR-000182 | NCR | DMI displayed doors to be open when they were actually closed |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-11-30 | 2021-11-04 12:28 | -26 | 2019-09-26 09:37 | Systems - Signalling | 500 |  | Software | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | During Dynamic Testing at Paddington on 14/01/19, DMI displayed doors to be open when they were actually closed; CFX00414282 was raised for the issue. On 07/07/19, similar issue was reported at Liverpool Street, whereby the PEDs Symbol showed open after Relevant CFX: CFX00426102
| 05SY - Systemwide | Cxxx-NCR-000183 | NCR | Bonding trackside cable length exceeds 30m |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-11-29 | 2020-01-15 14:16 | 47 | 2019-09-11 11:26 | Systems - Signalling | 5000 |  | Documentation and Records | Repair | 3 (3-6k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Engineering have highlighted (ChampFX refers) that some of the 10mm² bonding trackside cables have exceeded the 30m maximum length as referenced in the Cxxx E&B plan and PAN /102 standard for the following affected sites: Location EB/WB Asset ID Asset Chainage Cable Type Cable Length BDS-TCR E/B AP0607 4020.00m 10mm² SE955B 60.00m TCR-FAR E/B AP1003 6944.00m 10mm² SE955B 76.00m FAR-LIS W/B AP1008 7330.00m 10mm² SE955B 36.00m CUS-WWC E/B AP3331 17863.00m 10mm² SE955B 52.00m WWC-ABX E/B AP3551 21720.00m 10mm² SE955B 60.00m
| 05SY - Systemwide | Cxxx-NCR-000184 | NCR | Earthing of __R equipment is contrary to the Earthing & Bonding Plan |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-12-07 | 2020-11-10 14:59 | 339 | 2019-10-04 10:14 | Systems - Signalling | 24000 |  | Design | Repair | 2 (6-60k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Site review highlighted that the earthing of __R equipment is contrary to the Cxxx Earthing & Bonding Plan (Cxxx-SIC-R2-STP-CR001-50038)
| 05SY - Systemwide | Cxxx-NCR-000185 | NCR | No designs for temporary earthing arrangments for PSP at Plumstead Sidings |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-11-16 | 2020-11-10 13:57 | 360 | 2019-10-04 11:15 | Systems - Signalling | 3000 |  | Incomplete Works | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Site review highlighted that there are no designs in place for the temporary earthing arrangements for the PSP at Plumstead sidings.
| 05SY - Systemwide | Cxxx-NCR-000186 | NCR | Site Modbus Failures |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-12-10 | 2020-12-21 10:59 | 377 | 2019-10-07 12:08 | Systems - Signalling | 36000 |  | Equipment Breakdown | Repair | 2 (6-60k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Communication could not be established through the Modbus unit despite having previously worked and registered to Cxxx system. This hardware failure has occurred at LSX, FDX and CWX thus triggering an adverse trend which requires further investigation.
| 05SY - Systemwide | Cxxx-NCR-000187 | NCR | Abbeywood ESP enclosure flap (front panel) fell off when it was opened, during a a VAP walk out on 05 Sep 2019 |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-06-30 | 2020-06-26 10:09 | -4 | 2019-10-18 08:28 | Systems - Signalling | 6000 |  | Material | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During a joint RFLI / __ VAP walk out on 05 Sep 2019 at Abbey wood station platforms, when the ESP 3 at Platform 4 was inspected, the front panel fell off when it was opened. It looks to have been attached with glue. ESP = Emergency Stop Plunger VAP = Verification Activity Plan
| 05SY - Systemwide | Cxxx-NCR-000188 | NCR | Signage changes contary to CRL submitted/ accepted designs |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-12-31 | 2020-09-07 13:22 | 251 | 2019-10-23 11:46 | Systems - Signalling | 10000 |  | Design | Repair | 2 (6-60k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | Sighting committee remedial works have commenced with changes without CRL submitted/ accepted design being in place for signage relating to Cross Passages (CP).
| 05SY - Systemwide | Cxxx-NCR-000189 | NCR | Non-conforming product (faulty fixed red light) was found in the quarantine area at Plumstead, during the internal audit of Calibration Management |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-12-06 | 2020-02-17 15:11 | 73 | 2019-11-05 10:00 | Systems - Signalling | 500 |  | Material | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | During the internal audit of Calibration Management on 25/07/19 at Plumstead depot, there was a fixed red light found to be in the quarantine area. There was also a Reject / Quarantine form attached to the item, where the reason for rejection was stated to be: “LED board only half lights up”. However, there was no NCR number referenced in the form. Upon investigation, it transpired that the item did warrant an NCR, but the Storeman failed to inform the Quality department about the item, which is why the NCR was not raised at that time. Product description: Lamp Buffer Stop LED 230V Red Material No: 0055 / 050263 The Storeman has been briefed that if an item is returned to him for placing in the quarantine area, he should inform the Quality department, who could determine whether the item warrants an NCR / DRACAS or not, and then take the necessary action, if required.
| 05SY - Systemwide | Cxxx-NCR-000190 | NCR | Test case 254.3 ATO Inhibit area did not match the Area 5 Scheme Plan |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-09-30 | 2020-06-17 09:46 | -105 | 2019-12-05 12:37 | Systems - Signalling | 3000 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Issue captured in CFX00451441. Details from the CFX are as below: Date, Time: 04.11.2019; 03:00 Submitter: __ Train ID: 36 Train in integrated Mode: Yes Active cab: A OBCUs powered: A Location of Defect: Train Weather conditions / other influences: Test performed: 254.3 Expected result: When train enters Up Electric (2129 points), ATO should be inhibited and stepdown to PM enforced before train transitions to TPWS. Test result: Train running in AM from SRA platform 5 towards UP ELECTRIC transition (L244 approach released from red, route set to UR 518, Gas Factory Junction). Stratford Scheme Plan Rev EE shows ATO inhibit at 14958.40, at 2129 points. The train continued running in AM until transition to TPWS, when on ENB track (beyond 14754.40). ATS showed mode changed directly from AM to SY, train DMI was AM to TPWS. Deviation observed: ATO inhibit areas do not agree with scheme plan for Up and Down Electric. Additional information: It looks as though this also applies to the Down electric line, so please also consider this for any TDB updates (see attached pictures).
| 05SY - Systemwide | Cxxx-NCR-000191 | NCR | SCADA interface and S&D at RCC not fully functional |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-06-23 | 2020-09-18 14:33 | 87 | 2019-12-19 10:59 | Systems - Signalling | 6000 |  | System Defect | Repair | 3 (3-6k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | It was reported by CRL Cxxx Supervisor __ on 16/12/19 that S&D at the RCC was still not fully functional, and he requested that given PD+11 (scheduled for Dec-19) is the Trial Running baseline, the issue needs to be captured under an NCR to ensure a documented plan for a fix is in place.
| 05SY - Systemwide | Cxxx-NCR-000192 | NCR | BUCF non functioning due to software issues |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-08-31 | 2021-02-25 15:12 | 178 | 2020-01-09 11:15 | Systems - Signalling | 3000 |  | Software | Repair | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Communication issues with the BUCF signalling system which have had ChampFX's CFX00440047 (no general update from __ Wayside) and CFX00458911 (computers can not login to OCxxx) raised to manage the issues to resolution.
| 05SY - Systemwide | Cxxx-NCR-000193 | NCR | Line wide Westrace failure |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-03-26 | 2021-03-23 11:12 | -3 | 2020-01-17 15:22 | Systems - Signalling | 20000 |  | Testing and Commissioning | Repair | 2 (6-60k) | Complete | Material/Preservation Problems - Other | Completed |  | On Wednesday 15th January, during the morning construction progress call, __ advised an issue had arisen where by the Interlocking at all sites had failed or "gone dark" resulting in loss of correspondence on all points, axle counter sections, ESPs etc
| 05SY - Systemwide | Cxxx-NCR-000194 | NCR | Radio Coverage Issues |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-10-30 | 2021-02-03 14:26 | 96 | 2020-02-17 15:12 | Systems - Signalling | 6000 |  | System Defect | Repair | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | It was reported by __ (CRL Field Engineer) on 06/02/20 that the below issues were identified from the POMS testing update meeting: -All shafts have had an issue with the signal. Previously believed to be due to the metal doors yet testing with the doors open has made no difference. -2 boards at the extremities (374 Plumstead and North __ line NK501) have signal issues believed to be due to the distance.
| 05SY - Systemwide | Cxxx-NCR-000195 | NCR | XR201 and XR203: Train not able to reach Operational Stopping Point due to Interlocking Boundary issues |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-07-30 | 2021-06-30 13:00 | -30 | 2020-02-21 09:33 | Systems - Signalling | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | It was reported by CRL T&C Engineer __ on 07/02/20: Issue: XR201 and XR203: Train not able to reach Operational Stopping Point due to Interlocking Boundary issues. CRL has concluded that design has not been fully met. Impact: Will cause an EB intervention if the driver attempts to pull up to the RMB. XR203 can be seen from train cab but cannot be read by driver. References: CFX00350122, COL00756, COL00757, COL00836, COL00841, etc
| 05SY - Systemwide | Cxxx-NCR-000196 | NCR | Woolwich Signal Sighting Forms V4 - Various errors identified by CRL, indicating inadequate documents checking prior to submission by __ |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-04-03 | 2020-09-07 13:24 | 157 | 2020-02-21 11:38 | Systems - Signalling | 1000 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | It was reported by CRL Field Engineer __ on 21/02/20 that while checking the Woolwich Signal Sighting Forms Cxxx-SIC-R2-ZFM-CR147-50008 V4, there were several errors and discrepancies identified. For instance: 1. Signage IDs XR355, XR356 and XR357: all had one version referenced on both contents pages, but a different one in the actual content. 2. Signage IDs XR358, XR359, XR360 AND XR361 are all correctly listed in the contents as being in WWC SER area, but are completely missing from the package.
| 05SY - Systemwide | Cxxx-NCR-000197 | NCR | Asset Database and Labelling Issues |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-04-30 | 2020-07-15 08:38 | 76 | 2020-03-16 13:43 | Systems - Signalling | 10000 |  | Documentation and Records | Rework | 2 (6-60k) | Complete | Procedure Problem - Lack of procedure | Completed |  | NCR description (details of the issue, how was it found, any implications etc.) Discrepancies between database and labels on site for Access Point Cabinets and Antennas. Currently on site there are the labels installed in 2017/2018 are as per wrong naming convention and labels installed recently are as per Crossrail asset naming convention. Both label do have asset design name and unique Tag ID , and only difference is old labels do not have serial number per area tag codes. All earth cables are captured under wiring cables L-class and installed on site as per wiring cable naming convention. The source, destination , design ID are shown on the labels. Only discrepancies is wiring cable has letter P and earthwire L-class should letter E as cable type. Date of Issue : 4/3/20 Found during VAP and review of data base with Crossrail AIMS team Implication : Update data base and re-labelling.
| 05SY - Systemwide | Cxxx-NCR-000198 | NCR | Work has commenced without an approved MCR in place for Tratos cable |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-05-31 | 2020-06-19 13:36 | 19 | 2020-03-17 11:08 | Systems - Signalling | 1500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Work has commenced without an approved MCR in place for Tratos SE955 35mm² cable which has been used at Plumstead to bond the ESPs & ESP DBs at the East End Taps to the TSPs.
| 05SY - Systemwide | Cxxx-NCR-000199 | NCR | Non-compliance associated with the placement of asset labels |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-07-31 | 2020-11-10 15:01 | 102 | 2020-03-31 15:47 | Systems - Signalling | 3000 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | It was reported by the CRL Handover team that the AP cabinets, AP isolators, all types of Disconnection Boxes asset labels, axle counters and RFID MAP boards installed on site are non-compliant to Crossrail Asset Naming and Labelling Convention Document CRL1-XRL-Z3-ADDSD-CR001-50413. The document requires that all labels should be installed adjacent to the assets, however, currently labels are installed on the assets i.e. on the box. Furthermore, Crossrail Asset Naming and Labelling Convention Document CRL1-XRL-Z3-ADDSD-CR001-50413 mandates that the Antenna asset labelling shall be applied adjacent to the Antenna e.g. on the fixing bracket (if installed) or on a permanent structure. As the AP cabinet antennas are installed high level and not easily accessible, the antenna labelling has been placed on the side of the corresponding AP cabinet.
| 05SY - Systemwide | Cxxx-NCR-000200 | NCR | Asset label fixing method |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-07-31 | 2020-11-10 15:00 | 102 | 2020-04-17 09:08 | Systems - Signalling | 3000 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | The Asset Data Identification Standard CRL1-XRL-O6-STD-CR001-00031 states the fixing method for labels shall be by mechanical attachment. Cxxx have not mechanically fixed labels on to assets as per the requirements but instead installed the labels on to the assets using a self-adhesive label. The labels used are SEI Identification Solutions RPX raised panel labels. Please refer to the Material Compliance Record Cxxx-HTM-C-CER-CR148-50134 along with the data sheet for details. The data sheet confirms the labels meet a number of the requirements stipulated in section 13.5 of the asset data identification standard, including: - Fire requirements. - Shear strength and peel strength (with relation to steel which is the majority of Cxxx assets). - Temperature range - Suitability. (The labels are approved for use on London Underground). However, the above deviation from the Asset Data Identification Standard and the application of self-adhesive labelling was not agreed with CRL.
| 05SY - Systemwide | Cxxx-NCR-000201 | NCR | POMS Handhelds -Radio Reception |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-10-30 | 2021-03-04 14:18 | 125 | 2020-07-03 11:36 | Systems - Signalling | 6000 |  | System Defect | Repair | 3 (3-6k) | Complete | Material/Preservation Problems - Other | Completed |  | It was reported that when carrying out RFID correspondence testing at XWN, the POMS handhelds were unable to pick up any signal at several RMBs. It was previously noted that despite apps or laptops being able to detect signal in a portal, the handheld was unable to. This issue has been captured and investigated under CFX00487535.
| 05SY - Systemwide | Cxxx-NCR-000202 | NCR | TCI (Track Circuit Interrupter) system reported a failure against the current design at Plumstead Sidings |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-07-30 | 2021-07-20 15:45 | -10 | 2020-08-06 11:44 | Systems - Signalling | 500 |  | System Defect | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Please see below findings from the attached CRL Report by Jimmy James (CRL Lead EMC Engineer): Introduction: A stray DC voltage was reported on the Track Circuit Interrupters (TCI) signalling circuits at Plumstead sidings. A data logger was attached to measure the voltage across the incoming conductors to the REB over a period of several days from 28/2/20 to 03/03/20. TCI Circuits: The TCI circuit is powered from an earth-free 50 V DC supply (B50 & N50). It is believed the signalling power supply has earth leakage detectors (ELD) circuits fitted. When the TCI conductors return to the REB they go via a surge arrestor to the Westrace input. For these measurements the fuses in the B50 supply to the circuit was removed. The surge arrestors was removed so only the TCI conductors were present. Appendix A of the report shows the items removed (in yellow) and the measurement connection point (in orange). Results: Over the period of the measurement the measure voltage remained relatively constant and consisted of a square wave switching between approximately 12.5 V and 35 V (see Figure 1 and Figure 2 in the report). The frequency of the square wave was very low and was approximately 0.2 Hz. Discussion: The measured voltage across the incoming TCI lines to the REB consisted of a relatively constant square wave switching between approximately 12.5 V and 35 V at approximately 0.2 Hz. Stray voltage due to railway traction power is a function of the load and position of the rolling stock and as such fluctuates with time. The measurements at PLU are constant with time and from this a traction power source can be eliminated. However, traction power stray voltage will be referenced to earth so making measurements with respect to earth (as opposed to across the line) could be considered. The source of the measured voltage is not known but some ELDs use low frequency square waves and as such eliminating ELDs as the source in the first instant is recommended.
| 05SY - Systemwide | Cxxx-NCR-000203 | NCR | __ Fuse Holders' Insufficient Ampere Rating |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-11-30 | 2020-11-10 15:04 | -20 | 2020-08-07 10:48 | Systems - Signalling | 3000 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | __ Cxxx project is currently using __ WSI 6/2 fuse holders (617941059) in the points circuit. These fuse holders are rated up to 6.3A in the UK, as per the data sheets. However, the points circuit can draw up to 8A, making the ampere rating of __ Fuse Holders insufficient to be used on points circuit.
| 05SY - Systemwide | Cxxx-NCR-000204 | NCR | Dynamic Test Reporting |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-10-30 | 2020-10-26 10:22 | -4 | 2020-08-28 08:10 | Systems - Signalling | 6000 |  | Supervision/Management | Repair | 3 (3-6k) | Complete | Management Problem - Inadequate administrative control | Completed |  | A number of Test Books Results had tests passed in table 2 of the documents but on inspection they were not passed on the individual sheets. How did this get through the checking and approval process.
| 05SY - Systemwide | Cxxx-NCR-000205 | NCR | Goldwing Cable - Works progressed without a CRL Accepted MCR in place |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-12-11 | 2020-11-24 17:47 | -17 | 2020-09-09 10:40 | Systems - Signalling | 1000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | During a review of Custom House __ Site Assurance File, a delivery note for Goldwing Cable Ltd was noted. Upon further investigation, it transpired that there was no MCR in place for that particular cable from Goldwing Cable Ltd.
| 05SY - Systemwide | Cxxx-NCR-000206 | NCR | 50V Surge Arrestor Issue |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-04-30 | 2021-03-25 12:54 | -36 | 2020-09-15 14:17 | Systems - Signalling | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | It was observed that the Strukton RCM equipment uses 24v supply, which feeds the pump unit oil level sensor via a 50v surge arrestor. The outcome of a 24v circuit using a 50v surge arrestor resulted in a permanent under-voltage fault LED displayed on the surge arrestor.
| 05SY - Systemwide | Cxxx-NCR-000207 | NCR | AP BS7671 Certification Issue |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-11-27 | 2020-11-10 16:34 | -17 | 2020-09-15 14:21 | Systems - Signalling | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Currently, there is inadequate AP BS7671 certification submission in eB, for CRL acceptance. As per the __ BS7671 Test Certification Programme issued to CRL on 09/09/20, there were test certs shown to have been submitted. However, none of those test certs had actually been submitted. This also meant that the test certs had not been submitted within the time frame agreed with CRL, i.e. two weeks of assets installation.
| 05SY - Systemwide | Cxxx-NCR-000208 | NCR | Damaged WEA MAP board at XWN RRAP (DB Schenker) access on 01/12/2020 |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-02-19 | 2021-01-14 15:03 | -36 | 2020-12-02 15:01 | Systems - Signalling | 1500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | On 01/12/202, an overall incident Level 4 for Property Damage at Cxxx Signalling System was reported by Gareth __. See details below: Incident Type: Property Damage Overall outcome: Level 4 ID: 13959638 Date Occurred: 01 December 2020 Time Occurred: 09:30 Location: Cxxx - Signalling System Crossrail location: Westbourne Park - WEP Contractor: __ Description of the incident: WEA MAP board at XWN RRAP (DB Schenker) access has been damaged. Person Leading Investigation: TBC Person who raised incident: Gareth __
| 05SY - Systemwide | Cxxx-NCR-000209 | NCR | Inconsistent label text for Control Cable lclass L746291 |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-03-29 | 2021-03-09 11:40 | -20 | 2021-01-11 11:19 | Information Management - Asset Information | 0 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | Cxxx labels for control cable are not compliant with CRL naming pattern : Cxxx label showing : C- 1560B WM/WC DB, 1560B WM, 1560B WC (F1) CRL Require pattern: [CABLE TYPE]-[SOURCE]-[DESTINATION], [DESIGN ALTERNATIVE ASSET ID] Justification : hyphens are padded with spaces which is causing check errors. All other configuration are compliant. There are 264 affected labels. We would suggest that due to the nature of the error being extra spaces around hyphens within the naming pattern that this is an inconsequential error and does not impact the maintenance of the assets, that the deposition can be USE AS IS.
| 05SY - Systemwide | Cxxx-NCR-000210 | NCR | Wrong or absent Vent Section chainage in Scheme Plan as Single source of truth input to ATS/__ |  | Crossrail | PDP | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-03-31 | 2021-07-06 13:30 | 97 | 2021-01-11 11:01 | Systems - Signalling | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Due to investigations around Woolwich related to Ventilation system pressure on PSD and potential solution, we realise that the area 3 Scheme Plans rev 10.0 reads discrepancies in relation to its input i.e. your Cxxx/Cxxx TVS DIR rev 13.0 (oct 19) and 14.0. This is an area of concern against SIL2 requirements as this means the LTRZ layout ATS and __ Track Data Base are not right either since the Scheme Plans Cxxx-SIC-R2-DWG-CR001-50048 Rev 10.0 Area 3 Scheme Plan - Stepney Green Junction to Plumstead Portal, Single source of truth where the requirements from DIR below are reported, makes up the input for and your Cxxx-SIC-R2-GIN-CR001-50012 Rev 1.0 ATS TVSM Configuration Data Ventilation Section looks confirming as it does not include any chainages. We picked up discrepancies from the DIR as follows: Cxxx-SIC-R2-RSP-CR001-50029 14.0 DIR ATS-009-TVS Cxxx/Cxxx ATS to Tunnel Ventilation System (Signalling) Table 21 - Crossrail Eastbound VS20E - VSLP WB chainage (19,580) in DIR, SP incorrect as v10 Mod 60 Rev."FF" chainage changed to 19,461. VS22E - VSLP EB & VSSP WB chainage in DIR (Tunnel Eye 22,544), SP incorrect as chainage states (Tunnel Eye 22,557). VS22E - Above VSLP EB and VSSP WB identification at Tunnel Eye missing from SP Table 22 - Crossrail Westbound VS22W - VSLP EB and VSSP WB identification at Tunnel Eye missing from SP. How does the Scheme Plan make up the right input to ATS and __? Can you please provide explanations about the above and how __ and CRL can have certainties whether the LTRZ layout is right or not in the __ TDB and against which input if not the Scheme Plans since no submitted Engineering deliverable include these. It appears that according to the Scheme Plan the incorrect chainages are right side issues still preventing the signalling system to allow more than 2 trains in a vent section. This is unknown for those missing on the Scheme plan. Are there others issues of this nature in all Scheme Plans?
| 05SY - Systemwide | Cxxx-NCR-000212 | NCR | 24V Surge Arrestor Additional Mod |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-11-30 | 2021-11-05 12:41 | -25 | 2021-02-05 14:51 | Systems - Signalling | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | To address NCR-206 (50V Surge Arrestor Issue), __ Cxxx Engineering designed and implemented a 24V variant mod of surge arrestor. However, the 24V mod did not fix the issue and required another mod.
| 05SY - Systemwide | Cxxx-NCR-000213 | NCR | Damaged XR085 marker board |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-03-29 | 2021-03-09 11:30 | -20 | 2021-01-27 16:13 | Systems - Signalling | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | Cxxx site team have found damage to marker board XR085 and a level 4 RIVO (#14249666, see attached) has been raised to highlight damage to Cxxx assets. The outer edge of XR085 marker board has been dented (see attached photo) See details below: Incident Type: Property Damage Overall outcome: Level 4 ID: 14249666 Date Occurred: 22/01/2021 Time Occurred: 01:45 Location: Cxxx - Signalling System Crossrail location: WB Trace on approach to TCR Station Contractor: __ Description of the incident: Damage to XR085 marker board dented on outer edge see photo Person Leading Investigation: Gareth __ Person who raised incident: Terry McCarthy
| 05SY - Systemwide | Cxxx-NCR-000214 | NCR | Damaged CBTC signage at XWN/NR Fringe |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-07-16 | 2021-06-23 12:47 | -23 | 2021-03-16 15:04 | Systems - Signalling | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Cxxx site team have found damage to CBTC signage and a level 4 RIVO (#14442768, see attached) has been raised to highlight damage to Cxxx assets. The outer edge of the CBTC sign has been damaged post installation on both sides (see attached photo's)
| 05SY - Systemwide | Cxxx-NCR-000215 | NCR | Balise FB at WWC has been damaged by unknown third party |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-07-16 | 2021-09-10 13:10 | 56 | 2021-03-16 15:25 | Systems - Signalling | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Cxxx site team have found damage to Balise FB WWC 33 (EB road just East of CP19) by unknown third party and a level 4 RIVO (#14494678, see attached) has been raised to highlight damage to Cxxx assets. The bottom edge of the Balise has been damaged post installation (see attached photo's)
| 05SY - Systemwide | Cxxx-NCR-000216 | NCR | Asset data - Interface Units configuration and Switchboard assets |  | Crossrail | PDP | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-06-04 | 2021-05-28 12:53 | -7 | 2021-05-04 15:51 | Information Management - Asset Information | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | In the population of Signalling Asset Data Temporary LV/UPS Extract Scope, __ had used the L-Class Cabinet for the switchboard, along with a number of other L-Classes to cover the switchboard equipment within the switchboard case (cabinet). The RFLi review had commented on this: "Agreement that the FU within the temporary PFU will be full and complete - Main Switchboards, Switchboards are not included within the Main Switchboard - Can you confirm if you were saying that CRLs position on this was correct and acceptable, if not, what do we need?" In addition some of the L-Classes used are not allowable in the Main Switchboard Functional Unit. The Asset Data was reviewed by __ with CRL and the correct action in accordance with the baseline is to use a single L-Class Switchboard and not include any further details of the Assets contained within. This meant deleting circa 700 assets and replacing them with about 30. However RFLi declared that they wanted the new Switchboard assets and to keep all the others (as it seemed regrettable to discard the work done), despite the risks associated with unintended consequences of not sticking to the baseline. As a result the below was agreed:  RFLi want to keep the assets from the original submission  Agreed by CRL/RFLi/__ that cabinets assets should be deleted  NCR Use as Is to cover Interface Units configuration issue. This is to be a one off case and the same logic shall not be mandated on other MEP Scopes  Once switchboard assets are included, no further asset/Asset Classes required in this Extract Scope  RFLi accept the risk of unintended consequences This NCR is to confirm the Use as Is status for the Main Switchboard Functional Unit Asset Data population which includes Switchboard Asset and further asset breakdown within the Switchboard and associated configuration issues.
| 05SY - Systemwide | Cxxx-NCR-000217 | NCR | Asset data - “Battery Stands” - L215611/Cabinet to PFU061/LV Power System allocation |  | Crossrail | PDP | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-07-30 | 2021-06-30 13:20 | -30 | 2021-05-04 16:17 | Information Management - Asset Information | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During meeting between Cxxx, CRL and RFL on 18/03/2021 it was agreed that Battery Stands, recorded as "L215611 Cabinet" class, should be moved from LFU076 into LV PFU (see attached e-mail from __ sent on 18/03/2021 at 13:51). This was then raised as comment on RFLs comment sheet (see comment 3 within CRL1-RFL-Z3-XCS-CR001-50137 R1).
| 05SY - Systemwide | Cxxx-NCR-000218 | NCR | Non Bonding of Balise Ramp at Connaught Tunnel |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-11-01 | 2021-11-03 10:47 | 2 | 2021-10-06 11:24 | Systems - Signalling | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The Balise ramp design does not include bonding details for the ramp.
| 05SY - Systemwide | Cxxx-NCR-000219 | NCR | Plumstead PSP Incorrect Labelling Issue |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-12-17 | 2021-11-23 12:06 | -24 | 2021-11-11 11:37 | Systems - Signalling | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Site Test team reported that while replacing a failed isolating switch at Plumstead PSP, incorrect labelling was identified. The incorrect labelling resulted in the wrong circuit being isolated initially, which was only highlighted as part of __ testing checks whereby equipment on the ‘A’ leg went down, when it should have been equipment on the ‘B’ leg. As an immediate corrective action, the correct circuit was then identified and isolating switch replaced, with all signalling equipment reported as healthy on completion of works.
| 05SY - Systemwide | Cxxx-NCR-000220 | NCR | RCC bookwiring does not correct the wire count errors identified |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2022-05-31 | 2022-05-12 13:58 | -19 | 2021-11-12 16:26 | Systems - Signalling | 500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | As per the comment sheet the RCC bookwiring is incorrect compared to site meaning the RCC SER is difficult to maintain.
| 05SY - Systemwide | Cxxx-NCR-000221 | NCR | Westbourne Park SSF not updated as required for Trial Operations |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-12-17 | 2021-12-16 08:44 | -1 | 2021-11-12 16:32 | Systems - Signalling | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Comments not responded after 6 months.
| 05SY - Systemwide | Cxxx-NCR-000224 | NCR | Asset Labelling with Non-compliant label placement. Affecting ES-SYS-03-SC & ES-SYS-12-SC |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2022-02-28 | 2022-02-03 21:56 | -25 | 2021-11-30 12:30 | Information Management - Asset Information | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | Various Assets where labels have been installed directly onto the asset as opposed to on an adjacent permanent structure. This NCR is to raise awareness to RFL of this fact. CRL /Cxxx believe that it is not viable for cost and time to replace these labels. Affected lclasses are: L76818 RFID Plaque L76258 Emergency Alarm Unit L215661 Depot Test Magnet L21398 Disconnection Boxes L215615 Axle Counter Detection Head Junction Box L215667 Rack Mounted Line Matching Unit LMU L215667 Track side Line Matching Unit LMU L215674 Track Circuit PSU L215668 Rx Receiver L215671 Track Relay TR L215672 Tx Transmitter L746155 Isolator L7868 Remote Condition Monitoring L7414 Battery Chargers L7681 Fibre Optic Splice Cabinet L76819 Code Reader Writer L7642 Head End Computer L74221 Transformers L215651 Line Wide Overview Display (LWOD) L76116 Loudspeakers L215654 Automatic Power Control (APC) Magnets
| 05SY - Systemwide | Cxxx-NCR-000225 | NCR | Incorrect transducers installed at Westbourne Park |  | Contr | SIC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2022-03-31 | 2022-02-22 13:57 | -37 | 2021-11-25 14:19 | Systems - Signalling | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | Incorrect transducer type fitted to the MPEC remote monitoring sensors at XWN for the EBI low power track circuits. CFX00594860 has been raised to manage the issue to resolution
| 05SY - Systemwide | Cxxx-NCR-000001 | NCR | Lamp Column Strike during offload of materials |  | Contr | VLK | ATA - Aldersbrook Tunnelling Academy (Central) |  | 2018-04-30 | 2018-05-21 15:32 | 21 | 2018-01-17 15:22 | Logistics - Logistics - General | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Not Defined | Completed |  | During the delivery of 6F2 stone the delivery vehicle struck a lamp column, the delivery driver did not wait for the designated Banksman
| 05SY - Systemwide | Cxxx-NCR-000002 | NCR | Late Design Change to DN-05 door reveal width |  | Contr | VLK | ATA - Aldersbrook Tunnelling Academy (Central) |  | 2018-04-30 | 2018-05-14 15:35 | 14 | 2018-01-17 15:21 | Architectural - Doors | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Late Architectural change to widen door opening DN-05 for DDA compliance and to avoid door swing clash
| 05SY - Systemwide | Cxxx-NCR-000003 | NCR | Ramp detail missed from DN-05 |  | Contr | VLK | ATA - Aldersbrook Tunnelling Academy (Central) |  | 2018-02-15 | 2018-02-19 10:44 | 4 | 2017-10-18 14:07 | Architectural - Flooring | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | Architectural design excluded an External Ramp between DN-05 and external footpath
| 05SY - Systemwide | Cxxx-NCR-000004 | NCR | M&E IRN Handover Sign off |  | Contr | VLK | ATA - Aldersbrook Tunnelling Academy (Central) |  | 2018-04-30 | 2018-05-14 15:46 | 14 | 2018-01-17 15:00 | Information Management | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | IRN Not signed off prior to power on
| 05SY - Systemwide | Cxxx-NCR-000005 | NCR | BUCF - IMS M&E IRN |  | Contr | VLK | ATA - Aldersbrook Tunnelling Academy (Central) |  | 2018-04-30 | 2018-05-14 15:39 | 14 | 2018-01-17 15:02 | Information Management | 500 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | In line with the Project Quality Plan appendix 6 ‘IRN M&E handover procedure’, each of the specific M&E systems are to be signed off by installation contractor, __ and Crossrail prior to commissioning, the paperwork was not completed until after commissioning commenced
| 05SY - Systemwide | Cxxx-NCR-000006 | NCR | By Exception Drawing Approval |  | Contr | VLK | ATA - Aldersbrook Tunnelling Academy (Central) |  | 2018-01-31 | 2018-05-16 12:20 | 105 | 2018-01-17 15:20 | Information Management | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | CRL Process 'by exception' process (CRL-XRL-07-GPD-CR001-50023) for Option 2 works in lieu of Gate system
| 05SY - Systemwide | Cxxx-NCR-000007 | NCR | Mock Tunnel Setting Out |  | Contr | VLK | ATA - Aldersbrook Tunnelling Academy (Central) |  | 2018-02-16 | 2018-06-25 13:49 | 129 | 2018-01-17 14:46 | Architectural - Walls | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Mock tunnel constructed short from Grid-H (see design drawing 50117)
| 05SY - Systemwide | Cxxx-NCR-000010 | NCR | Mock Tunnel Steel protruding into Tunnel |  | Contr | VLK | ATA - Aldersbrook Tunnelling Academy (Central) |  | 2018-02-07 | 2018-05-14 15:41 | 96 | 2018-01-24 10:43 | Architectural - Partitions | 500 |  | Planning | Rework | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | Option 2 – Mock Tunnel - Crossrail RFL Training Facility Steel Encroaching into Head of Mock Tunnel
| 05SY - Systemwide | Cxxx-NCR-000011 | NCR | Crossrail Cxxx System wide Contractor __ Fixing Setting out |  | Contr | VLK | ATA - Aldersbrook Tunnelling Academy (Central) |  | 2018-02-16 | 2018-06-25 14:14 | 129 | 2018-01-24 10:49 | Civil - Tunnelling | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Mock Tunnel missing Cxxx contractor __ - the assured design (screenshot below; circled in red) shows two channels, 340mm apart, towards the top of the walkway bracket. These have not been installed on site
| 05SY - Systemwide | Cxxx-NCR-000012 | NCR | Cxxx contractor __ Station Platform hight discrepancy 40mm |  | Contr | VLK | ATA - Aldersbrook Tunnelling Academy (Central) |  | 2018-04-30 | 2018-06-25 13:56 | 56 | 2018-03-05 13:32 | Track - Walkways | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Mock Tunnel missing Cxxx contractor __ Platform height is 40mm above assured drawing The staircase landing platform height indicated on Assured drawing C626-VLK-S-DWG-CR527-50026 is 1414mm AFFL, the __ Platform height is 1455mm AFFL
| 05SY - Systemwide | Cxxx-NCR-000001 | NCR | Option 1 - Concrete Upstand Design |  | Contr | VLK | ATA - Aldersbrook Tunnelling Academy (Technical (Design)) |  | 2018-08-28 15:38 | 2018-08-15 10:11 | -13 | 2018-01-17 14:56 | Architectural - General | 25000 |  | Design | Repair | 2 (6-60k) | Complete | Design Problem - Inadequate or defective design | Completed |  | __ require South elevation MEWP access and setting out dimension of 6000mm between North & South boundary Concrete upstand, actual installed 5864mm
| 05SY - Systemwide | Cxxx-NCR-000002 | NCR | OHLE Pad 5 Base Setting Out |  | Contr | VLK | ATA - Aldersbrook Tunnelling Academy (Technical (Design)) |  | 2018-07-06 08:45 | 2018-06-22 09:17 | -14 | 2018-04-18 13:24 | Structural Engineering - Concrete Member | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Pad 5 setting out of Eastings & Northings will encroach into the road by 500mm, and been cast only 5500mm which has effected the OHLE Post positions SOP020 – E 543174.165 / N 186248.589 SOP018 – E 543175.370 / N 186246.118
| 05SY - Systemwide | Cxxx-NCR-000003 | NCR | Mock tunnel walkway clash with PSD |  | Contr | VLK | ATA - Aldersbrook Tunnelling Academy (Technical (Design)) |  | 2018-05-18 | 2018-07-30 14:20 | 73 | 2018-05-04 08:46 | Information Management | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Clash with the mock train and the walkway at the end of the mock station box. Centreline of the PSD do not line up with the centre line of the doors on the train and there is about 300mm difference.
| 05SY - Systemwide | Cxxx-NCR-000001 | NCR | Work comenced without an accepted ITP |  | Crossrail | PDP | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2015-09-07 | 2016-02-05 09:12 | 151 | 2015-08-21 16:45 | Systems - Other | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Not Defined | Completed |  | Work has commenced on the build of the prototype platform screen doors at Melksham without an accepted ITP in place.
| 05SY - Systemwide | Cxxx-NCR-000002 | NCR | KBR Product Breakdown Structure (__) document has been at a Code 3 Decal for 11 weeks with comments not addressed within Contractual Period of Reply |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-04-28 | 2016-05-03 07:58 | 5 | 2016-03-31 08:31 | Mechanical - Platform Edge Doors | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | During a planned Crossrail surveillance undertaken on 24th March 2016 which looked at s management of the __, Materials Proposal Schedule (MPS) and Demonstration of Materials Compliance requirements, it was identified that the __ document (Cxxx--R-STP-CR001-50036) has been at a Code 3 Decal since Jan 2016. It was also identified at the time of the surveillance that none of the comments had started to be addressed/ actioned, with procurement looking to commence in around 4 weeks time. Under Crossrail Document Management Procedure CRL1-XRL-Z3-GPD-CR001-50001 (Rev 3) a Code 3 Decal stands for “Not Accepted. Revise and resubmit. Work may not proceed”. Furthermore, it was stated by that the __ review process is as follows; > ISA (30 days approx. review) > ASBO (30 days approx. review) > CRL. As the comments had yet to be addressed, and taking into account the __ review process, this could have an impact on material procurement timeframes. Additionally, when discussing the __ requirements, it was clear that were unsure on what products required incorporation into this document; this will require clarity and time before any resubmission is made. As it has been 11 weeks since the comments were made, s response to the comments has not been undertaken within the Contractual Period of Reply. Works Information Vol 2B Part 14 states “In the case of the first submission of a deliverable, in this section, for the Project Manager’s acceptance, the Project Manager replies within 4 weeks of the date of submission. Any further revisions, submissions and responses by the Contractor or Project Manager shall be made within the period for reply.” Crossrail ‘Process and Format for Product Breakdown Structures for Systems’ procedure CRL1-XRL-08-GPS-CR001-50002 states under section 6 “The __ is to be prepared as a formal contract deliverable for each of the CRL Delivery Contracts, and for each Elementary System”….”These are to be made available to CRL prior to the equipment procurement phase for each of the Delivery Contracts to manage the risk of procuring equipment which is subsequently not approved for use on the Crossrail Project”.
| 05SY - Systemwide | Cxxx-NCR-000007 | NCR | Surveillance of Competency Management System (KAMMS) for PSD Production |  | Contr | KBR | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-01-13 | 2017-03-21 11:02 | 67 | 2016-12-22 09:47 | Mechanical - Platform Edge Doors | 3000 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Although the scope of the Surveillance was __ Production, it was noted that there was no evidence of the equivalent KAMMS competency management process in place for Installation, T&C, and miscellaneous others who will be involved in the CRL on-site operations. Cxxx--R-CR001-5001 section 2.1 states the scope of competency management to be "all S employees (including agency staff) engaged on the Cxxx project"
| 05SY - Systemwide | Cxxx-NCR-000008 | NCR | EED Door - Roller wave on glass visible - PW1 - KBPD00A/0002 - FP/ASD/EED MODULE |  | Contr | KBR | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-12-08 | 2019-05-14 10:56 | 157 | 2017-05-05 09:51 | Materials - General | 90000 |  | Manufacturing Defect | Repair | 1 (>60k) | Complete | Subcontractor Problems - Insufficient surveillance of subcontractors | Completed |  | EED Door - Roller wave on glass visible
| 05SY - Systemwide | Cxxx-NCR-000009 | NCR | Material Proposal Schedule (MPS) has not been updated since April 2016 |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-04-04 | 2017-04-12 08:50 | 8 | 2017-03-07 13:13 | Mechanical - Platform Edge Doors | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Counterfeit Items | Completed |  | A planned Crossrail surveillance was undertaken on 7th March 2017 to look at offsite manufacture of Platform Screen Doors (PSDs) at __. During the documentation review it was identified that the MPS, Cxxx--R-TSC-CR001-50001, Revision 7 had last been submitted to Crossrail April 2016, 10 months ago. As a result, the current MPS document in parts does not align with those materials and suppliers being used as part of the manufacturing process. Works Information Vol 2B Part 20.7 states “The Contractor shall regularly submit the Materials Proposal Schedule and a matrix of approvers for all materials and products..”
| 05SY - Systemwide | Cxxx-NCR-000010 | NCR | SOPs have not been signed and approved, with some that are controlling the works still in progress |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-04-04 | 2017-04-24 08:19 | 20 | 2017-03-07 13:20 | Mechanical - Platform Edge Doors | 500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | A planned Crossrail surveillance was undertaken on 7th March 2017 to look at offsite manufacture of Platform Screen Doors (PSDs) at __. During the documentation review, were requested to provide the Standard Operating Procedures (SOPs) which have been produced to control the stages of works. On review the following was identified: 3 had been written into the CAA system and a SOP document produced (motor assembly, solenoid lock assembly and header EED/SD/FP assembly) 3 had been written into CAA but no SOP document had been produced (horizontal build, vertical build and test) 1 had not been written into CAA and no SOP document had been produced (loading and dispatch) In addition it was identified that off those SOPs where a document had been produced, none showed evidence that they had been ‘checked and approved’ prior to use. Production Assembly ITP Cxxx--R-ITP-CR001-50004 (Revision 1) states a requirement under Inspection Number 1.6 for ‘Approval of SOPs’ with ‘ to Check and Approve’ ‘Prior to Mass Production’. This is a Hold Point for under the Pre-Start Documentation section. In addition, ISO 9001 under 4.2.3 ‘Control of Documents’ states “Documents required by the quality management system shall be controlled … A documented procedure shall be established to define the controls needed for a) to approve documents for adequacy prior to issue..”
| 05SY - Systemwide | Cxxx-NCR-000011 | NCR | Surveillance schedule last produced and submitted in July 2016 |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-04-04 | 2017-05-11 11:29 | 37 | 2017-03-07 13:23 | Mechanical - Platform Edge Doors | 500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | A planned Crossrail surveillance was undertaken on 7th March 2017 to look at offsite manufacture of Platform Screen Doors (PSDs) at __. During the documentation review it was identified that the Surveillance Schedule, Cxxx--R-TSC-CR001-50002, Revision 10 had last been submitted to Crossrail July 2016, 7 months ago. In addition, the current revision has been at a Code 2 decal since Crossrail review and comment (Sept 2016). Works Information Vol 2B Part 20.2 states “the Contractor shall perform quality-related site surveillance activities including in-process monitoring against method statements in accordance with a planned schedule”. In addition, Monitoring and Surveillance Procedure CRL1-XRL-Z-GPD-CR001-50001 4.8 states “The Contractor is responsible for the following: Producing a Surveillance Schedule, for Delivery acceptance…” Moreover, surveillance procedure Cxxx--R-GPD-CR001-50008 2.1 states “The Quality Manager will continuously review the surveillance plan in the light of any emerging issues or concerns…”. The current schedule dated July 2016 is currently out of alignment with those works progressing, and the Code 2 comments have not been addressed within the Period of Reply.
| 05SY - Systemwide | Cxxx-NCR-000012 | NCR | No evidence produced showing KBR checks as part of the SAP goods in process and Block 300 release |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-04-04 | 2017-04-21 10:35 | 17 | 2017-03-07 13:26 | Mechanical - Platform Edge Doors | 500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | A planned Crossrail surveillance was undertaken on 7th March 2017 to look at offsite manufacture of Platform Screen Doors (PSDs) at __. During the production walk around the goods in and SAP process was discussed. It was stated that as part of the SAP process, goods with a certain coding would require additional checks by operatives prior to release into the stores. In addition it was stated that any ‘defective’ items quarantined in Block 300 would require additional checking prior to release to dispatch/stores. Three products were sampled; Trolly Assembly (LH) (located in dispatch area), Door Post and Glass Panel (located in stores). These items required additional checking at goods in prior to release to stores. Records were requested to show evidence of what checks were required and that they are being carried out, however no verifiable evidence could be provided. The respective FAIs had been uploaded into SAP, however no records with additional visual/dimensional checking (product dependant) is produced/uploaded into SAP. In addition, the Trolly Assembly products had been subject to Block 300 quarantine. Records were requested as evidence to show that the Block 300 release checks are being carried out; none could be provided or were located in SAP. The SAP system was scrutinised, however it was not clear whether the system ‘deletes’ this information following release to stores. As part of the closure, the SAP process should be looked at to ensure verifiable evidence of checks is being retained to assure the process.
| 05SY - Systemwide | Cxxx-NCR-000013 | NCR | The current PSD Factory Acceptance Testing document has been at a Code 3 decal since Sept 2015 |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-04-04 | 2017-05-12 11:16 | 38 | 2017-03-07 13:32 | Mechanical - Platform Edge Doors | 500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | A planned Crossrail surveillance was undertaken on 7th March 2017 to look at offsite manufacture of Platform Screen Doors (PSDs) at __. During the documentation review it was identified that the PSD Factory Acceptance Testing (FAT) document, Cxxx--R-STP-CR001-50027, Revision 1 has been at a Code 3 decal since September 2015. A Code 3 decal stands for ‘Not Accepted. Revise and resubmit. Work may not proceed”, as such works have been progressing without an agreed document in place. It was stated during the surveillance that this plan is being used to control the FAT for each Module prior to release. On review of the system, it was identified that the document was currently at Revision 4 on their internal system referencing PTS/CRL/003 ( internal document). It was however unclear what document Revision is being used to control the FAT testing.
| 05SY - Systemwide | Cxxx-NCR-000014 | NCR | No evidence of product assembly checks as required by the ITP |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-04-04 | 2017-06-22 10:49 | 79 | 2017-03-07 13:38 | Mechanical - Platform Edge Doors | 500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | A planned Crossrail surveillance was undertaken on 7th March 2017 to look at offsite manufacture of Platform Screen Doors (PSDs) at __. On the morning of the surveillance, Modules 11, 12 and 13 had been dispatched; these were selected as a sample for the surveillance. The Contractor was requested to provide evidence of Product Assembly Checks for these Modules as required by ITP Cxxx--R-ITP-CR001-50004 (Revision 1) Inspection Numbers 3.1-3.9 which are Hold Points within the ITP. Under these activities, the ITP asks for 100% checking (visual and dimensional) with the deliverable being ‘Completed Check Sheet MD/CRL/028’. On request, it was identified that the Check Sheet had not been completed for Modules 11, 12 and 13. The CAA system was referred to with regards to capture of these checks as part of the automated process; however, a verifiable report from the .txt file generated from the CAA system is still in progress, as such the manual entry is the current approved process. As the surveillance was based on a sample it is unclear on whether Module 1-10 had under gone such checking, as such this should be investigated by to identify the extent.
| 05SY - Systemwide | Cxxx-NCR-000015 | NCR | No evidence of Factory Acceptance Testing for Modules 11, 12 and 13 outside of the un-verified ‘ATE’ software |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-04-04 | 2017-09-19 07:29 | 168 | 2017-03-07 13:41 | Mechanical - Platform Edge Doors | 500 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | A planned Crossrail surveillance was undertaken on 7th March 2017 to look at offsite manufacture of Platform Screen Doors (PSDs) at __. On the morning of the surveillance, Modules 11, 12 and 13 had been dispatched; these were selected as a sample for the surveillance. Evidence of acceptable FAT was requested. It was stated that the ATE ‘Metal Mickey’ software/equipment was being used to undertake FAT. However, it was confirmed by Crossrail that this software initially required validation against manual checking in order to obtain acceptance for the use ATE going forward. This had yet to be completed. ISO 9001 7.6 ‘Control of Monitoring and Measuring Equipment’ states ‘When used in the monitoring and measurement of specified requirements, the ability of computer software to satisfy the intended application shall be confirmed. This shall be undertaken prior to initial use and reconfirmed as necessary”. As the ATE system had yet to be validated, manual FAT records were requested, however no evidence was provided for Modules 11, 12 and 13. Based on this it can not be verified that adequate FAT has been completed based solely on the ATE outputs. In addition, ITP Cxxx--R-ITP-CR001-50004 (Revision 1) states requirements for ‘Functional Tests’ however it was unclear whether this was part of the FAT or separate. The ITP makes no reference in text to ‘FAT’ and outputs associated. Works Information Vol 2B Part 28.2.2.1 states “FATs shall be satisfactorily completed by the Contractor before shipment to the Site and/or the Working Areas of any item of Plant and Materials in order to verify that it and its components are fit for its intended use and otherwise comply with the Works Information”. The production of Factory Acceptance Certificates (FACs) is defined as an output from FAT. Part 28.3.7 states “Factory Acceptance Certificates … shall be issued by the Contractor …” As the surveillance was based on a sample it is unclear on whether Module 1-10 had under gone FAT with verifiable evidence available to demonstrate, as such this should be investigated by to identify the extent.
| 05SY - Systemwide | Cxxx-NCR-000016 | NCR | No weekly schedule of inspections and tests has been issued to the Supervisor |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-04-04 | 2018-02-26 10:59 | 328 | 2017-03-07 13:44 | Mechanical - Platform Edge Doors | 500 |  | Planning | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | A planned Crossrail surveillance was undertaken on 7th March 2017 to look at offsite manufacture of Platform Screen Doors (PSDs) at __. During the documentation review it was identified that are not issuing the Supervisor with a weekly schedule of inspections and tests which is non compliant with the Contract requirements. Works Information Vol 2B Part 20.8 states “The Contractor shall provide to the Supervisor a weekly schedule of inspections and test to be undertaken (to include planned and achieved).”
| 05SY - Systemwide | Cxxx-NCR-000017 | NCR | KBPD/001A/0003 - Adaptor Plate Assy - threaded insert seized |  | Contr | KBR | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-04-20 | 2017-05-12 10:43 | 22 | 2017-03-23 09:34 | Mechanical - Platform Edge Doors | 500 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | What: The threaded insert seizes into the main bracket body when it is turned to be height adjested in situ on the platform. When: 10/3/17 How many: 3 of 151 brackets used in this installation. NOTE: defect will always be detected on istallation, therefore there is no risk from installed components NOTE: Raised under S Q Notification 210144298
| 05SY - Systemwide | Cxxx-NCR-000018 | NCR | PSD post with incorrect part number marking |  | Contr | KBR | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-04-20 | 2017-06-01 09:59 | 42 | 2017-03-23 15:37 | Mechanical - Platform Edge Doors | 500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Personnel Error - Other human error | Completed |  | A PSD Post delivered to S __ was marked as KBPD/001C/0001, however upon inspection it was established the the post was a KBPD/001C/0032
| 05SY - Systemwide | Cxxx-NCR-000019 | NCR | PSD missing part number |  | Contr | KBR | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-04-20 | 2017-05-16 15:17 | 26 | 2017-03-23 15:52 | Mechanical - Platform Edge Doors | 500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Error by manufacturer in shipping or marking | Completed |  | PSD post KBPD/001C/0042 arrived at PSD wolverton with no part markinngs
| 05SY - Systemwide | Cxxx-NCR-000020 | NCR | ASD POST REAR COVER DOES NOT SIT FLUSH TO THE POST |  | Contr | KBR | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-04-26 | 2017-09-11 08:56 | 138 | 2017-03-29 11:11 | Mechanical - Platform Edge Doors | 500 |  | Manufacturing Defect | Reject | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | ASD post rear cover KBPD/006C/0001 does not align with fixing holes & does not fit flush to the post. This was found at S __, and does not affect any product delivered to CRL. The defect was comfined to a sign batch delivered from Transcal.
| 05SY - Systemwide | Cxxx-NCR-000021 | NCR | EED front Threshold Assy is twisted / will not fit PSD Module |  | Contr | KBR | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-04-26 | 2017-09-18 08:05 | 145 | 2017-03-29 11:25 | Mechanical - Platform Edge Doors | 500 |  | Manufacturing Defect | Reject | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | EED front Threshold Assy KBPD/005A/0006 is twisted & will not fit correctly to the PSD Module. The issue was found & contained in the S __ facility. All stock has been check, issue contained to a single batch from Transcal.
| 05SY - Systemwide | Cxxx-NCR-000022 | NCR | ASD Door Post footer bracket is distorted causing mis-alignment to Header |  | Contr | KBR | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-04-26 | 2017-09-12 13:47 | 139 | 2017-03-29 11:42 | Mechanical - Platform Edge Doors | 500 |  | Manufacturing Defect | Reject | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | KBPD/001C/0003 ASD RH Door Post - footer bracket away from drawing. Discover during module assy process at S __ - would not assemble. Post returned to supplier (Responsive Engineering) for root cause / prevent recurrence actions. Issue being managed through S Q Note 210144555. Issue is contained and will not affect CRL installation.
| 05SY - Systemwide | Cxxx-NCR-000023 | NCR | Media Panel kick-strip - not to length |  | Contr | KBR | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-04-26 | 2017-09-12 14:25 | 139 | 2017-03-29 11:59 | Mechanical - Platform Edge Doors | 500 |  | Manufacturing Defect | Reject | 4 (0.5-3k) | Complete | Subcontractor Problems - Other | Completed |  | Media Panel kick strip KBPD/002C/0067 is not to drawn length (9mm short to drawing). Discovered in S Production. Parts rejected to supplier. Modules supplied to CRL not affected. Issue being managed through S Q note 210144570.
| 05SY - Systemwide | Cxxx-NCR-000024 | NCR | Door Guide ASD damaged |  | Contr | KBR | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-04-26 | 2017-09-12 14:49 | 139 | 2017-03-29 12:13 | Mechanical - Platform Edge Doors | 500 |  | Damaged | Reject | 4 (0.5-3k) | Complete | Personnel Error - Other human error | Completed |  | Door Guide ASD KBPD/003A/0018 found damaged in S __ stores. Damage to plastic guide cover. Stock checked for damage, NOK parts scrapped. Defects will not escape __ plant - modules will not pass automated test. Issue being managed under S Q note 300233969
| 05SY - Systemwide | Cxxx-NCR-000026 | NCR | Busbar assy - incorrect mod strike recorded |  | Contr | KBR | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-05-24 | 2017-05-12 09:02 | -12 | 2017-03-29 16:27 | Mechanical - Platform Edge Doors | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Personnel Error - Other human error | Completed |  | The Busbar sub-assy supplied into S shows the incorrect mod strike on the ID label. No mod level is struck-through, whereas the correct condition should have the 0 struck-through. This affects all modules built to date. This is being controlled under S Q note 210144699
| 05SY - Systemwide | Cxxx-NCR-000027 | NCR | Terminal Block Assy - incorrect mod strike |  | Contr | KBR | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-05-24 | 2017-05-12 08:55 | -12 | 2017-03-29 16:36 | Mechanical - Platform Edge Doors | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Personnel Error - Other human error | Completed |  | Externally supplied Terminal Block Assy KBPD/004S/0006 should have mod state 2 indicated on thr ID label. The current mod strike is shown as 2. This is due to supplier confussion between drawing revision level & mod state. All Modules built to date are effected. This issue is being controlled though S Q note 210144693.
| 05SY - Systemwide | Cxxx-NCR-000028 | NCR | Calibration QSP does not align with actual practice |  | Contr | KBR | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-05-16 | 2017-10-10 08:00 | 147 | 2017-04-18 09:23 | Mechanical - Platform Edge Doors | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Cxxx – Platform Screen Doors Calibration Procedure CRL Document Number: Cxxx--R-GPD-CR001-50004 The QSP is is not aligned to the __ practice of holding calibration certification on the KAMMS system
| 05SY - Systemwide | Cxxx-NCR-000029 | NCR | PSD glass panels stored at WBP unprotected and adjacent to vehicle access way with no separation |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-06-19 | 2017-07-21 10:18 | 32 | 2017-05-22 13:25 | Mechanical - Platform Edge Doors | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper storage of material | Completed |  | A planned Crossrail surveillance was undertaken on 18th May 2017 to look at delivery, handling and storage of PSDs at WBP, and onsite installation of PSDs at Paddington Station. After witnessing the delivery of PSD modules at WBP, the storage area was checked where Glass Stillage’s and Non Modular items were being stored. On inspection it was identified that (see photos): a) The glass contained no protection which had been onsite for approximately 10 days; b) There was no barrier/separation between the Glass Stillage’s and the road access way; c) The Glass Stillage’s were stored on an uneven ballast surface; and d) The storage area is not a dedicated area with Cxxx using the same location for material laydown. Suitable storage and protective materials should be considered when works progress from Plumstead.
| 05SY - Systemwide | Cxxx-NCR-000030 | NCR | PSD Setting Out and Surveying MS Not Accepted and currently at a Code 3 Decal |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-06-19 | 2017-06-30 13:41 | 11 | 2017-05-22 13:28 | Mechanical - Platform Edge Doors | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Other management problem | Completed |  | A planned Crossrail surveillance was undertaken on 18th May 2017 to look at delivery, handling and storage of PSDs at WBP, and onsite installation of PSDs at Paddington Station. During the documentation review it was identified that the ‘Setting Out and Surveying’ Method Statement (MS) (Cxxx--R-GPD-CR001-50016) Rev 1 was at a Code 3 Decal. This has been so since January 2017. This MS is included in the ITP *50006 Rev 2 under Inspection Number 1.8 and is a Hold Point for . The MS is also cross referenced in a number of other MS including the Livis onsite MS.
| 05SY - Systemwide | Cxxx-NCR-000031 | NCR | Protection of installed PSDs at Paddington Station non compliant with Contract |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-06-19 | 2017-10-02 09:30 | 105 | 2017-05-22 13:36 | Mechanical - Platform Edge Doors | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | A planned Crossrail surveillance was undertaken on 18th May 2017 to look at delivery, handling and storage of PSDs at WBP, and onsite installation of PSDs at Paddington Station. Eastbound Platform – on checking the modules it was noted that the stainless steelwork has been protected with a tape type product (see photo), however the edges had been left exposed on both the verticals and horizontals. The tread plat also had no protection. Westbound Platform – on checking, Cordek material had been applied to the modules to aid protection. However this had only been applied to the platform side, the track side contained no protection. In addition, the Cordek had been ‘stuck’ to the glass, stainless steel etc with ‘Duct Type Tape’ which has a high tack and may impact critical finish surfaces. A low tack tape fit for this use should be used.
| 05SY - Systemwide | Cxxx-NCR-000032 | NCR | Westinghouse sheeting used for temporary protection of PSD modules could not be confirmed as fire compliant with LPCB or equivalent |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-06-29 | 2017-10-02 09:50 | 95 | 2017-06-01 11:50 | Mechanical - Platform Edge Doors | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | A planned Crossrail surveillance was undertaken on 18th May 2017 to look at delivery, handling and storage of PSDs at WBP, and onsite installation of PSDs at Paddington Station. It was noted during the site visit that the PSD Modules had been temporarily protected/ covered with blue Westinghouse named sheeting (see attached pictures). This remained in place during offloading at WBP and transit to the station platform work. As part of an Exit Note request (19/05), the Contractor was requested to provide evidence that the Westinghouse sheeting is approved by the Loss Prevention Certification Board (LPCB) or equivalent as required by the Project Insurance Policy contained in the Contract Data Part 1 Clause 8 of the main Contract. This states; “all temporary protective materials are to be approved by evaluation and/or testing of products by the Loss Prevention Certification Board (LPCB) (or equivalent standard approval as stated in Joint Code of Practice Fire Prevention on Construction Sites ref 14,16”. Following multiple requests for supply of acceptable certification to allow closure of the surveillance, no information has been provided. As such it could not be verified that the material used to temporarily protect the modules is compliant with the Contract requirements concerning fire, as such this Non-Conformance was raised.
| 05SY - Systemwide | Cxxx-NCR-000033 | NCR | No evidence provided as part of a CRL Quality Surveillance that the PSD lower adaptor plate galvanised thicknesses comply with the design/corrosion requirements |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-08-03 | 2018-12-04 18:26 | 488 | 2017-06-01 11:54 | Mechanical - Platform Edge Doors | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | A planned Crossrail surveillance was undertaken on 18th May 2017 to look at delivery, handling and storage of PSDs at WBP, and onsite installation of PSDs at Paddington Station. Fabrication (galvanising and welding) records for the lower adaptor plates were requested for post review (19/05). Weld records and galvanising CoC’s were provided on 23/05. On review it was noted that the adaptor plates had either been galvanised to 112 microns or 122 microns as noted on the CoC’s. On checking the Cxxx PSD Performance Specification (Cxxx-MMD-O8-RSP-CR001-00005 Rev 19) the following clauses were noted: 6.4 Structural Design PSD-104 “All materials, treatments and fixings used in the fixed structure shall be selected to provide the 30 years life under the defined environmental conditions without compromising the fire, smoke and toxicity requirements”. 13.3 Corrosive Conditions PSD-363 “The Contractor shall, when determining materials to be used, refer to BS EN 12500:2000 …. For qualitative estimations of the amount of corrosion likely to occur at typical areas along the route (- Tunnel areas – C5). In summary, the Specification requires a 30 year design life in a C5 environment. The lower adaptor plates have been galvanised to either 112 or 122 microns. Based on the rate of corrosion for a C5 environment (4 < Rcorr ≤ 8) as stated in Table 1 of ISO 14713-1:2009 Zinc Coatings – Guidelines and Recommendations for the Protection Against Corrosion of Iron and Steel in Structures, the 112 micron coating would give an expected durability of 14/28 years calculated life to first maintenance (Table 2 of the standard), with the average durability being 21 years. In similar terms, the 122 micron coating would give an expected durability of 15/30 years with the average being 23 years. Based on the average durability from the calculations, the 30 year design life would not be met. The Contractor was requested to clarify the above to confirm compliance with the Contract requirements (23/05). Following multiple requests no information has been provided, as such it can not be confirmed whether the galvanising thickness is compliant, as such this NCR was raised to allow closure to the surveillance.
| 05SY - Systemwide | Cxxx-NCR-000034 | NCR | Dissimilar metals in contact for PSD lower adaptor plates and associated fixings with potential for galvanic corrosion – no evidence provided confirming acceptance |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-08-04 | 2018-12-03 16:15 | 486 | 2017-06-01 12:00 | Mechanical - Platform Edge Doors | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | A planned Crossrail surveillance was undertaken on 18th May 2017 to look at delivery, handling and storage of PSDs at WBP, and onsite installation of PSDs at Paddington Station. During the site visit to Paddington Station the following metal interfaces were observed (see pictures attached): 1) Stainless Steel fixings, washers and nuts in direct contact with the Galvanised lower adaptor plates; 2) Stainless Steel module tread plate in contact with the Galvanised module bracket. On checking the Cxxx PSD Performance Specification (Cxxx-MMD-O8-RSP-CR001-00005 Rev 19) Section 13.3 Corrosive Conditions PSD-364 states; “The Contractor shall design the PSD system so that the effects of galvanic corrosion are avoided”. The stainless steel/ galvanising contact may cause potential for bi-metallic corrosion. A post surveillance request was made (19/05) to understand whether this had been discussed and accepted as part of the design. Following multiple requests no information has been provided, as such it can not be confirmed whether the design and installation is compliant with the Specification requirements, as such this NCR was raised to allow closure to the surveillance.
| 05SY - Systemwide | Cxxx-NCR-000035 | NCR | Bowing of Lower Covers seen at Bond Street West |  | Contr | KBR | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-05-03 | 2019-05-03 15:09 | 0 | 2017-06-05 15:35 | Mechanical - Platform Edge Doors | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Error by manufacturer in shipping or marking | Completed |  | During a Cxxx site inspection at Bond Street West (15/5/17) it was reported that "Stainless steel trim bowing to the underside of header panel along the horizontal length"
| 05SY - Systemwide | Cxxx-NCR-000036 | NCR | Contract Master Deliverables List (CMDL) – period submission requirement |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-09-06 | 2017-09-12 15:01 | 6 | 2017-08-23 15:08 | Information Management | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Period MDL Cxxx--R-MDL-CR001-50001, Rev 7.0, Effective Date: 07/11/2016 is 36.5 weeks late. An NCR has been raised because period MDLs are required to be submitted by the contractor every 4-week period. Cxxx has failed to meet requirements of the Works Information - Systems; Volume 2B part 29.2.3.1.
| 05SY - Systemwide | Cxxx-NCR-000037 | NCR | IRF Schedule & Witness points |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-05-08 | 2018-06-06 15:56 | 29 | 2018-03-09 13:21 | Electrical - General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Cxxx-NCR-000016 was initiated one year ago for the reason of failure to issue a weekly schedule of inspections. Works Information Vol 2B Part 20.8 states “The Contractor shall provide to the Supervisor a weekly schedule of inspections and test to be undertaken (to include planned and achieved).” The issue was negotiated in January with a view to closing the NCR. An arrangement was put in place with quality to issue a weekly IRF with a schedule of inspections whereby Crl have visibility of checks where Crl mechanical and electrical Field Engineers can witness these checks at their own discretion moving on to 2.1 testing and the remaining critical T&C stages. The NCR was closed by Crossrail on the back of this arrangement. Crl Field engineers did not receive an IRF schedule notification this week commencing 5th March 2018. However, the Crl construction team noted that 2.1 mechanical checks were being included on contractor shift reports for Tuesday 6th for Canary Wharf. Woolwich 2.1 mechanical checks on Tuesday 6th and Thursday 8th. Crossrail Mechanical & Electrical FE’s need to have visibility of checks that are occurring for any given week – albeit with an understanding that times and circumstance may change. This needs to be managed through communication through on site quality rep and Crl Mechanical and Electrical FE’s. This NCR will remain open until this process is happening seamlessly on a weekly basis. See attached correspondence.
| 05SY - Systemwide | Cxxx-NCR-000038 | NCR | Incorrect Lugs installed |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-07-22 | 2019-07-22 10:40 | 365 | 2018-05-30 14:36 | Electrical - Earthing & Bonding | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Insufficient quantity of material to do the job | Completed |  | During Earthing & Bonding installation prior to energisation of zones 3&4, the contractor has stated that replacement of lug connectors inside DAD's at a number of Locations will be necessary as alternative Lugs have been utilised as materials were not available on site. The contractor has stated they are surveying the necessary re work and are to report back with extent of necessary replacement work.
| 05SY - Systemwide | Cxxx-NCR-000039 | NCR | Intermittant failure of Lock Mechanism on Media Panels |  | Contr | KBR | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-06-04 | 2019-06-06 15:58 | 2 | 2018-06-13 10:14 | Mechanical - Platform Edge Doors | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | QRN029 - Lock mechanisms on media panels are not operating reliably, intermittant faults found on doors (lock fails to release using the key and can only be reset by manually pushing the shootbolt back).
| 05SY - Systemwide | Cxxx-NCR-000040 | NCR | Threshold Too Short (Gapping) |  | Contr | KBR | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-08-17 | 2019-10-01 15:53 | 45 | 2018-06-13 10:22 | Mechanical - Platform Edge Doors | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | QRNCB001 - Following the installation of a non-modular fixed panel kit KBPD/000A/0062 on the Eastbound platform at Woolwich it was found that the threshold provided was too short (gapping). On further investigation it was noted that the correct part numbers had been supplied, however the gap left was far too big (this was particularly noticable on the platform side). It is worth noting that other parts, such as the lower cover and header, that also span the gap betwen the posts seem to fit correctly.
| 05SY - Systemwide | Cxxx-NCR-000041 | NCR | Solenoid Lock Remaining on after operation of ERM Handle (TUCA Training Rig) |  | Contr | KBR | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-07-29 | 2019-08-14 13:27 | 16 | 2018-06-13 10:32 | Mechanical - Platform Edge Doors | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | 1. Whilst training maintenance teams at TUCA using the latest DCUs programmed by specialist contractors (TAC) to latest design criteria SDS V10.1, it was observed that after operating the Emergency Release Mechanism (ERM) on the Automatic Sliding Doors (ASD), the solenoid lock mechanism remained on and the ASD remained in a "Fault" condition with the Door Status Indicator (DSI) flashing. There was no way to get out of the situation unless powering down and back up the whole System. (DCU was made production type to fix Snag on TUCA Installation checks as the earlier version had a Learn Run and Obstruction operational problem) 2. 95mm Earth Installation at TUCA stops removal of some items ie the DCU in the photo. 3. The DCU version used for EMC and environmental testing is older than the production model.
| 05SY - Systemwide | Cxxx-NCR-000042 | NCR | Lock Shootbolt Pin - Topbush Missing |  | Contr | KBR | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-07-18 | 2019-07-19 10:05 | 1 | 2018-06-13 10:45 | Mechanical - Platform Edge Doors | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | QRN027 - Bush missing from end of shootbolt, part fitted correctly during assembly, is found to be missing during onsite testing of door operation.
| 05SY - Systemwide | Cxxx-NCR-000043 | NCR | Bowed Protective Strip |  | Contr | KBR | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-06-04 | 2019-06-06 16:01 | 2 | 2018-06-13 11:42 | Mechanical - Platform Edge Doors | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | QRN035 - When checking the gaps beneath media panels and EEDs the lower protective strip has been found to be bowed along the length by up to 3mm. This makes achieving the required gaps in accordance with the requirements of Cxxx--R-LLG-CR001-50003 very difficult, especially at the extreme ends of the doors. Woolwich WB Drivers door is particularly bad and requires adjustment.
| 05SY - Systemwide | Cxxx-NCR-000044 | NCR | Shootbolt does not return fully when the crew lock is operated. |  | Contr | KBR | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-05-31 | 2019-06-11 16:07 | 376 | 2018-07-20 06:58 | Mechanical - Platform Edge Doors | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | Shootbolt does not return fully when the crew lock is operated.
| 05SY - Systemwide | Cxxx-NCR-000045 | NCR | Vertical alignment of covers |  | Contr | KBR | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-10-02 | 2019-10-04 12:00 | 2 | 2018-07-20 07:05 | Mechanical - Platform Edge Doors | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | In some instances, covers are not aligned with each other vertically. As there is no way to adjust the potential of adding shims beneath the hinges would help with alignment. These could be fitted to the cover side or the chassis side to allow up/down adjustment as required.
| 05SY - Systemwide | Cxxx-NCR-000046 | NCR | Installation, Inspection & Test Plan – PID and Ethernet Switch to be Updated |  | Contr | KBR | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-05-15 | 2019-05-21 12:58 | 6 | 2018-08-09 12:35 | Mechanical - Platform Edge Doors | 0 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Previous Construction - Interfacing issues | Completed |  | Current ITP is Code 3 - ITP to be updated in order to allow correct installation of works.
| 05SY - Systemwide | Cxxx-NCR-000047 | NCR | Paddington Installation of the Supply and Load Cables |  | Contr | KBR | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-09-03 | 2019-09-09 09:58 | 6 | 2019-07-05 11:25 | Electrical - Cable Management | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | The supply and load cables of the PSD system have been in installed within the same containment meaning that with the isolator in the off position there would still be live cables within the CMS creating a potential hazard.
| 05SY - Systemwide | Cxxx-NCR-000048 | NCR | Poster Installation |  | Contr | KBR | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-03-26 | 2021-02-18 10:40 | -36 | 2021-02-04 17:08 | Systems - Platform Screen Doors | 6000 |  | Workmanship | Rework | 3 (3-6k) | Complete | Material/Preservation Problems - Other | Completed |  | Line map and poster frit at Bond Street contain visual defects, typically white milky transparent marks. These marks are not location specific on the line map or frit, not at each line map per platform and not at every platform. The marks are not visible prior to application and may develop post application. X1 Line Map not fitted at Canary Wharf due to existing Frit fitted for Media Panel, removal and f__ent- complete 4/2/21 - All stations line maps expect Whitechapel have been repaired or replaced, Whitechapel currently planned for 12/2/21 due to material and access requirements.
| 05SY - Systemwide | Cxxx-NCR-000052 | NCR | Asset Data - Wiring Cable |  | Contr | KBR | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-08-31 | 2021-07-05 10:30 | -57 | 2021-06-10 10:01 | Information Management - Asset Information | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | BACKGROUND The Contractor has installed asset labels onsite to correspond with asset data for the L-Class L746211 – Wiring Cables. Within this L-Class the Contractor has provided data for a single asset per platform. This asset is the main power cable from the platform isolator to the Platform Screen Door Control Cabinet (PDCC). The Contractor part number (DDAID) for this cable is 77120396. Total 16 assets at each of the Central Operating Section (COS) platforms. The text contained on these labels is as follows: TEXT LINE 1: ASSET TAG CODE (UNIQUE ID PER ASSET) TEXT LINE 2: ISO-EB or ISO-WB (DEPENDENT UPON PLATFORM BOUND ASSET IS LOCATED) TEXT LINE 3: CABLE-P-LV: 77120396 TEXT LINE 4: CAB-001 or CAB-002 (DEPENDENT UPON PLATFORM BOUND ASSET IS LOCATED)
| 05SY - Systemwide | Cxxx-NCR-000053 | NCR | Drivers Door Crew lock |  | Contr | KBR | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-12-24 | 2021-11-18 15:28 | -36 | 2021-09-22 09:53 | Systems - Platform Screen Doors | 30000 |  | Design | Rework | 2 (6-60k) | Complete | Design Problem - Other | Completed |  | have witnessed a single incident associated with the Drivers Door crew lock whereby when the the lock is rotated from the platform side using the standard key and the door lock did not disengage.
| 05SY - Systemwide | Cxxx-NCR-000054 | NCR | PID support bracket |  | Contr | KBR | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2022-08-26 | 2022-08-18 15:25 | -8 | 2021-11-03 21:03 | Systems - Platform Screen Doors | 6000 |  | Damaged | Repair | 3 (3-6k) | Complete | Personnel Error - Other human error | Completed |  | The folded element of the aluminium rear tray, a sub-component of the ASD front cover, has been bent when the ASD front cover is forced closed by maintenance/site personnel. The RH gas strut connects from the door post bracket to the rear of the ASD front cover at this folded element of the aluminium rear tray. The RH gas strut has a locking feature where a collar is disengaged prior to closing the ASD front cover. There have been instances where the front cover has been forced closed without disengaging the locking collar and therefore the folded aluminium has been bent. There has been no safety issue to date, however S suggest a product improvement to mitigate any future problems due to the issue described. Update 19th Jan 2022 • Material sourced by project available (steel items for free issue) • works to be carried out by Maintenance • Transferring this formally through __
| 05SY - Systemwide | Cxxx-NCR-000055 | NCR | Digital Advertising Tripping __ |  | Contr | KBR | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2022-03-25 | 2022-05-24 13:35 | 60 | 2021-09-15 08:23 | Systems - Platform Screen Doors | 500 |  | System Defect | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | have witnessed an issue with the advertising screen __s tripping, first advised to Crossrail in Cxxx-RFI-000066 dated 22/10/19. To rectify this issue, it is recommended that Crossrail instruct either the revised __ type required, or alternatively the requirements from which the __ sizing could be calculated. This NCR is raised at Crossrail’s request to record the issue with the overall integrated system. Update 19th Jan 2022 • Monitoring equipment and replacement __ on order. Once delivered, to be installed on site and trial will start • Trial to be concluded then assessment to confirm if suitable for transfer via __ paper, to clarify responsibilities split (sourcing versus install via maintenance) • NICEIC certification will also need confirmation of how to manage. • Sourcing 16Amp type Ds difficult
| 05SY - Systemwide | Cxxx-NCR-000056 | NCR | WNC+ Link Issue |  | Contr | KBR | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-04-30 | 2022-02-21 15:56 | 297 | 2021-09-28 15:33 | Systems - Platform Screen Doors | 0 |  | System Defect | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Unstable WNC+ communications Link between the Cxxx PSD system and the Cxxx Signaling system
| 05SY - Systemwide | Cxxx-NCR-000057 | NCR | EED Lock Mechanism |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2022-05-31 | 2022-05-25 10:44 | -6 | 2021-11-18 15:54 | Systems - Platform Screen Doors | 6000 |  | Design | Repair | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | have witnessed an incident associated with the Drivers Door crew and EED locks whereby when the the lock is rotated from the platform side using the standard key and the door lock did not disengage. Update 19th Jan 2022 • CRL stating the EED crew lock is a defect for Cxxx to fix. • project to be instructed to carry out the fix on "limited Mobility Access" EEDs. • Remaining EEDs to be transferred to RFL through __ paper and to clarify the cost of parts with 631.
| 05SY - Systemwide | Cxxx-NCR-000058 | NCR | PED / PID Glass Delamination |  | Crossrail | PDP | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2022-06-20 | 2022-05-19 12:00 | -32 | 2022-03-22 11:42 | Architectural - Glazing | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Delamination at the corners of some of PID glass front covers observed, the affected panels initially found at Bond Street station as can be seen in the attached report titled '' Crossrail PID Glass delamination SAP 8D Report - V9 09_02''. Further investigation undertaken by the Contractor suggested a total of eight affected parts installed across the COS.
| 05SY - Systemwide | Cxxx-NCR-000059 | NCR | EED Lock Mechanism |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2022-08-05 | 2022-08-04 13:01 | -1 | 2022-06-16 11:00 | Systems - Platform Screen Doors | 6000 |  | Design | Repair | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | This NCR is raised as a replacement for Cxxx-NCR-000057 which was closed prematurely. This NCR is now pending the completion of EED amendment works as per Cxxx-PMI-00615.
| 05SY - Systemwide | Cxxx-NCR-000001 | NCR | Ground preparation activity started without an approved ITP |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-07-22 | 2016-07-20 09:50 | -2 | 2016-03-17 18:34 | Civil - Excavation | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Supervision - Supervisor does not have access to all pertinent information | Completed |  | 1. Sword has started excavation work for ground preparation at Plumstead ATS without accepted ITP 2. Work information 2B, clause 20.8 requires ITP The Contractor and his subcontractors and suppliers of any tier engaged in supplying, manufacturing, construction, installation, commissioning and testing or any other service connected with the works, shall maintain ITPs appropriate for the services they provide that are accepted by the Supervisor. The Contractor shall not start the relevant works until the Supervisor has accepted the ITP
| 05SY - Systemwide | Cxxx-NCR-000002 | NCR | Concrete workability slump test failed to meet the specification |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-06-17 | 2016-06-20 15:51 | 3 | 2016-03-17 23:02 | Civil - Civil Engineering General | 500 |  | Material | Reject | 4 (0.5-3k) | Complete | Material/Preservation Problems - Not Defined | Completed |  | 1. Sword has brought concrete for routing chamber construction at Plumstead ATS at 14.55 on 15/03/2016. The concrete failed the slump test as it was too dry. Concrete was sent away and it was decided to abandon concrete operation in routing chamber as the cold joint would be formed 2. Slump test was recorded as 40mm which is against the requirements of the ITP- Plumstead ATS civil works- Reinforced concrete (Cxxx-AC-O4-ITP-CR148-50005 v2.0) and the Piling Materials and Workmanship Specification (Cxxx-ALC-C-RSP-CRG03-50001) 4. Required slump test is S3: S3: 100-150, tolerance +/-20mm. 5. Appropriate PPE were not used during the construction
| 05SY - Systemwide | Cxxx-NCR-000004 | NCR | Lack of evidence shown for compliance with respect to the management of constructability reviews |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-02-28 | 2017-02-15 16:13 | -13 | 2016-03-29 13:09 | Systems - Other | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Management Problem - Not Defined | Completed |  | No evidence of constructability reviews taking place before design gate 3 reviews. The requirements state that a review shall be signed off by PM, CM and DM or their delegates, at which point drawings will be stamped confirming the status of each document.
| 05SY - Systemwide | Cxxx-NCR-000005 | NCR | Remedial works – RC__ Concrete base – No approved repair procedure |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-07-19 | 2016-07-15 11:53 | -4 | 2016-04-05 14:33 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 1. Remedial works have been carried out to areas of grout loss on the RC__ concrete base, without an approved repair procedure in place when doing so. 2. There is currently no approved MAR for __ HBS reinstatement mortar (the material used for the remedial works), therefore mix ratio, material application, temperature restraints and curing times have also not been approved. 3. No photographic evidence or any other types of records in regards to the grout loss have been made. 4. No sealant was used between formwork and structure, increasing the risk of grout loss. 5. Sword has not done work in accordance with Cxxx-ALC-C-RSP-CRG03-50001 Concrete and Piling M&W Specifications clause 3.4
| 05SY - Systemwide | Cxxx-NCR-000006 | NCR | Galvanised paint damage- Plumstead Fencing |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-11-20 | 2016-11-18 10:33 | -2 | 2016-05-20 13:19 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper handling of material | Completed |  | __ has delivered fencing material for Plumstead ATS fencing work. 1. Fencing material was not properly cleaned before delivery on site. 2. Disintegrate rusting (Staining) were spotted in the fence. 3. Marking and ashes were found in the fence elements.
| 05SY - Systemwide | Cxxx-NCR-000007 | NCR | Civils design drawing not including backfill material category |  | Contr | ALC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-05-25 | 2016-05-23 14:26 | -2 | 2016-04-29 10:13 | Civil - Fill | 2000 |  | Design | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Backfill was being undertaken around the cast Routing Chamber structure using Specification for Highways Works (SHW) Cl 803 Type 1 material. On checking the drawing, there was no note to the material category required for the backfill to the structure, only mention to Type 1 for the structure sub-base.
| 05SY - Systemwide | Cxxx-NCR-000008 | NCR | Verticality of pile casings not checked during installation |  | Contr | ALC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-06-15 | 2016-05-06 13:16 | -40 | 2016-04-29 10:29 | Geotechnical Engineering - Steel - Driven Pile | 2500 |  | Documentation and Records | Reject | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Checks had not been undertaken for verticality of installed steel pile casings (bubble level). Based on this, the verticality for the piles can not be verified .
| 05SY - Systemwide | Cxxx-NCR-000009 | NCR | Plumstead routing chamber prepour inspection failed |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-05-29 | 2016-05-27 13:10 | -2 | 2016-04-29 13:54 | Civil - Civil Engineering General | 2000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 1. Plumstead, IRF number 021 regarding prepour inspection and concrete check was failed. 2. Plumstead routing chamber prepour inspection failed as the concrete surface was not meeting the requirements of concrete and piling M&W specification (Cxxx-ALC-RSP-CRG03-50001) clause 3.3, placing of ready ready mix concrete 2. Routing chamber existing concrete surface was not ready. The surface was found with standing water, rebar wires, loose concrete flecks, loose aggregate and small block of stones and dust.
| 05SY - Systemwide | Cxxx-NCR-000010 | NCR | Grade of steel in pile casings not as per Specification |  | Contr | ALC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-06-10 | 2016-06-13 09:02 | 3 | 2016-05-27 14:27 | Geotechnical Engineering - Steel - Driven Pile | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | As identified during the PAF round 6 quality site tour, the Mill Certificate for the steel casings supplied refers to a Grade X60 PSL1 which compares to a grade S420. This is not the grade specified. Further, __ has approved the use of the wrong grade steel.
| 05SY - Systemwide | Cxxx-NCR-000011 | NCR | Failure to obtain PM acceptance of a non-UKAS certified supplier prior to appointment |  | Contr | ALC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-06-07 | 2016-06-07 12:36 | 0 | 2016-05-24 16:03 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | As identified during the PAF round 6 Quality assessment, Sword Construction UK Ltd is certified to ISO 9001:2008, but not by a UKAS accredited certification body. They were appointed by AC jv without first having obtained Project Manager agreement.
| 05SY - Systemwide | Cxxx-NCR-000012 | NCR | Palisade Fence-Holes drilled in the wrong position on straining posts, and holes missing on pales |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-12-16 | 2016-12-15 16:20 | -1 | 2016-09-20 17:20 | Civil - Landscaping | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 1. __ fencing element’s holes are not made as requirement of design drawing (Cxxx-ALC-C-DDD-CR148_SW004_Z-00312 ) and the specification (Cxxx-ALC-C-RSP-CRG03-50004 ) 2.Straining post’s holes are drilled at wrong position 3.Holes are missing on pales 4. Wrong rail length at corner fencing
| 05SY - Systemwide | Cxxx-NCR-000013 | NCR | Factory Acceptance Testing failed – equipment performance |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-11-23 | 2016-11-23 12:42 | 0 | 2016-08-10 07:23 | Communications and Control Systems - SCADA/Central Management System | 2800 |  | Manufacturing Defect | Reject | 4 (0.5-3k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | 1. During testing the server and operating screen froze, requiring being re-set to continue testing 2. DAP server freezing during multiple control instruction
| 05SY - Systemwide | Cxxx-NCR-000014 | NCR | Potential defect on piling design at Plumstead ATS |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-02-15 | 2017-01-23 16:11 | -23 | 2016-08-19 15:42 | Civil - Civil Engineering General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | There might be a potential defect on piling design at Plumstead ATS as the ground investigation from Cxxx-OVE-C2-RGN-CR148-50001 may have not been fully considered by Cxxx designer. Therefore, the issue with the piling installation and water table pressure at Plumstead ATS as described in Cxxx-NCE-00078 might have been anticipated at design stage.
| 05SY - Systemwide | Cxxx-NCR-000015 | NCR | Defective trough supplied by __ Ltd at Plumstead |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-01-28 | 2017-01-25 15:09 | -3 | 2016-11-29 09:58 | Electrical - Cable Management | 500 |  | Supervision/Management | Reject | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | 1. __ ltd delivered cable troughing at Plumstead ATS. 2. Quality of the trough was found not good. It was found honeycombing and holes in the product 3. Joints are cracked 4. Small cable troughing product was broken
| 05SY - Systemwide | Cxxx-NCR-000016 | NCR | Palisade Fence manufacturers pre-drilled fishplate holes in wrong location on fence posts. |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-01-27 | 2017-01-23 16:37 | -4 | 2016-10-24 09:01 | Civil - Landscaping | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Palisade Fence manufacturers pre-drilled fishplate holes in wrong location on fence posts. __ fence design does not account for two sections being a greater width than standard 2.75m section. __ has not provided detailed installation or IFC drawings, only General Arrangement Schematics. - 1. __ fencing element’s holes are not made as requirement of design drawing (Cxxx-ALC-C-DDD-CR148_SW004_Z-00312) and the specification (Cxxx-ALC-Y-RSP-CR076-50004) 2. Post’s fishplate holes are drilled at wrong position on posts 10, 12, 13, 15 & 16. The pre-installed slots do not match the positions shown in the __ detailed drawings. 3. Wrong fence section length between posts 4 to 5 & 5 to 6, section is greater than 2.75m fence panel.
| 05SY - Systemwide | Cxxx-NCR-000017 | NCR | Palisade fence surface corrosion and staining to the galvanized finished coating to the pales and rails. |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-01-27 | 2017-01-20 12:07 | -7 | 2016-10-28 14:40 | Civil - Civil Engineering General | 500 |  | Material | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Contamination | Completed |  | Location: Plumstead – Entire Palisade Fence overall appearance. A surveillance of the Palisade Fence installation at Plumstead revealed surface corrosion and staining to the galvanised finished coating to the pales and rails along the entire fence line. The surface corrosion is known as “White Rust” and is believed to affect the overall finish/aesthetics of the product and not its integrity. The corrosion condition was also observed on the Palisade Fence elements in the OHLE yard.
| 05SY - Systemwide | Cxxx-NCR-000018 | NCR | Slump test kit not accordance with the standard |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-03-05 | 2017-01-25 15:01 | -39 | 2016-12-05 14:00 | Civil - Structural Engineering | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | 1. Sword construction has conducted concrete Slump test for North retaining wall concrete work at Westbourne Park against the requirement of BSEN 12350-2:2009 (Testing fresh concrete) part 2 slump test clause 4, apparatus. 2. There was no thermometer at site to check the temperature of the fresh concrete which is the requirement in accordance with BS 8500-2:2006 clause 5.4, Concrete temperature 3. Despite the slump test apparatus was not in accordance with BSEN 12350-2:2009, the slump test conducted met the required values in accordance with BS 8500-1:2006, Table B.1 (S3= 80mm to 180mm). Slump test check sheet is attached.
| 05SY - Systemwide | Cxxx-NCR-000019 | NCR | Armco barrier products with surface corrosion |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-02-10 | 2017-02-08 12:57 | -2 | 2016-12-12 12:56 | Materials - General | 500 |  | Manufacturing Defect | Reject | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A surveillance of the delivered Armco Barrier products supplied by “First Fence” was inspected within the OHLE goods yard. The Armco “Fishtails” and barriers were viewed in their as delivered state, remaining on their pallets and wrapped with plastic wrapping. It was noted that the products were in a very poor condition with both surface corrosion/staining and light surface damage to the galvanised finished coating. The surface corrosion is thought to be “White Rust” and is believed to affect the overall finish/aesthetics of the product and depending on the depth of damage to the galvanised coating may or may not affect its integrity.
| 05SY - Systemwide | Cxxx-NCR-000020 | NCR | Failure to update Comm__ents Delivery Tracker (C__) at required frequency |  | Contr | ALC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-01-27 | 2017-01-25 12:48 | -2 | 2016-12-02 14:50 | Consents - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | __ has not been loading evidence onto the Comm__ents Delivery Tracker (C__), in accordance with the Comm__ents Compliance Plan.
| 05SY - Systemwide | Cxxx-NCR-000021 | NCR | Mast S1 missing pre-drilled fixings |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-02-04 | 2017-01-27 15:15 | -8 | 2016-12-06 09:43 | Electrical - General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Location: Plumstead ATS – mast S1 for switchgear BS1 and BS1/1. - The fixing (pre-drilled) holes in mast S1 are missing, the fixing F11 cannot be attached to the mast S1. Therefore the voltage transformers PMLA/VT1; PMLA/VT2; PMLA/VT3; PMLA/VT4 cannot be installed on the structures BS1 and BS1/1. It is noted the masts have been erected and aligned by the electrical works subcontractor.
| 05SY - Systemwide | Cxxx-NCR-000023 | NCR | Disconnector 101R control box thread damaged |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-06-30 | 2017-06-26 16:25 | -4 | 2017-03-03 14:33 | Materials - General | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper handling of material | Completed |  | The thread to attach to the mounting bracket is broken on the following: 00049983-1-000002 – PLUA/101R/AES The fixing point to the bracket is damaged. Unable to install the control box, unable to cable, unable to test, unable to handover to T&C team.
| 05SY - Systemwide | Cxxx-NCR-000024 | NCR | The cable support F9 needs to be drilled from opposite edge of it in Pudding Mill Lane. |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-05-02 | 2017-05-02 16:11 | 0 | 2017-03-03 16:28 | Structural Engineering - Bolted Connections | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The cable support F9 on the mast has been drilled from top side during the manufacturing according to approved drawings. But the fixing cannot be mounted. The drawing should be updated and the other edge of structure should be drilled in order to be able to install it.
| 05SY - Systemwide | Cxxx-NCR-000025 | NCR | Wrong type of duct has been received from APS |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-05-05 | 2017-05-04 12:19 | -1 | 2017-03-06 13:07 | Electrical - Cable Management | 500 |  | Material | Reject | 4 (0.5-3k) | Complete | Discipline/Workmanship - Error by manufacturer in shipping or marking | Completed |  | Associated Polymer Services Ltd sent __ wrong type of duct. It needs to be replaced as electrical duct which is called 6m Lengths of RB225XPE.
| 05SY - Systemwide | Cxxx-NCR-000026 | NCR | Cleveland cable drum found damaged |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-05-05 | 2017-04-19 14:12 | -16 | 2017-03-07 10:23 | Electrical - Power Distribution | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | 25kV, 1x800, XLPE cable drum has been found damaged just after the delivery at site.
| 05SY - Systemwide | Cxxx-NCR-000027 | NCR | The fixing F25 is drilled incorrectly |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-08-12 | 2017-06-30 11:52 | -43 | 2017-05-04 11:47 | Mechanical - Mechanical Engineering General | 500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The fixing F25 should have been drilled 20mm from the open edge but is drilled 20mm from the closed edge. For the mast fixing point. We cannot use the fixing as it will not fit on the mast in this state.
| 05SY - Systemwide | Cxxx-NCR-000029 | NCR | Subcontractor used of none-approved material on site |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-07-20 | 2017-07-19 13:51 | -1 | 2017-04-11 14:24 | Materials - Approval | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | In Westbourne Park, subcontractor VGC used of non-approved Type 1 material as backfill to south east retaining wall, in place of approved 6N material. Type 1 and 6N primary are similar material in grading specification and fit for purpose application. No impact to other works.
| 05SY - Systemwide | Cxxx-NCR-000030 | NCR | Subcontractor VGC didn't follow the approved SOB instruction |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-07-27 | 2017-07-21 12:26 | -6 | 2017-04-18 11:44 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | Westbourne Park Substation – South West Retaining Wall Stem Top Cover. Subcontractor VGC didn't follow the approved SOB instruction. - In an area of approx. 2lin.m, from expansion joint west, 2no. H12 horizontal bars were installed on top of existing (as designed) H12 ligature to provide cover. This was not as per approved SOB, which required a new capping U bar to be installed where cover was greater than 65mm.
| 05SY - Systemwide | Cxxx-NCR-000031 | NCR | Rebar cover less than 50mm at AT1 base |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-07-27 | 2017-05-08 10:34 | -80 | 2017-04-18 11:43 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | Westbourne Park Substation – rebar cover less than 50mm at AT1 base.
| 05SY - Systemwide | Cxxx-NCR-000032 | NCR | Armco Barriers at PLU- wrong ones were ordered and delivered |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-07-29 | 2017-06-30 11:55 | -29 | 2017-04-20 10:02 | Civil - Civil Engineering General | 500 |  | Material | Reject | 4 (0.5-3k) | Complete | Subcontractor Problems - Interfacing problems | Completed |  | Armco Barriers at PLU- wrong ones were ordered and delivered
| 05SY - Systemwide | Cxxx-NCR-000033 | NCR | Down pipes on P&C building not into the gutter in PLU. |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-08-31 | 2017-08-03 09:50 | -28 | 2017-04-20 10:04 | Civil - Drainage | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | Design issue of the P&C building.  The design position of gulleys GU03 and GU04 are to the west of the P&C slab, however the independent rainwater downpipes of the P&C building are located on the East elevation of the building. No compliance with the design. Gulleys useless if the rainwater cannot reach them.
| 05SY - Systemwide | Cxxx-NCR-000034 | NCR | SDCEM terminations are not suitable for the common wiring at PLU/PML |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-07-29 | 2017-06-30 11:56 | -29 | 2017-04-20 10:07 | Electrical - General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | SDCEM terminations are not suitable for the common wiring at PLU/PML
| 05SY - Systemwide | Cxxx-NCR-000035 | NCR | Labelling for equipment fallen loose after shipment/incomplete door assembly |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-08-31 | 2017-09-04 11:32 | 4 | 2017-04-18 14:45 | Electrical - General | 500 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Plumstead ATS – 5No. “O” open indications from the shaft drive/door hinge fallen from product – no holding washer on either hinges/1No. SBE rating plate loose. The labels are all glued (each label is drilled for a mechanical fix). The glue has failed to hold the label to the material
| 05SY - Systemwide | Cxxx-NCR-000036 | NCR | PLU Transformer oil leakage |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-07-29 | 2017-07-04 12:13 | -25 | 2017-04-20 09:18 | Electrical - Electrical Engineering General | 500 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Plumstead ATS – the transformer is leakage oil from the gasket joint between the radiator and the main tank (bottom flange joint – only one of three leaking) A radiator valve in the below that appears to have dripping residue from the gasket AT1 - serial number 1LF142105086014 * Testing & Commissioning of the transformer delayed till repair undertaken
| 05SY - Systemwide | Cxxx-NCR-000037 | NCR | WBP Earthing mat works has been carried out without accepted ITP |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-06-16 | 2017-06-15 14:51 | -1 | 2017-04-24 17:05 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Lack of procedure | Completed |  | 1. __ has started Earthing Mat works at Westbourne Park without accepted ITP. 2.Work information 2B, clause 20.8 requires ITP The Contractor and his subcontractors and suppliers of any tier engaged in supplying, manufacturing, construction, installation, commissioning and testing or any other service connected with the works, shall maintain ITPs appropriate for the services they provide that are accepted by the Supervisor. The Contractor shall not start the relevant works until the Supervisor has accepted the ITP
| 05SY - Systemwide | Cxxx-NCR-000038 | NCR | Damage to Earth Switch Control __le PMLA/318A/A ES |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-08-13 | 2017-08-09 14:08 | -4 | 2017-05-05 13:46 | Electrical - Electrical Engineering General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Personnel Error - Other human error | Completed |  | Pudding Mill Lane ATFS – The control cubicle for the Earth Switch PMLA/318A/A ES has been damaged such that the pins securing the manual operating handle guide bracket have been broken off, allowing the manual winding handle guide bracket to fall into the cubicle. Handover to of the switch to Testing & Commissioning may be delayed until the guide plate is installed.
| 05SY - Systemwide | Cxxx-NCR-000039 | NCR | The HV terminations installed at Plumstead are incorrect product. |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-09-16 | 2017-09-18 10:28 | 2 | 2017-06-08 10:01 | Electrical - General | 500 |  | Material | Reject | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Plumstead ATS – the HV terminations installed at Plumstead are incorrect product. The cable end to the switchgear masts. The incorrect termination was supplied from __ Cxxx stores to site following a material request for the correct termination. The incorrect termination was accepted by site and installed by the subcontractor. The 3M QTII should have been installed the __s AFN-52D was installed. * Testing & Commissioning - the site cannot be put into service and HV testing works will have to be repeated if the cable and terminations are not replaced before this aspect of T&C
| 05SY - Systemwide | Cxxx-NCR-000040 | NCR | Damaged trough lids following permanent installation of Tro-Trof/Tred cable troughing in PML and PLU |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-08-31 | 2017-08-02 14:23 | -29 | 2017-05-17 11:25 | Civil - Civil Engineering General | 500 |  | Damaged | Reject | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Plumstead & Pudding Mill Lane– Trough lids damaged to both Tro-Trof and Tro-Tred. 1. Some troughs especially the lids, previously installed by the Civils subcontractor SWORD, have been damaged. 2. Prefabricated manufactured angled bend trough units have fractured at joints under vehicle loadings. * Due to time constraints (programme) and the scale of works/resources involved, the right solution should be to “Reject”. The other advantages are: - The few damaged troughs do not require a lot of resources/plant to replace. - Damaged lids are simply required to be replaced. * 1. The installation of the non-approved design is not guaranteed against future issues/failures. 2. The damaged materials used is not guaranteed against “fit for purpose” use and will not perform as the materials specified in the approved design is intended.
| 05SY - Systemwide | Cxxx-NCR-000041 | NCR | Damage to Pin kerbs following permanent installation of kerbs in PLU |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-08-31 | 2017-08-02 12:19 | -29 | 2017-05-17 11:38 | Civil - Civil Engineering General | 500 |  | Damaged | Reject | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Plumstead – Cracked/Fractured Edging Kerbs CMS - Pin kerbs Some pin kerbs, previously installed by the Civils subcontractor SWORD, have been damaged * 1. The installation of the damaged product is not guaranteed against future issues/failures. 2. The damaged materials used are not guaranteed against “fit for purpose” use and will not perform as the materials specified in the approved design as intended.
| 05SY - Systemwide | Cxxx-NCR-000042 | NCR | In Stepney Green the GIS panels not compliant with design |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-09-16 | 2017-08-10 14:43 | -37 | 2017-06-08 10:07 | Electrical - General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | In Stepney Green the GIS panels not compliant with design. __ switchboard orientation incorrect.
| 05SY - Systemwide | Cxxx-NCR-000043 | NCR | SDCEM SBE disconnector with earth switch installation |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-08-26 | 2017-08-10 14:56 | -16 | 2017-05-18 15:55 | Electrical - General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | Plumstead ATS. Asset ID: PLUA/AT1/A ; PLUA/AT1/AES; PLUA/AT2/A ; PLUA/AT2/AES; PLUA/102T1/A ; PLUA/102T1/AES; PLUA/102T2/A ; PLUA/102T2/AES; PLUA/IC102/A ; PLUA/IC102/AES; PLUA/101R/A ; PLUA/101R/AES; PLUA/102Q/A ; PLUA/102Q/AES; PLUA/BS1/1 ; PLUA/ BS1/1 ES; PLUA/BS1/2 ; PLUA/ BS1/2 ES. * 1. Inspection of linkage assembly – the teeth of the half moon insert between the operating arm of the control box mechanism and the linkage pole clamp where not all aligned. 2. The switch blade contacts “jarred” in and out of the contact jaws * T&C unable to accept product from stage 2.1 to stage 2.2
| 05SY - Systemwide | Cxxx-NCR-000044 | NCR | PLU trough route tolerance of height |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-08-30 | 2017-08-11 12:24 | -19 | 2017-05-22 14:25 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | PLU trough route tolerance of height. Plumstead ATS - To ensure Tro-Trofs are at the same finished level. Trough route within tolerant level. The trough route presents no issues to the cables to be installed, the troughing route is adequate for purpose and meet the specification. Cable installation on hold.
| 05SY - Systemwide | Cxxx-NCR-000045 | NCR | Failure of Tro-Trof pre-manufactured welded angled bends |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-09-01 | 2017-08-30 11:41 | -2 | 2017-05-24 11:35 | Civil - Civil Engineering General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Defective troughs received at PLU yard. The weldings were weak and they became broken. Not enough strong for heavy duty works. The damaged troughs used are not guaranteed against “fit for purpose” use and will not perform as the materials specified in the approved design are intended.
| 05SY - Systemwide | Cxxx-NCR-000046 | NCR | Anchor bolts not galvanised top of the all foundations |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-09-23 | 2017-09-27 11:27 | 4 | 2017-06-15 16:29 | Civil - Civil Engineering General | 500 |  | Material | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Some anchor bolts have been installed on top of various foundations without being galvanised at all sites. Please find attached pictures.
| 05SY - Systemwide | Cxxx-NCR-000047 | NCR | WBP - No compaction testing completed for 6N backfill to south retaining wall structure |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-06-28 | 2017-07-07 13:10 | 9 | 2017-05-31 12:53 | Civil - Civil Engineering General | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | A planned Crossrail surveillance was undertaken on 25th May 2017 to look at Reinforced Concrete works and associated foundations/backfill operations at WBP. During the surveillance it was witnessed that the South Retaining wall had been backfilled. On checking, the drawing (Cxxx-ALC-C-DDBCR076_SW001-50004) noted a 6N material classification for the granular fill to retaining wall per the SHW 600 series. A request was made concerning compaction testing to SHW Table 6/1 which defines End Product compaction for a 6N class material. It was stated that no testing had been completed to verify that 95% compaction had been achieved to Maximum Dry Density (MDD) (Vibrating Hammer Method). As such, the compaction cannot be confirmed as compliant to the SHW requirements for a 6N. Furthermore, ITP (Cxxx-ALC-O4-ITP-CRG03-50093) refers to compaction testing under item 6.6.8 (Hold Point for QC/AC QA); however it must be noted that the parameters refer to the Type 1 material (SHW 800 series material). No MDD/OMC laboratory testing for the granular material was provided during the visit, for which compaction testing is to be confirmed against.
| 05SY - Systemwide | Cxxx-NCR-000048 | NCR | WBP – Concrete cube storage not compliant with standard requirements |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-08-31 | 2017-08-02 12:05 | -29 | 2017-05-31 12:59 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Supervision - Other | Completed |  | A planned Crossrail surveillance was undertaken on 25th May 2017 to look at Reinforced Concrete works and associated foundations/backfill operations at WBP. During the site visit concrete cube manufacture by the VGC site team was witnessed. It was stated by the site team that the concrete cubes are stored on site until such time they are stripped and transported to __ in Uxbridge a number of day’s later (unknown timeframe). On inspection it was noted that there is no controlled facility/system in place to allow storage of concrete cubes at the required environmental conditions until such time they are transported to the laboratory. This results in the cubes being stored on site/ in the cabin in in-controlled conditions. The ambient temperature on the day of the surveillance exceeded that allowable. As a result, the cubes could be subject to dehydration with potential of a reduced compressive strength result at testing. Temporary storage should be in place to ensure a controlled environment is maintained for site storage as part of the allowance for VGC/__ operatives to completed testing, cube manufacture and transportation in lieu of a UKAS accredited company.
| 05SY - Systemwide | Cxxx-NCR-000049 | NCR | Pudding Mill Lane – Manhole MH2 damaged |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-10-30 | 2017-11-02 14:33 | 3 | 2017-05-31 14:43 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Leaks observed on the MH2 (not observed on the MH1). Waterproof issue. The damaged ducts used are not guaranteed against “fit for purpose” use and will not perform as the materials specified in the approved design are intended.
| 05SY - Systemwide | Cxxx-NCR-000050 | NCR | Pudding Mill Lane – Duct routs damaged |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-10-07 | 2017-10-09 09:01 | 2 | 2017-05-31 15:32 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Duct routs-Ducts between manhole 1 and 2 : - Tam 130 product. 2no of duct routs are damaged under the pressure of resin expanding. Water ingress in ducts. Condition of the ducts : silt in the ducts. *
| 05SY - Systemwide | Cxxx-NCR-000051 | NCR | PML - No detail investigation done to prepare the Method Statement |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-09-29 | 2017-09-29 15:50 | 0 | 2017-05-31 17:03 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | No detail investigation done to prepare the Method Statement Cxxx-ALC-O1-GMS-CR094-50009. These followings items are due to no detail investigation : 1. 2no of duct routs are damaged under the pressure of resin expanding 2. Water ingress in ducts 3. Condition of the ducts : silt in the ducts
| 05SY - Systemwide | Cxxx-NCR-000052 | NCR | PML - Not meeting the design according to the site condition |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-10-31 | 2017-10-02 16:29 | -29 | 2017-05-31 17:15 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | PML - Not meeting the design according to the site condition. No detail study was done to design team. These followings items are due to no detail investigation: 1. 2no of duct routs are damaged under the pressure of resin expanding 2. Water ingress in ducts 3. Condition of the ducts : silt in the ducts
| 05SY - Systemwide | Cxxx-NCR-000053 | NCR | Missing Earths at Pudding Mill Lane |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-09-20 | 2017-08-30 10:35 | -21 | 2017-06-12 17:39 | Electrical - Earthing & Bonding | 500 |  | Incomplete Works | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Missing earths to structure PMLA/318V. Pudding Mill Lane ATFS – The structure PMLA/318B should be connected connections to the buried earth mat 2 x 2 x 120mm² earths (total 4), but there are only two connections available from the earth mat. The other two connections are missing. It can be seen on site that only two earth connections are available to connect the structure of PMLA/318B to the earth mat.
| 05SY - Systemwide | Cxxx-NCR-000054 | NCR | No evidence of calibration provided for concrete test equipment at WBP during/following a CRL surveillance |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-08-31 | 2017-08-02 12:08 | -29 | 2017-06-16 11:36 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | A planned Crossrail surveillance was undertaken on 25th May 2017 to look at Reinforced Concrete works and associated foundations/backfill operations at WBP. On witnessing the concrete testing being completed, it was identified that the cube moulds and slump equipment contained no identification to allow traceability to a current calibration certificate. During the Exit Meeting the Contractor was requested to provide the calibration certificates for the equipment (cube moulds, slump cone, tamping rod and thermometer). Following multiple requests following the visit(25/06,12/06, 14/06, 15/06), no evidence of calibration was provided as such it can not be confirmed whether the testing equipment used is within the allowable tolerances.
| 05SY - Systemwide | Cxxx-NCR-000055 | NCR | PLU - SDCEM SBE disconnector with earth switch installation |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-09-24 | 2017-09-27 11:31 | 3 | 2017-06-16 12:24 | Electrical - General | 500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | SDCEM SBE disconnector with earth switch installation. * PLUA/AT1/AES; PLUA/AT2/AES; PLUA/102T1/AES; PLUA/102T2/AES; PLUA/IC102/AES; PLUA/101R/A ; PLUA/101R/AES;; PLUA/102Q/AES; PLUA/ BS1/1 ES; PLUA/ BS1/2 ES; * The switch blade contacts “jarred” in and out of the contact jaws due to misalignment of the earth switch arm. This causes undue stress and strain on the linkage installation and the control box installation. This was agreed on site with the manufacturer, __ and the installation subcontractor. * T&C unable to complete commissioning.
| 05SY - Systemwide | Cxxx-NCR-000056 | NCR | Impact Damage to __ Wearing Course Surface |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-09-24 | 2017-09-27 11:34 | 3 | 2017-06-16 14:52 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Plumstead Car Park Area– Multiple spot location damage to surface wearing course layer of __ asphalt on the entrance ramp to Plumstead Cxxx Traction Power compound, caused by plant lifting forks. * 1. Surface is no longer tight and contains loose materials in impact affected areas. 2. Minimum thickness of 25mm to surface course no longer conforms. 3. Potential damage to sub-base binding course at 90mm +/- 15mm. * - Rainwater runoff will reach the binding course layer where the surface course has been compromised. - The damaged areas of asphalt are not guaranteed against “fit for purpose” use and will not perform as the materials specified in the approved design are intended.
| 05SY - Systemwide | Cxxx-NCR-000057 | NCR | Oil leak at Westbourne Park AT2 autotransformer |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-10-22 | 2017-10-02 16:33 | -20 | 2017-07-14 09:25 | Electrical - Transformers | 500 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Westbourne Park ATS – Auto transformer AT2 is leaking oil from the gasket joint between the radiator and the main tank (bottom flange joint – only one of three leaking). AT2 - Serial Number 1LF142105086013. A radiator valve in the below that appears to have dripping residue from the gasket. The transformer remains off load and has not undergone any further testing since delivery.
| 05SY - Systemwide | Cxxx-NCR-000058 | NCR | STG __ 8DA12 LV compartment damage |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-10-12 | 2017-09-08 08:20 | -34 | 2017-07-04 08:38 | Electrical - General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | STG Level 3 - __ 8DA12 LV compartment damage Track Feeder 101A (panel JA04 – design JZ03). Door hinges (top and bottom) are sanpped off – the door is loose on the hinged side pf the panel. Switch S03 (Isolator Control Switch) is damaged – the padlock action is snapped off. T&C unable to accept the product from stage 2.1 to stage 2.2.
| 05SY - Systemwide | Cxxx-NCR-000059 | NCR | Battery charger component found faulty in Plumstead |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-10-15 | 2017-10-02 16:34 | -13 | 2017-07-07 09:10 | Electrical - General | 500 |  | Material | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Battery Charger component A1 (DC Controller/Rectifier Assembly) was found faulty when switched on during phase 2.2 testing, component was not set up correctly and part VR2 was missing from A1 component.
| 05SY - Systemwide | Cxxx-NCR-000060 | NCR | AT2 Autotransformer Oil Leakage at Stepney Green |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-10-21 | 2017-10-02 16:32 | -19 | 2017-07-13 10:48 | Electrical - General | 500 |  | Material | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Stepney Green Shaft – Auto transformer AT2 is leaking oil from the gasket joint between the radiator and the main tank (bottom flange joint – only one of three leaking). AT2 - Serial Number 1LFI42105086011. A radiator valve in the below that appears to have dripping residue from the gasket.
| 05SY - Systemwide | Cxxx-NCR-000061 | NCR | Damaged Cable – 27c 2.5mm2 LSZH – PML ATFS to NG control cable |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-10-22 | 2017-08-30 10:39 | -53 | 2017-07-14 09:44 | Electrical - General | 500 |  | Material | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Damaged Cable – 27c 2.5mm2 LSZH – PML ATFS to NG control cable. National Grid compound – Pudding Mill Lane 400kV Substation (off Cooks Road). Cable ID 7700/7701/7702/7703/7704. * Actual condition: 1. The cable had been pulled through the duct route and the remaining cable run pulled off the drum and looped – to be pulled through to NG site cable route at a later date 2. The cable was pulled on Friday 7th July and left as pulled over the weekend 3. On inspection on Monday 10th July the cable was found with sections of the cable sheath opened up exposing the SWA underneath 4. On first inspection it was deemed the cable was opened up from a trespasser checking the cable contents 5. This was later revised and the cable supplier Cleveland Cable have been called to site and taken samples of the cable away for testing/analysis
| 05SY - Systemwide | Cxxx-NCR-000062 | NCR | WBP A cable lead of the earthing mat was cut during planned civils excavations |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-11-08 | 2017-11-20 10:15 | 12 | 2017-07-31 09:32 | Electrical - General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | A cable lead of the earthing mat was cut during planned civils excavations. The damage is located inside the car park area of the substation and this area need to be tarmacked. The cable lead need to be reconnected before the area is tarmacked. The civil works subcontractor unable to tarmac the parking area before the damage is repaired.
| 05SY - Systemwide | Cxxx-NCR-000063 | NCR | Pudding Mill Lane BSP – negative feeder cable (F2)-Damaged Cable |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-03-03 | 2018-01-24 11:14 | -38 | 2017-08-25 14:15 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Reject | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Pudding Mill Lane BSP – negative feeder cable (F2)-Damaged Cables Asset ID:-BSP cable PMLA/C17/2/2 & PMLA/C17/2/3 The outer sheath is gouged along a length of the cable. The cable is rejected along the length of gouge.
| 05SY - Systemwide | Cxxx-NCR-000064 | NCR | Wrong wiring in P&C Building- NR side |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-04-05 | 2018-02-05 17:10 | 306 | 2017-09-20 08:27 | Electrical - General | 100000 |  | Incorrect Installation | Rework | 1 (>60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The internal wiring in the P&C building NR side is not reflective of the actual drawings. This is valid for F1, F2, BS1, BS2 protections.
| 05SY - Systemwide | Cxxx-NCR-000065 | NCR | PML- Marshalling cabinets in NR part of P&C Building |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-04-05 | 2018-02-16 14:43 | -48 | 2017-09-22 13:58 | Electrical - General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | In sufficient capacity within the existing Marshalling Cabinets within the NR part of the P&C Building. Spare cores need to be terminated onto a termination rail, and are currently laying in the trunking out of sight.
| 05SY - Systemwide | Cxxx-NCR-000066 | NCR | Wrong dimensions of the both 4m posts installed on the North West Retaining Wall |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-01-23 | 2018-01-25 15:52 | 2 | 2017-09-25 16:44 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | Westbourne Park – 2no 4m posts installed on the North West Retaining Wall at the entrance. The both 4m posts with Base plate (to be installed on the RW) have been delivered by __ with wrong dimensions (too big). See the SOB-Cxxx-0215 for more details.
| 05SY - Systemwide | Cxxx-NCR-000067 | NCR | Wrong dimensions of the hinges located on the CRL gate posts at the entrance |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-01-23 | 2018-01-26 14:58 | 3 | 2017-09-25 16:30 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Westbourne Park – 2no CRL gate posts the entrance – Main entrance gate. The hinges on the posts are approx 20mm too low and as a result clash with the gate bolt which fastens to the post. See the SOB-Cxxx-0216 for more details.
| 05SY - Systemwide | Cxxx-NCR-000068 | NCR | PML Busbars do not make full contact with droppers |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-10-02 | 2018-09-26 12:04 | -6 | 2017-09-26 12:06 | Electrical - General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Busbars don't appear to have been installed correctly, we have now checked all of them and all of them have gaps where the busbars do not make full contact with the droppers for the disconnector blades, this will cause significant problems when energised. Please see attached sample picture from Site.
| 05SY - Systemwide | Cxxx-NCR-000069 | NCR | PML- GE ferule numbering is not as per NR standard |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-10-02 | 2018-08-24 10:13 | -39 | 2017-09-28 10:00 | Electrical - General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | The ferule numbering provided in GE design is not as per the NR standard and therefore need to be redesigned.
| 05SY - Systemwide | Cxxx-NCR-000070 | NCR | STG – excessive oil on top of the Transformer (AT1) |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-01-26 | 2017-12-04 16:55 | -53 | 2017-10-18 09:55 | Electrical - General | 500 |  | Incomplete Works | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | During Inspection of the Auto Transformer at Stepney Green it was noticed that there was excessive oil on top of the Transformer.
| 05SY - Systemwide | Cxxx-NCR-000071 | NCR | PML- Protections settings not relevant for P746 busbar protection ( RfL and NR) |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-10-02 | 2018-07-31 10:18 | -63 | 2017-10-18 14:14 | Electrical - General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Protections settings not relevant for P746 busbar protection ( RfL and NR) in PML.
| 05SY - Systemwide | Cxxx-NCR-000072 | NCR | PML - Corrosion issue on Cable plug |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-04-29 | 2019-06-03 15:17 | 35 | 2017-10-24 14:36 | Electrical - Electrical Engineering General | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | There is a big difference in terms of quality of material for the umbilical cable plug connecting to the CB. It might be a difference on material or no coating on 6 of them
| 05SY - Systemwide | Cxxx-NCR-000073 | NCR | PML- lamp hook broken in one cubicle |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-02-01 | 2018-02-16 14:34 | 15 | 2017-10-24 14:45 | Electrical - Electrical Engineering General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | The lamp hook is broken in one cubicle in PML
| 05SY - Systemwide | Cxxx-NCR-000074 | NCR | PML- Door switch/Limit switch for lights in the protection panels broken |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-10-02 | 2018-09-26 12:07 | -6 | 2017-10-24 15:05 | Electrical - General | 500 |  | Damaged | Reject | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | PML - Door switch/Limit switch for lights in the protection panels broken. Asset ID: Bus Coupler BS1&BSP INCOMER F1- Protection Panel. The condition of the protection panels are not the best and the works cannot be carried out properly in these conditions
| 05SY - Systemwide | Cxxx-NCR-000075 | NCR | PLU – surge arrestor is damaged |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-02-01 | 2018-02-05 17:05 | 4 | 2017-10-24 15:46 | Electrical - General | 5000 |  | Damaged | Reject | 3 (3-6k) | Complete | Discipline/Workmanship - Counterfeit Items | Completed |  | During Inspection on site it was noticed that a surge diverter was damaged
| 05SY - Systemwide | Cxxx-NCR-000076 | NCR | PLU – 102T2 __ Control __le issue |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-02-02 | 2018-03-27 11:06 | 53 | 2017-10-25 12:58 | Electrical - General | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Following site visit in Plumstead the 102T2 __ Control __le is temperamental to Open/Close operations in both Local and Remote. Only managed to get it to operation a few times. Capacitor bank seems to be holding voltage ? May need a replacement.
| 05SY - Systemwide | Cxxx-NCR-000077 | NCR | PLU – installation issue for disconnector |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-02-02 | 2018-06-28 12:50 | 146 | 2017-10-25 13:22 | Electrical - General | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following site visit in Plumstead some issues were noticed regarding the operation of the disconnectors. Please find attachment.
| 05SY - Systemwide | Cxxx-NCR-000078 | NCR | Westbourne Park – One of the both NR gate posts was delivered without hinge on it |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-02-08 | 2018-02-02 14:04 | -6 | 2017-10-31 11:50 | Civil - Civil Engineering General | 500 |  | Material | Reject | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Westbourne Park – One of the both NR gate posts was delivered without hinge on it. (at the entrance – NR gate)
| 05SY - Systemwide | Cxxx-NCR-000079 | NCR | PML- Busbar termination is cracked |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-10-02 | 2018-09-26 14:32 | -6 | 2017-10-31 15:27 | Electrical - Electrical Engineering General | 500 |  | Damaged | Reject | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | PML- Busbar termination is cracked Aspect Under Investigation – X3- Busbar termination is cracked (Hairline) Description & Operating Condition The defect is at the clamp connection interface designed to connect aluminium terminations (Ø31,5 cable, Ø80 busbar) to copper and aluminium bolted connections this is in order to avoid electrolytic corrosion that would occur by coupling metals with different electrochemical potentials at the presence of electrolyte thus bimetallic clamps are used. Bimetallic clamps are composed by one part of aluminium alloy and the other one of copper alloy; the coupling between the two parts is realized through a threaded connection and blocked by compression after placing a electrocupal washer at the interface of the two metals.
| 05SY - Systemwide | Cxxx-NCR-000080 | NCR | PML- Busbar termination is broken- (R8) |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-02-11 | 2017-12-18 13:55 | -55 | 2017-11-03 11:01 | Electrical - Electrical Engineering General | 500 |  | Damaged | Reject | 4 (0.5-3k) | Complete | Discipline/Workmanship - Information not detailed | Completed |  | PML- Busbar termination is broken- (R8)
| 05SY - Systemwide | Cxxx-NCR-000081 | NCR | PML – control wiring not as per standard |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-10-02 | 2018-09-26 14:34 | -6 | 2017-11-10 14:33 | Electrical - Electrical Engineering General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | PML – control wiring colour not as per NR standards
| 05SY - Systemwide | Cxxx-NCR-000082 | NCR | PML- Gland to be replaced |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-10-02 | 2018-10-23 12:08 | 21 | 2017-11-10 14:42 | Electrical - General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | PML- Gland to be replaced. (as attached).Some cables are not correctly glanded to the control boxes as you can see on the pictures the armour of the cable is exposed . See below the number of glands with the number of the control box associated. number Cable number Control box 1 6021 F2/A 2 5027 F2/A 3 7081 F2/A 4 6022 F2/A 5 7082 F2/A ES 6 7134 6302A/A 7 5055 6302A/A 8 6050 6302A/A 9 5051 320A 10 6046 320A 11 7126 320A 12 6047 320A/A 13 7127 320A/A 14 7532 320A/A 15 5053 320A/A 16 7535 6302A/A ES 17 5050 319A/A ES 18 6045 319A/A ES 19 7114 318A/A ES 20 7525 318A/A ES 21 7526 318A/A ES 22 5047 318A/A ES 23 7112 318A 24 6040 318A 25 6041 318A/A 26 6038 317A/A 27 7523 317A/A 28 7521 317A/A 29 7064 6302B 30 6067 6302B 31 5072 6302B 32 7501 6301B 33 6032 BS2/2 34 7557 BS2/2 ES 35 6068 6302B/A 36 7515 6302B/A 37 5074 6302B/A 38 7517 6302B/A 39 7514 320B/A ES 40 7057 320B 41 5069 320B 42 6065 320B/A 43 6066 320B/A 44 7058 320B/A 45 5070 320B/A 46 5071 320B/A 47 7052 BS2/1 48 7072 BS2/1 49 5036 BS2/1 50 5035 BS2/1 51 7555 BS2/1 52 7553 BS2/1 53 6031 BS2/1 54 6030 BS2/1 55 7523 317A/A 56 6038 317A/A 57 7521 317A/A 58 7555 BS2/1/ES 59 6031 BS2/1/ES 60 7073 BS2/1/ES 61 6032 BS2/2 62 6062 319B/A 63 7509 319B/A 64 7511 319B/A 65 7051 319B/A 66 7507 318B/A/ES 67 5065 318B/A/ES 68 6059 318B/A 69 5065 318B/A 70 6060 318B/A 71 5064 318B/A 72 7044 318B/A 73 7508 318B/A 74 7039 317B/A ES 75 7505 317B/A ES 76 6055 317B/A ES 77 6054 6301B/A ES 78 5059 6301B/A ES 79 7501 6301B/A ES 80 7502 6301B/A ES 81 7032 6301B/A ES 82 6056 317B/A 83 7038 317B/A 84 6017 F1/A 85 5023 F1/A 86 7013 F1/A 87 7537 F1/A ES 88 704 F1/A ES 89 7541 F1/A ES 90 6025 BS1/1 91 6026 BS1/1 92 7002 BS1/1 93 7547 BS1/1 94 7549 BS1/1 95 6026 BS1/1 ES 96 7003 BS1/1 ES 97 7015 F1/L3 98 7540 F1/L4 99 5016 101A/A 100 7500 101A/A 101 6006 101A/A 102 7502 101A/A 103 5015 101A/A 104 6005 101A/A 105 7002 101A/A 106 7501 101A/AE 107 7502 101A/AE 108 5016 101A/AE 109 7003 101A/AE 110 7082 F2/A ES 111 5051 320A 112 7133 6302A
| 05SY - Systemwide | Cxxx-NCR-000083 | NCR | All sites - Bus bar clamp having defect |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-02-18 | 2017-12-18 13:59 | -62 | 2017-11-10 14:52 | Electrical - General | 500 |  | Damaged | Reject | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | ALL sites – Busbar clamp have been defective. It has been discovered at PML ATFS that the following clamp have gap as shown on the pictures below :R1, R4, R5 R16 R22 R27 R28 R33 R35
| 05SY - Systemwide | Cxxx-NCR-000084 | NCR | Failure of VT on BS2 during Energisation in PML |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-02-21 | 2018-02-14 14:12 | -7 | 2017-11-13 09:20 | Electrical - General | 500 |  | Damaged | Reject | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Failure of VT on BS2 during Energisation in PML
| 05SY - Systemwide | Cxxx-NCR-000085 | NCR | PML F1-L3 disconnector switch is damaged |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-02-23 | 2018-06-26 14:57 | 123 | 2017-11-15 14:59 | Electrical - General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | PML F1-L3 disconnector switch is damaged by MEWP. Please find attached picture
| 05SY - Systemwide | Cxxx-NCR-000086 | NCR | PML Contact surface imperfection of busbar termination |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-10-02 | 2018-09-26 14:36 | -6 | 2017-11-15 15:06 | Electrical - General | 500 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Aspect Under Investigation - X5- Contact surface imperfection of busbar termination Description & Operating Condition The defect is at the clamp connection interface designed to connect aluminium terminations (Ø31,5 cable, Ø80 busbar) to copper and aluminium bolted connections this is in order to avoid electrolytic corrosion that would occur by coupling metals with different electrochemical potentials at the presence of electrolyte thus bimetallic clamps are used. Bimetallic clamps are composed by one part of aluminium alloy and the other one of copper alloy; the coupling between the two parts is realized through a threaded connection and blocked by compression after placing a electrocupal washer at the interface of the two metals.
| 05SY - Systemwide | Cxxx-NCR-000087 | NCR | ALL SITES Disconnector __ 6A C to be changed |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-02-24 | 2018-02-16 14:36 | -8 | 2017-11-16 13:00 | Electrical - General | 500 |  | Design | Reject | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | ALL the sites – Disconnector __ 6A C to be changed to 10A C __ (6A C) for disconnector are tripping under normal load
| 05SY - Systemwide | Cxxx-NCR-000088 | NCR | STG- HV cables connected may be the other way around |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-03-03 | 2018-02-16 14:40 | -15 | 2017-11-23 11:56 | Electrical - General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The HV cables connected may be the other way around: The chamber closer to the back wall is the negative and the other one the positive. But on the drawings, the red cable (negative) connects the positive chamber and the blue cable (positive) connects the negative chamber. Site Observation already raised to Design dept to clarify it.
| 05SY - Systemwide | Cxxx-NCR-000090 | NCR | Corrosion to external control boxes and corrosion to bolted sections of the structures |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-04-21 | 2019-06-03 15:19 | 43 | 2017-12-05 17:32 | Consents - General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Contamination | Completed |  | 1. Outdoor switchgear boxes show signs of degradation. 2. White residue is visible on metallic surfaces. 3. Surface of control boxes and ends of threaded bars corroded.
| 05SY - Systemwide | Cxxx-NCR-000091 | NCR | Earth Tail-Outs too short for termination point on Masts & P&C building |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-02-03 | 2018-02-02 12:53 | -1 | 2017-12-05 18:42 | Electrical - Earthing & Bonding | 500 |  | Workmanship | Reject | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Earth Cable does not reach the termination point
| 05SY - Systemwide | Cxxx-NCR-000092 | NCR | The ITP hold points where not adhered too |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-01-12 | 2018-03-02 10:45 | 49 | 2017-12-13 11:02 | Consents - General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | ITP hold points were not adhered by to and installation work continued without formal inspections
| 05SY - Systemwide | Cxxx-NCR-000093 | NCR | WBP Palisade Fence Corrosion on North Side Fence |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-02-16 | 2018-05-14 09:37 | 87 | 2017-12-18 12:46 | Civil - Civil Engineering General | 2000 |  | Material | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Contamination | Completed |  | Palisade Fence installation at WBP revealed surface corrosion and staining to the galvanised finished coating to the pales and rails along the 4m of section at North Side Palisade fence (Marked up drawing attached) The surface corrosion is known as “White Rust” and is believed to affect the overall finish/aesthetics of the product and not its integrity.
| 05SY - Systemwide | Cxxx-NCR-000094 | NCR | Stepney Green Sub Station HV Cables-Water in GIS 101M positive after removing pfisterer terminal. |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-04-17 | 2018-02-28 16:42 | -48 | 2017-12-18 17:47 | Electrical - General | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | When removing the HV cable in panel 101M POS (cable 33) we found water inside the Pfisterer terminal
| 05SY - Systemwide | Cxxx-NCR-000095 | NCR | PML-MEWP Struck Motor Control Box for Earth Switch PMLA101AAES on structure 101A |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-04-17 | 2018-03-05 13:45 | -43 | 2017-12-18 18:55 | Electrical - General | 500 |  | Damaged | Reject | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | PML-MEWP Struck Motor Control Box for Earth Switch PMLA101AAES on structure 101A
| 05SY - Systemwide | Cxxx-NCR-000096 | NCR | CT and VT cables have wrongly cut a 2 core control cable tagged 0204, it runs between PMLA/F2/A and PMLA/BS2 |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-04-19 | 2018-03-05 14:14 | -45 | 2017-12-20 15:16 | Electrical - General | 500 |  | Damaged | Reject | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | PSP while removing the CT and VT cables have wrongly cut a 2 core control cable tagged 0204, it runs between PMLA/F2/A and PMLA/BS2.
| 05SY - Systemwide | Cxxx-NCR-000097 | NCR | WBP- +25kv & -25kv Termination points on AT2 Transformer are opposite to design |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-05-04 | 2018-04-12 13:33 | -22 | 2018-01-04 09:51 | Electrical - General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | +25kv & -25kv Termination points on AT2 Transformer are opposite to design
| 05SY - Systemwide | Cxxx-NCR-000098 | NCR | PLU – P+C Building Transit Glands – wrong/incorrect installation |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-10-02 | 2018-10-17 12:38 | 15 | 2018-01-04 10:56 | Electrical - General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | See phot attached as an example of the non-conformity. Cables Affected refer below:- Transit Plate-To-Marshalling Kiosk 2 5011, 5018, 5019, 5021, 5022, 5024, 5025, 5027, 5028, 5030, 5044, 6008, 6011, 6014, 6017, 7041, 7043, 7033, 7034, 7035, 7039, 7029, 7030. Transit Plate-To-Marshalling Kiosk 1 5012, 5032, 5033, 5035, 5036, 5038, 5039, 5041, 5042, 5045, 6022, 6023, 6025, 6026, 6028, 6031, 7036, 7037, 7038, 7042, 7031, 7032, 7040.
| 05SY - Systemwide | Cxxx-NCR-000099 | NCR | WBP– Errors on termination schedule + Incorrect suffix installed,allocation of cable colours and termination points. |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-05-04 | 2018-03-05 15:31 | -60 | 2018-01-04 14:53 | Electrical - General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Westbourne Park – errors on termination schedule, incorrect suffix installed, incorrect allocation of cable colours and incorrect termination points.
| 05SY - Systemwide | Cxxx-NCR-000100 | NCR | No IP washers have been installed on LV CT & VT cables on the Field End Termination boxes PG21 adaptors |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-10-02 | 2018-10-05 13:19 | 3 | 2017-12-29 14:31 | Electrical - LV Equipment | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 1. No IP washers have been installed on LV CT & VT cables on the Field End Termination boxes PG21 adaptors 2. PTFE Thread Tape has been installed as an added measure until such times that the IP washers can be installed
| 05SY - Systemwide | Cxxx-NCR-000102 | NCR | PML-Termination box water ingress Lid not being secured with the correct fixing bolts |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-05-09 | 2018-04-24 14:59 | -15 | 2018-01-09 15:41 | Electrical - General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | When inspecting CT & VT field end terminations the termination box had water ingress. This was due to the lid not being secured with the correct fixing bolts (not the manufactures fixings) see attached photo. This was on the BS1 CT1 termination.
| 05SY - Systemwide | Cxxx-NCR-000103 | NCR | 50yr Design Life for Busbar Clamp manufacture has not been demonstrated by __ __/__ |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-01-30 | 2018-03-27 10:13 | 56 | 2018-01-10 13:10 | Systems - Traction Power Systems | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Other | Completed |  | A planned Crossrail surveillance was undertaken on 15th December 2017 which looked at re-manufacture of Busbar Clamps by __ __. The Technical Specification, Cxxx-ALC-Y-RGN-CRG03-50039 at Rev 1 Decal Code 2, Section 4 includes a requirement for the Busbar Clamps to have an expected life of at least 50 years. It was found during discussions with __ __ and __ that the 50 year design life of the manufactured Busbar Clamps could not be demonstrated. No evidence was provided. __ __/__ is to demonstrate with supporting evidence how the Busbar Clamps will achieve a 50 year design life to assure the forthcoming installation. It was also found that this 50yr design life requirement had never been included in the Purchase Order requirements stipulated to __ __ under initial agreements.
| 05SY - Systemwide | Cxxx-NCR-000104 | NCR | No evidence/information on purpose of crimping for Busbar Clamp manufacture, including how crimp pressure/displacement values have been derived |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-01-30 | 2018-03-27 10:19 | 56 | 2018-01-10 13:13 | Systems - Traction Power Systems | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | A planned Crossrail surveillance was undertaken on 15th December 2017 which looked at re-manufacture of Busbar Clamps by __ __. As part of the investigation into defect Types X1 (gapped) and X2 (face contact/overlap), __ __ had implemented the following changes; 1) change in the crimping machine, 2) change in the crimping tool; from plate to a radial hexagonal tool, and 3) change from applied pressure (20 bar used previously) to a measure of displacement (noted on drawings). The purpose of crimping was asked to fully understand the importance of the process and changes made; however no explanation could be given as to what the crimp is doing with respect to the performance of the Busbar Clamp. In addition no correlation was provided between the 20 bar pressure used on the defective batch (previous manufacture) and the newly used displacement measures, including where the 20 bar pressure had originally been derived from. Furthermore, it was found that different Type RXX Clamps had different displacement values defined on the drawings. No evidence could be provided as to where they had been derived from. No information is contained within the Technical Specification, Cxxx-ALC-Y-RGN-CRG03-50039 at Rev 1 Decal Code 2. __ __/__ should define the purpose of the crimping process and its impact with respect to performance and functionality of the Busbar Clamp when energised to provide assurances prior to energisation.
| 05SY - Systemwide | Cxxx-NCR-000105 | NCR | Testing and Calibration for Busbar Clamp manufacture is not being completed by a UKAS (or equivalent) accredited company |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-01-31 | 2018-03-28 12:37 | 56 | 2018-01-10 13:15 | Systems - Traction Power Systems | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | A planned Crossrail surveillance was undertaken on 15th December 2017 which looked at re-manufacture of Busbar Clamps by __ __. The following testing is being carried in-house by __ __; Chemical Analysis, Short Circuit (Mechanical Load), Dye Penetrant and Brinell Hardness. It was stated by __ __ that they are not accredited by a UKAS or equivalent (Italian equivalent Accredia) organisation. It was further confirmed that no Project Managers acceptance is in place for __ __ to undertake off-site testing activities in lieu of relevant accreditation. Works Information Volume 2B Part 20.8 which states; “All on-site and off-site testing shall be carried out by laboratories accredited by UKAS or similar, acceptable national body or by persons accredited to a similar standard. The samples shall be taken by staff appointed by the laboratory. The requirement for UKAS accreditation may be waived for the testing of systems and their components, subject to an alternative testing proposal by the Contractor and the acceptance of the proposal by the Project Manager.” __ should submit a proposal to Crossrail for Project Managers acceptance of __ __ in-house testing. The proposal should contain evidence of competency management, documented procedures, and calibration for equipment. Similar to testing, it was stated that the majority of equipment is calibrated in-house by __ __. As __ __ are not UKAS (or equivalent) accredited to undertake calibration activities, __’s proposal to the Project Manager should include in-house calibration activities
| 05SY - Systemwide | Cxxx-NCR-000106 | NCR | No WPQR for __ __ operative undertaking Busbar Clamp manufacture welding |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-01-30 | 2018-03-27 10:22 | 56 | 2018-01-10 13:18 | Systems - Traction Power Systems | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Training Deficiency - Other | Completed |  | A planned Crossrail surveillance was undertaken on 15th December 2017 which looked at re-manufacture of Busbar Clamps by __ __. Welding being carried out on a Type R5 Clamp was witnessed. The WPQR was requested for operative Riva Guido who was carrying out the welding. It was stated that the operative had recently undergone assessment by an Assessment Body (AsBo) for this type of weld, with test samples still being assessed prior to confirming acceptability and issuing the WPQR. Until the WPQR certificate has been issued by the AsBo, competence cannot be confirmed. If the operative fails this assessment, it brings into question the integrity of the welds being completed for Types R5 and R30 as part of the next batch release. The WPQR should be provided before any installation of welded clamps takes place. ISO 9001 6.2.2 ‘Competence, Training and Awareness’ states; The organization shall e) maintain appropriate records of education, training, skills and experience (see 4.2.4).
| 05SY - Systemwide | Cxxx-NCR-000107 | NCR | Short Circuit (equivalent load) testing of newly manufactured Busbar Clamps has not been completed |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-03-05 | 2018-08-16 13:18 | 164 | 2018-01-10 13:21 | Systems - Traction Power Systems | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | A planned Crossrail surveillance was undertaken on 15th December 2017 which looked at re-manufacture of Busbar Clamps by __ __. It was stated that no load testing has been completed on the Busbar Clamps which have been manufactured under new processes, design and conditions; as such the revised process could not be confirmed to meet the requirements of ‘Calculation of Efforts on 25kV Busbars – Calculation Note’ Cxxx-ALC-Y-XCL-CRG03-50004 which requires the Clamps to be able to withstand the maximum short circuit current of 681,14N. ISO 9001 7.3.6 ‘Design and Development Validation’ states; Design and development validation shall be performed in accordance with planned arrangements (see 7.3.1) to ensure that the resulting product is capable of meeting the requirements for the specified application or intended use, where known. Wherever practicable, validation shall be completed prior to the delivery or implementation of the product. Records of the results of validation and any necessary actions shall be maintained (see 4.2.4). This testing should be carried out to confirm compliance of the new methodologies and parameters prior to energisation.
| 05SY - Systemwide | Cxxx-NCR-000108 | NCR | Chemical Analysis of raw or post casting materials (copper and aluminium) not provided for Busbar Clamp manufacture |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-01-30 | 2018-03-27 11:01 | 56 | 2018-01-10 13:23 | Systems - Traction Power Systems | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | A planned Crossrail surveillance was undertaken on 15th December 2017 which looked at re-manufacture of Busbar Clamps by __ __. No chemical analysis results were provided to confirm compliance of the raw aluminium and copper materials (ingots) prior to casting. Chemical analysis certificates are required for the current batch to confirm acceptability against BS EN 1706:2010 ‘Aluminium and Aluminium Alloys. Casting. Chemical Composition and Mechanical Properties’ and BS EN 1982:2008 ‘Copper and Copper Alloys – Ingots and Castings’. In addition, it was stated that no chemical analysis testing is being carried post casting, where __ __ have the equipment to do so. Composition should be verified pre and post casting to ensure the composition remains in alignment with the TS requirements. Until this is provided chemical composition cannot be confirmed for those re-manufactured pieces.
| 05SY - Systemwide | Cxxx-NCR-000109 | NCR | Calibration records for newradial crimping machine used for Busbar Clamp manufacture not provided |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-01-30 | 2018-03-28 12:34 | 57 | 2018-01-10 13:26 | Systems - Traction Power Systems | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | A planned Crossrail surveillance was undertaken on 15th December 2017 which looked at re-manufacture of Busbar Clamps by __ __. Hexagonal Radial Crimping Machine (Displacement) - Preea Idraulica Tubomaic V125 ES (Code PR003). This machine has been used for all crimping since the restart of manufacture. At the time of writing the calibration certificate for this machine has still yet to be provided. Until this is provided, the displacement parameters being applied by the machine cannot be confirmed as acceptable in alignment with the drawings, bringing into question those clamps newly manufactured. In addition, __ __ made available post visit an internal calibration certificate. However on review it was found that the certificate makes no mention of calibration measures, including who carried out this calibration; i.e. __ __ or the manufacturer. The calibration for this equipment needs further information. ISO 9001 7.6 ‘Control of Monitoring and Measuring Equipment’ states; Where necessary to ensure valid results, measuring equipment shall a) be calibrated or verified, or both, at specified intervals, or prior to use, against measurement standards traceable to international or national measurement standards; where no such standards exist, the basis used for calibration or verification shall be recorded (see 4.2.4);
| 05SY - Systemwide | Cxxx-NCR-000110 | NCR | No MAR in place for Busbar Clamps; this is required by ITP and QSP |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-01-30 | 2018-03-28 12:36 | 57 | 2018-01-11 14:20 | Systems - Traction Power Systems | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | A planned Crossrail surveillance was undertaken on 15th December 2017 which looked at re-manufacture of Busbar Clamps by __ __. It was found during the review that no Material Approval Request (MAR) or equivalent has been produced by __ for the Busbar Clamp materials being used. This was not in place prior to initial manufacture and prior to re-starting manufacture where concerns had been raised. Cxxx ‘Procedure for Approval and Acceptance of Materials, Products and Plant’ Cxxx-ALC-O4-GPD-CRG03-50034 (Rev 4) which is a QSP under the Works Information requires a MAR to be produced by __ to provide technical justification for the procurement of a specific product or material against specified requirements. This is a requirement in the ITP (Cxxx-ALC-O4-ITP-CRG03-50097 at Rev 1 Decal Code 1) under 6.1.4 and is a Hold Point for __ prior to starting manufacture.
| 05SY - Systemwide | Cxxx-NCR-000111 | NCR | Damaged F2 HV feeder cables |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-10-02 | 2018-08-15 13:45 | -48 | 2018-01-30 15:56 | Electrical - General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | F2 HV Feeder Cable damaged trough lids from MEWP’s as attached photo Feeder cable label-
| 05SY - Systemwide | Cxxx-NCR-000112 | NCR | 4No 50mm ducts not installed as per design at WBP |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-04-14 | 2018-04-17 15:36 | 3 | 2018-02-13 20:37 | Civil - Civil Engineering General | 500 |  | Incomplete Works | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | 4No 50mm ducts underneath the Gate entrance at WBP have not been installed by the subcontractor VGC.
| 05SY - Systemwide | Cxxx-NCR-000113 | NCR | No PSP Signature on the installation check sheet |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-05-30 | 2018-03-29 08:57 | -62 | 2018-02-15 13:00 | Electrical - Transformers | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Insufficient surveillance of subcontractors | Completed |  | No Signature on the PSP installation check sheet A83-WP-TCP-0002 HV Switchgear A83-WP-TCP-0003 Contact Resistance A83-WP-TCP-0004 HV Cable Testing A83-WP-TCP-0005 LV Cable Inspection & Testing A83-WP-TCP-0006 Instrument Transformer Check Sheet A83-WP-TCP-0007 Surge Arrestor & Insulator Check Sheet A83-WP-TCP-0008 RC__ Installation Check Sheet A83-WP-TCP-0009 Bund Pump Inspection & Testing A83-WP-TCP-0010 Installation Completion Check Sheet/Certificate A70-AA-RGD-0001 P01 o Mechanical Build & Low Voltage Cabling Inspection & Testing Checklists o Protection & Control __le – LV Wiring Checklist o ow Voltage Cabling Inspection Checklist
| 05SY - Systemwide | Cxxx-NCR-000114 | NCR | No MAR for materials in use as part of Busbar Installation at WBP |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-03-16 | 2018-06-20 15:24 | 96 | 2018-02-16 08:03 | Systems - Traction Power Systems | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | A planned Crossrail surveillance was undertaken on 14th February 2018. This looked at installation of Busbar Clamps and associated activities at Westborune Park Substation. During the site visit, the following materials formed part of the installation: - Tubular Busbar - Aluminium Bare Cable - Contact Lubricant (BI CON X1) The MAR was requested for each of these materials in use. On review it was found that an MAR had not been produced for these materials. Cxxx - Procedure for Approval and Acceptance of Materials - Products and Plant Cxxx-ALC-O4-GPD-CRG03-50034 at Rev 4 Code 1 states: “Subcontractor completes a MAR (Appendix 3) for each product or material they propose to supply and submits MAR together with supporting evidence to __. The ‘Approver’ for the product, identified on the MPS, reviews the submitted MAR and evidence against the Compliance Matrix and signs approval if appropriate. The Package Manager transmits the approved MAR to the subcontractor, who then purchases the material or product.” In addition, the Westbourne Park Substation Installation ITP, which covers Busbar Installation states a requirement for the production of a MAR for Material Acceptance under Requirement Number 6.1.6; this is a readiness activity and a Hold Point for __ QC and QA.
| 05SY - Systemwide | Cxxx-NCR-000115 | NCR | No evidence to confirm 27Nm torque has been applied to Busbar Clamp bolts (aluminium section) on installation |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-05-13 | 2018-04-11 13:07 | -32 | 2018-02-16 08:08 | Systems - Traction Power Systems | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | A planned Crossrail surveillance was undertaken on 14th February 2018. This looked at installation of Busbar Clamps and associated activities at Westborune Park Substation. During the site visit the following installed Busbar Clamps were inspected; R1 at Mast IC2/L3, R4 at Mast 102B, R4 at Mast BS1/1 and R17 at Mast IC2. The R1 and R4 variants formed part of the new manufacture process by Cariboni (bi-metallic); R17 is remaining in place (non bi-metallic). The Contractor made available PSP checksheets for this installation (A83-WP-TCP-0003). On checking, it was found that the checksheet only recorded an applied torque of 80Nm; this being for the copper lug connection bolts. This was confirmed in alignment with the Mounting Specification. However, no checksheet existed showing evidence of applied torque for the aluminium clamp bolts which requires a torque of 27Nm (manufacture drawings and stamped on clamp). As such it can not be assured that the bolts for those installed clamps have been torqued to the required 27Nm. In addition to this, __ only hold on file a calibration certificate for one PSP torque wrench in use on site; this being Serial Number 0482 with a working range of between 42Nm – 201Nm. No calibration records exist for a torque wrench with a lower working range, which would be required under this installation. Furthermore, the ITP (*50023) for Substation Installation does not include torqueing as an installation activity with associated parameters defined for different bolt tightening. __ will need to propose how they will confirm and assure Crossrail that the aluminium connections have not been torqued over the manufacturer defined 27Nm. The ITP will require updating to include torqueing as a construction activity, including associated checksheets to evidence applied torque. It is recommended that this is checked on other areas where PSP have been installing Busbar Clamps.
| 05SY - Systemwide | Cxxx-NCR-000116 | NCR | PML Circuit Breaker Pin falling out |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-08-31 | 2018-11-12 14:16 | 73 | 2018-02-27 20:53 | Electrical - Switchgear | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Pins are part of the Circuit Breaker to mechanically operate it. This should stay at all time. Attached photo shows the Circuit Breaker with no pin
| 05SY - Systemwide | Cxxx-NCR-000117 | NCR | Autotransformer rust in many places on the autotransformer AT1 and AT2- Westbourne Park |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-04-21 | 2019-04-25 15:29 | 4 | 2018-03-19 10:27 | Electrical - Transformers | 500 |  | Material | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Autotransformer rust in many places on the autotransformer AT1 and AT2
| 05SY - Systemwide | Cxxx-NCR-000118 | NCR | WBP Earth switch control box of WEPA/BS1/1/E damaged |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-11-30 | 2018-10-16 11:57 | -45 | 2018-03-22 16:10 | Electrical - Switchgear | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | There is an impact on the lid and damaging the inside of the control box as shown in the photo
| 05SY - Systemwide | Cxxx-NCR-000119 | NCR | Possible Incorrect operation of the unit protection at PML F2 |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-07-20 | 2018-08-07 11:55 | 18 | 2018-03-22 16:49 | Electrical - Switchgear | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | The unit protection activated which is due to either - Fault on the Cable - Incorrect Unit Protection wiring or settings - Incorrect Specification of CT (by GE) - CT supplier by SA__EM defective
| 05SY - Systemwide | Cxxx-NCR-000120 | NCR | PML P&C Building labels Incorrectly installed |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-07-30 | 2018-08-07 11:58 | 8 | 2018-05-01 15:48 | Communications and Control Systems - General | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Insufficient information made available to the worker. | Completed |  | P&C buildings at PML require signage for each protection and control room, at present each room has a incorrect labels as Current RFL sign PMLA – C664 RFL (Crossrail) P&C Building Current NR sign PMLA – C664 __ P&C Building
| 05SY - Systemwide | Cxxx-NCR-000121 | NCR | CT and VT Cable Reworks |  | Crossrail | PDP | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-09-02 | 2018-08-29 15:23 | -4 | 2018-05-25 14:49 | Electrical - Power Distribution | 2000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | CT and VT cable remedial works including: reglanding of cables; installation of CMS to the approved design; installation of new VT cables; installation of insulated cable glands.
| 05SY - Systemwide | Cxxx-NCR-000124 | NCR | PLU Incorrect Ferruling Installaltion |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-09-14 | 2018-10-16 12:38 | 32 | 2018-06-07 12:15 | Electrical - Power Generation | 1000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The ferrule numbering provided in GE design is not correct therefore need to be redesigned
| 05SY - Systemwide | Cxxx-NCR-000125 | NCR | Disconnector and Earth Switch Error code at LCD panel |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-10-06 | 2018-06-28 12:57 | -100 | 2018-06-18 15:42 | Electrical - Switchgear | 500 |  | Material | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The defect is on Disconnector and Earth Switch control boxes at WBP as shown on the SDCEm report at AT1/A (DISCONNECTOR) _ S/N : 00061203-1-000001, AT1/A (EARTHING SWITCH) _ S/N : 00061990-1-000004, BS1/1 (EARTHING SWITCH) _ S/N : 00060057-1-000004 (Separate NCR 118 created), 101H/A (DISCONNECTOR) _ S/N : 00061203-1-000004 and BS1/2 (DISCONNECTOR) _ S/N : 00061203-1-000003
| 05SY - Systemwide | Cxxx-NCR-000126 | NCR | SF6 pressure low on GIS at Stepney Green |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-10-10 | 2018-09-07 09:55 | -33 | 2018-07-02 12:58 | Electrical - Power Generation | 500 |  | Equipment Breakdown | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Contamination | Completed |  | In various location (bus section with AT1) the pressure is low (105kPa, which is decreasing), at Stepney Green Shaft-25kV room-lvl3
| 05SY - Systemwide | Cxxx-NCR-000128 | NCR | Stepney Green Bypass 3 local earth switch control selector |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-10-31 | 2018-09-07 14:46 | -54 | 2018-07-09 14:26 | Electrical - General | 500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Bypass 3 circuit the Kraus & Naimer CA10.A711.600 EG Earth Switch control selector (S04) found not to close or open the earth switch as part of re-testing following DAP software update Because the existing switch is not fit for duty Replacement delivered to site. Left in front of panel due to insufficient time to fix all issues and take __ Switchgear round all items requiring fixing/attention once access had been granted
| 05SY - Systemwide | Cxxx-NCR-000129 | NCR | Stepney Green BS1 Circuit Breaker the closed DBI is not being raised on the LCP or the RTU |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-08-30 | 2019-09-02 15:27 | 3 | 2018-07-09 15:45 | Electrical - General | 500 |  | Material | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | At Stepney Green on BS1 Circuit Breaker the closed DBI is not being raised on the LCP or the RTU. The wiring has been relocated previously. More time is required to investigate
| 05SY - Systemwide | Cxxx-NCR-000131 | NCR | Stepney Green On BS1/2 Earth Switch neither the open nor the closed |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-08-30 | 2019-09-03 14:39 | 4 | 2018-07-19 07:53 | Electrical - General | 500 |  | Testing and Commissioning | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Stepney Green on BS1/2 Earth Switch neither the open nor the closed DBI are being raised at the LCP or the RTU.
| 05SY - Systemwide | Cxxx-NCR-000132 | NCR | Stepney Green AT2 LAN A A fibre damaged at termination at back of relay |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-08-30 | 2019-07-02 15:47 | -59 | 2018-07-25 10:30 | Electrical - General | 500 |  | Material | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Stepney Green AT2 LAN A A fibre damaged at termination at back of relay – yellow strands showing. Protective covering of fibre out of place and fibres showing. Fibres not sufficiently protected as designed at connection point to rear of IED
| 05SY - Systemwide | Cxxx-NCR-000133 | NCR | Stepney Green 101A Spring Charged Indication not received at LCP or RTU |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-08-30 | 2019-09-03 09:32 | 4 | 2018-07-12 09:56 | Electrical - General | 500 |  | Testing and Commissioning | Repair | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | Spring Charged indication being tested as part of the full and complete re-testing following DAP software update. Indication not received at LCP and RTU. Without the spring charged indication the RCC will send the SAP out to see why the spring charged indication isn’t received
| 05SY - Systemwide | Cxxx-NCR-000134 | NCR | Stepney Green AT1 CB open DBI not received on the LCP or RTU |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-08-30 | 2019-09-03 14:26 | 4 | 2018-07-12 12:22 | Electrical - General | 500 |  | Testing and Commissioning | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | DBI not raised when one status indication wire removed or both indication wires shorted as found during testing following DAP software update and subsequent re-testing
| 05SY - Systemwide | Cxxx-NCR-000136 | NCR | Interlocking DAP issue between PML and WBP |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-10-21 | 2018-11-12 14:53 | 22 | 2018-07-13 10:09 | Electrical - Switchgear | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | During MS146 interlock testing it was found that when the interlock was enabled via the hard-wiring and the IED inhibit tested, the IED inhibit failed and the Busbar Disconnector closed
| 05SY - Systemwide | Cxxx-NCR-000137 | NCR | PML Mast 102J Insulation tape of the earth drain wire damaged |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-12-09 | 2018-12-06 16:12 | -3 | 2018-08-31 13:56 | Electrical - Switchgear | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | At mast termination point, the Insulation tape of the earth drain wire, has damaged & open Insulation. This is between the exit point of the HV cable sheath (Cable PMLA/102J +Ve 25kV Cable), and the earth bonding point to the mast structure (HV Mast 102J)-Photo attached
| 05SY - Systemwide | Cxxx-NCR-000138 | NCR | Cable support structure not level- PML 317B Positive Side |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-01-15 | 2018-12-10 14:10 | -36 | 2018-09-18 15:25 | Electrical - Switchgear | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | HV cable structure is not Leveled, correct height, tighten & toque Bolts on supporting screwed rods. This is at GEML – 317B Positive Side of the Mast Structure – Lower Cable Support for 317B & 6301B Cables
| 05SY - Systemwide | Cxxx-NCR-000139 | NCR | PML BS2/2 ES terminal and BS1/1 Disconnector terminal broken |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-12-27 | 2018-12-10 15:26 | -17 | 2018-09-18 16:24 | Electrical - Switchgear | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 1. BS1/1 Disconnector MR41ED Electrical Operating Mechanism. Riser Terminals Broken, used for Field Cable Connection 2. BS2/2 Disconnector MR41ED Electrical Operating Mechanism. Riser Terminals Broken, used for Field Cable Connection
| 05SY - Systemwide | Cxxx-NCR-000140 | NCR | PML 317B ES – error code 417 |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-04-08 | 2019-04-09 12:50 | 1 | 2018-09-18 16:39 | Electrical - Switchgear | 500 |  | Testing and Commissioning | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | GEML-B-317B-Earth Switch Controller – error code 417
| 05SY - Systemwide | Cxxx-NCR-000141 | NCR | No MAR implemented for Clip on wire ferrule and control cables in PLU |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-01-09 | 2019-01-08 13:03 | -1 | 2018-10-01 16:26 | Electrical - Switchgear | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | No MAR implemented for Clip on wire ferrule and control cables in PLU. It was found during the PLU surveillance
| 05SY - Systemwide | Cxxx-NCR-000142 | NCR | WBP-R10 clamp broken in WEPA/IC1/L3 |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-02-03 | 2018-12-10 15:41 | -55 | 2018-10-26 11:35 | Electrical - General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | R10 clamp broken in WEPA/IC1/L3 negative busbar
| 05SY - Systemwide | Cxxx-NCR-000143 | NCR | Bund pump equipment installed without EMC in all sites |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-04-14 | 2019-04-11 13:27 | -3 | 2018-11-28 14:10 | Electrical - General | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Bund pump equipment installed without EMC in WBP ATFS, STG ATS, PLU ATS
| 05SY - Systemwide | Cxxx-NCR-000144 | NCR | Failure of DAP server at multiple Cxxx Traction power sites |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-12-04 | 2020-12-03 15:07 | -1 | 2018-12-10 13:10 | Electrical - General | 500 |  | Material | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Failure of DAP server at multiple Cxxx Traction power sites GE DAP server within LCP at 4 x ATS sites (PLUA, PMLA, STGA, WEPA). (excl NWR side of PMLA ATFS). As of 05/12/18 – DAP has been removed from PMLA & PLUA and sent to GE for repair. A temporary DAP unit has been supplied by GE and is currently installed at PMLA. There is currently no DAP at PLUA and hence no local control available at the site. 2 new DAP units have been ordered by GE for install at STGA & WEPA. Currently the LCP at both sites is operational albeit with sporadic performance.
| 05SY - Systemwide | Cxxx-NCR-000145 | NCR | Plumstead 48 Volt Battery Charger - Faulty alarm indication (LV Disconnect Fail) |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-06-30 | 2019-06-25 13:59 | -5 | 2019-02-19 13:42 | Communications and Control Systems | 500 |  | Equipment Breakdown | Reject | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Standing SCADA Alarm, LV Disconnect Fail Dale 48V DC Battery charger, Alarm Interface/Display Module (K1 PCB) which controls the Remote Alarm Relays (K5 PCB) isn’t operating Relay K8. There is a standing ‘LV Disconnect Fail’ alarm, the drawing supplied from Dale does not show in enough detail how this alarm is generated. Document: Cxxx-ALC-E-XDS-CRG03-50005 Manufacturers Drawing Number: U153751-D011 Sheet 3
| 05SY - Systemwide | Cxxx-NCR-000146 | NCR | Plumstaed ATS P&C building power supply cables to heater burned |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-12-19 | 2019-10-16 11:27 | -64 | 2019-09-10 10:55 | Electrical - General | 500 |  | Material | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The heater on AT2 & Track Feeder 102Q protection cubicle was replaced and the power supply cable PVC 2 CORE 2.5mm - BN & BU reconnected. The end of the supply cables connected inside the heaters was burned.
| 05SY - Systemwide | Cxxx-NCR-000147 | NCR | Missing Calibration Certificates of Test Equipments at Pudding Mill Lane ATFS RFL side Switchgears |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-03-31 | 2021-01-18 10:29 | -72 | 2020-12-22 09:35 | Electrical - Switchgear | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | During the Cxxx CRAF2 CRL surveillance, it was found out that 3 nos. Calibration Certificates of the test equipments used in Cxxx - Pudding Mill Lane RFL side Switchgears- Pre-Commissioning Test Report - Cxxx-ALC-O4-RGN-CR094-50010, Rev 4.0 were missing as listed below: • Fluke (serial number 88450304) • Omicron CT Analyzer (JC203D) • Cibano (EF533G)
| 05SY - Systemwide | Cxxx-NCR-000148 | NCR | Cracked R8 Busbar Connection Plate |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-06-16 | 2021-06-24 14:50 | 8 | 2021-03-18 19:51 | Electrical - Power Distribution | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During a routine maintenance inspection regime at Westbourne Park, Plumstead & Pudding Mill Lane traction sites, cracking was discovered on the R8 palm plates by the bolt holes. 3 hairline cracks were detected at Plumstead and 1 partial fracture was detected at Westbourne Park. The attached Slide pack from the QIEP shows the details of the incident and the attached spreadsheet shows the findings of the surveys completed to date.
| 05SY - Systemwide | Cxxx-NCR-000149 | NCR | __ FSKII Circuit Breaker collar​ manufacturing defect |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-10-31 | 2021-07-05 11:33 | -118 | 2021-04-07 09:32 | Electrical - Power Distribution | 500 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Other | Completed |  | __ have notified __ we procured a batch of breakers which contain a sub-standard manufactured white plastic collar used to operate the I/O indictor. The full report is attached and demonstrates how these pieces have cracked at other sites, rendering the circuit breaker stuck and unable to operate. From __ complete list of serial numbers 5 confirmed as affected. These are: • Plumstead ATS: 101R Negative • Westbourne Park ATS: 101H Positive • Westbourne Park ATS: 101H Negative • Westbourne Park ATS: IC1 Negative (currently decommissioned and sat in Plumstead stores) • Pudding Mill Lane ATFS: 101A Negative The serial numbers are not known for 16no circuit breakers installed at Pudding Mill Lane ATFS which have been handed over to __. This will need to be confirmed.
| 05SY - Systemwide | Cxxx-NCR-000150 | NCR | Issues with lugs and crimping at Plumstead |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-05-28 | 2021-07-05 11:30 | 38 | 2021-04-28 17:34 | Electrical - Electrical Engineering General | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Upon rectification of Cxxx-NCR-000148 instances of incorrectly crimped VT primary cables connected to the Busbar. Cables were found to be loose and could be pulled out of the lug by hand. It was found that some of the lugs had been cut back, for reasons unknown. At Plumstead ATS, 3 such aluminium lugs and a copper lug were found incorrect. See attached report.
| 05SY - Systemwide | Cxxx-NCR-000151 | NCR | Circuit breaker plate clash with R8 clamp at PML |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-08-04 | 2021-07-15 14:46 | -20 | 2021-05-06 12:17 | Electrical - Power Distribution | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the R8 plate checking exercise it was noted that the R8 clamps were inverted at 17 locations. 6301B NEG 317B POS 317B NEG 318B POS 318B NEG 319B POS 319B NEG 320B POS 320B NEG 6302B POS 6302B NEG 6301A NEG 317A POS 318A POS 319A POS 320A POS 6302A NEG It was found the circuit breaker plates at these locations have 4 centrally located holes which differs from the 9 hole arrangement in use where other R8 plates are in use. Due to the profile of the R8, and the greater dimension between the edge of the circuit breaker palm plate and the R8 clamp palm plate the R8 could not be installed in the correct rotation. As a result on site it was installed in the opposite rotation to avoid this clash. On the manufacturers datasheet the 4 hole circuit breaker plate was shown to be smaller, which would make it acceptable due to the decreased dimension between the edge of the plate and the drilled holes.
| 05SY - Systemwide | Cxxx-NCR-000152 | NCR | Arcing F2 disconnector PML |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-08-31 | 2021-06-30 13:10 | -62 | 2021-05-24 11:39 | Electrical - Power Distribution | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | PMLA/F2 disconnector discovered to be arcing by __ in it's closed position. See photos for damage.
| 05SY - Systemwide | Cxxx-NCR-000153 | NCR | Over-torqued bolts on CT clamp IC2/L3 positive |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-08-31 | 2021-08-03 15:08 | -28 | 2021-06-22 13:41 | Electrical - Power Distribution | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Information not detailed | Completed |  | The bolts connect the clamp on CT on IC2/L3 positive side was over-torqued to 150Nm instead of 50Nm.
| 05SY - Systemwide | Cxxx-NCR-000154 | NCR | Disconnector drive assembly alignment issues - PML |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-09-30 | 2021-10-06 11:30 | 6 | 2021-05-27 11:52 | Electrical - Power Distribution | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Issues with the disconnector assembly were observed during the dilapidation survey causing excessive torque requirements from the operating motor. The transition between the bottom and top pole was in the wrong operating position. Drive poles have been installed at the incorrect lengths, the initial position of the cranks were outside the required 45 degrees, and pieces of the assembly are in the wrong orientation.
| 05SY - Systemwide | Cxxx-NCR-000155 | NCR | M6 tension spring bolts coming loose on disconnector at PML |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-09-30 | 2021-06-28 09:56 | -94 | 2021-06-03 09:39 | Electrical - Power Distribution | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | M6 bolts which hold the tension springs in place on the disconnectors at the pudding mill lane __ ATFS are able to be unscrewed by hand so were not at the correct torque.
| 05SY - Systemwide | Cxxx-NCR-000156 | NCR | Brass pins not rotating within the Aluminium Block on the SDCEM cranks for disconnector |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2022-05-19 | 2022-05-25 15:12 | 6 | 2021-07-20 13:59 | Electrical - Power Distribution | 500000 |  | Design | Rework | 1 (>60k) | Complete | Design Problem - Other | Completed |  | Following a dilapidation survey of the disconnectors on the NR side of the PML ATFS, it has been found that the brass pin through the aluminium block at the top of the disconnector crank assembly, does not rotate. These components are part of the SBE/SBI type Disconnector supplied by SDCEM and attached are the installation instructions which have been followed on site. This was presented to SDCEM on the 15th July 2021 and they confirmed that the pin should be rotating as part of the designed operation and therefore non conforming. The consequence of this is that the brass pin is rotating inside the slotted hole in the end plate which is being damaged on operation by the hexagonal shape of the brass pin designed to prevent rotation. This is causing the setup of the disconnector to deteriorate over time, eventually causing the operating angles to fall out of tolerance. Total numbers of locations using this disconnector type are 20 no. Westbourne Park, 40 no. Pudding Mill Lane NR, 6 no. Pudding Mill Lane RFL, 24 no. Plumstead
| 05SY - Systemwide | Cxxx-NCR-000157 | NCR | Pudding Mill Lane Cable labels - Several labels have been printed with a missing Underscore (_). |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2022-03-24 | 2022-03-17 13:23 | -7 | 2022-03-10 19:54 | Information Management - Asset Information | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Several Labels for Control Cables have been printed with missing Underscore (_). It seems as if the label cutting, alignment through printing or font size are slightly off on some labels. Full Quantity unknown as examples have been identified through VAP photographs. Example photographs attached to NCR. The format , syntax and expected cable information within the cable label text is all correct and consistent with AIMS data. The impact of this missing underscore is extremely low. The correct Design ID can still be found within the AIMS/ Maximo CEAMS data. Therefore CRL would suggest that a USE AS IS deposition be acceptable and that any New labels printed over the asset lifecycle be thoroughly checked for similar printing issues. Please ensure this NCR is directed towards __ for RFL deposition. __, Please ensure that this is raised with __ / __
| 05SY - Systemwide | Cxxx-NCR-000158 | NCR | P143 IED Spurious Alarms |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2023-08-25 |  | -200 | 2022-09-12 11:56 | Electrical - Electrical Engineering General | 500 |  | Material | Repair | 4 (0.5-3k) | Open |  | ENGINEERING ROUTING |  | Following reported issues from RFLi and the RCC loss of comms on the P143s has been documented in the "HV Switching Issues Tracker” - CRL1-XRL-O8-LST-CRG03-50001. Further investigations by GE, RFLi, Cxxx and __ have taken place and found issues at all 4no. HV AT sites relating to P143 IEDs. See attached GE report findings for further details relating to P143 loss of comms. No of P143 IEDs at each site: PMLA (RFLI) – 2 PLUA – 8 WEPA – 5 SYGA – 14
| 05SY - Systemwide | Cxxx-NCR-000001 | NCR | Failure on LV bushing during short circuit type test (IEC 60076-5) |  | Contr | SKC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2015-08-06 | 2015-08-10 12:13 | 4 | 2015-07-06 21:44 | Electrical - Transformers | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | The LV bushing of the transformer is a cast resin product, all four LV terminals (L1/L2/L3/N) are cast into a single ‘monobloc’ bushing. Following the first shot of the 9No. short circuits applied to the transformer it was observed during post testing that the transformer impedance had increased (though it remained within the limits in accordance with IEC 60076-5). Upon visual inspection of the transformer a hairline crack was detected between the edge of the monobloc and the L2 terminal of the bushing, transformer oil was observed to be seeping through this crack. The product manufacturer, __, suspended further testing to avoid further damage to the transformer. The non-conformance is reported against the suspension of the short circuit testing and failure of the LV bushing.
| 05SY - Systemwide | Cxxx-NCR-000002 | NCR | Failure during detanking of transformer Serial Number 1LTR0028384 (Type TSPH-14475/900) following short circuit type test (IEC 60076-5) |  | Contr | SKC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2015-09-18 | 2015-09-11 10:32 | -7 | 2015-07-06 21:53 | Electrical - Transformers | 500 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | During visual inspection deterioration of low voltage winding (in linb A) could be observed. Some of the spacers slipped out from the damaged winding.
| 05SY - Systemwide | Cxxx-NCR-000003 | NCR | Failure of Monobloc on Transformer SCT #3 |  | Contr | SKC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2015-10-30 | 2015-11-03 16:30 | 4 | 2015-08-05 17:17 | Electrical - Transformers | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | The LV bushing of the transformer is a cast resin product, all four LV terminals (L1/L2/L3/N) are cast into a single ‘monobloc’ bushing. Following the first shot of the 9No. short circuits applied to the transformer a hairline crack was detected between the edge of the monobloc and the L2 terminal of the bushing. The product manufacturer, __, suspended further testing to avoid further damage to the transformer. The non-conformance is reported against the suspension of the short circuit testing and failure of the LV bushing.
| 05SY - Systemwide | Cxxx-NCR-000004 | NCR | Start of Works without Accepted ITP |  | Contr | SKC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2015-09-25 | 2015-09-22 12:27 | -3 | 2015-09-03 15:51 | Electrical - Switchgear | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | Installation of switchgear at Mile End Park Shaft started on 13th July 2015 without an accepted ITP in place, contrary to the requirement of WI vol 2B part 20.8.
| 05SY - Systemwide | Cxxx-NCR-000005 | NCR | __ 250kVA (22/0.433kV) Type Test Failure |  | Contr | SKC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-01-29 | 2016-01-27 12:14 | -2 | 2015-12-18 17:24 | Electrical - Transformers | 500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Transformer 1LTR0028420 was undergoing factory acceptance testing. A failure was observed during the Lightning Impulse test. The 250kVA transformer (1LTR0028420) was subject to 125kV (1.2/50µs) voltage impulse as per the requirements of BS EN 60067 – 3 – Power Transformers: Part 3: Insulation levels, dielectric tests and external clearances in air. The standard requests a reduced level impulse followed by three 100% voltage impulses. The following was noted during witness of the test on phase A: Reduced impulse – 87 kV (0.976/48 µs) 1st 100% impulse -125 kV (0.989/42 µs) 2nd 100% impulse -125 kV unit flashed over 3rd 100% impulse -125 kV unit flashed over Initial report and photographs attached.
| 05SY - Systemwide | Cxxx-NCR-000006 | NCR | Cracked Radiator on CWS Transformer s/n 1LTR0028385 |  | Contr | SKC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-07-31 | 2016-08-01 13:38 | -364 | 2016-02-22 16:42 | Electrical - Transformers | 500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Hairline cracks were identified on the base of 2 of the radiator fins, following discovery of a small amount of leaked coolant within the bund. Attached photo shows the location of the cracks.
| 05SY - Systemwide | Cxxx-NCR-000007 | NCR | Lack of evidence shown for compliance with respect to the management of constructability reviews |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-04-28 | 2016-04-29 12:12 | 1 | 2016-03-29 14:09 | Systems - Other | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Evidence of constructability reviews shown in regards to management of IFC drawings. However they only show to be commented on by Construction Manager and do not show return response from design.
| 05SY - Systemwide | Cxxx-NCR-000008 | NCR | F11010 11kV 185mm² core 2 (drum 055) was damaged in 2 places whilst pulling into position |  | Contr | ALC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-11-25 | 2016-11-17 16:47 | -8 | 2016-09-06 11:14 | Electrical - Power Distribution | 500 |  | Damaged | Reject | 4 (0.5-3k) | Complete | Discipline/Workmanship - Inadequate/insufficient tooling. | Completed |  | The cable sheath and armour was torn in two locations as it was fed from the drum onto the cable management system. Attached photos show the damage.
| 05SY - Systemwide | Cxxx-NCR-000009 | NCR | Short Circuit HV Cable Straps Incorrectly sized and delivered to Plumstead Portal. |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-03-24 | 2017-03-23 14:46 | -1 | 2016-10-07 14:58 | Electrical - Power Distribution | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Error by manufacturer in shipping or marking | Completed |  | Incorrectly sized HV Short Circuit Cable Straps have been delivered to Plumstead Portal, and then installed onto the CRL network between chainages 21050m - 19600m within the Westbound tunnel.
| 05SY - Systemwide | Cxxx-NCR-000010 | NCR | Failure to update Comm__ents Delivery Tracker (C__) at required frequency |  | Contr | ALC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-01-27 | 2017-01-25 14:11 | -2 | 2016-12-02 14:52 | Consents - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | __ has not been loading evidence onto the Comm__ents Delivery Tracker (C__), in accordance with the Comm__ents Compliance Plan.
| 05SY - Systemwide | Cxxx-NCR-000011 | NCR | __ drawings to be based on the accepted __ General Arrangement drawings |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-03-23 | 2017-04-25 13:32 | 33 | 2017-02-03 16:01 | Electrical - Power Distribution | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | __ have produced shipped bunds that are larger that the agreed Code 1 drawings.
| 05SY - Systemwide | Cxxx-NCR-000012 | NCR | HV Cable Failure F22123 – Limmo to Canary Wharf mid tunnel joint eastbound, drum 081 |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-08-31 | 2017-08-31 16:14 | 0 | 2017-02-03 16:12 | Electrical - Power Distribution | 500 |  | Material | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Core L2 from Drum 0081,was installed into the CRL Trace within the trefoil configuration, and made up a 22kv feeder designated as F22123 failed a pre -energization pressure test.
| 05SY - Systemwide | Cxxx-NCR-000013 | NCR | HV Switchgear – VT gas seal’s under torqued |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-08-31 | 2017-08-31 16:18 | 0 | 2017-02-03 16:20 | Electrical - Power Distribution | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Inadequate/insufficient tooling. | Completed |  | SF6 gas leak on the __ HV Switchboard VT chamber located in HV Switch Room “B”. This occurred on releasing SF6 Gas into the VT chamber.
| 05SY - Systemwide | Cxxx-NCR-000014 | NCR | Damaged HV Bushing at NWP |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-07-21 | 2017-08-24 11:24 | 34 | 2017-04-11 09:37 | Electrical - Power Distribution | 40000 |  | Damaged | Rework | 2 (6-60k) | Complete | External Phenomenon - Other | Completed |  | NWP (tier 1 contractor) handed over the rooms to __ on the 27/10/16. __ then proceeded to commence their installation activities at NWP. Subsequently NWP agreed that __ would have exclusive access to these rooms, if additional works need to take place within these rooms access would be controlled via a permit system. __ temporarily demobilised from NWP and covered the Switchgear until __ where available to attend to witness the gassing of the HV switchboard. Upon returning to NWP __ discovered that a significant amount of scaffolding had been erected within the room without a permit and without __’s knowledge despite them having ownership of the rooms.
| 05SY - Systemwide | Cxxx-NCR-000015 | NCR | Damaged Cable on 26/06/2017 in WB Connaught Tunnel, 1x185 11kV ,LUL , 085 Drum No – 1068995005 |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-10-31 | 2017-09-26 15:27 | -35 | 2017-08-25 07:11 | Electrical - Power Distribution | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Cable damage was noticed during installation 26/06/2017 Cable Type – 1 x 185 11kV – LUL – 085; Drum No – 1068995005; Length – 1206m; Installation method – by cable train, pulled off using rollers controlled by brake; Location – Connaught Tunnel West Bound – at 630m mark; Damage recorded over length of approximately 4 metres; This damage was noticed immediately as it was being reeled off and before it came into any contact with our containment.
| 05SY - Systemwide | Cxxx-NCR-000016 | NCR | Damaged Cable on 10/07/2017 in EB Connaught Tunnel, 1x185 11kV ,LUL |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-10-31 | 2017-11-20 09:59 | 20 | 2017-08-25 07:18 | Electrical - Cable Management | 500 |  | Manufacturing Defect | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Damaged Cable damaged outer sheath of the cables, as you can see (refer attached photo) attached these marks are on new cable half way through the drums so not as a result of installation. New cable with scuffs/scratches, isn't the start of the drum it's had a few hundred meters laid off. The black marks are on the sheath.
| 05SY - Systemwide | Cxxx-NCR-000017 | NCR | Open command from the P521 protection relay of the __ switchboard |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-01-31 | 2018-06-20 12:08 | 140 | 2017-09-22 13:30 | Communications and Control Systems | 500 |  | System Defect | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The Relay P521 cannot be programmed to send an open command to the __ switchgear. The SCADA RTU should send an open command through the IEC 60870-5-103 in order to open the CB with the open relay RLY4
| 05SY - Systemwide | Cxxx-NCR-000018 | NCR | Damaged HV Cable- SW3 Tool Box Contact |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-09-06 | 2017-09-06 11:03 | 0 | 2017-08-23 14:42 | Train - General | 500 |  | Damaged | Reject | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | The HV cables within the WB of Connaught Tunnel where installed into there final location. On the 16th July 2017, SW3 when travelling towards the Welfare at the West Compound made contact with a Tool Box. The access ladder on the Cable Wagon caught the Tool Box, subsequently dragging it between 15 and 20 metres along the Cess. Due to the excess materials within the area, the Tool Box caught various items, causing damage to Cxxx HV (dead) cables and other materials along the way.
| 05SY - Systemwide | Cxxx-NCR-000019 | NCR | Earthing Cable-Potential Non-Compliance against LU fire Safety Standard |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-08-31 | 2018-07-19 15:04 | -43 | 2017-10-09 16:36 | Electrical - Earthing & Bonding | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | Earthing Cable-Potential Non-Compliance against LU fire Safety Standard All Cxxx HV switch rooms and HV / LV Transformer rooms Installed earth cable is __ SAFIRE OHLS 6491B
| 05SY - Systemwide | Cxxx-NCR-000020 | NCR | Design & Manufacture drawings of LV Boxes misaligned 40mm difference |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-08-31 | 2018-07-31 15:37 | -31 | 2018-01-03 12:03 | Electrical - General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | The height of LV transformer box has been manufactured 40mm shorter than the __ drawings.
| 05SY - Systemwide | Cxxx-NCR-000021 | NCR | Damage to Transformer during storage |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-10-31 | 2018-10-24 09:39 | -7 | 2018-01-03 13:40 | Electrical - General | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | A 2.5 MVA transformer has sustained minor damage to the cooling fins while in storage. See attached photos.
| 05SY - Systemwide | Cxxx-NCR-000022 | NCR | Damage to HV ladder rack at chainage 13980-13985-WB |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-08-31 | 2018-08-02 15:11 | -29 | 2018-01-03 15:07 | Electrical - General | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | A Section of HV ladder rack between chainage 13980-13985-WB was reported to be damaged by others outside of Cxxx. No photos available of the damage.
| 05SY - Systemwide | Cxxx-NCR-000023 | NCR | STG-Water ingress into the cable-Feeder Cable (F22122) |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-05-12 | 2018-03-09 12:39 | -64 | 2018-01-12 14:15 | Electrical - General | 500 |  | Damaged | Reject | 4 (0.5-3k) | Complete | Discipline/Workmanship - Contamination | Completed |  | STG-Water ingress into the cable-Feeder Cable (F22122) - Westbound - 22kv, 400mm -In the STG shaft
| 05SY - Systemwide | Cxxx-NCR-000024 | NCR | Faulty VT LIM HVSB B 22kV |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-08-31 | 2018-08-13 14:09 | -18 | 2018-05-01 08:34 | Electrical - Power Distribution | 60000 |  | Manufacturing Defect | Reject | 2 (6-60k) | Complete | Design Problem - Inadequate or defective design | Completed |  | On the 16 April a notification was received that the incoming HV power had tripped at LIM on the 22kV network, upon investigation it was noted that a voltage transformer monitoring the incoming cable failed. The power has been isolated and the faulty unit has been removed and sent for testing.
| 05SY - Systemwide | Cxxx-NCR-000025 | NCR | Woolwich Arsenal Failed Current Transformer (HVSB A) |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-05-27 | 2018-06-12 15:52 | 16 | 2018-05-13 21:37 | Electrical - Switchgear | 1000 |  | Manufacturing Defect | Reject | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | As part of the stage 2.2 pre-commissioning testing for the Crossrail Cxxx non-traction project, testing was carried out on the current transformer (CT) for the overcurrent & earth fault protection on panel JO1 on the 11kV ‘A’ switchboard at Royal Arsenal Woolwich Station substation. This CT has a ratio of 150:1 and a class of 5P20. The testing was carried out on the 26th April, 2018, using a CT Analyser, manufactured by Omicron Electronics which tests the characteristics of a CT in an automated fashion. The results obtained for L3 were indicative of a failure of the CT.
| 05SY - Systemwide | Cxxx-NCR-000026 | NCR | F11107 Failed HV Presure Testing |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-06-27 | 2018-06-20 12:11 | -7 | 2018-05-13 22:04 | Electrical - Power Distribution | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | On the 27.03.18 while completeing pressure testing on HV Feeder Cable F11107. The Hv cables F11107 between Woolwich Arsenal HVSB A & North Woolwich Portal, HVSB A on east bound, it was found that Phase L2 Failed the pressure test. F11107 – L1 – 100% tested F11107 – L2 – 0% tested F11107 – L3 – 100% tested
| 05SY - Systemwide | Cxxx-NCR-000027 | NCR | F22042 Damaged, CWS TX B2 Feeder |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-10-31 | 2018-10-26 15:11 | -5 | 2018-05-13 22:26 | Electrical - Power Distribution | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | External Phenomenon - Not Defined | Completed |  | On the 26thof April 2018, during a site assurance visit, it was observed that a Cxxx cable had sustained damage ofits outer sheathing. Although the cables where not live, they are due to be and such damage will have an adverse effect on the integrity of the cable. The Cable has been pressure tested approx. 4/5 week prior and it suspected that the damage may have occurred at some point afterwards.
| 05SY - Systemwide | Cxxx-NCR-000028 | NCR | HV Feeder Cable Damage at Mile End shaft on the "A" leg |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-05-27 | 2018-06-22 10:37 | 26 | 2018-05-13 22:42 | Electrical - Power Distribution | 12000 |  | Damaged | Reject | 2 (6-60k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | The HV Feeder Cable From MES HVSB A to the Trace has been critically damaged while installing the trace doors.
| 05SY - Systemwide | Cxxx-NCR-000030 | NCR | Damaged Battery Charger at Liverpool Street Moorgate Box |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-08-31 | 2018-07-19 15:06 | -43 | 2018-06-13 12:01 | Electrical - Switchgear | 500 |  | Damaged | Reject | 4 (0.5-3k) | Complete | External Phenomenon - Not Defined | Completed |  | Damaged Battery Charger at Liverpool Street Moorgate Box. See attached photos 1 to 6 • Switchgear and BC delivered and stored into empty clean switch room on 06/11/17 • Works continued at Blomfield Box • Cxxx team went to commence works at Moorgate on 04/01/18, where scaffold was discovered within the switch room, works could not start. • No WRA’s were issued by Cxxx for works in the switchroom • Scaffold was eventually removed on 08/01/18 • Cxxx commenced installing the switchboard on 09/01/18, no damage to Battery Charger was noticed as it was still wrapped and protected. • Cxxx removed packaging from Battery Charger on 15/01/18 in order to install, no visible damage to packaging but once removed the extensive damage was discovered. • It would seem the likely cause was the battery charger to have tipped over and impacted on the front.
| 05SY - Systemwide | Cxxx-NCR-000031 | NCR | PLU 11 kV Earthing Arrangements |  | Crossrail | PDP | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-08-31 | 2018-07-03 14:57 | -59 | 2018-06-13 14:58 | Electrical - Earthing & Bonding | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The earthing arrangements at PLU were not installed to the works information i.e. the design issued by __. The impact to this was LIM 11 kV switchboard was not energised as planned on the 08-06-2018 as the earthing was not installed to the design or as stated in the IRS which lead to the SAP from __ refusing the energisation.
| 05SY - Systemwide | Cxxx-NCR-000032 | NCR | Vibration of VTs |  | Crossrail | PDP | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-08-31 | 2018-07-16 11:36 | -46 | 2018-06-13 15:14 | Electrical - Switchgear | 500 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | LIM 22 kV - following the initial catastrophic failure of the VT’s at LIM a replacement set of VT’s was issued by __ in order to mitigate further issues with the VT’s. The new VTs were installed and during the testing process vibration of the VTs was noted and the testing was stopped immediately. This has lead to a further change out of the VTs.
| 05SY - Systemwide | Cxxx-NCR-000033 | NCR | General VT failure |  | Crossrail | PDP | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-08-31 | 2018-08-13 15:37 | -18 | 2018-06-13 15:18 | Electrical - Switchgear | 500 |  | Design | Reject | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | On removal and rectification of the VTs throughout the Cxxx HV non Traction switchgear it was noticed that cracking within the resin had occurred around the internal fuse of the VT which could be a contributing factor to the VT failure. This could be due to low resin coverage over the VT which is not to the design of 11.1mm or the fuse has been impacted during transport and installation to cause this damage as the relays left the factory in perfect condition according to the Zelisko report.
| 05SY - Systemwide | Cxxx-NCR-000034 | NCR | Cable identifier label not as per CR-STD-015 Asset Identification Standard |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-08-31 | 2018-08-02 12:30 | -29 | 2018-06-15 14:33 | Electrical - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | It has been noted that some of the Cable Identifier Labels are not in line with CRL1-XRL-O6-STD-CR001-00031 appendix 13.4 - label layouts. See attached Cable Identifiers labels Photos, which shows larger labels used to suit the perforations of the HV ladder lids.
| 05SY - Systemwide | Cxxx-NCR-000035 | NCR | Earth conductors not connected in the Trace |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-08-31 | 2018-09-27 12:54 | 27 | 2018-07-11 13:31 | Electrical - Earthing & Bonding | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Following pressure test of a 22K, it has been identified that an earth cable termination was not reinstated. Immediate action was to power down and attach the drain earths to the 22KV system fed from Limmo. A full check is to be instigated of all earths prior to powering back up.
| 05SY - Systemwide | Cxxx-NCR-000036 | NCR | Pudding Mill Lane Transformer -Oil pressure alarm unit |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-12-31 | 2019-01-18 15:00 | 18 | 2018-07-11 12:48 | Electrical - Transformers | 500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Pudding Mill Lane (500kVA 22kV) Transformer -Oil pressure alarm unit cover cannot be fully opened, This is restricted by the LV supply connection box. (Factory Fitted). Transformer Serial numbers TRX 1= 1LTR0028418 and TRX 1= 1LTR0028419 See attached Photos of PML Transformer Oil pressure alarm 1 & 2
| 05SY - Systemwide | Cxxx-NCR-000037 | NCR | Limmo 22kV SB B L2 Surge Arrestor Failure |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-08-31 | 2018-09-07 12:03 | 7 | 2018-07-16 15:57 | Electrical - Switchgear | 500 |  | Equipment Breakdown | Reject | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The Limmo 22kV SB B L2 Surge Arrestor Failed during Energisation from __ on 13/07/2018
| 05SY - Systemwide | Cxxx-NCR-000038 | NCR | ROP to PAD HV Feeder Cables incorrect installation |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-08-31 | 2018-09-27 13:09 | 27 | 2018-07-20 13:31 | Electrical - Cable Management | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The ROP to PAD HV Feeder Cables have been incorrectly installed. Cable F22101 has been installed from ROP Switchboard A to PAD Switchboard B, not to PAD Switchboard A as design.(Cxxx-ALC-E-DDE-CRG03-00100) Cable F22102 has been installed from ROP Switchboard B to PAD Switchboard A, not to PAD Switchboard B as design.(Cxxx-ALC-E-DDE-CRG03-00100)
| 05SY - Systemwide | Cxxx-NCR-000039 | NCR | TCR Transformer Feeds |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-09-15 | 2018-09-27 13:12 | 12 | 2018-07-26 08:00 | Electrical - Power Distribution | 4000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Transformer A & B feeder cables F22013 and F22016 incorrectly routed.
| 05SY - Systemwide | Cxxx-NCR-000040 | NCR | Cable type XLPE/CWS/LSF/AWA/LSF exposed to sun at Connaught Tunnel Portals |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-11-30 | 2019-01-22 13:48 | 53 | 2018-08-15 10:00 | Electrical - Cable Management | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Sections of Cables F11013 and F11014 Cable type XLPE/CWS/LSF/AWA/LSF are exposed to the sun at Connaught Tunnel Portals See attached Cxxx-NCR-000040 Photos
| 05SY - Systemwide | Cxxx-NCR-000041 | NCR | Water in cable F22110 between Farringdon and Fisher Street |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-11-30 | 2018-11-21 11:17 | -9 | 2018-08-17 12:16 | Electrical - Power Distribution | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Contamination | Completed |  | Water in cable F22110 between Farringdon and Fisher Street chainage 5982 to 6891 (1020 metres) - During the HV cable joint preparation stripping the outer sheath it was found that the HV cable had water within the cable. The water was dripping from the inner core. See attached Video - The second cable was stripped and found the same issue. - The third cable was stripped which also had small traces of water, not to the extent of the 1st & 2nd cores. - All damaged cable are FAR side and come through the local UTX (which is dry). Stripped back FSS side cables and no visible signs of water
| 05SY - Systemwide | Cxxx-NCR-000042 | NCR | HV Joints not connected toTunnel Earth |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-12-20 | 2019-11-18 14:50 | -32 | 2018-09-05 13:41 | Electrical - Earthing & Bonding | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | Some of the HV joints are not connected to the tunnel earth, please see attached marked up westbound and eastbound schematics for the locations. Where the joint is not earthed, __ have earthed the screen and armour of the HV cable at the HV switchboard as a temporary arrangement as agreed via Cxxx-RFI-000215 "Temporary earthing for energisation " with CRL, this has allowed __ to proceed to energise with the agreed energisation schedule.
| 05SY - Systemwide | Cxxx-NCR-000043 | NCR | Farringdon Transformer Feeder Cables incorrectly routed. |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-12-31 | 2019-02-01 15:45 | 32 | 2018-09-12 14:26 | Electrical - Cable Management | 2000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The transformer feeders cables for TB1 have been installed to TB2 and vice versa. See attached Farringdon As Built on Site and Farringdon Extract from SLD
| 05SY - Systemwide | Cxxx-NCR-000044 | NCR | Liverpool Street Cable F22112 damaged in Riser B |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-12-31 | 2018-11-07 11:09 | -54 | 2018-09-20 15:32 | Electrical - Cable Management | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | Cable F22112 on the vertical ladder rack in the HV B Riser was reported as damaged with the attached the Damaged cable - photo 1 and 2, by the Cxxx Electrical supervisor.
| 05SY - Systemwide | Cxxx-NCR-000045 | NCR | Incorrect type of cable joints used. |  | Crossrail | PDP | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-10-31 | 2019-10-29 11:40 | -2 | 2018-09-14 11:07 | Electrical - Power Distribution | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Incorrect type of cable joint used at numerous locations. The type of joint installed does not enable the screens and armours of the cables to be earthed to the local traction spider plate as per the Cxxx design and the Crossrail earthing and bonding strategy. Installation of new joints or other remedial action is therefore required.
| 05SY - Systemwide | Cxxx-NCR-000046 | NCR | Incomplete Cable Works |  | Crossrail | PDP | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-03-31 | 2018-10-05 13:59 | -177 | 2018-09-18 13:54 | Electrical - Cable Management | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate resources | Completed |  | Missing cable from LIS Switchboard to TA2.
| 05SY - Systemwide | Cxxx-NCR-000047 | NCR | Limmo 11kV BSP cables |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-10-31 | 2019-10-29 11:44 | -2 | 2018-10-04 10:03 | Electrical - Electrical Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Previous Construction - Other | Completed |  | The installed Limmo external Feeder cables F110X1 and F110X2 are MDPE and not LSF as Cxxx 11kV Cable Schedule: Cxxx-ALC-E-TSC-CRG03-50004 , this cable doesn’t comply with the LU 1-085 specification or Specification Cxxx-ALC-Y-RSP-CRG03- 50005 section 4.4.1 "Cables identified for Section 12 areas" The cables come from Limmo __ 11kV RMU, through ducts and then the cables drop directly in the Cxxx Switchroom rooms that are just underneath the higher level of the shaft, as per "Limmo Peninsula Shaft, BSP & Cxxx HV Cable / Duct Routing Site Layout Cxxx-SKC-E-DDL-CR144_SH011-01601" See attached cable technical data sheet
| 05SY - Systemwide | Cxxx-NCR-000048 | NCR | LST Damaged control cable on feeder B route |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-12-31 | 2018-11-07 11:16 | -54 | 2018-09-25 13:19 | Electrical - General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | LST: Damaged control cable on feeder B route (Room 789 riser platform +0.5) See attached photos LST Damaged control cable on feeder B route (1) and LST Damaged control cable on feeder B route (2)
| 05SY - Systemwide | Cxxx-NCR-000050 | NCR | TCR Switchboard A - VT Malfunction |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-12-31 | 2019-01-18 14:58 | 18 | 2018-10-03 13:21 | Electrical - Transformers | 500 |  | Equipment Breakdown | Reject | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | During the energisation of TCR SB A on 25/09/18, it was observed that the reported voltages on the protection relays and at the RCC was not as expected. At BOS SB A and FIS SB A either side of TCR SB A, the voltages were showing correctly. It was decided to de-energise SB A at TCR to investigate the problem. Upon investigation on 28/09/18 it was discovered that the VT on Phase L1 was not working as expected. The voltage on the secondary side of the transformer was lower than expected. See attached Voltage Transformer Test 01-Oct-2018 15-24-58.
| 05SY - Systemwide | Cxxx-NCR-000052 | NCR | Bond Street Transformer B1 oil leaking from LV bushing |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-05-16 | 2019-04-11 14:19 | -35 | 2019-02-05 16:56 | Electrical - Transformers | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | 1. Bond Street Transformer B1 (Asset ID 1LTR0028393) oil leaking from LV bushing 2. Electrical LV Energy cannot be provided to Cxxx 3. Cxxx SAP encountered oil leak at Bond Street Transformer B1(Asset ID 1LTR0028393) on 04/02/2019 at 14:22
| 05SY - Systemwide | Cxxx-NCR-000053 | NCR | Bond Street Transformer TB2 oil leak (1LTR0028395) |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-07-04 | 2019-07-17 09:34 | 13 | 2019-03-26 11:15 | Electrical - Transformers | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | On 20/03/19 an oil leak on Transformer TB2 with serial number 1LTR0028395 was reported. __ took the opportunity with __(Turkey)and in attendance to investigate the leak on 22/03/19. The attached photos show the findings on site. Although new oil was visible in the bund a lot of residual oil from filling the transformer was also present to the underside of the cooling fins
| 05SY - Systemwide | Cxxx-NCR-000054 | NCR | Woolwich Transformer leaking FR3 oil from LV connection bushings |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-10-31 | 2019-11-01 15:33 | 1 | 2019-05-23 10:48 | Electrical - Transformers | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | Woolwich 1.6 MVA Transformer B1 (Serial No 1TLR0028424) leaking FR3 oil from LV connection bushings. Similar issue was recorded in Bond Steet transformer B1 as well. Cxxx-CCM-00924 was issued to CRL.
| 05SY - Systemwide | Cxxx-NCR-000055 | NCR | Liverpool Street Transformer leaking FR3 oil from LV connection bushings |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-08-31 | 2019-08-30 14:16 | -1 | 2019-05-23 11:03 | Electrical - Transformers | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | Liverpool Street 2.5MVA Transformer A1 (Serial No 1LTR0028400) leaking FR3 oil from LV connection bushings. Similar issue was recorded in Bond Steet transformer B1 as well. Cxxx-CCM-00924 was issued to CRL.
| 05SY - Systemwide | Cxxx-NCR-000056 | NCR | Bond Street TB2 leaking oil from a pin prick in front fin |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-12-20 | 2019-12-03 15:23 | -17 | 2019-05-30 12:41 | Electrical - Transformers | 500 |  | Material | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Bond street TCR Transformer Tb2.0 MVA 22000/400v (Serial No 1LTR0028411) oil leak from a pin There appears to be a very tiny pin prick to one of the front fins, which is seeping a minute amount of oil.
| 05SY - Systemwide | Cxxx-NCR-000057 | NCR | Canary Wharf Station Switchroom A Battery Charger Rectifier 2 Fault |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-11-24 | 2019-09-18 12:30 | -67 | 2019-08-16 10:42 | Electrical - Power Generation | 500 |  | System Defect | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Canary Wharf Station Switchroom A, battery charger 001 – during a LV supply outage to the battery charger (CR143-HVP-00007), rectifier #2 hasn’t appeared to recover once supply was re-instated to the battery charger. Currently system although operational is running with only one rectifier meaning a single point of failure to supply HV protection relays if remaining rectifier was to fail.
| 05SY - Systemwide | Cxxx-NCR-000058 | NCR | 11kV HV Cable damaged at CH17,650 W/B on the Connaught Tunnel West End |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-03-31 | 2020-03-11 15:45 | -20 | 2019-10-03 09:48 | Electrical - Power Distribution | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | 11 kV HV cable (F11104 Custom House to North Woolwich) has been damaged and the aluminium armouring has been severed. Photo attached. Cable damage inspection report is attached
| 05SY - Systemwide | Cxxx-NCR-000059 | NCR | Control cables Identified with incorrect Function code |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-12-30 | 2022-01-13 14:20 | 14 | 2021-12-16 11:56 | Information Management - Asset Information | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | 169 Cxxx cables were created with TVS function coding. Assets are labelled and due to lengths may have many labels. Cables run in trace in cable trays / racking under walkways from HV rooms to next station, shaft, portal facility HV rooms. These assets would need to be recreated and relabelled. CRL suggest USE AS IS deposition. Time and cost would prohibit __ rectifying this.
| 05SY - Systemwide | Cxxx-NCR-000060 | NCR | HV Cable F11104 seath damaged at W/B ch.18347 Connaught tunnel |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-05-01 | 2020-03-19 16:28 | -43 | 2020-02-28 13:39 | Electrical - Power Distribution | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 11 kV HV Cable F11104 seath damaged at W/B ch.18347 Connaught tunnel Photo attached.
| 05SY - Systemwide | Cxxx-NCR-000061 | NCR | HV Cable F11012 Sheath damaged at W/B ch.21090 Woolwich Station |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-06-21 | 2020-07-02 08:23 | 11 | 2020-03-13 13:37 | Electrical - General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | HV Cable F11012 Sheath damaged at W/B ch.21090 Woolwich Station west end Photo attached
| 05SY - Systemwide | Cxxx-NCR-000062 | NCR | Drop 6 - NTP - Non Traction HV Power - name check failed |  | Crossrail | PDP | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-07-09 | 2020-07-21 10:25 | 12 | 2020-05-11 12:19 | Information Management - Asset Information | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Asset data name check failed for 28 earthwires at North Woolwich Portal. These assets are missing a comma in their name.
| 05SY - Systemwide | Cxxx-NCR-000063 | NCR | HV Cable F22114 Sheath damaged at LIV CAMBRIDGE HEATH Shaft |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-09-16 | 2020-12-08 08:26 | 83 | 2020-09-02 12:57 | Electrical - General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | "HV Cable F22114 Sheath damaged at Liverpool Cambridge Heath Shaft"
| 05SY - Systemwide | Cxxx-NCR-000064 | NCR | Missing Test Equipment Calibration Certificate at Woolwich Station 11kV B System |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-03-31 | 2021-02-17 15:03 | -42 | 2020-12-22 09:51 | Electrical - Power Distribution | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Not Defined | Completed |  | During Cxxx CRAF2 surveillance, ITP deliverable record package (SAF): Cxxx - Woolwich Station 11kV B System - Site Assurance File (Cxxx-ALC-O4-LRC-CR147-50002) found out with missing correct calibration certificate for Megger MIT400, UNI-T UT513A, serial no: 060706/1131 (817000200) with calibration due date: 20/09/2018
| 05SY - Systemwide | Cxxx-NCR-000001 | NCR | Failed Incoming Inspection - Router - CISCO |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2014-10-28 | 2014-11-07 13:45 | 10 | 2014-07-24 11:35 | Communications and Control Systems - Crossrail Data Network | 0 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Other | Completed |  | Router ASR-903 failed during incoming inspection. Additional testing identified a faulty power supply, GES17333838.
| 05SY - Systemwide | Cxxx-NCR-000002 | NCR | Failed Incoming Inspection - Router - CISCO |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2014-10-28 | 2014-11-07 13:52 | 10 | 2014-07-24 11:45 | Communications and Control Systems - Crossrail Data Network | 500 |  | Manufacturing Defect | Reject | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Router 2951, serial number FCZ1815717V failed incoming inspection. Fault: Router fialing to load IOS. Rommon mode only. Possible Cause: Corrupt IOS and/or corrupt Rommon. Actions taken: Reimage the device with various methods, however this failed to resolve the problem. Replacement request from NSC Global (CISCO supplier).
| 05SY - Systemwide | Cxxx-NCR-000004 | NCR | Comms cabinet construction in factory without Crossrail accepted ITP |  | Crossrail | PDP | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2015-05-17 | 2015-05-14 10:50 | -3 | 2015-03-04 09:44 | Communications and Control Systems | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Lack of procedure | Completed |  | Construction of comms cabinets for Custom House and Canary Wharf Stations has commenced within the __ factory in Ashby. An Inspection & Test Plan has not been submitted to Crossrail for acceptance for this activity as required by the WI Vol 2B Part 20.8
| 05SY - Systemwide | Cxxx-NCR-000005 | NCR | PAVA Cable (Firetuf FT30) Installation in abscence of CofC paperwork |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2015-03-31 | 2015-04-07 17:08 | 7 | 2015-03-17 15:24 | Communications and Control Systems - Public Address Systems | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Lack or improper material identification and traceability | Completed |  | On 16/03/2015 the installation of Firetuf FT30 cable commenced on Level -6 of Canary Wharf station without the required CofC paperwork as specified in ITP ( Cxxx-SMN-R3-ITP-CR143-50002 - Section 6.2 ) Prior to installation Inspection Number 3.2 requires that __ Site Manager / Sub Contractor verifies Certificate of Conformity (CofC). This paperwork was not available on site.
| 05SY - Systemwide | Cxxx-NCR-000007 | NCR | Change of location - Telephone Units Level -2 (S1 to S5) |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2015-05-11 | 2015-05-12 16:25 | 1 | 2015-04-27 10:47 | Communications and Control Systems - Telephony | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Relocation of Telephone units in line with CMS installed and to avoid existing equipment.
| 05SY - Systemwide | Cxxx-NCR-000009 | NCR | Re-number PAVA Speakers Level -2 (S1 to S5 & S18 to S22) |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2015-05-11 | 2015-05-11 09:55 | 0 | 2015-04-27 10:46 | Communications and Control Systems - Public Address Systems | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | CMS as installed by CWCL is not inline with the __ PAVA design.
| 05SY - Systemwide | Cxxx-NCR-000010 | NCR | Goods Received and Inspection Register not being populated at site as per ITP |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2015-06-11 | 2015-06-04 15:23 | -7 | 2015-05-14 16:24 | Communications and Control Systems | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Goods Received and Inspection Register not being populated at site as per ITP Site Inspection & Test Plan – Cable Containment Installation Cxxx-SMN-R3-ITP-CR143-50001 (Rev 3.0 ) Inspection Number 3.2
| 05SY - Systemwide | Cxxx-NCR-000011 | NCR | Competency Matrix |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2015-09-30 | 2015-08-25 11:06 | -36 | 2015-05-14 16:30 | Communications and Control Systems | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Competency Matrix doesn’t highlight tester(s) who have carried out testing. This applies to Item 9 & 18 from Quality Surveillance Checklist.
| 05SY - Systemwide | Cxxx-NCR-000012 | NCR | PAVA Containment Requirements |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2015-06-11 | 2015-06-02 13:03 | -9 | 2015-05-14 16:34 | Communications and Control Systems - Public Address Systems | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Cxxx-SMN-R3-GPD-CR001-50021 Installation and Procedures Guidelines Rev 01. Page 14 Section 4.2.4 Containment Requirements states that flexible conduit is not to be used for cabinets speakers as they are fixed assets with no adjustment required. Flexible conduit has been installed.
| 05SY - Systemwide | Cxxx-NCR-000013 | NCR | PA/VA Speaker Installation Checklist Cxxx-14-0016 not populated |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2015-06-11 | 2015-06-04 15:24 | -7 | 2015-05-14 16:37 | Communications and Control Systems - Public Address Systems | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | PA/VA Speaker Installation Checklist Cxxx-14-0016 not populated. Item 11, 14 & 16 from Quality Surveillance Checklist cover the same Checklist.
| 05SY - Systemwide | Cxxx-NCR-000014 | NCR | Telephony Cable Installation / Termination Checklist |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2015-06-19 | 2015-06-04 15:25 | -15 | 2015-05-22 14:35 | Communications and Control Systems - Telephony | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Telephony Cable Installation / Termination Checklist Cxxx-14-0008 are blank although the works have been started and near completion.
| 05SY - Systemwide | Cxxx-NCR-000015 | NCR | Drum Number not recorded on As-Installed cable schedule |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2015-06-19 | 2015-07-07 10:22 | 18 | 2015-05-22 14:41 | Communications and Control Systems - Public Address Systems | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | Drum Number not recorded on As-Installed cable schedule. As installed cable schedule not being populated
| 05SY - Systemwide | Cxxx-NCR-000016 | NCR | LVAC Cable Installation / Termination Checklist |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2015-06-23 | 2015-06-23 10:26 | 0 | 2015-05-26 08:23 | Communications and Control Systems - Power Supplies | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | LVAC Cable Installation / Termination Checklist Cxxx-14-0010 not being populated at site.
| 05SY - Systemwide | Cxxx-NCR-000017 | NCR | CCTV As installed cable schedule not being populated against Site Inspection & Test Plan – Cable Installation & Termination Cxxx-SMN-R3-ITP-CR143-50002 (Rev 2.0) |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2015-07-31 | 2015-07-17 10:44 | -14 | 2015-06-18 11:53 | Communications and Control Systems - CCTV | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | CCTV As installed cable schedule not being populated against Site Inspection & Test Plan – Cable Installation & Termination Cxxx-SMN-R3-ITP-CR143-50002 (Rev 2.0)
| 05SY - Systemwide | Cxxx-NCR-000018 | NCR | Breakdown in Audit and Surveillance processes |  | Crossrail | PDP | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2015-08-15 | 2015-08-10 10:37 | -5 | 2015-06-12 13:44 | Communications and Control Systems - General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | The following audits and surveillance activities have not been carried out as per the surveillance and audit schedule Cxxx-MSN-R3-LST-CR001-50021 rev 1.0 Surveillance 13th May : Canary Wharf CCTV cabling, termination & equipment Audit 15th May : Canary Wharf ITP procedure Surveillance 27th May : Canary Wharf Hardware Surveillance 28th May : ASHBY Cabinet builds Surveillance 29th May : Canary Wharf LVAC cabling, termination & equipment Audit 29th May : MPS / MCR procedure Surveillance 2nd June : ASHBY Cabinet testing Surveillance 6th June : Canary Wharf radio
| 05SY - Systemwide | Cxxx-NCR-000019 | NCR | No evidence of Red line drawings being scanned in and kept in the relevant Cxxx Modifications folder in __ Z drive. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2015-09-30 | 2015-08-24 13:23 | -37 | 2015-07-22 11:40 | Systems - Systems Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | During the cabinet build surveillance it was found that there wasn't any evidence of Red line drawings being scanned in and kept in the relevant Cxxx Modifications folder in __ Z drive.
| 05SY - Systemwide | Cxxx-NCR-000020 | NCR | Design changes and evidence available to support the changes throughout the build of the cabinets. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2015-09-30 | 2015-11-03 14:55 | 34 | 2015-07-22 12:23 | Systems - Systems Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | It was unclear how design changes are captured and there wasn’t any evidence available to support the changes throughout the build of the cabinets.
| 05SY - Systemwide | Cxxx-NCR-000021 | NCR | Infotec NCR |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2015-10-01 | 2015-08-25 11:08 | -37 | 2015-08-13 17:57 | Electrical - General | 500 |  | Testing and Commissioning | Reject | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | Whilst carrying out an audit at Infotec it was found that the electrical test outputs aren't being captured on the current Infotec test sheets. Throughout the manufacturing process the product will be visually inspected. All items are then electrically tested prior to shipping, at this point the tester will also carry out a quick visual inspection prior to connecting any live voltages. Within the red job file there is a test specification, within the process there is a blank form to be completed to ensure that all tests are carried out, however this is not being completed, currently on the Job Traveller document is stamped to show it has undertaken the electrical test. The absence of this sheet means that no test outputs are recorded, and any calibrated equipment used to measure is not stated.
| 05SY - Systemwide | Cxxx-NCR-000023 | NCR | Type 6A FOSC in production without an approved ITP at Passcomm Ltd. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2015-10-28 | 2015-10-27 14:16 | -1 | 2015-09-30 10:37 | Communications and Control Systems - Fibre Optic Network | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Type 6A FOSC (Fibre Optic Splicing Cabinet) in production without an approved ITP.
| 05SY - Systemwide | Cxxx-NCR-000027 | NCR | Type 5D cabinet in build without approved design. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2015-11-13 | 2015-11-17 15:01 | 4 | 2015-10-16 12:06 | Communications and Control Systems - CCTV | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Type 5D back plates have been built & tested at Ashby De La Zouch. The Application Design Cxxx-SMN-R3-RSP-CR001-50153 has Placeholder status only on eB.
| 05SY - Systemwide | Cxxx-NCR-000030 | NCR | Verint (CCTV) Damaged Delivery |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2015-11-30 | 2015-11-20 11:13 | -10 | 2015-11-11 16:24 | Communications and Control Systems - General | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper handling of material | Completed |  | Delivery of CCTV equipment was received into Ashby Goods Inwards, with the packaging damaged. Further investigation found that the damage was caused by poor packing and distribution by Verint's courier/Logistics.
| 05SY - Systemwide | Cxxx-NCR-000031 | NCR | MSD - Delivery Damage |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2015-11-25 | 2015-11-20 14:52 | -5 | 2015-11-11 16:35 | Communications and Control Systems - General | 3000 |  | Damaged | Reject | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | Cabinets delivered __ Ashby to __ Lewes were found to be inappropriately handled and delivered resulting in one cabinet being scrapped and the remaining cabinets being used as spares
| 05SY - Systemwide | Cxxx-NCR-000032 | NCR | Infotec ITP |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2015-12-07 | 2015-12-04 13:57 | -3 | 2015-11-19 17:16 | Communications and Control Systems - Customer Information System | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Infotec have built & test CH-FM1 Custom House Full Matrix Display without an approved Crossrail ITP.
| 05SY - Systemwide | Cxxx-NCR-000033 | NCR | Type 5F Junction Box installed with placeholder staus. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2015-12-16 | 2015-12-03 09:11 | -13 | 2015-12-02 16:05 | Communications and Control Systems - General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Type 5F Junction Box has been supplied by Rittal and installed at Canary Wharf without the application design (Cxxx-SMN-RSP-CR001-50167) being submitted to eB for Crossrail to approve.
| 05SY - Systemwide | Cxxx-NCR-000034 | NCR | Type 5G Junction Box installed with placeholder status. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2015-12-16 | 2015-12-03 09:08 | -13 | 2015-12-02 16:15 | Communications and Control Systems - General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Type 5G Junction Box has been supplied by Rittal and installed at Canary Wharf without the application design (Cxxx-SMN-RSP-CR001-50168) being submitted to eB for Crossrail to approve.
| 05SY - Systemwide | Cxxx-NCR-000035 | NCR | Infotec EMC Test Organisation Non UKAS accredited |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-02-28 | 2016-02-22 16:10 | -6 | 2015-12-09 17:17 | Communications and Control Systems - Customer Information System | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Personnel Error - Other human error | Completed |  | __ Organisation has Non UKAS accredited.
| 05SY - Systemwide | Cxxx-NCR-000036 | NCR | Application Solutions Ltd have built and test PA/VA cabinets without an approved Crossrail ITP. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-02-03 | 2016-02-12 16:59 | 9 | 2016-01-06 11:49 | Communications and Control Systems - Public Address Systems | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Improper resource allocation | Completed |  | __ have built and carried out FAT at their premises on Custom House and Canary Wharf PA/VA System cabinets without an approved Crossrail ITP. __ follow their own procedures and have an equivalent System Acceptance Test Plan / Record that covers ITP although it's not on the Crossrail format.
| 05SY - Systemwide | Cxxx-NCR-000038 | NCR | Incorrect cable schedule for TCR |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-03-15 | 2016-03-15 09:15 | 0 | 2016-01-19 11:33 | Communications and Control Systems - General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | T1 Review of Cable schedule issues has identified a number of inconsistencies
| 05SY - Systemwide | Cxxx-NCR-000039 | NCR | Cxxx drawings not following Crossrail standards. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-02-29 | 2016-02-25 12:42 | -4 | 2016-01-20 18:51 | Communications and Control Systems | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Drawings are being amended and resubmitted without identifying changes or following Crossrail CAD standard CR-STD-005 Version 5.0.
| 05SY - Systemwide | Cxxx-NCR-000040 | NCR | Delevery of Type 6A FOSC Cabinets - Mile End Shaft |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-02-19 | 2016-02-19 14:57 | 0 | 2016-02-01 19:15 | Communications and Control Systems | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | 2No Cabinet Type 6A (FOSC's) delivered to Mile End shaft without the correct documentation as defined within the ITP Cxxx-SMN-R3-ITP-CR001-50002 Rev 2.0
| 05SY - Systemwide | Cxxx-NCR-000041 | NCR | MCR Not accepted for Conduit - Mile End Shaft |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-02-19 | 2016-02-19 14:17 | 0 | 2016-02-01 19:41 | Communications and Control Systems | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | MCR Submitted and awaiting acceptance for Galvanised steel conduit at Mile End Shaft, works commenced. (MCR Ref: CRL-MCR-002725)
| 05SY - Systemwide | Cxxx-NCR-000042 | NCR | Mile End SCADA Cable |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-03-18 | 2016-03-18 11:44 | 0 | 2016-02-12 12:53 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate resources | Completed |  | MCR Submitted and awaiting acceptance for 2 Core SCADA cable at Mile End Shaft, works commenced. (MCR Ref: CRL-MCR-002648)
| 05SY - Systemwide | Cxxx-NCR-000043 | NCR | MCR not accepted for Cable Tray - Mile End Shaft |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-03-18 | 2016-03-18 12:38 | 0 | 2016-02-12 13:03 | Communications and Control Systems - Radio | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate resources | Completed |  | MCR Submitted and awaiting acceptance for __ Swift Heavy Duty cable Tray at Mile End Shaft, works commenced. (MCR Ref: CRL-MCR-002718)
| 05SY - Systemwide | Cxxx-NCR-000044 | NCR | MCR Not accepted for __ - Mile End Shaft |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-03-18 | 2016-03-18 12:39 | 0 | 2016-02-12 13:16 | Communications and Control Systems | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate resources | Completed |  | MCR Submitted and awaiting acceptance for UniStrut Channel at Mile End Shaft, works commenced. (MCR Ref: CRL-MCR-002818)
| 05SY - Systemwide | Cxxx-NCR-000045 | NCR | MCR Not accepted for __ RJ45 Outlets - Mile End Shaft |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-03-25 | 2016-03-22 09:50 | -3 | 2016-02-12 13:25 | Communications and Control Systems - Telephony | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate resources | Completed |  | MCR Submitted and awaiting acceptance for __ RJ45 outlets at Mile End Shaft, works commenced. (MCR Ref: CRL-MCR-002828)
| 05SY - Systemwide | Cxxx-NCR-000046 | NCR | MCR Not accepted for __ HY270 - Mile End Shaft |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-03-18 | 2016-03-18 12:40 | 0 | 2016-02-12 13:30 | Communications and Control Systems | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate resources | Completed |  | MCR Submitted and awaiting acceptance for __ HY270 Fixings at Mile End Shaft, works commenced. (MCR Ref: CRL-MCR-002826)
| 05SY - Systemwide | Cxxx-NCR-000047 | NCR | MCR Not Submitted/accepted for TYPE 5F & 5G Junction Boxes - Mile End Shaft |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-03-22 | 2016-03-22 09:52 | 0 | 2016-02-12 13:37 | Communications and Control Systems | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate resources | Completed |  | MCR not Submitted for Type 5F or 5G junction boxes at Mile End Shaft, works commenced. (Rittal Junction boxes for Door contacts and CCTV CDN connections)
| 05SY - Systemwide | Cxxx-NCR-000048 | NCR | Cabinet build not following ITP |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-04-01 | 2016-04-25 09:28 | 24 | 2016-02-22 22:30 | Communications and Control Systems | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Desktop review of evidence gathered after carrying out surveillance visit on __ cabinet at Ashby De La Zouch found that there hadn't been any BS7671 electrical certificate or PTS001 Inspection sheet issued.
| 05SY - Systemwide | Cxxx-NCR-000049 | NCR | MCR Not accepted for __ HY200 - Mile End Shaft |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-03-25 | 2016-03-18 11:38 | -7 | 2016-02-26 16:22 | Communications and Control Systems - General | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate resources | Completed |  | MCR Submitted and awaiting acceptance for __ HY200 Fixings at Mile End Shaft, works commenced. (MCR Ref: CRL-MCR-002823)
| 05SY - Systemwide | Cxxx-NCR-000050 | NCR | MCR Not Submitted/accepted for __ __ Fixings Mile End Shaft |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-03-25 | 2016-03-18 11:39 | -7 | 2016-02-26 16:27 | Communications and Control Systems | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate resources | Completed |  | MCR Submitted and awaiting acceptance for __ __ Fixings at Mile End Shaft, works commenced. (MCR Ref: CRL-MCR-002827)
| 05SY - Systemwide | Cxxx-NCR-000051 | NCR | MCR Not accepted for Type 5C Cabinet - Mile End Shaft |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-03-25 | 2016-03-18 11:41 | -7 | 2016-02-26 16:43 | Communications and Control Systems | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate resources | Completed |  | MCR Submitted and awaiting acceptance for 5C Cabinet at Mile End Shaft, works commenced. (MCR Ref: CRL-MCR-002875)
| 05SY - Systemwide | Cxxx-NCR-000052 | NCR | MCR Not accepted for Type 6A Cabinet - Mile End Shaft |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-03-25 | 2016-03-18 11:42 | -7 | 2016-02-26 16:51 | Communications and Control Systems | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate resources | Completed |  | MCR Submitted and awaiting acceptance for 6A Cabinet at Mile End Shaft, works commenced. (MCR Ref: CRL-MCR-002793)
| 05SY - Systemwide | Cxxx-NCR-000053 | NCR | Key elements missing from CCTV System Cable Wiring Schedule |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-04-22 | 2016-05-11 15:15 | 19 | 2016-03-14 14:37 | Communications and Control Systems - CCTV | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Surveillance visit picked up that CCTV System Cable Wiring Schedule - 1.0 Cxxx-SMN-R3-LST-CRG03-50051 S08.012 Mile End & Eleanor St Shaft has key elements missing from the schedule. Design lengths, asset ID’s & destination are missing from the cable schedules.
| 05SY - Systemwide | Cxxx-NCR-000054 | NCR | Earth not installed in cabinet |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-08-31 | 2016-07-29 16:33 | -33 | 2016-03-10 17:33 | Communications and Control Systems - General | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Type 2B MEP.00.5B.U5 Cabinet Inspection of cabinet delivered to MEP Inspection of drawings against cabinet build found that X1/PE/XEO 1.5mm2 GNYE cable hadn’t been installed between __ Unit 1 and Earth Bar.
| 05SY - Systemwide | Cxxx-NCR-000055 | NCR | PTS01 Stage 2 Inspection hasn’t been carried out by the second engineer. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-08-31 | 2016-08-30 14:26 | -1 | 2016-03-10 17:55 | Communications and Control Systems - General | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Type 2B MEP.00.5B.U5 Cabinet Inspection Review of PTS01 on server found that the Stage 2 Inspection hadn’t been carried out by the second engineer.
| 05SY - Systemwide | Cxxx-NCR-000056 | NCR | Loose earth cable in cabinet 2A MEP.00.5B.U1 at MEP |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-08-15 | 2016-07-28 14:57 | -18 | 2016-03-11 08:56 | Communications and Control Systems - General | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Type 2A MEP.00.5B.U1 Cabinet Inspection - X1/PE/XEO 1.5mm2 GNYE cable wasn’t terminated into the earth bar at __ Unit 1.
| 05SY - Systemwide | Cxxx-NCR-000057 | NCR | Cabinets delivered to MEP without current revision of drawing. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-04-27 | 2016-04-25 09:20 | -2 | 2016-03-30 10:26 | Communications and Control Systems - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | 1 No cabinet sampled has been delivered to MEP site with 0.1 Rev drawing. Type 2B MEP.00.5B.U5.
| 05SY - Systemwide | Cxxx-NCR-000058 | NCR | Installation of Omni antennas at Mile End Park Shaft |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-08-31 | 2016-08-23 17:05 | -8 | 2016-03-18 12:22 | Communications and Control Systems - General | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate resources | Completed |  | Installation of Omni antennas at Mile End Park Shaft without accepted MCR.
| 05SY - Systemwide | Cxxx-NCR-000059 | NCR | Installation of Panel antennas at Mile End Park Shaft |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-08-31 | 2016-08-23 17:04 | -8 | 2016-03-18 12:31 | Communications and Control Systems - General | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Management Problem - Improper resource allocation | Completed |  | Installation of Panel antennas at Mile End Park Shaft without accepted MCR
| 05SY - Systemwide | Cxxx-NCR-000060 | NCR | Earth cables for cabinets at MEP. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-04-22 | 2016-07-04 11:21 | 73 | 2016-03-18 12:35 | Communications and Control Systems - General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Earth cables for cabinets at MEP haven't been included on any cable schedules.
| 05SY - Systemwide | Cxxx-NCR-000061 | NCR | Installation of Stainless Steel cable ties at Mile End Park Shaft |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-04-22 | 2016-04-28 09:46 | 6 | 2016-03-18 12:40 | Communications and Control Systems - General | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate resources | Completed |  | Installation of Stainless Steel cable ties at Mile End Park Shaft without accepted MCR
| 05SY - Systemwide | Cxxx-NCR-000062 | NCR | Installation of earth cable at Mile End Park Shaft. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-04-22 | 2016-04-29 11:55 | 7 | 2016-03-18 12:44 | Communications and Control Systems - General | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate resources | Completed |  | Installation of earth cable at Mile End Park Shaft without accepted MCR.
| 05SY - Systemwide | Cxxx-NCR-000064 | NCR | FT30 PAVA cable installed without approved MCR |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-08-31 | 2016-08-23 17:03 | -8 | 2016-03-30 09:56 | Communications and Control Systems - General | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | FT30 (CRL-MCR-003022) cable for PA/VA installed at Canary Wharf without approved MCR
| 05SY - Systemwide | Cxxx-NCR-000065 | NCR | PAVA Installation carried out with drawings at P0 status |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-05-05 | 2016-04-27 10:27 | -8 | 2016-04-07 11:22 | Communications and Control Systems - Public Address Systems | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Cxxx-SMN-R3-DDA-CR143_5-4004 drawing is currently at P0 status in eB. Works have been carried out at Canary Wharf Station against the drawing that should be at C0 status for installation.
| 05SY - Systemwide | Cxxx-NCR-000066 | NCR | Cable delivery to storage facility - surveillance visit. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-05-24 | 2016-06-03 14:29 | 10 | 2016-04-26 16:14 | Communications and Control Systems - General | 3000 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper storage of material | Completed |  | Surveillance visit found that cable delivered to Tier 1 sub contractor (Tew Plus) at Harlow storage facility found cable drums had been delivered on their side and not kept upright for delivery or storage. This was previously picked up as an observation (QS13-01) on Quality Surveillance visit to Lutterworth on 12th January 2016. (Quality Survillance Report QS13 - Lutterworth Storage Facility Cxxx-SMN-R3-RGN-CR001-50318)
| 05SY - Systemwide | Cxxx-NCR-000067 | NCR | Incorrect internal termination on Penton speakers delivered to Canary Wharf. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-10-10 | 2016-10-10 07:48 | 0 | 2016-04-26 17:01 | Communications and Control Systems - Public Address Systems | 2000 |  | Material | Rework | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | During PA/VA speaker installation at Canary Wharf, one of Coral Communications electricians found that there was an internal wiring crossover of the SENTRY6ST/ENC cabinet speakers. We have been assured by Penton that this has been contained to 140 No speakers delivered to Canary Wharf.
| 05SY - Systemwide | Cxxx-NCR-000068 | NCR | Canary Wharf - SENTRY 6, MHS20TC & CELL10__ PAVA Speaker MCR |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-08-06 | 2016-08-02 14:51 | -4 | 2016-05-04 18:25 | Communications and Control Systems - Public Address Systems | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate resources | Completed |  | MCR Submitted and awaiting acceptance for SENTRY 6, MHS20TC & CELL10__ PAVA speakers at Canary Wharf Station, works commenced. (MCR Ref: CRL-MCR-003114)
| 05SY - Systemwide | Cxxx-NCR-000069 | NCR | Canary Wharf - MCS20 PAVA Speaker MCR |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-08-09 | 2016-08-02 14:50 | -7 | 2016-05-04 18:30 | Communications and Control Systems - Public Address Systems | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Management Problem - Improper resource allocation | Completed |  | MCR Submitted and awaiting acceptance for MCS20 PAVA Speakers at Canary Wharf Station, works commenced. (MCR Ref: CRL-MCR-003117)
| 05SY - Systemwide | Cxxx-NCR-000070 | NCR | Damaged FT30 cable drum. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-06-10 | 2016-06-07 16:28 | -3 | 2016-05-09 16:24 | Communications and Control Systems - General | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper handling of material | Completed |  | 100mts Firetuff FT30 4C&E 1.5mm cable drum has been damaged in transit, it was placed in the quarantine area at site although the quarantine register wasn't up to date to include the cable drum. QC/Drum No 14-6314-10. Prod O/No 1373250.
| 05SY - Systemwide | Cxxx-NCR-000071 | NCR | Canary Wharf - PAVA Junction Box internal Labels |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-08-31 | 2016-08-30 14:30 | -1 | 2016-05-09 15:16 | Communications and Control Systems - Public Address Systems | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Management Problem - Improper resource allocation | Completed |  | Internal PAVA Circuit IN/OUT labels missing. Approx 60No recently installed are without labels.
| 05SY - Systemwide | Cxxx-NCR-000072 | NCR | __ flexible conduit - Canary Wharf. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-08-31 | 2016-08-30 14:32 | -1 | 2016-05-09 17:08 | Communications and Control Systems - General | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Lack or improper material identification and traceability | Completed |  | __ LFHU20B-50M flexible conduit has been delivered and installed at Canary Wharf site without an accepted MCR. Low smoke pvc flexible conduit isn't allowed to be installed at site. Small amounts of low smoke __ LFHU20B-50M flexible conduit has been installed around site and the proposal is to remove the pvc coating to make the flexible conduit compliant against CRL-MCR-002869 Type FU flexible conduit. Email has been sent to __ to confirm if low smoke pvc is removed if it will then be compliant with CRL-MCR-002869 Type FU flexible conduit that has been accepted by CEG.
| 05SY - Systemwide | Cxxx-NCR-000074 | NCR | VDP Radio Cable |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-06-10 | 2016-06-07 16:13 | -3 | 2016-05-10 09:56 | Communications and Control Systems - General | 1000 |  | Material | Reject | 4 (0.5-3k) | Complete | Discipline/Workmanship - Error by manufacturer in shipping or marking | Completed |  | 100 meters Cellflex 7/8" in low loss flexible cable (part number LCF78-50JFNA-A0) delivered to site boxed up, not on cable drum
| 05SY - Systemwide | Cxxx-NCR-000076 | NCR | FAC not issued with cabinets delivered to VDP. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-06-10 | 2016-06-10 10:17 | 0 | 2016-05-12 16:15 | Communications and Control Systems - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Cabinets delivered to VDP on 11th May 2015 without Factory Acceptance Certificate. 4 No Type 4A, 2 No 6A Fibre Optic Splicing Cabinet & 1 No Type 2B cabinet. Drawings also at issued with cabinets at Rev 0.1
| 05SY - Systemwide | Cxxx-NCR-000077 | NCR | Stage 2 checks not carried out on BTS2 Build Test Sheet |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-07-19 | 2016-07-18 09:56 | -1 | 2016-05-12 16:39 | Communications and Control Systems - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | VDP.2.FOSC.U1 delivered to VDP on 11th May 2015 with BTS2 Build Test Sheet not signed by second engineer. 1 No screw missing from panel door and this also wasn't highlighted on BTS2 Build Test Sheet.
| 05SY - Systemwide | Cxxx-NCR-000078 | NCR | Type 4A cabinet deliverd to VDP with screws missing from front cover plate. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-07-19 | 2016-07-18 09:59 | -1 | 2016-05-12 16:49 | Communications and Control Systems - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Type 4A VDP.01.661.U1 delivered to site at VDP on 11th May with 8 out of 10 screws missing from the front cover plate. BTS2 Build Test Sheet was included and signed by second engineer although there was no record of screws missing.
| 05SY - Systemwide | Cxxx-NCR-000079 | NCR | Electrical certificates not issued with 2 No Type 4A cabinets delivered to VDP. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-06-09 | 2016-06-08 08:52 | -1 | 2016-05-12 17:04 | Communications and Control Systems - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | 2 No Type 4A cabinets delivered to VDP on 11th May 2015 without Electrical Certificate. VDP.01.661.U1 & VDP.01.662.U1
| 05SY - Systemwide | Cxxx-NCR-000081 | NCR | Radio Design Change to Tunnel Infrastructure at VDP |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-06-17 | 2016-06-15 15:24 | -2 | 2016-05-18 10:05 | Communications and Control Systems - Radio | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | Attached Schematic layout Cxxx-SMN-R3-DWG-CR144_PT003-50004 Rev 1.0 for radio design at VDP shows changes to tunnel infrastructure cabling, schematic shows 4- 7/8" radio cables routing from CER to both E/B & W/B tunnel infrastructures being reduced to 2- 7/8" cables to both tunnels. Plus radio cable schedule & Drawings will need to be updated.
| 05SY - Systemwide | Cxxx-NCR-000082 | NCR | Cxxx cable delivery to Cxxx storage area |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-08-25 | 2016-06-15 09:00 | -71 | 2016-05-27 09:37 | Communications and Control Systems - General | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper handling of material | Completed |  | 1. All Fibre Optic cable drums: ends not sealed or covered; 2. All Fibre Optic cables: no C of C number on delivery schedule, cannot be verified; 3. 1 no. cable drum: impact damage to packaging; 4. 1 no. cable drum: loose packaging, cable outside edge of drum; 5. 3 x Radiaflex cable drums: damaged battens; 6. Radiaflex cables: 5 drums on each delivery not 6 as per delivery schedule. 7. No individual identification labels on pallets (several pallets share the same number) 8. One pallet has not identification number or list of contents and does not reconcile with part numbers on Advanced Delivery Note 9. Pallets have no content / quantity information on labels 10. Pallet labels/numbers do not match Advanced Delivery Note
| 05SY - Systemwide | Cxxx-NCR-000083 | NCR | Errors on __ schematics leading to inconsistency with other __ application designs. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-07-21 | 2016-07-21 15:53 | 0 | 2016-06-23 13:44 | Communications and Control Systems - Fibre Optic Network | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | Errors on __ schematics leading to inconsistency with other __ application designs. See attached examples.
| 05SY - Systemwide | Cxxx-NCR-000084 | NCR | Port allocation schedules / hardware application designs |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-09-02 | 2016-09-02 11:06 | 0 | 2016-06-23 14:02 | Communications and Control Systems - General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Port allocation schedules / hardware application designs lagging behind cable schedules leading to inconsistent information issued to tier. Other inconsistencies also identified as per spreadsheet.
| 05SY - Systemwide | Cxxx-NCR-000085 | NCR | Victoria Dock Portal (VDP) - Incomplete cabinets delivered to site |  | Crossrail | PDP | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-11-30 | 2016-11-25 11:47 | -5 | 2016-07-20 10:40 | Communications and Control Systems - Radio | 5000 |  | Supervision/Management | Rework | 3 (3-6k) | Complete | Management Problem - Other management problem | Completed |  | Cabinets CR503-CAB-00006 and 00007 have been delivered to VDP CER week commencing 4th July completely unpopulated with intention of retrofitting on site. This has not been agreed with Crossrail and is not in line with the Factory Acceptance Test process. The benefits of installing an empty shell on site is not clear as this will cost more to fit on-site and introduce downstream risk as the FAT process has now been bypassed.
| 05SY - Systemwide | Cxxx-NCR-000087 | NCR | Type 3A DC4 cabinet CAW.2.5.12.U1 not compliant with Material Compliance Record. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-06-30 | 2017-05-16 14:18 | -45 | 2016-07-29 11:56 | Communications and Control Systems - Crossrail Data Network | 2000 |  | Design | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | Type 3A DC4 cabinet CAW.2.5.12.U1 has been installed and not compliant with CRL-MCR-002333 that states the room should be <200 cubic metres. CRL-MCR-002333 has been accepted by CEG with conditions: Rittal Type 3A cabinet is not compliant to 1-085 criteria due to rubber seal and plastic vents used on doors and resin glands used on top of cabinet. The equipment is to be installed and used in a fire compartmented, non-public room with fire detection and <200 cubic metres.
| 05SY - Systemwide | Cxxx-NCR-000089 | NCR | Radio connectors dust ingress |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-09-23 | 2016-09-21 08:01 | -2 | 2016-08-26 10:57 | Communications and Control Systems - Radio | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | During site surveillance visit to Canary Wharf on Radio installation there were Radio connectors installed on the ends of the superflex cable without any protection against dust ingress.
| 05SY - Systemwide | Cxxx-NCR-000090 | NCR | Cable ties overtightened on radio cable installation. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-09-23 | 2016-09-22 10:31 | -1 | 2016-08-26 11:14 | Communications and Control Systems - Radio | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | During site surveillance visit to Canary Wharf on Radio installation there were Radio superflex cables installed on cable tray with metal cable ties. The metal cable ties had been over tightened with the cable tie being embedded into the cable insulation. Sharp edges also found on some of the cable ties.
| 05SY - Systemwide | Cxxx-NCR-000091 | NCR | Non Conformance- Drum Delivery |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-10-17 | 2016-09-28 07:23 | -19 | 2016-09-19 13:16 | Communications and Control Systems - Fibre Optic Network | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Delivery of 10 Fibre Optic Cable drums from __ to PLU. On inspection of the drums, one was rejected and two required quarantine for potential problems
| 05SY - Systemwide | Cxxx-NCR-000092 | NCR | Canary Wharf PAVA Cable asset Labels |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-01-27 | 2017-03-28 09:32 | 60 | 2016-09-22 19:21 | Communications and Control Systems - Public Address Systems | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | PAVA Cable asset labels installed with incorrect CRL asset numbers as detailed on Cable schedule Cxxx-SMN-R3-LST-CR143-50006 Rev 4.0
| 05SY - Systemwide | Cxxx-NCR-000093 | NCR | Asset cable labels not aligned with ADCS. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-01-31 | 2017-01-31 17:54 | 0 | 2016-10-26 17:19 | Communications and Control Systems | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Surveillance on the __ & RADIO trackside asset labels (__ & RADIO) cables found that the Asset Data Collection Sheet in eB - ADCS Cxxx-XRL-Z3-XDS-CR001-50012 Rev 5 & ADCS Cxxx-XRL-Z3-XDS-CR001-50014 Rev 4 doesn't align with the printed labels or cable schedules - Trackside Cable Schedule – __ Cxxx-SMN-R3-LST-CR001-50042 Rev 5 & PMR-RI System Cable and Wiring Schedule - Tunnels, CP's and Surface Cxxx-SMN-R3-LST-CRG03-50072 Rev 4.
| 05SY - Systemwide | Cxxx-NCR-000094 | NCR | GSM-R Capacity |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-03-31 | 2017-03-31 12:21 | 0 | 2016-12-19 16:41 | Communications and Control Systems - Radio | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Crossrail has concerns over the GSM-R capacity assessment completed by __, as it appears to be overly optimistic. --------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------- Currently __ are not complying with Works Information Section 2C Part 11 (Cxxx-PBF-R3-RSP-CRG03-00011) requirement “GSR063 – The Contractor shall asses the channel capacity requirements of the GSM-R Radio System BTSs”, this requirement is fundamentally affiliated to the following requirements, considered also non-compliant: GSR018, GSR034, GSR071, GSR044, GSR046, GSR047 and GSR048. __ are non-compliant, as they have failed to deliver supporting evidence, proving that they are delivering the following requirement in the Generic Technical Requirements Specification (Cxxx-PBF-R3-RSP-CRG03-00034) “GEN001 – C&C Systems shall meet their operational and performance requirements under conditions of full load and in normal, degraded and emergency scenarios.” This requirement is again stipulated in the Works Information Volume 2B – Part 32 – Contractor’s Engineering Safety Management Requirements (CRL1-XRL-V3-XWI-CR001-50131). Crossrail requires __ to deliver a suitable resolution that demonstrates compliance with the above and a true reflection of capacity usage. Crossrail are available to support __ here. --------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------- 02/02/2017 Following the collaborative work between Crossrail and __ Cxxx, and the Central Section GSM-R Capacity Assessment (the Report) the output of that work, Crossrail desire to review the closure of Cxxx-NCR-000094 ensuring the outputs of the Capacity Assessment are incorporated and absorbed. The Report’s objectives were to assess the required capacity of GSM-R on Central Section and that it provided sufficient capacity to meet such requirements, the findings and conclusions of the report were follows: 1. Current GSM-R design capacity is sufficient but exceptions have been identified. 2. A requirement for ETCS has been acknowledged and noted that this was not a Cxxx Works Information requirement. 3. Near full capacity utilisation in the Paddington/TCR cell was noted, any mitigations work that is required shall not jeopardise the initial opening of Crossrail. 4. Current GSM-R design capacity does not provide additional capacity to support ETCS implementation on Central Section, Crossrail’s intention is to instruct a ETCS requirement at Paddington however no immediate cell enhancement or adjustment is required at this stage. To enable prompt closure of Cxxx-NCR-000094 the following requirements are required: 1. The GSM-R Detailed Design Specification to be updated that takes account of the Report’s findings. 2. The preparation of a preliminary assessment considering the options to upgrade the capacity in the Central Section either as, a selective cell approach or across the Central Section – if a selective upgrade approach would not feasible. This assessment should include estimate of costs and resources and an implementation plan highlighting the degree of disruption to the GSM-R system – that may have been commissioned. These works will be communicated and instructed by Crossrail. ------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------
| 05SY - Systemwide | Cxxx-NCR-000095 | NCR | Type 5E dinrail design |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-01-19 | 2017-01-19 10:13 | 0 | 2016-11-22 17:31 | Communications and Control Systems | 3000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Type 5E din rail is flexing due to the weight of the Traco Power Supplies installed on the length of din rail.
| 05SY - Systemwide | Cxxx-NCR-000096 | NCR | Cable damage on Cable drum Cxxx/RFS/RLKU/84 - CR142-RAD-00165 |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-01-30 | 2016-12-20 14:03 | -41 | 2016-11-29 09:53 | Communications and Control Systems - Radio | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper handling of material | Completed |  | During installation of Cable CR142-RAD-00165 from Cable drum Cxxx/RFS/RLKU/84 damage was seen to the cable on the cable drum. The damage was a cut to the outer sheath
| 05SY - Systemwide | Cxxx-NCR-000098 | NCR | CCTV Brackets |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-01-19 | 2017-01-19 11:22 | 0 | 2016-12-21 16:44 | Communications and Control Systems - CCTV | 5000 |  | Manufacturing Defect | Reject | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | __ Cxxx received delivery of bracket assemblies from the manufacturer WRES at Canary Wharf station on Friday 16th Dec 2016. Upon inspection and when assembling the 3No separate components that complete a bracket it was identified that several threaded sections would not fully engage due to issues with the thread. A total of 151 brackets where delivered with a sample of 10 selected at random to carry out further investigation/testing. It was found that an average of 35% where defective with no common cause identified. All materials where placed in quarantine whilst communications with the manufacture progressed as to identify an acceptable solution. Arrangements have been made for the manufacturer to collect all of the bracket assemblies on Friday 23rd Dec 2016 to carry out further investigation and corrective action. Attached is a copy of the test carried out with photos for reference.
| 05SY - Systemwide | Cxxx-NCR-000099 | NCR | PAVA Cable CMS Allocation |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-02-17 | 2017-02-16 17:01 | -1 | 2016-12-22 16:21 | Communications and Control Systems - Public Address Systems | 500 |  | Equipment Breakdown | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | It has been identified that incorrect information is detailed with the PAVA installation procedures and guidelines documentation Cxxx-SMN-R3-GPD-CR001-50021 Rev 2.0 section 3.1 Cable types (table 2) in relation to cable function and CMS compartment. The following 3No cables are required to be installed within the general communications compartment and not the PAVA as detailed in the aforementioned table. 1. PAVA Rack to Fire Panel and Emergency Fire Microphone (Shall be in the General Comms CMS Compartment) 2. SAP/RRM to Antenna (Shall be in the General Comms CMS Compartment) 3. PAVA Fibre Ring (Shall be in the General Comms CMS compartment) Attached is a copy of Table 2 from the guidelines for reference.
| 05SY - Systemwide | Cxxx-NCR-000100 | NCR | Damaged Radio Cable Level -3 |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-02-28 | 2017-01-30 17:30 | -29 | 2017-01-04 15:36 | Communications and Control Systems - Radio | 2000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | On Friday 16th December __(Cxxx Operative) brought to our attention a damaged 7/8” Radio Cable on level -3 East. A temporary scaffold has been installed to allow access to the cables that link between level -2 and -3. This is where the damaged cable lies. It appears that the cable has been damaged by others in the period from Cxxx installing the cable 19th August 2016 and after the scaffolding was installed 16th December 2016. Cxxx have 2No options to repair or replace as detailed below; 1. Replace the damaged cable - FD011 from CER to level -2 at 65mtrs 2. Install a 1/2" coupler cable at an accessible level in the riser to repair the damaged section (approx 500mm) Crossrail to advise on corrective works required.
| 05SY - Systemwide | Cxxx-NCR-000101 | NCR | Plumstead Portal cable delivery not captured by ITP. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-02-08 | 2017-02-08 08:20 | 0 | 2017-01-25 13:23 | Communications and Control Systems - Power Supplies | 100 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Lack or improper material identification and traceability | Completed |  | During the surveillance site visit it was noted that 1 No 100 mts 6mm & 1 No 100mts 10mm single earth cable drums were stored in the CER alongside fibre cable. Both drums hadn't been captured on the delivery note, goods received register or the cable drum register. There was also no evidence of Certificates of Conformity for the cable or the cable drum inspection checklist being completed. All the above are hold points within Site Inspection and Test Plan - Cabling and Termination Cxxx-SMN-R3-ITP-CR001-50003 Rev 2.0
| 05SY - Systemwide | Cxxx-NCR-000102 | NCR | Fibre Cables incorrectly dressed on the tray |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-02-28 | 2017-02-03 11:12 | -25 | 2017-01-25 14:11 | Communications and Control Systems - Crossrail Data Network | 250 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | Fibre cables dressed incorrectly on the tray, Radio cable will cross over in both FOSC'S
| 05SY - Systemwide | Cxxx-NCR-000103 | NCR | Minor Scratch to Cab |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-02-28 | 2017-02-03 11:17 | -25 | 2017-01-25 14:25 | Communications and Control Systems - Crossrail Data Network | 100 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Insufficient work planning by the subcontractors | Completed |  | Minor scratch to cab NWP-11-CAB-1731U1. This has happened whilst __ wasn't on site
| 05SY - Systemwide | Cxxx-NCR-000104 | NCR | Incorrect Type 5E Cabinets at TCR |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-03-31 | 2017-04-10 12:11 | 10 | 2017-01-31 16:32 | Communications and Control Systems - General | 2000 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Lack or improper material identification and traceability | Completed |  | There are two instances of the incorrect design of Type 5E cabinet that have been delivered (and subsequently installed) at TCR. Details of the two cabinets are within the enclosed documents. The cabinets are designated as DC11 and DC12.
| 05SY - Systemwide | Cxxx-NCR-000105 | NCR | WRES CCTV bracket doesn't have approved MCR for installation. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-06-30 | 2017-05-16 14:16 | -45 | 2017-02-06 18:53 | Communications and Control Systems - CCTV | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | WRES CCTV brackets have been delivered to Canary Wharf site and they do not have an approved MCR for installation. Surveillance visit desktop exercise found that the MCR hasn't been submitted for approval.
| 05SY - Systemwide | Cxxx-NCR-000106 | NCR | MCR's for Barco CID Media Wall |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-05-26 | 2017-05-25 11:42 | -1 | 2017-02-13 18:15 | Communications and Control Systems - General | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | Equipment has been installed without accepted MCR's in place. CRL-MCR-004125, CRL-MCR-004128, CRL-MCR-004129, CRL-MCR-004130, CRL-MCR-004131, CRL-MCR-004135, CRL-MCR-004137, CRL-MCR-004139. Also to check that all other associated materials are covered under the submitted MCRs.
| 05SY - Systemwide | Cxxx-NCR-000108 | NCR | Works commenced without approved design |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-06-23 | 2017-05-18 16:28 | -36 | 2017-02-13 18:37 | Communications and Control Systems - General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | The installation of the rotary isolators and frame has commenced with drawings at PO status and not CO.
| 05SY - Systemwide | Cxxx-NCR-000109 | NCR | Installation of Barco CID Media Wall without approved design / drawings |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-05-14 | 2017-04-28 13:58 | -16 | 2017-02-13 18:43 | Communications and Control Systems - General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | No approved drawings / design in place for the installation of Barco media wall. No location design, all positions agreed locally on site.
| 05SY - Systemwide | Cxxx-NCR-000110 | NCR | CER cabinets LIP-01-CAB-00001 & LIP-01-CAB-00008 have been drilled on roof plate. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-03-31 | 2017-03-31 14:01 | 0 | 2017-02-13 20:28 | Communications and Control Systems - Power Supplies | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During the surveillance visit to Limmo for the first IRN it was noted that there was swarf in the bottom of the cabinet LIP-01-CAB-B19EU4. Further inspection found that the cabinet roof section had been drilled to allow 6mm brass nut & bolt to be installed for the earth tag on the gland for the power supply to the cabinet. It wasn't conclusive where the swarf had come from within the cabinet, if it was a site or cabinet build activity. Roof section of the cabinets haven't to be drilled.
| 05SY - Systemwide | Cxxx-NCR-000112 | NCR | Top of cabinets in CER not sealed. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-03-20 | 2017-03-20 17:01 | 0 | 2017-02-13 21:48 | Communications and Control Systems - General | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Insufficient quantity of material to do the job | Completed |  | Cabinets LIP-01-CAB-00001 & LIP-01-CAB-00008 installed in CER haven't had the cable transit blocks sealed at the top of the cabinet to stop dust ingress. Temporary method of sealing is acceptable until all cables have been installed and transit blocks have been permanently installed.
| 05SY - Systemwide | Cxxx-NCR-000113 | NCR | Swarf & loose bolt found in cabinet __-01-CAB-B16CU1 at Stepney Green. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-03-31 | 2017-03-31 10:12 | 0 | 2017-02-13 22:30 | Communications and Control Systems - General | 500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | __-01-CAB-B16CU1 cabinet delivered to Stepney Green and was found to have swarf and a loose bolt in the base of the cabinet. It has been established that this has been from the cabinet build at Ashby De La Zouch.
| 05SY - Systemwide | Cxxx-NCR-000114 | NCR | Custom House - Power distribution in Type 1A cabinet doesn't align with ePlan drawing. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-04-25 | 2017-04-18 16:22 | -7 | 2017-02-28 12:20 | Communications and Control Systems - Power Supplies | 500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On my recent surveillance visit to Custom House this week I have picked up on an issue between the eplan drawing Cxxx-SMN-R3-DWG-CR145-50041 Rev 1.0 for cabinet CUH-00-CAB-731U9. The eplan drawing shows F1B/L/CF1-2 being connected to –F1B when in is actually terminated into Circuit Q1B.
| 05SY - Systemwide | Cxxx-NCR-000115 | NCR | Asset & equipment labels not available at installation stage or IRN. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-04-30 | 2017-04-28 12:26 | -2 | 2017-03-07 17:53 | Communications and Control Systems - General | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Management Problem - Other management problem | Completed |  | There hasn't been any asset & equipment labels available at the time of installation / IRN handover to T&C at the following sites - Eleanor Street, Canary Wharf, Pudding Mill Lane, North Woolwich Portal, Limmo Peninsular, Victoria Dock Portal, Stepney Green & RCC. To date the only labels shipped to site are the following: Stepney Green to Pudding Mill BSP - Cable Asset Labels - __, Stepney Green to Pudding Mill BSP - Cable Asset Labels - RAD MIMO, CAW - Equipment Asset Labels - PAVA & VDP - Cable Asset Label - __. 4 No Label types missing: Cable asset labels wrap around (White) Cable asset labels (White - cable tie on type) Equipment labels (Yellow) Equipment Asset tags (White)
| 05SY - Systemwide | Cxxx-NCR-000116 | NCR | LVAC power supplies & earth cables not captured on cable schedules. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-06-16 | 2017-06-16 16:19 | 0 | 2017-03-17 10:48 | Communications and Control Systems - Power Supplies | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | LVAC power supplies from isolators to cabinets in the CER and earth cables to hardware cabinets haven't been included in any cable schedules leading to confusion over cable sizing and asset labels not being available for installation. This applies to Canary Wharf, Custom House and all shafts & portals.
| 05SY - Systemwide | Cxxx-NCR-000121 | NCR | No MCR for installed DETA Conduit |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-05-19 | 2017-05-18 14:59 | -1 | 2017-03-31 11:10 | Communications and Control Systems | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | During the quality surveillance at Cxxx Romford Control Centre it was noted that conduit manufactured by DETA had been installed. Upon investigation on eB CRL-MCR-002725 was produced which showed Barton conduit to be installed not DETA.
| 05SY - Systemwide | Cxxx-NCR-000122 | NCR | Trunking lid has been fixed with Turnbuckles |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-04-28 | 2017-04-28 09:25 | 0 | 2017-03-31 11:41 | Communications and Control Systems | 0 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | During the quality surveillance at Cxxx Romford Control Centre it was noted that two types of trunking (100mmx100mm and 50mmx50mm) had been installed within the Communication Equipment Room LO-29 with the lid being fixed via turnbuckles, not screwed.
| 05SY - Systemwide | Cxxx-NCR-000123 | NCR | Conduit and Tray installed within 150mm of Fire Alarm __ Pipe |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-04-28 | 2017-05-02 15:49 | 4 | 2017-03-31 11:40 | Electrical - Cable Management | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | During the quality surveillance at Cxxx Romford Control Centre it was noted that conduit fixed to the ceiling and tray fixed under the raised floor in Communication Equipment Room LO-29 is tight to the existing Fire Alarm __ Pipe.
| 05SY - Systemwide | Cxxx-NCR-000124 | NCR | IP2X protection not achieved in cabinet build distribution board. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-05-26 | 2017-05-03 08:40 | -23 | 2017-04-03 16:24 | Communications and Control Systems - Power Supplies | 3000 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | During the quality surveillance at Canary Wharf it was noted that there was a 35mm gap to the rear of CAW-02-CAB-2112U1 internal distribution board that there was the potential to touch live busbar terminals. Note that this was a pre IRN inspection and that the cabinet wasn't live.
| 05SY - Systemwide | Cxxx-NCR-000125 | NCR | Type S3 cabinet CAW.4.3.21A.U1 located in cupboard at Canary Wharf with restricted access for maintenence. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-06-30 | 2017-06-29 13:26 | -1 | 2017-04-03 21:01 | Communications and Control Systems | 1000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Type S3 cabinet located in cupboard at Canary Wharf with restricted access.
| 05SY - Systemwide | Cxxx-NCR-000126 | NCR | Cab Installation Quality Check |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-05-17 | 2017-05-17 14:08 | 0 | 2017-04-19 13:51 | Communications and Control Systems - General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | On a survey of cabs came across Cab WOO-02-CAB-731EU5 cable termination was lose on the fan connections
| 05SY - Systemwide | Cxxx-NCR-000127 | NCR | Cxxx-SMN-R3-ITP-CR143-50002 (Rev 2.0) Cable Installation & Termination ITP requires an update. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-05-25 | 2017-05-25 10:48 | 0 | 2017-04-27 12:50 | Communications and Control Systems - Fibre Optic Network | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | Previous surveillance visits to Canary Wharf on 29/06/16 - QS24-Canary Wharf __ Cxxx-SMN-R3-RGN-CR143-50024 found that the Cable Installation & Termination ITP Cxxx-SMN-R3-ITP-CR143-50002 (Rev 2.0) had to be updated to capture improvements and removal of tests that aren't required any more. This still hasn’t been completed.
| 05SY - Systemwide | Cxxx-NCR-000128 | NCR | Splice Allocation Schematic - Canary Wharf Station Cxxx-SMN-R3-DWG-CR143-50024 Rev 3.0 at placeholder status. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-05-31 | 2017-05-25 11:47 | -6 | 2017-04-27 12:51 | Communications and Control Systems - Fibre Optic Network | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | During my surveillance visit to Canary Wharf it was found that Splice Allocation Schematic - Canary Wharf Station Cxxx-SMN-R3-DWG-CR143-50024 Rev 3.0 was being used for the splicing at FOSC 3. Check in eB found that this version was still at placeholder status.
| 05SY - Systemwide | Cxxx-NCR-000129 | NCR | FAR CCTV Missing coverage |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-08-03 | 2017-09-04 10:46 | 32 | 2017-04-26 14:58 | Communications and Control Systems - CCTV | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Gridline K and service yard missing CCTV coverage, which has previously been instructed via PMI.
| 05SY - Systemwide | Cxxx-NCR-000130 | NCR | TCR CCTV Coverage |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-07-21 | 2017-07-31 15:26 | 10 | 2017-04-26 15:18 | Communications and Control Systems - CCTV | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Three additional cameras needed at each Northern Line link cross passage. These form part of the current Works Information but were missed off the design.
| 05SY - Systemwide | Cxxx-NCR-000131 | NCR | LIS Camera Mounting Arrangements |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-06-30 | 2017-05-25 11:08 | -36 | 2017-04-26 15:23 | Communications and Control Systems - CCTV | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Cameras to be relocated from walls to totems. This is the Cxxx design intent, addressed in workshops and instructed via workshop comments.
| 05SY - Systemwide | Cxxx-NCR-000132 | NCR | NWP CCTV Coverage |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-06-30 | 2017-06-02 11:36 | -28 | 2017-04-26 15:41 | Communications and Control Systems - CCTV | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | North Woolwich CCTV design is showing CCTV cameras about 300m away from the tunnel portal.
| 05SY - Systemwide | Cxxx-NCR-000133 | NCR | GSM-R Design Omissions |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-08-04 | 2017-08-21 15:21 | 17 | 2017-04-26 15:55 | Communications and Control Systems - Radio | 6000 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The 1511BA PMUX has been omitted from the design.
| 05SY - Systemwide | Cxxx-NCR-000134 | NCR | Comments not incorporated in issued drawings |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-06-30 | 2017-06-08 14:16 | -22 | 2017-04-26 16:02 | Communications and Control Systems | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | IFC or other drawings issued without incorporated comments.
| 05SY - Systemwide | Cxxx-NCR-000135 | NCR | Com lots missing cable schedules |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-06-30 | 2017-06-29 13:00 | -1 | 2017-04-26 16:08 | Communications and Control Systems | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Com lots require updates to reflect missing cable schedules.
| 05SY - Systemwide | Cxxx-NCR-000136 | NCR | Cross Passage Frame Drawings not at C0 status |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-06-09 | 2017-06-09 16:15 | 0 | 2017-05-03 08:10 | Communications and Control Systems | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Cross passage frames have been built using drawings at Code P0 status Cxxx-SMN-R3-DDD-CRG02_Z-00020 Generic Detail, Cross Passage Drawing, Bare __ Frame – P01 status Cxxx-SMN-R3-DDD-CRG02_Z-00021 Generic Detail, Cross Passage Drawing, Populated __ Frame - P01 status Cxxx-SMN-R3-DDE-CR001_Z-60021 Telephony Locations, Central Operating Section P01 status.
| 05SY - Systemwide | Cxxx-NCR-000137 | NCR | Cabinets delivered without E-Plan drawings uploaded to eB |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-06-13 | 2017-05-25 12:04 | -19 | 2017-05-05 11:13 | Communications and Control Systems | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | the following cabinets have been delivered to site with out the E-plan drawings being uploaded to eB. 4405 U7, U13 4264 U2, U3, U15.
| 05SY - Systemwide | Cxxx-NCR-000138 | NCR | Cxxx Drawing for PPA at P05 status |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-06-21 | 2017-06-14 10:45 | -7 | 2017-05-10 11:49 | Communications and Control Systems - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | Drawing No Cxxx-ALC-E-DDA-CR148_SW004-00100 is at P05 status
| 05SY - Systemwide | Cxxx-NCR-000139 | NCR | __ trunking installed without an approved MCR |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-07-03 | 2017-07-03 12:15 | 0 | 2017-05-16 15:34 | Communications and Control Systems - Power Supplies | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | __ trunking installed in CER at Canary Wharf without an approved MCR.
| 05SY - Systemwide | Cxxx-NCR-000140 | NCR | Isolators installed in CER at Canary Wharf without an approved MCR |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-07-31 | 2017-07-03 12:04 | -28 | 2017-05-16 16:11 | Communications and Control Systems - Power Supplies | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | __ Isolators installed in east & west CER's at Canary Wharf without an approved MCR.
| 05SY - Systemwide | Cxxx-NCR-000141 | NCR | Distribution Board installed in CER at Canary Wharf without an approved MCR. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-07-03 | 2017-05-31 11:33 | -33 | 2017-05-16 16:28 | Communications and Control Systems - Power Supplies | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | __ Distribution Boards installed east & west CER's at Canary Wharf without an approved MCR. CRL-MCR-004925 has been submitted to CEG and awaiting approval.
| 05SY - Systemwide | Cxxx-NCR-000142 | NCR | Cxxx Equipment cabinet containment deficiencies. |  | Crossrail | PDP | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-09-30 | 2017-09-26 13:56 | -4 | 2017-05-22 10:37 | Communications and Control Systems | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Works at Custom House and Canary Wharf station in early March 2017 has highlighted deficiencies in the containment available within the equipment cabinets to manage the incoming quantities of CAT6 data cables. The provisioned finger/slotted trunking is inadequate to contain the bundles of cable within the cabinet. For Custom House and Canary Wharf stations, this has been remedied by the Cxxx installation team by replacing the finger trunking with suitable cable tray. Please see attached pictures and RFI. The most congested cabinet is the patching cabinet where most field cables converge. As the cabinet arrangement is of a generic type, this issue is expected at all stations for cabinets which have already been manufactured and delivered to site. Similar CMS modifications to that of Canary Wharf and Custom House need to be implemented. The scale of this NCR needs to be defined following the survey that is currently ongoing. The close out date is to be jointly reviewed and agreed.
| 05SY - Systemwide | Cxxx-NCR-000144 | NCR | DOO CCTV Cable & Wiring Schedule |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-07-10 | 2017-07-10 14:29 | 0 | 2017-05-22 13:47 | Communications and Control Systems - Driver only Operation CCTV | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | DOO Camera cabling was installed to DOO CCTV Cabling & Wiring Schedule Cxxx-SMN-R3-LST-CR145-50010 Rev 2.0. Once DOO cabling was installed & checked against termination details of the interlinking cables as shown in Cabinet & Related Hardware Cable & Wiring Schedule Rev 1.0 discrepancies became apparent between the two documents. on request of confirmation of termination details from __ Ashby we was issued with a non coded document. this resulted in reworking of DOO cabling to the non coded document.
| 05SY - Systemwide | Cxxx-NCR-000145 | NCR | Fibre damaged in FOSC 2 EB East Box |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-06-30 | 2017-06-30 08:08 | 0 | 2017-05-22 13:39 | Communications and Control Systems - Crossrail Data Network | 1000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Fibre Cable REF CR147-DAT-00792 has been damaged whilst cable was being stripped/ prepped for splicing
| 05SY - Systemwide | Cxxx-NCR-000147 | NCR | SCADA RTU (MS146) Insufficient Protection Against Mains Voltages |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-09-30 | 2017-09-26 13:55 | -4 | 2017-05-23 07:48 | Communications and Control Systems - SCADA/Central Management System | 7500 |  | Manufacturing Defect | Rework | 2 (6-60k) | Complete | Design Problem - Other | Completed |  | The __ Cxxx Test & Commissioning team have identified a potential safety concern with the MS146 PCBs. There are exposed links on the PCB adjacent to the 240V connector which present a hazard should the enclosure be opened whilst the cabinet remains powered.
| 05SY - Systemwide | Cxxx-NCR-000148 | NCR | Inconsistent Power Information in DOO Application Designs |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-07-17 | 2017-06-27 16:52 | -20 | 2017-05-25 08:53 | Communications and Control Systems - Driver only Operation CCTV | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Sites are reporting inconsistent design information within application designs in respect of the power requirements for DOO cabinets.
| 05SY - Systemwide | Cxxx-NCR-000149 | NCR | Additional CCTV cameras required to achieve LU compliance |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-07-24 | 2017-07-26 16:15 | 2 | 2017-05-25 16:58 | Communications and Control Systems - CCTV | 10000 |  | Design | Rework | 2 (6-60k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Whitechapel CCTV design review with LU established that approximately 12 additional CCTV cameras are required to provide a design compliant with the Works Information.
| 05SY - Systemwide | Cxxx-NCR-000150 | NCR | Duct grade cabling required due to lack of cable management installed |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-07-17 | 2017-07-04 09:17 | -13 | 2017-05-25 17:17 | Communications and Control Systems - General | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | CCTV, PA/VA and HP require duct grade cables at Whitechapel over a stretch of 120m from GSM building onwards towards Canopy area. Tier 1 believes their design showed ducts instead of CMS at least in Whitechapel selective areas. Cable schedules issued back in 2015 identified the cable types.
| 05SY - Systemwide | Cxxx-NCR-000151 | NCR | Quality issues with LV termination within cabinets |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-09-27 | 2017-09-26 14:13 | -1 | 2017-05-30 11:59 | Communications and Control Systems - General | 6000 |  | Manufacturing Defect | Rework | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | This NCR has been raised as a "catch all" to ensure that all potential instances of LV termination quality issues (as previously noted under Cxxx-NCR-000126) are identified and rectified across all sites.
| 05SY - Systemwide | Cxxx-NCR-000152 | NCR | Additional CCTV cameras required to achieve LU compliance (TCR) |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-07-21 | 2017-07-31 15:35 | 10 | 2017-06-09 10:03 | Communications and Control Systems - CCTV | 1000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Following a meeting Crossrail/LU/__ a number of issues wit the CCTV design have been identified which require addressing, refer to MoM 17th May 2017.
| 05SY - Systemwide | Cxxx-NCR-000153 | NCR | Additional CCTV cameras required to achieve LU compliance (FAR) |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-08-03 | 2017-09-04 10:47 | 32 | 2017-06-09 10:08 | Communications and Control Systems - CCTV | 5000 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Following a meeting Crossrail/LU/__ a number of issues with the CCTV design at Farringdon have been identified which require addressing, refer to MoM 12th May 2017.
| 05SY - Systemwide | Cxxx-NCR-000154 | NCR | Additional CCTV cameras required to achieve LU compliance (BOS) |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-08-25 | 2017-09-04 15:06 | 10 | 2017-06-09 10:12 | Communications and Control Systems - CCTV | 5000 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Following a meeting Crossrail/LU/__ a number of issues with the CCTV design at Bond Street have been identified which require addressing, refer to MoM 16th May 2017.
| 05SY - Systemwide | Cxxx-NCR-000155 | NCR | Additional CCTV cameras required to achieve LU compliance (LIS) |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-08-25 | 2017-09-04 15:08 | 10 | 2017-06-09 10:16 | Communications and Control Systems - CCTV | 5000 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Following a meeting Crossrail/LU/__ a number of issues with the CCTV design at Liverpool Street have been identified which require addressing, refer to MoM 18th May 2017.
| 05SY - Systemwide | Cxxx-NCR-000157 | NCR | WHI D061-CAB-00028 Door Contact Broken |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-10-03 | 2017-10-03 16:22 | 0 | 2017-06-13 14:46 | Communications and Control Systems - General | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | Door contact for D061-CAB-00028 is broken
| 05SY - Systemwide | Cxxx-NCR-000158 | NCR | Airwave Radio BTS has non-compliant cabinet IP rating |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-08-04 | 2017-08-16 16:49 | 12 | 2017-06-19 14:22 | Communications and Control Systems - Radio | 500 |  | Design | Reject | 4 (0.5-3k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | The Airwave Radio BTS has non-compliant cabinet IP rating, being rated as IP20 whereas the technical specification calls for IP54.
| 05SY - Systemwide | Cxxx-NCR-000159 | NCR | Splice holders missing from splice box at Cross Passage 11 RTU |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-07-27 | 2017-07-19 08:47 | -8 | 2017-06-29 15:47 | Communications and Control Systems - Fibre Optic Network | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | During __ testing at Cross Passage 11 it was highlighted that the splice holders were missing from the patch panels and that the splice protectors were being held together by insulation tape. This was a temporary measure to allow works to progress.
| 05SY - Systemwide | Cxxx-NCR-000160 | NCR | CCTV coverage cones discrepancy |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-07-30 | 2017-07-31 15:30 | 1 | 2017-06-29 18:29 | Communications and Control Systems - CCTV | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | The distances of CCTV coverage listed in the CCTV Coverage Report(s) are different to the areas of coverage used in the CCTV layout drawings with cones.
| 05SY - Systemwide | Cxxx-NCR-000162 | NCR | Broken Cabinet Fan |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-10-05 | 2017-10-06 10:39 | 1 | 2017-07-07 13:38 | Communications and Control Systems - General | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | Cooling fan in cabinet BOS-6731U9 has a broken fixing flange and should be replaced.
| 05SY - Systemwide | Cxxx-NCR-000163 | NCR | ITP process not adhered to |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-07-27 | 2017-07-19 13:17 | -8 | 2017-07-11 18:52 | Communications and Control Systems - Fibre Optic Network | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | The installation of __ cables between CER and __ interface was completed without sufficient design detail or material compliance records. This falls outside of the processes outlined in the ITP, and should have stopped works as this is the verifying document for the primary control acceptance criteria.
| 05SY - Systemwide | Cxxx-NCR-000165 | NCR | Asset location labels to be fixed to wall |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-09-18 | 2017-09-18 15:28 | 0 | 2017-07-20 11:49 | Communications and Control Systems | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | The asset location labels supplied to fix to wall in the location of the asset are not fit for purpose due to them not sticking to the wall etc.
| 05SY - Systemwide | Cxxx-NCR-000166 | NCR | Asset Label Installation |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-08-24 | 2017-08-17 16:22 | -7 | 2017-07-20 11:06 | Communications and Control Systems - General | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | Asset labels installed adjacent equipment (CCTV & Radio) which have been fixed direct to brick, block or concrete are to be removed as adhesive is insufficient for surface type. Label installation to be included on outstanding works list until a more robust solution to be provided.
| 05SY - Systemwide | Cxxx-NCR-000167 | NCR | Radio connectors disconnected and not protected for IRN visit at Custom House |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-08-29 | 2017-08-17 12:46 | -12 | 2017-07-25 16:54 | Communications and Control Systems - Radio | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Contamination | Completed |  | During IRN visit to Custom House for handover to T&C for Radio installation, Radio connectors were found to be disconnected from antennas / splitters on the concourse area Level +1 and within the CER. None of the connectors /antennas splitters had any protective covers and all were open to the elements with dust & water contamination likely.
| 05SY - Systemwide | Cxxx-NCR-000168 | NCR | Misalignment between 3D Models and 2D CCTV Drawings at WHI, LIS, FAR, TCR and BOS |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-09-01 | 2017-09-04 10:27 | 3 | 2017-08-01 14:57 | Communications and Control Systems - CCTV | 3000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Discrepancies have been noted between the coordinated 3D model and 2D CCTV layout drawings at WHI, LIS, FAR, TCR and BOS. Although these are already being addressed, the purpose of the NCR is to ensure that any process improvements (which may be required to ensure model updates are effectively communicated) are captured.
| 05SY - Systemwide | Cxxx-NCR-000169 | NCR | P0 Status Hardware Drawing PLP |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-09-22 | 2017-09-22 13:51 | 0 | 2017-08-09 07:04 | Communications and Control Systems - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Fitted cab PLP-00-CAB-1320U1 in room 320 CER II. installed the cab off a PO status drawing and not a CO1 drawing number Cxxx-SMN-R3-DDA-CR148_PT005_1-00004
| 05SY - Systemwide | Cxxx-NCR-000170 | NCR | SCADA trackside Cabinet top cable entry |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-10-01 | 2017-10-04 09:13 | 3 | 2017-08-11 10:25 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The cabinets have cable entries on the top which are mounted externally at trackside. This effects the following cabinets: CUH-01-CAB-101/13U3 CUH-01-CAB-102/11U1 CUH-01-CAB-102/12U2 PPA-00-CAB-102/15RU1 PPA-00-CAB-101/16U1 PPA-00-CAB-102/17U1 PPA-00-CAB-102/20U1 PPA-00-CAB-102/21U1 PPA-00-CAB-102/22U1 ABW-00-CAB-101/17U1 ABW-00-CAB-102/16U1 ABW-00-CAB-102S/101TU1
| 05SY - Systemwide | Cxxx-NCR-000172 | NCR | ITP - Non Conformance |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-09-15 | 2017-09-15 12:06 | 0 | 2017-08-11 10:42 | Communications and Control Systems - General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Installation works at Abbey Wood station have progressed in order to support Rail Systems with Drawings at P status and not Construction. This is identified within Cxxx ITP's as a Hold point. The Following drawings were used and have subsequently been revised to X01 drawings during recent IRN's; 1. Cxxx-SMN-R3-DDA-CR149_Z-00001 (Was P now X01) 2. Cxxx-SMN-R3-DDC-CR149_Z-00001 (Was P now X01)
| 05SY - Systemwide | Cxxx-NCR-000173 | NCR | Installation of SCADA Trackside cabinets commenced without ITP |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-08-18 | 2017-09-04 10:49 | 17 | 2017-08-11 10:46 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | Work has commenced without a Code 1 ITP being in place
| 05SY - Systemwide | Cxxx-NCR-000174 | NCR | Trunking Installation |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-12-29 | 2017-12-29 11:22 | 0 | 2017-08-11 10:55 | Communications and Control Systems - General | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | __ Trunking has been installed to suite existing within the CER. The trunking is IP4X with turn buckles and does have screwed lid as per Crossrail requirements. The Trunking is to be used for LVAC singles cable supplying the cabinets.
| 05SY - Systemwide | Cxxx-NCR-000175 | NCR | Drawings being used for installation at not a "C" status |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-11-10 | 2017-11-10 10:11 | 0 | 2017-08-11 11:41 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Failure to follow status stamp | Completed |  | Drawings being used for the installation of trackside SCADA cabinets are still at 'P' revision and not issued as fit for construction 'C' status.
| 05SY - Systemwide | Cxxx-NCR-000176 | NCR | Cabinet damage |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-01-31 | 2018-01-31 13:48 | 0 | 2017-08-11 11:57 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | PLP-TR-CAB-101RU1 Has been damaged during transit/installation
| 05SY - Systemwide | Cxxx-NCR-000177 | NCR | 4a locking insuffucient |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-01-31 | 2017-12-20 10:08 | -42 | 2017-08-14 14:09 | Materials - General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Approval of Design Change Notice (FCN/FCR) in CTI excessive | Completed |  | The 4a type enclosure (cabinet) does not come with a locking mechanism as required
| 05SY - Systemwide | Cxxx-NCR-000178 | NCR | 7B labels are not adhering to the outside of the enclosures |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-01-31 | 2018-01-31 14:04 | 0 | 2017-08-14 14:15 | Materials - General | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | The labels and stickers on the 7B type enclosure are not adhering as they should be. This could be a case of a mixture of the enclosure being manufactured from an external supplier and perhaps the main asset label not being fully pressed into place at the time of receipt of the cabinet from the external supplier. Some of the labeling I am aware is coming away from the enclosures of this type (7B)
| 05SY - Systemwide | Cxxx-NCR-000179 | NCR | Non-conforming cable type installed |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-01-26 | 2018-01-22 13:21 | -4 | 2017-08-25 12:46 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | 2 x incorrect 12core 1.5mm2 cables were installed at Abbey Wood SER for the W/B and E/B Point Heaters. While ordering cables, communication was lost between Site Engineer and Logistics Manager resulting in a non-armoured cable being delivered to site for installation trackside. Cable was then installed. Site Construction Manager raised concern of the cable type post installation resulting in investigation leading to NCR being raised.
| 05SY - Systemwide | Cxxx-NCR-000180 | NCR | ASR 903 Fans |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-10-31 | 2017-10-31 16:51 | 0 | 2017-08-29 15:01 | Communications and Control Systems - Crossrail Data Network | 500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Multiple ASR 903 units failed on site during startup, following investigation it was found to be Fan Module fault within the units. All fans had the same manufacture date of Jan 2014, these units need to be replaced.
| 05SY - Systemwide | Cxxx-NCR-000181 | NCR | Clock defect |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-10-26 | 2017-11-09 12:38 | 14 | 2017-09-11 17:03 | Communications and Control Systems - General | 500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Previous Construction - Problems based on previous construction errors | Completed |  | The plastic screen covering the digital numerical display built into the clock unit had become loose. Two clocks arrived in this condition and a 3rd became loose after installation.
| 05SY - Systemwide | Cxxx-NCR-000182 | NCR | Quality of __ cables within cabinets in CER not satisfactory. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-10-11 | 2017-10-11 12:10 | 0 | 2017-09-13 14:37 | Communications and Control Systems - Fibre Optic Network | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Surveillance visit to Canary Wharf found that the fibres had been dressed to an unsatisfactory standard within CAW-04-4405U1 & CAW-04-4405U2. See attached photos.
| 05SY - Systemwide | Cxxx-NCR-000183 | NCR | Missing termination details for SCADA Cables |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-10-27 | 2017-11-09 10:12 | 13 | 2017-09-12 11:32 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | SCADA termination schedules specify the need to earth the screens and spare cores of cables. There has been no detail provided to assist with the construction of this. Further, entry through bushes is used regularly with no indication as to whether/how overall screens need to be terminated.
| 05SY - Systemwide | Cxxx-NCR-000184 | NCR | External cabinets fitted with glands prior to anti-corrosion treatment |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-11-30 | 2017-12-01 11:45 | 1 | 2017-09-12 15:49 | Communications and Control Systems - General | 3000 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Type 6B2 cabinets have had glands fitted prior to treating the hole to prevent corrosion. In some instances this has resulted in some staining of the paintwork adjacent to the gland.
| 05SY - Systemwide | Cxxx-NCR-000185 | NCR | Rework of terminations on SCADA VX boxes and trackside MS146 due to new termination schedules |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-09-29 | 2017-09-29 11:29 | 0 | 2017-09-13 12:49 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The SCADA terminations within trackside MS146 cabinets and associated VX termination cabinets have had to have terminations reworked due to revision of termination schedules and test cards.
| 05SY - Systemwide | Cxxx-NCR-000187 | NCR | Earth gapping kit installation without design or FCD |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-09-29 | 2017-09-28 12:07 | -1 | 2017-09-13 12:58 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Earth gapping kits are planned to be installed with no design detail.
| 05SY - Systemwide | Cxxx-NCR-000188 | NCR | SCADA termination without an approved design / FCD |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-09-27 | 2017-09-26 14:12 | -1 | 2017-09-13 13:14 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | SCADA cabling was being undertaken without an approved design or FCD.
| 05SY - Systemwide | Cxxx-NCR-000191 | NCR | Designs Incomplete - CN264 (Additional CCTV Cabinets at Portals) |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-11-17 | 2017-12-20 14:35 | 33 | 2017-09-26 08:38 | Communications and Control Systems - CCTV | 1000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Hardware Application Designs need re-issuing to complete scope of this change.
| 05SY - Systemwide | Cxxx-NCR-000192 | NCR | Defective powder coating on 20 no. DOO housings |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-10-31 | 2017-10-31 16:42 | 0 | 2017-09-18 08:33 | Communications and Control Systems - Driver only Operation CCTV | 3000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | DOO __ camera housings have been powder coated and delivered to site. An issue has been identified where the quality of the refinished housings prevents the housing from being opened and closed without having to use excessive force.
| 05SY - Systemwide | Cxxx-NCR-000193 | NCR | Telephone Post 98 installed at different location to that documented on the sightings forms between PLU - ABW |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-11-24 | 2017-12-14 14:41 | 20 | 2017-09-19 13:56 | Communications and Control Systems | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | A planned Crossrail surveillance was undertaken on 14th September 2017 to look at comms equipment installed in the Open Section between Plumstead Portal and Abbey Wood Station, and in the Running Tunnels at Cross Passage 19. During the site visit the location of Telephone Post 98 was recorded as taken from the chainage marker fixed to the fencing panels. This was recorded as chainage 23970. On checking the sightings forms in the office, Cxxx-SMN-R3-ZFM-CR001-50001 Rev 3, the form for Telephone Post 98 was found to detail the required installation location as chainage 23957; this being a 13m difference to that installed. No further evidence is in place showing acceptance of this change following compilation of the sightings form, and co-ordination with other Contractors who may be impacted by such change; such as an FCD. As the surveillance was based on a sample, it is unknown how many posts have been installed in confliction with accepted sightings forms, without any form of acceptance or change control.
| 05SY - Systemwide | Cxxx-NCR-000194 | NCR | __ Hit 200 chemical fixings have been over torqued on Coral installed CMS |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-11-24 | 2017-12-07 12:58 | 13 | 2017-09-19 14:01 | Communications and Control Systems | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | A planned Crossrail surveillance was undertaken on 14th September 2017 to look at comms equipment installed in the Open Section between Plumstead Portal and Abbey Wood Station, and in the Running Tunnels at Cross Passage 19. During the documentation review, pull test records were made available for instances where Coral have installed CMS to blockwork and concrete substrates. At this point torqueing of such fixings was discussed. It was noted that the pull test record also detailed the ‘tightening torque’ value applied by Coral operatives. On review of pull test record ‘Site Ref: PMA-CAB-102J/EU1’ as sampled from the records pack, the ‘tightening torque’ applied was 40Nm (see attached). This was for a __ Hit 200 chemical fixing of size M10 fixed into concrete. A calculation document was presented (see attached photo) which noted toque parameters for M10 size fixings using either a Hit V Rod or HIS Anchor with __ Hit 200 resin. The torque details were 25Nm and 20Nm respectively. It was unknown what type rod/anchor had been used. Moreover, the __ Technical Datasheet was checked post surveillance to align the torqueing requirements for each type fixing with a) the calculation document and b) the applied torque on installation. On inspection the __ Datasheet recorded a tmax (maximum torque) value for both type fixings as 20Nm. Based on this, the chemical fixings installed by Coral have been over torqued by double that allowable and guaranteed by __. It is unclear what impact this over torqueing would have on the cured resin interface with the rod/anchor and its long term performance. As the surveillance was based on a sample, it is unclear on the number of chemical fixings affected. This review should also be completed for mechanical type anchors where typically an impact wrench pre-set with a prescribed torque for that type fixing is used. The noted applied torque for mechanical anchors is also 40Nm as recorded on a further PML pull test record
| 05SY - Systemwide | Cxxx-NCR-000195 | NCR | Standing water found inside type 7B cabinet 101/17U1 between PLU - ABW |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-11-29 | 2017-11-30 08:17 | 1 | 2017-09-19 14:20 | Communications and Control Systems | 3000 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | A planned Crossrail surveillance was undertaken on 14th September 2017 to look at comms equipment installed in the Open Section between Plumstead Portal and Abbey Wood Station, and in the Running Tunnels at Cross Passage 19. During the site visit, type 7B cabinet 101/17U1 was inspected. This was fixed to gantry XRA 2333. On checking it was found that the cabinet had sitting water inside. The cabinet was locked at the time. This brings into question the manufacture, design or gasket performance which needs investigating where the cabinet(s) will be exposed to environmental conditions. In addition, a review of other cabinets should be completed to see if this is an isolated issue.
| 05SY - Systemwide | Cxxx-NCR-000197 | NCR | Type 7B cabinets installed without an accepted MCR |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-10-27 | 2017-10-11 09:18 | -16 | 2017-09-29 12:59 | Communications and Control Systems | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | A planned Crossrail surveillance was undertaken on 14th September 2017 to look at comms equipment installed in the Open Section between Plumstead Portal and Abbey Wood Station, and in the Running Tunnels at Cross Passage 19. MCRs were checked. It was found that the ‘Type 7B Enclosure’ CRL-MCR-005319 was showing as ‘Not Approved’. On checking, the Chief Engineers Group (CEG) review comments refer to evidence required to demonstrate that the cabinet internal temperature will not exceed the maximum operating temperature of 55 degrees in the summer months. Calculation data populated by __ had recently been linked to the MCR under Cxxx-CCM-08518 and is under review. The installation of these cabinets without an accepted MCR contravenes the accepted ITP ‘Equipment Installation’ Cxxx-SMN-R3-ITP-CR001-50005 which requires MCRs to be accepted prior to installation; this is a Hold Point for all parties. Until the MCR is accepted, the installation of these cabinets remains at risk.
| 05SY - Systemwide | Cxxx-NCR-000198 | NCR | Woolwich Cxxx Equipment cabinet containment deficiencies |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-12-01 | 2017-12-05 09:53 | 4 | 2017-10-03 09:17 | Communications and Control Systems - General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | Cxxx Equipment cabinet containment deficiencies in cabinets within CERs
| 05SY - Systemwide | Cxxx-NCR-000199 | NCR | Abbey Wood Cxxx Equipment cabinet containment deficiencies |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-12-29 | 2018-01-02 10:15 | 4 | 2017-10-04 14:12 | Communications and Control Systems - General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate man -machine interface | Completed |  | Cxxx Equipment cabinet containment deficiencies in cabinets within CERs
| 05SY - Systemwide | Cxxx-NCR-000200 | NCR | __ desk installation at Canary Wharf - worktop unaceptable |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-12-08 | 2017-12-21 14:28 | 13 | 2017-10-11 09:08 | Communications and Control Systems - General | 3000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | __ have carried out the installation of the workstation at Canary Wharf. The joints on the workstation desktop haven't been joined properly and are unacceptable.
| 05SY - Systemwide | Cxxx-NCR-000201 | NCR | Incorrect cabling dressing within the CAB |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-10-23 | 2017-10-10 14:27 | -13 | 2017-10-09 16:02 | Communications and Control Systems - Crossrail Data Network | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Cabling dressing inside the cab was not up to standard
| 05SY - Systemwide | Cxxx-NCR-000203 | NCR | Loose 2 pair cable in gland on MS146 Trackside |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-12-05 | 2017-12-01 11:34 | -4 | 2017-10-10 07:57 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | During pre-IRN inspection it was found that the 2 pair TEL-Surface cable was loose within the nickel 32mm stuffing glands on the 6B2 MS146 cabinets trackside.
| 05SY - Systemwide | Cxxx-NCR-000204 | NCR | Loose 70mm Earth cable |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-12-05 | 2017-12-05 15:40 | 0 | 2017-10-10 09:04 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Inadequate/insufficient tooling. | Completed |  | During inspection it was found that a 70mm2 earth cable had separated from it's crimp.
| 05SY - Systemwide | Cxxx-NCR-000205 | NCR | Termination Standards on 6B2 MS146 cabinets |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-12-19 | 2017-12-19 11:40 | 0 | 2017-10-10 12:06 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Personnel Error - Other human error | Completed |  | During pre-IRN inspection it was noted that multiple MS146 6B2 cabinets had loose 10mm earth cables on the internal gland plate. Within Cabinet 102/12U2 two of the 2 pair Tel-Surface cores were loose within their terminals and with a gentle pull became detached. Both of the above were inspected as part of the ITP process and a checklist was incorrectly signed.
| 05SY - Systemwide | Cxxx-NCR-000208 | NCR | Cxxx Equipment cabinet containment deficiencies |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-12-01 | 2017-12-01 14:38 | 0 | 2017-10-16 10:14 | Communications and Control Systems | 2000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Cxxx Equipment cabinet containment deficiencies, installation of CMS within cabinet required.
| 05SY - Systemwide | Cxxx-NCR-000209 | NCR | Cxxx Equipment cabinet containment deficiencies |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-01-04 | 2017-12-21 13:24 | -14 | 2017-10-16 12:32 | Communications and Control Systems | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Approval of Design Change Notice (FCN/FCR) in CTI excessive | Completed |  | Cxxx Equipment cabinet containment deficiencies, installation of CMS within cabinet required.
| 05SY - Systemwide | Cxxx-NCR-000210 | NCR | Cxxx Equipment cabinet containment deficiencies |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-11-30 | 2017-12-05 07:21 | 5 | 2017-10-16 12:43 | Communications and Control Systems | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Cxxx Equipment cabinet containment deficiencies, installation of CMS within cabinet required.
| 05SY - Systemwide | Cxxx-NCR-000211 | NCR | Cxxx Equipment cabinet containment deficiencies |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-12-11 | 2017-12-13 14:58 | 2 | 2017-11-15 14:20 | Communications and Control Systems | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Farringdon Cxxx Equipment cabinet containment deficiencies, installation of CMS within cabinet required
| 05SY - Systemwide | Cxxx-NCR-000212 | NCR | Cxxx Equipment cabinet containment deficiencies |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-12-30 | 2017-12-21 11:08 | -9 | 2017-11-15 14:23 | Communications and Control Systems | 2500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Cxxx Equipment cabinet containment deficiencies, installation of CMS within cabinet required.
| 05SY - Systemwide | Cxxx-NCR-000214 | NCR | Cxxx Equipment cabinet containment deficiencies |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-12-29 | 2018-01-09 11:27 | 11 | 2017-10-19 10:01 | Communications and Control Systems | 1000 |  | Design | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Cxxx Equipment cabinet containment deficiencies, installation of CMS within cabinet required.
| 05SY - Systemwide | Cxxx-NCR-000215 | NCR | Cxxx Equipment cabinet containment deficiencies |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-01-31 | 2018-01-30 11:23 | -1 | 2017-11-15 14:31 | Communications and Control Systems | 2000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Cxxx Equipment cabinet containment deficiencies, installation of CMS within cabinet required.
| 05SY - Systemwide | Cxxx-NCR-000216 | NCR | IP rating of MS146 enclosre installed trackside has not been maintained. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-11-30 | 2017-11-30 08:33 | 0 | 2017-10-19 14:26 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | Trackside visit found that MS146 Type 6B2 (PPA-00-CAB-102/17U1) had missing IP rated stop ends for the hinges. Further visit to cross passages found similar issues with missing or damaged stop ends for hinges on Type 4C cabinets.
| 05SY - Systemwide | Cxxx-NCR-000217 | NCR | Abbey Wood E&B no conformance |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-11-24 | 2017-11-30 08:29 | 6 | 2017-10-24 07:42 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Previous Construction - Interfacing issues | Completed |  | Currently the E&B strategy employed for the SE spur does not cater for bonding of the Type 7A cabinets compliant to RIS-1855-ENE.
| 05SY - Systemwide | Cxxx-NCR-000219 | NCR | Design detail missing for Yagi antenna installation |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-12-09 | 2017-12-14 08:17 | 5 | 2017-11-08 10:19 | Communications and Control Systems - Radio | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Design requires updating to address a) pole earthing arrangements and b) size of arrestor earth cable
| 05SY - Systemwide | Cxxx-NCR-000220 | NCR | Insufficient space within RTU to locate all common cabling |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-03-31 | 2017-12-21 10:03 | -100 | 2017-11-18 17:38 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | RTU is congested with equipment and there is a lack of cable management available for all the common cables
| 05SY - Systemwide | Cxxx-NCR-000221 | NCR | Updates to MS146 Installations |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-03-31 | 2018-01-10 15:07 | -80 | 2017-11-20 19:05 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Minor discrepancies between design documents and field installations following recent revisions to the design, specifically; 1. Spare pair of telephony cable no longer terminated onto CONN 7. 2. Terminations for voltage transformer interface to be re-labeled in accordance with termination schedule
| 05SY - Systemwide | Cxxx-NCR-000222 | NCR | Type S3 cabinet CAW.4.3.21A.U1 located in cupboard at Canary Wharf with restricted access for maintenance. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-03-31 | 2018-03-20 17:07 | -11 | 2017-11-24 14:26 | Communications and Control Systems - General | 600 |  | Design | Rework | 4 (0.5-3k) | Complete | Previous Construction - Other | Completed |  | Type S3 cabinet located in cupboard at Canary Wharf with restricted access.
| 05SY - Systemwide | Cxxx-NCR-000223 | NCR | Radio Scissor Stairwell Coverage |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-03-22 | 2018-03-20 17:03 | -2 | 2017-12-01 14:43 | Communications and Control Systems - Radio | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Scissor stairs only have coverage to one of the stairwells, the duplicate does not have
| 05SY - Systemwide | Cxxx-NCR-000224 | NCR | LCF cable bends found to be below the minimum requirement of 70mm. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-01-27 | 2018-01-18 14:33 | -9 | 2017-12-08 11:12 | Communications and Control Systems - Radio | 1000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | During site surveillance visit to Canary Wharf on Radio installation at -6 North the minimum bending radius on some LCF cable bends were found to be below the minimum requirement of 70mm.
| 05SY - Systemwide | Cxxx-NCR-000225 | NCR | Materials installed without an MCR approval |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2017-12-25 | 2017-12-20 14:22 | -5 | 2017-12-11 12:46 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | Installation of non conformance anchor bolts for the MS146 cabinets PMA-00CAB-102J/EU1 and PMA-00-CAB-101A/EU1.
| 05SY - Systemwide | Cxxx-NCR-000226 | NCR | Damaged Radio Cable |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-02-16 | 2018-02-15 10:25 | -1 | 2017-12-12 17:35 | Communications and Control Systems - Radio | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | External Phenomenon - Not Defined | Completed |  | A damaged Radio cable Ref: FD001 has been identified during the inspection and testing stage of the installation. The cable appears to have kinked on a bend as it enters/exits the Riser on Level -4. The cable is of 7/8th's LCF type @ approx. 40mtrs in length. The cable shall be replaced and tested to verify the installation with evidence provided to close out this NCR.
| 05SY - Systemwide | Cxxx-NCR-000227 | NCR | Incorrect length bolts supplied with Trackside 4A cabinets lids |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-01-26 | 2017-12-20 09:25 | -37 | 2017-12-16 09:29 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | During inspection it was apparent that the bolts supplied with the trackside 4A cabinets to secure the lid to the cabinet were too long in length resulting in the thread protruding the cabinet and touching the internal cabling (picture attached). For clarity, there is no damage to the cores however in time the movement from removing and reinstalling the bolt during inspections may cause wear on the insulation of the cores. In one of the 4A cabinets (picture attached) there is discolouration of the insulation but no damage. Installers have been tasked with removing the original bolts and replacing with shorter bolts of a length of 10mm. As a temporary measure the original bolts were installed with a nut on the exterior of the cabinet acting as a spacer (picture attached). Trackside cabinets affected: PMA-00-CAB-102J/EU1 PMA-00-CAB-101A/EU1 VDP-TR-CAB-101NEU1 VDP-TR-CAB-102LEU1 CUH-01-CAB-101Q/E CUH-01-CAB-102P/E PLP-TR-CAB-101RU1 PLP-TR-CAB-102QU1 WPA-00-CAB-101/8U1 FIS-04-CAB-101EU1 FIS-04-CAB-102EU1 WHI-05-CAB-665U2
| 05SY - Systemwide | Cxxx-NCR-000228 | NCR | __ Coupler Orientation |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-04-02 | 2018-03-27 16:11 | -6 | 2018-01-02 11:04 | Communications and Control Systems - Fibre Optic Network | 500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Previous Construction - Other | Completed |  | During the Optical Fibre splicing works, it has been identified at Paddington that some ODP (Optical Distribution Panel) have the SC/APC Couplers inserted in a non similar orientation. An inspection took place of Paddington CER 2 ODF Rack PAD-02-CAB-3732-U8 Panels XH01 - XH06, in which 53 out of 144 (37%) of the couplers were found to be inserted in the patch panels with the connector 'key' reversed. This can be seen in the attached photograph ('ODP Example Paddington.jpg'). Without rectification, duplex patch leads will appear reversed when connected, the fibre optic path will operate correctly. This can be rectified on site during the planned splicing activity, but requires additional time to carry out the activity.
| 05SY - Systemwide | Cxxx-NCR-000229 | NCR | Canary Wharf SOR Workstation worktop |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-04-06 | 2018-03-15 16:49 | -22 | 2018-01-05 12:23 | Communications and Control Systems - General | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Worktop joints misaligned, requires joint alignment re-setting
| 05SY - Systemwide | Cxxx-NCR-000231 | NCR | Installation of Commscope BUDI Boxes prior to approval of an MCR (CRL-MCR-005229) |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-01-31 | 2018-01-25 17:13 | -6 | 2018-01-10 15:36 | Communications and Control Systems - Fibre Optic Network | 0 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | Commscope BUDI Splice Boxes have been installed at Pudding Mill Lane ATFS and Westbourne Park ATS prior to the approval of CRL-MCR-005229.
| 05SY - Systemwide | Cxxx-NCR-000232 | NCR | Newly installed locks on cabinets are incorrectly installed |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-03-02 | 2018-01-26 10:40 | -35 | 2018-01-11 13:25 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During IRN inspection it was found that the newly replaced locks on cabinets VDP-01-CAB-EBU2 and VDP-01-CAB-WBU1 could be opened without use of the key.
| 05SY - Systemwide | Cxxx-NCR-000233 | NCR | Water found inside 6B2 cabinet 102/17U1 |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-01-30 | 2018-01-24 13:57 | -6 | 2018-01-16 13:30 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | During IRN inspection of MS146 cabinet 102/17U1 at Plumstead ATS it was found there was moisture build up on the internal roof of the cabinet.
| 05SY - Systemwide | Cxxx-NCR-000234 | NCR | Loose 70mm earth cable lug |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-01-30 | 2018-01-24 13:53 | -6 | 2018-01-16 13:46 | Communications and Control Systems - Power Supplies | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During IRN Inspection a loose earth lug was found on the 70mm2 Cxxx MS146 101/RU1 backplate to Cxxx earth bar bonding cable. This issue has previously been raised as an NCR requiring re-crimping of all 70mm2 earth bonds and was closed out. Further to the loose lug, the cable is the incorrect size and should be 35mm2.
| 05SY - Systemwide | Cxxx-NCR-000235 | NCR | Damage to PHP at Canary Wharf |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-03-30 | 2018-03-28 08:36 | -2 | 2018-01-19 12:17 | Communications and Control Systems - Telephony | 3000 |  | Damaged | Reject | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | As part of the walk with RFL and Crossrail it was identified that PHP 00401 on Level -4 has been damaged after installation. There was a protective cover on the PHP and it looks as if somebody has not had the correct security bit to open the hinged door.
| 05SY - Systemwide | Cxxx-NCR-000236 | NCR | Water found inside MS146 102/17U1 |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-06-21 | 2018-02-06 11:41 | -135 | 2018-01-22 12:16 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | During IRN inspection of MS146 cabinet 102/17U1 at Plumstead ATS it was found there was moisture build up on the internal roof of the cabinet.
| 05SY - Systemwide | Cxxx-NCR-000237 | NCR | Incorrect wiring on __ |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-02-13 | 2018-02-08 11:31 | -5 | 2018-01-30 15:36 | Communications and Control Systems - Power Supplies | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | After completion of deadtest, cables were inserted into the incorrect terminals indicated on the __ in cabinet 101/16U1
| 05SY - Systemwide | Cxxx-NCR-000238 | NCR | Type S3 cabinet PAD restricted access for maintenance. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-05-31 | 2018-06-01 08:57 | 1 | 2018-02-02 13:26 | Communications and Control Systems - General | 500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | Cxxx: Installation Procedures and Guidelines - Hardware Document Number Cxxx-SMN-R3-STD-CR001-50001 Revision 1.0 3.1.5 Cabinet Positioning All cabinets will be positioned based on consultation and agreement with the necessary body responsible for a site. C&C will not be placing any cabinet’s trackside, plus all locations will conform to H&S regulations ensuring clear access to located cabinets in each case for maintenance and support.
| 05SY - Systemwide | Cxxx-NCR-000239 | NCR | Type S3 cabinet BOS restricted access for maintenance. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-05-31 | 2018-05-24 23:33 | -7 | 2018-02-02 13:31 | Communications and Control Systems - General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Cxxx: Installation Procedures and Guidelines - Hardware Document Number Cxxx-SMN-R3-STD-CR001-50001 Revision 1.0 3.1.5 Cabinet Positioning All cabinets will be positioned based on consultation and agreement with the necessary body responsible for a site. C&C will not be placing any cabinet’s trackside, plus all locations will conform to H&S regulations ensuring clear access to located cabinets in each case for maintenance and support.
| 05SY - Systemwide | Cxxx-NCR-000240 | NCR | Type S3 cabinet TCR restricted access for maintenance. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-05-31 | 2018-05-30 05:46 | -1 | 2018-02-02 14:13 | Communications and Control Systems - General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - NCR excessive closure due to design issue | Completed |  | Cxxx: Installation Procedures and Guidelines - Hardware Document Number Cxxx-SMN-R3-STD-CR001-50001 Revision 1.0 3.1.5 Cabinet Positioning All cabinets will be positioned based on consultation and agreement with the necessary body responsible for a site. C&C will not be placing any cabinet’s trackside, plus all locations will conform to H&S regulations ensuring clear access to located cabinets in each case for maintenance and support.
| 05SY - Systemwide | Cxxx-NCR-000241 | NCR | Type S3 cabinet BOS restricted access for maintenance. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-05-31 | 2018-05-29 11:06 | -2 | 2018-02-02 14:33 | Communications and Control Systems - General | 500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Cxxx: Installation Procedures and Guidelines - Hardware Document Number Cxxx-SMN-R3-STD-CR001-50001 Revision 1.0 3.1.5 Cabinet Positioning All cabinets will be positioned based on consultation and agreement with the necessary body responsible for a site. C&C will not be placing any cabinet’s trackside, plus all locations will conform to H&S regulations ensuring clear access to located cabinets in each case for maintenance and support.
| 05SY - Systemwide | Cxxx-NCR-000242 | NCR | Type S3 cabinet LIS restricted access for maintenance. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-05-31 | 2018-05-18 07:24 | -13 | 2018-02-02 14:46 | Communications and Control Systems - General | 500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | Cxxx: Installation Procedures and Guidelines - Hardware Document Number Cxxx-SMN-R3-STD-CR001-50001 Revision 1.0 3.1.5 Cabinet Positioning All cabinets will be positioned based on consultation and agreement with the necessary body responsible for a site. C&C will not be placing any cabinet’s trackside, plus all locations will conform to H&S regulations ensuring clear access to located cabinets in each case for maintenance and support.
| 05SY - Systemwide | Cxxx-NCR-000243 | NCR | CMS Simulator/Training UI is not interacting with the MEP assets at any location |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-04-30 | 2018-05-01 15:03 | 1 | 2018-02-13 16:18 | Communications and Control Systems - SCADA/Central Management System | 1000 |  | Software | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | While __, RfL Training Specialist, and __, Crossrail SCADA Engineer, were reviewing the delivered training simulator functionality, software release 2.4.4, in the RCC Training Suite on 05 February 2018, it was found that interaction with the configured MEP equipment through the Training UI was not possible (non-responsive). Remote connection to the training simulator server found that the OPC server script was not running. Once remotely connected, the OPC server script auto launched and after a short period of time, equipment could be manipulated via the Training UI. This occurs quite regularly, e.g. the OPC server command script has not auto launched when the system has been freshly rebooted for some reason. This fault was reported to Cxxx on 05 January 2018 using a Training/Simulator Fault Reporting Sheet. __ confirmed to __ on 13 February 2018 that the OPC server crashing is a regular occurrence (almost every night) and has had to be restarted by the delivery trainer each day to prevent impacting on Traffic Manager training.
| 05SY - Systemwide | Cxxx-NCR-000244 | NCR | Canary Wharf - Current RIR not available at site. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-03-09 | 2018-03-09 09:51 | 0 | 2018-02-19 13:40 | Communications and Control Systems - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | During site surveillance visit to Canary Wharf it was noted that Register & Issue record (RIR) Cxxx-SMN-R3-LRG-CR143-50001 held at site was Rev 22.0. Rev 32.0 is the current version in eB.
| 05SY - Systemwide | Cxxx-NCR-000245 | NCR | Canary Wharf -SCADA I/O Cable and Wiring Schedule installed against not current in eB. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-04-02 | 2018-03-28 09:01 | -5 | 2018-02-19 15:04 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | Canary Wharf -SCADA I/O Cable and Wiring Schedule installed against not current version in eB.
| 05SY - Systemwide | Cxxx-NCR-000246 | NCR | Canary Wharf -SCADA Cable Schedule installed against is not current version in eB. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-04-02 | 2018-03-28 09:04 | -5 | 2018-02-19 15:12 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | SCADA System Cable Termination Schedule – Canary Wharf Station Cxxx-SMN-R3-LST-CR143-50021 is currently Rev 2.0 has Current Document Status on eB and RIR. The Site team are currently installing against Cxxx-SMN-R3-LST-CR143-50021 Rev 3.0 which has been issued with SAF Cxxx CAW-SAF-032
| 05SY - Systemwide | Cxxx-NCR-000247 | NCR | Uncontrolled copy of __ Splice schedule at Canary Wharf. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-03-07 | 2018-03-06 16:10 | -1 | 2018-02-21 09:11 | Communications and Control Systems - Fibre Optic Network | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Not Defined | Completed |  | Site visit to Canary Wharf found that __ Engineers have been working against Optical Fibre Network System Wide Splice Allocation Schedule - Canary Wharf Station Cxxx-SMN-R3-LST-CR143-50026 Rev 4.0. Engineers should be working against the latest revision in eB. Rev 3.0 is the current version in eB.
| 05SY - Systemwide | Cxxx-NCR-000248 | NCR | Connaught Tunnel Resilience |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-05-16 | 2019-06-21 15:10 | 36 | 2018-02-21 14:35 | Communications and Control Systems - Radio | 30000 |  | Design | Rework | 2 (6-60k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | The Connaught Tunnel is an isolated section of tunnel, all radiating cables within this tunnel section are fed from respective single remote units (RU) located within the head house CER. Failure of any PMR RU would result in no coverage within Connaught Tunnel for that corresponding technology.
| 05SY - Systemwide | Cxxx-NCR-000249 | NCR | Canary Wharf __ Patch Wiring Schedule hasn't been issued to eB - works have progressed. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-03-07 | 2018-03-07 13:18 | 0 | 2018-02-21 15:16 | Communications and Control Systems - Fibre Optic Network | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | Installation works have progressed on site against __ Patch Wiring Schedule Cxxx-SMN-R3-LST-CR143-50032 Rev 1.0. Check in eB found that the document is obsolete.
| 05SY - Systemwide | Cxxx-NCR-000250 | NCR | Uncontrolled copy of __ Patch Wiring Schedule at Victoria Dock Portal |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-03-07 | 2018-03-01 14:04 | -6 | 2018-02-21 17:28 | Communications and Control Systems - Fibre Optic Network | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Not Defined | Completed |  | Installation works have been carried out at VDP against __ Patch Wiring Schedule at Victoria Dock Portal Cxxx-SMN-R3-LST-CR144_PT003-50019 Rev 2.0. Engineers should be working against the latest revision in eB. eB status of the document is obsolete.
| 05SY - Systemwide | Cxxx-NCR-000251 | NCR | Uncontrolled copy of __ Patch Wiring Schedule at Mile End Park |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-03-07 | 2018-03-01 14:04 | -6 | 2018-02-21 17:44 | Communications and Control Systems - Fibre Optic Network | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Not Defined | Completed |  | Installation works have been carried out at MEP against __ Patch Wiring Schedule at Mile End Park Cxxx-SMN-R3-LST-CR094_SH006-50013 Rev 1.0. Engineers should be working against the latest revision in eB. eB status of the document is obsolete.
| 05SY - Systemwide | Cxxx-NCR-000252 | NCR | Uncontrolled copy of __ Patch Wiring Schedule at Custom House |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-03-07 | 2018-03-07 13:18 | 0 | 2018-02-22 12:48 | Communications and Control Systems - Fibre Optic Network | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | Installation works have progressed on site against __ Patch Wiring Schedule Cxxx-SMN-R3-LST-CR145-50029 Rev 1.0. Check in eB found that the document is obsolete. Uncontrolled copy on site also found 2 No documents for different sites with the same document number(See attached photos) __ Patch Wiring Schedule Victoria Dock Portal Cxxx-SMN-R3-LST-CR144_PT003-50019 & __ Patch Wiring Schedule Custom House Station Cxxx-SMN-R3-LST-CR144_PT003-50019
| 05SY - Systemwide | Cxxx-NCR-000254 | NCR | TM Workstation 2 Simulator - Server crashed - FOR 271 |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-06-15 | 2018-06-18 10:31 | 3 | 2018-03-16 08:33 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Software | Rework | 4 (0.5-3k) | Complete | Previous Construction - Other | Completed |  | Simulator workstation on the Traffic Manager 2 desk within the simulator room is stating that the Server has crashed. Training UI inaccessible, Training __ server stating that all emulators are 'Offline' & 'Not Conected'
| 05SY - Systemwide | Cxxx-NCR-000256 | NCR | Cxxx Radio - Canary Wharf Asset Labelling Descrepencies |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-04-30 | 2018-04-30 15:29 | 0 | 2018-03-09 12:26 | Communications and Control Systems - Radio | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | During IRN handover it was highlighted that discrepancies existed between Schematic and Cable Schedules.
| 05SY - Systemwide | Cxxx-NCR-000257 | NCR | Canary Wharf -Rittal Sealing Modules not installed in top of cabinets in CER. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-04-30 | 2018-04-30 15:36 | 0 | 2018-03-12 15:03 | Communications and Control Systems - General | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Previous Construction - Not Defined | Completed |  | Canary Wharf -Rittal Sealing Modules not installed in top of cabinets in CER. The attached images are from Cabinets CR143-CAB-00049, 00067, 00068, 00088
| 05SY - Systemwide | Cxxx-NCR-000258 | NCR | User Stories and the associated Test Scripts had not been through any internal review |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-04-06 | 2018-05-25 10:17 | 49 | 2018-03-19 09:11 | Communications and Control Systems - General | 500 |  | Software | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | The Software Quality Plan identified that User Stories are written for each element of software development. These User Stories and the associated Test Scripts had not been through any internal review process to verify compliance against requirements. This had the potential to introduce rework for both development and testing works.
| 05SY - Systemwide | Cxxx-NCR-000259 | NCR | Cable Schedule Detail |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-05-31 | 2018-06-01 13:50 | 1 | 2018-03-19 16:22 | Communications and Control Systems - General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Tunnelling and Underground construction academy Cxxx System cable wiring schedule eB Ref: Cxxx-SMN-R3-LST-CR527-50006 Rev 2.0 does not detail all equipment identified on construction drawings and/or within application design. Additional cables have been included on the as-installed cable schedule submitted as part of TUCA IRN 001 and can be found within Site Assurance File Cxxx-TUCA-SAF-001 eB Ref: Cxxx-SMN-R3-CER-CR527-50044 Rev 1.0
| 05SY - Systemwide | Cxxx-NCR-000260 | NCR | SOR Desk Layout Drawings |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-04-30 | 2018-04-30 15:39 | 0 | 2018-03-19 16:34 | Communications and Control Systems - General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | TUCA SOR Equipment Layout Drawing Ref: Cxxx-SMN-R3-DDA-CR527_1-30002 at Rev P01 during construction. Information conflicts with Application design regarding screen allocations. Drawing has been Redlined during the IRN process and will be submitted to eB accordingly.
| 05SY - Systemwide | Cxxx-NCR-000261 | NCR | TUCA SCADA Termination Schedule Availability |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-05-28 | 2018-05-11 11:48 | -17 | 2018-03-19 16:55 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | SCADA Termination Schedule not available at the time of installation/construction works. SCADA Cables identified on Cable Schedule eB Ref: Cxxx-SMN-R3-LST-CR527-50006 Rev 2.0 have been installed with inspection and verification completed inline with Cxxx ITP's. Cable termination transferred to outstanding works list and shall be submitted to eB Punchworks as part of TUCA IRN 002 eB Ref: Cxxx-SMN-R3-CER-CR527-50042. Works shall be completed once Termination schedule available @ code 1 on eB.
| 05SY - Systemwide | Cxxx-NCR-000262 | NCR | Cxxx Radio - Scissor Stairs |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-06-08 | 2018-06-11 10:15 | 3 | 2018-03-21 16:06 | Communications and Control Systems - Radio | 1000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Scissor Stairs only have coverage to the intervention stairwells and not the fire stairwells
| 05SY - Systemwide | Cxxx-NCR-000263 | NCR | Cxxx Radio - Tottenham Court Road Scissor Stairs |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-05-24 | 2018-05-14 16:14 | -10 | 2018-03-23 14:57 | Communications and Control Systems - Radio | 1000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Scissor Stairs only have coverage to the intervention stairwells and not the fire stairwells
| 05SY - Systemwide | Cxxx-NCR-000264 | NCR | Lack of design detail - Cross passages electrical distribution |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-07-13 | 2018-07-17 11:12 | 4 | 2018-03-28 10:43 | Communications and Control Systems - Power Supplies | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The Cross Passage Hardware Requirements Application Design Cxxx-SMN-R3-RSP-CRG01-50001 Revision 3.0 has not been updated to reflect agreements/instructions to include LV distribution to radio equipment. Specific elements to address are 1) Calculations to support the proposed ring main design 2) Schematic diagram of design 3) Identification of a suitable double pole isolating fused spur unit 4) Confirmation of how IP rating is to be achieved.
| 05SY - Systemwide | Cxxx-NCR-000265 | NCR | Process not followed for IRN at Westbourne Park ATS |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-04-12 | 2018-04-11 09:45 | -1 | 2018-03-29 06:58 | Communications and Control Systems - Power Supplies | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Personnel Error - Not Defined | Completed |  | Attendance to Westbourne Park ATS for IRN handover to T&C found that WPA-00-CAB-00U1 had been energised without going through the IRN process.
| 05SY - Systemwide | Cxxx-NCR-000266 | NCR | Canary Wharf CAB CAW 4.2.64 U1 Exposed Rectifier Terminals - permanent covers required. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-05-18 | 2018-05-14 08:29 | -4 | 2018-03-29 07:06 | Communications and Control Systems - Power Supplies | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | During IRN visit to Canary Wharf it was found that there were exposed terminals in cabinet CAW-04-CAB-4264U1. Temporary covers have been placed on the terminals for the purpose of the IRN with permanent covers being ordered from the manufacturer.
| 05SY - Systemwide | Cxxx-NCR-000267 | NCR | Faulty DS Armoured __ Patch Cords - various stations. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-05-28 | 2018-05-29 13:37 | 1 | 2018-04-04 13:07 | Communications and Control Systems - Fibre Optic Network | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | During T&C activities it was found that there was a high quantity of failures / dB loss over DS Armoured __ Patch Cords installed for the RADIO system at various sites.
| 05SY - Systemwide | Cxxx-NCR-000268 | NCR | Radio connectors dust ingress CP/14 |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-04-20 | 2018-04-20 10:38 | 0 | 2018-04-06 08:20 | Communications and Control Systems - Radio | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Personnel Error - Other human error | Completed |  | During site visit to Cross Passage 14 on Radio installation there were Radio connectors installed on the ends of the LCF cable without any protection against dust ingress.
| 05SY - Systemwide | Cxxx-NCR-000269 | NCR | Inefficient working CUH |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-05-11 | 2018-05-10 12:54 | -1 | 2018-04-13 11:10 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | Scada testing and termination taking longer than expected to complete due to inefficient working.
| 05SY - Systemwide | Cxxx-NCR-000270 | NCR | Containment in WEP Cxxx REB |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-06-15 | 2018-05-25 08:20 | -21 | 2018-04-16 10:02 | Communications and Control Systems - General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The containment installed by Cxxx for Cxxx use is not suitable for Cxxx installation, Cxxx will design and install new containment to accommodate the Cxxx cabling Due to restrictive REB height of 2300mm the armoured cable bend radius does not allow installation into the top of the 4B cabinet, a new spreader box is to be installed to the top of the 4B cabinet and extended to one side to allow the cables to enter from underneath
| 05SY - Systemwide | Cxxx-NCR-000271 | NCR | Incorrect Termination CUH Base Station |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-04-27 | 2018-04-27 10:43 | 0 | 2018-04-16 14:33 | Communications and Control Systems - Radio | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Incorrect terminations for the supply for the BTS Base Station in the CER at CUH
| 05SY - Systemwide | Cxxx-NCR-000272 | NCR | Software FORs 311, 312, 327, 353 and 354 |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-07-31 | 2018-08-02 08:43 | 2 | 2018-04-17 07:42 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Software | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | As per Cxxx-PMC-06607 5 No FORS classified as defects; 1. FOR 311 – Not Critical CMS CONFIRMED Values inverted at RCM 2. FOR 312 – Not Critical CMS CONFIRMED Analogue unit values not shown Analogues Page 1 and 2 3. FOR 327 – Not Critical CMS CONFIRMED Out of Service function not as Test Specifications 4. FOR 353 Temp fix by T&C before energisation. - Critical Ashby to either incorporate the fix into next build i.e. 3.1.2.2 or create a patch for T&C for all the sites. CMS Jordan Rowland UNCONFIRMED Energised level on Power "lines" too low. 5. FOR 354 Not Critical Ashby to investigate and resolve ASAP. Alarms will be remained on the Alarm List Will become critical once many HV sites are live; the alarm page will become full with nuisance alarms. This needs fixing prior to CUH or NWP. CMS Jordan Rowland UNCONFIRMED All changes - including analogues causing MIND and ETHC Alarms
| 05SY - Systemwide | Cxxx-NCR-000273 | NCR | Outstanding Alarm Descriptions on CMS/__ Software |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-03-31 | 2019-02-18 12:57 | -41 | 2018-04-17 17:17 | Communications and Control Systems - SCADA/Central Management System | 15000 |  | Software | Rework | 2 (6-60k) | Complete | Design Problem - Other | Completed |  | Outstanding design works related to Alarm Descriptions on CMS/__ Software – Sites which are to be corrected by software Drop 3.1.x series.
| 05SY - Systemwide | Cxxx-NCR-000274 | NCR | Materials installed whilst awaiting approval of MCRs |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-07-31 | 2019-08-15 11:28 | 15 | 2018-04-20 10:31 | Communications and Control Systems | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | A review has identified that a small number materials have been installed although the MCR, although submitted, has not been approved. Materials affected are: Frequentis Dispatcher Terminal CRL-MCR-004900 __ AFIL LMT CRL-MCR-003548 __ Safety Isolating Transformer CRL-MCR-004288 Rittal Cabinet Type 5I CRL-MCR-003918 __ SF300 PoE Switch CRL-MCR-004133 __ MIPP000991 Fibre-optic Patch Panel CRL-MCR-003936 Westermo Ethernet Media Converter 1G CRL-MCR-006185 G M Plastics HDPE TWIN WALL DUCT CRL-MCR-005314 Lasnek HDRF-225-03 - SS Cable Tray CRL-MCR-005335 Beyerdynamic CID Audio Headphones CRL-MCR-004132 MCL Data Solutions SCA Series Fibre Patch Cords CRL-MCR-005786
| 05SY - Systemwide | Cxxx-NCR-000275 | NCR | Trunking Lid Change |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-08-31 | 2018-09-14 08:43 | 14 | 2018-04-20 10:50 | Communications and Control Systems - General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | __ Trunking installed within CER's currently has turnbuckle lid. Cxxx are now to replace the Lid with a screwed type for all LVAC trunking installed. All trunking shall be of screwed lid type for LVAC circuits moving forward. The above shall then satisfy the Crossrail JY60 Specification requirements.
| 05SY - Systemwide | Cxxx-NCR-000276 | NCR | Internal cabinet wiring at CUH |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-06-07 | 2018-06-22 12:59 | 15 | 2018-04-25 14:42 | Communications and Control Systems - Driver only Operation CCTV | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Insufficient information made available to the worker. | Completed |  | The internal cabinet wiring for the DOO terminations on cab 731U4 currently has two blade terminals used in the same termination point and not double bootlace ferrules. When comparing this to the second DOO cab 606U1 double bootlace ferrules have been used but the wiring configuration differs between cabinets. Wiring should be the same format across the DOO cabinets with only a single crimp used in each terminal.
| 05SY - Systemwide | Cxxx-NCR-000277 | NCR | Paddington stack cables damged |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-06-22 | 2018-06-22 11:56 | 0 | 2018-04-27 15:14 | Communications and Control Systems | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | stack cable at the rear of the switch has been damaged due to lack of space at the rear of the cabinet
| 05SY - Systemwide | Cxxx-NCR-000278 | NCR | __ team not recording snag items |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-08-31 | 2018-09-10 13:20 | 10 | 2018-05-02 15:28 | Communications and Control Systems - Fibre Optic Network | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Training Deficiency - Other | Completed |  | During a surveillence of __ and certification it was noted that snag items were not being recorded on the site snag register and punchworks in eB It was also noted that there was no evidence of red lines being captured and issued to eB
| 05SY - Systemwide | Cxxx-NCR-000279 | NCR | Damaged speaker at Canary Wharf |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-05-24 | 2018-05-16 15:45 | -8 | 2018-05-10 16:14 | Communications and Control Systems - Public Address Systems | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Contractor Delatim accidentally damaged PAVA speaker (MCS20) whilst moving scaffold.
| 05SY - Systemwide | Cxxx-NCR-000280 | NCR | Incorrect asset equipment label installed on camera 8409 at VDP |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-06-25 | 2018-07-02 08:27 | 7 | 2018-05-10 16:56 | Communications and Control Systems - General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During site visit to VDP it was found that the asset equipment label installed on VDP-00-CAM-8409 was incorrect. This is defined by Equipment Serial column in CCTV System Equipment Schedule - VDP - Cxxx-SMN-R3-LST-CR144_PT003-50017.
| 05SY - Systemwide | Cxxx-NCR-000281 | NCR | Incorrect Radio Diplexers installed in CP13, CP14 , CP16 & CP18 |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-06-11 | 2018-06-07 08:56 | -4 | 2018-05-15 08:39 | Communications and Control Systems - Radio | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Incorrect Radio Diplexers installed in CP13, CP14, CP16 & CP18.
| 05SY - Systemwide | Cxxx-NCR-000282 | NCR | DC blocks & grounding kits not installed as per design in Crosspassages. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-11-29 | 2018-12-05 11:59 | 6 | 2018-05-15 08:52 | Communications and Control Systems - Radio | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | During site visit to CP13,14 & 15 it was noted that DC blocks & grounding kits were not installed as per design in Crosspassages. All earth cables for both DC blocks and grounding kits had been terminated onto Cxxx earth bars within the Crosspassage. Design shows that these should be installed to earth bars in the tunnel. No evidence of design change during visit.
| 05SY - Systemwide | Cxxx-NCR-000283 | NCR | Incorrect sized crimps installed on cable at VDP. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-07-29 | 2018-07-19 12:26 | -10 | 2018-05-15 15:40 | Communications and Control Systems - Power Supplies | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A recent site visit for IRN identified an incorrect and potentially dangerous wiring assembly. It was found that the final circuit (48v) from the isolator to the MS146 mains incoming had the wrong sized crimps on the incoming power supply. To achieve this the cores of the 4mm multi strand cable had been cut to allow the red crimp(max size 1.5mm) to be installed. Inspections had been carried out as per the Site Inspection & Test Plan with both LVAC power cable installation inspection & test check sheet and BS7671 Electrical Certificate being signed off as satisfactory. Both inspections failed to highlight the cable had been trimmed to accommodate the wrong sized crimp. Note: The crimps have been changed to the correct sized crimps (yellow) before being energised.
| 05SY - Systemwide | Cxxx-NCR-000285 | NCR | Stainless Steel Cable Ties not being Trimmed Correctly |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-06-22 | 2018-06-21 14:00 | -1 | 2018-05-23 13:59 | Communications and Control Systems - General | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | Within Cross Passage 15 it is noted that Stainless Steel cable ties installed are not being trimmed as detailed in Installation Procedures and Guidelines – Structured Cabling Document Number Cxxx-SMN-R3-GPD-CR001-50017 section 5.1 securing Cables which states: Cable ties shall be of a size such that they can be tightened down to grip the cable without exerting undue pressure, distortion or strain. Additional care shall be taken when using a tensioned cutting tool for securing metal ties. Cable ties shall be trimmed flush following installation ensuring no protruding sharp edges remain.
| 05SY - Systemwide | Cxxx-NCR-000287 | NCR | Damaged SCADA Cable |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-06-07 | 2018-06-04 13:45 | -3 | 2018-05-24 10:48 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During recent SCADA cable testing activities the following cable has been identified as damaged. Cable Ref: CR143-CCC-01099 (18-Core Lift interface IFU-L4) Several cores have failed the continuity test and requires further investigation. (Open Circuit) It should be noted that the damage has been located approx. 10mtrs away from the field termination end which was installed by 3rd party contractors (Seapam) who installed final CMS and cabling.
| 05SY - Systemwide | Cxxx-NCR-000288 | NCR | Paddington- Damaged equipment in CDN cab PAD-02-CAB-3732U2 |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-08-16 | 2018-08-01 14:26 | -15 | 2018-05-31 08:42 | Communications and Control Systems - Crossrail Data Network | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | At Paddington site- in CER2- Damage to the rear RS232 interface plug sockets ( in CDN cabinet PAD-02-CAB-3732U2) as below and pictures attached: a) Two XZ3 - Description - 48V DC, RS232 TO RS422/485 CONVERTER ; Manufacturer- Westermo; Type MD-45; Part number - MD-45 LV; S/N: 22879 b) Two cables -101
| 05SY - Systemwide | Cxxx-NCR-000289 | NCR | Incorrect cable asset labels installed on Radio at Victoria Dock Portal. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-07-23 | 2018-07-19 12:03 | -4 | 2018-05-31 11:24 | Communications and Control Systems - Radio | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | 2 No RADIO cables have identical cable asset ID’s with further sample checks found that asset labels have been installed in the incorrect locations.
| 05SY - Systemwide | Cxxx-NCR-000290 | NCR | White asset tag labels installed on equipment. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-07-23 | 2018-07-19 12:09 | -4 | 2018-05-31 15:10 | Communications and Control Systems - Radio | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Information not detailed | Completed |  | White Asset Tag labels have been attached to each of the antennas at site. Asset Identification Standard CRL1-XRL-O6-STD-CR001-00031 Section 10.2 Label positioning states that White Asset Tag labels should not be attached to Equipment fulfilling the duty of the Asset Tag.
| 05SY - Systemwide | Cxxx-NCR-000291 | NCR | Induction Loop Damaged Cable |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-06-28 | 2018-07-04 14:58 | 6 | 2018-05-31 16:16 | Communications and Control Systems - Public Address Systems | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Not Defined | Completed |  | During ongoing installation and testing works at Canary Wharf Station a damaged cable has been identified. The Cable is for the an induction loop on level -5 and was being tested when an open circuit was found. Further investigation within the chamber shown no signs of damage however when the cable was removed from the conduit a clean break was found.
| 05SY - Systemwide | Cxxx-NCR-000292 | NCR | Victoria Dock Portal – Radio Fibre Patching insufficient gland type installed to support cable. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-06-15 | 2018-06-15 09:17 | 0 | 2018-06-01 09:44 | Communications and Control Systems - Radio | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | Inspection of the radio fibre patching found that where the fibre enters the Radio repeaters there isn’t a sufficient gland type installed to take the strain off the fibre installed.
| 05SY - Systemwide | Cxxx-NCR-000293 | NCR | Damaged Asset - Canary Wharf Station |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-06-15 | 2018-06-18 14:00 | 3 | 2018-06-01 10:39 | Communications and Control Systems - Radio | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | Radio antenna found damaged following routine inspection. Antenna was damaged by scaffolding contractors who failed to report it.
| 05SY - Systemwide | Cxxx-NCR-000294 | NCR | Radio - Radiating Cable Lengths |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-07-28 | 2018-07-26 07:39 | -2 | 2018-06-04 13:45 | Communications and Control Systems - Radio | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | It has been found that the radiating cable drum lengths at Liverpool Street Station are approximately 80m short.
| 05SY - Systemwide | Cxxx-NCR-000295 | NCR | Software - RCM regularly fails with loss of comms from plant items |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-06-19 | 2018-06-22 09:14 | 3 | 2018-06-05 15:16 | Communications and Control Systems - SCADA/Central Management System | 4500 |  | Software | Rework | 3 (3-6k) | Complete | Verification Problems - Other | Completed |  | The RCM regularly fails with loss of comms from plant items. This fault is believed to be related to the DNP3 driver which crashes and then (as it is a critical driver) switches to the standby server to resume system functionality.
| 05SY - Systemwide | Cxxx-NCR-000296 | NCR | Design changes on Radio at Mile End Park resulting in incorrect asset ID's and differences between schedules, schematics, drawings and assets . |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-07-28 | 2018-08-02 08:57 | 5 | 2018-06-07 09:08 | Communications and Control Systems - Radio | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | The Radio design at Mile End Park has changed since the original installation. A recent site visit to Mile End Park to check assets has found that the Radio design at Mile End Park has changed since the original installation was installed. This was handed over to T&C as part of Installation Release Notice on 1st September 2017. The original installation was carried out against Cxxx-SMN-R3-LST-CRG03-50070 PMR-RI System Cable and Wiring Schedule current Rev 5.0 dated 8th March 2017. Revision 6.0 that was issued on 18th September 2017 and given Code 1 decal on 19th December 2017 has now changed leading to 2 x Radio cable asset IDs now being incorrect. Further checks have found further anomalies between the original installation and the new design.
| 05SY - Systemwide | Cxxx-NCR-000297 | NCR | MEP Optical Fibre Network - Fibre spliced and tested at FOSC 1 instead of FOSC 2. Field Change Design process not followed. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-09-03 | 2018-09-12 08:23 | 9 | 2018-06-07 11:22 | Communications and Control Systems - Fibre Optic Network | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | A recent site visit for asset labels surveillance at Mile End Park has identified design change that hasn’t been captured for the __ System. It was found that 4 No 96 core fibres (trackside) and 2 No 24 core fibres (CER) have been installed to FOSC 1 at Level -9 instead of FOSC 2 at Level -7 All splicing & testing works are now complete and at no point has any Field Change Design, red line drawings, cable schedules or schematics been updated to reflect the changes to FOSC 1 or FOSC 2.
| 05SY - Systemwide | Cxxx-NCR-000298 | NCR | Radio Coverage of Levels A and B at Whitechapel |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-11-11 | 2019-11-15 15:37 | 4 | 2018-07-24 10:25 | Communications and Control Systems - Radio | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Crossrail believe there should be radio coverage provided for above ground areas. This NCR will be used to track any design updates in parallel with commercial discussions to resolve the scope gap.
| 05SY - Systemwide | Cxxx-NCR-000299 | NCR | Anritsu Test Equipment Calibration |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-07-31 | 2018-07-05 16:04 | -26 | 2018-06-14 15:55 | Communications and Control Systems - Radio | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | An item of Anritsu test equipment used to test coaxial cables in CP14 was out of date. Calibration Certs for ANS331E-M12 Ser No 1223015 have a Gap from 04.01.2018 to 17.01.2018 The test trace example shown in the SAF was carried out with this test instrument on 09.01.2018
| 05SY - Systemwide | Cxxx-NCR-000300 | NCR | Cabinet loading information not updated for cabinets at Victoria Dock Portal |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-07-06 | 2018-07-03 08:23 | -3 | 2018-06-15 11:41 | Communications and Control Systems - Power Supplies | 5000 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Document Cxxx-SMN-R3-RSP-CRG03-50009 the "Application Design – Victoria Dock Portal (Cabinets and Related Hardware)" does not include the correct definition of current ratings for the equipment cabinets. As a result, power design calculations have been completed with the wrong loading and will need to be performed again to verify discrimination.
| 05SY - Systemwide | Cxxx-NCR-000301 | NCR | Cross Passage Electrical Design |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-03-31 | 2019-05-24 14:24 | 54 | 2018-06-20 09:50 | Communications and Control Systems - Power Supplies | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Current Cross Passage (CP) Electrical design (as installed) specifies equipment that does not meet the IP rating required within Cross Passages. Once the new design is finalized (closure of Cxxx-NCR-000264 - Lack of design detail - Cross passages electrical distribution) existing CP installations will require modification to comply with the revised design.
| 05SY - Systemwide | Cxxx-NCR-000302 | NCR | DOO - LF Cable Cleats |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-12-31 | 2018-12-17 12:43 | -14 | 2018-06-19 11:38 | Communications and Control Systems - Driver only Operation CCTV | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | The cable cleats used for installation of the DOO Leaky Feeder Cable do not clamp the cable tightly as the RFS 1.1/4 cleats are designed for a 36mm cable and the cable supplied by Bombardier is a non standard 32-33.6mm cable. Scotch 2210 tape has been used at each cleat to provide padding to the cable to allow it to fit snuggly within the larger cleat. Issues with ensuring uniformity for installation of the Scotch tape necessitate the need for an alternative cleat/clip solution.
| 05SY - Systemwide | Cxxx-NCR-000303 | NCR | MEP - Damaged telephone fixings. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-07-04 | 2018-07-09 10:02 | 5 | 2018-06-20 08:06 | Communications and Control Systems - Telephony | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | MEP-00-TEL-10009 mounting brackets at rear of telephone have been damaged.
| 05SY - Systemwide | Cxxx-NCR-000304 | NCR | TCR - Rittal Sealing Modules not installed in top of cabinets in CER. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-08-31 | 2018-08-08 10:03 | -23 | 2018-06-20 14:46 | Communications and Control Systems - General | 0 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | During T&C surveillance visit to TCR it was noted that Rittal Sealing Modules not installed in top of cabinets N105-CAB-00019 & N105-CAB-00019 in CER 4/734. With the modules not being installed, the cabinet doesn't maintain its IP rating and there is potential for failure of equipment due to dust ingress.
| 05SY - Systemwide | Cxxx-NCR-000305 | NCR | Woolwich Cabinets 731WU1-731UE1 Eplans and schedules not aligned |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-07-20 | 2018-07-17 12:50 | -3 | 2018-06-20 13:08 | Communications and Control Systems - General | 500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The Current termination schedule on EB for Woolwich in cabs 731UE1 and 731WU1 at the time of termination has cables terminating on a C2 card that doesn't exist The current Eplan on EB is out of date and shows the wrong cards. CN811 was raised to correct the termination schedule but the eplan remains unchanged. As a result terminations of the cables are potentially to the wrong cards according to the out of date eplan
| 05SY - Systemwide | Cxxx-NCR-000306 | NCR | Asset Equipment Label Barcode not including Serial number |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-12-31 | 2018-12-11 15:18 | -20 | 2018-06-20 17:53 | Communications and Control Systems | 20000 |  | Manufacturing Defect | Rework | 2 (6-60k) | Complete | Design Problem - Inadequate or defective design | Completed |  | On inspection of asset labeling during a VAP at Victoria Dock Portal it was noted that the barcode scan was resulting in only the Equipment Number, whereas the Serial Number is also required.
| 05SY - Systemwide | Cxxx-NCR-000307 | NCR | DOO Internal cabinet wiring at CUH |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-07-05 | 2018-07-03 10:17 | -2 | 2018-06-21 16:46 | Communications and Control Systems - Driver only Operation CCTV | 500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | The internal cabinet wiring for the DOO terminations on cab 731U4 currently has two blade terminals used in the same termination point and not double bootlace ferrules. When comparing this to the second DOO cab 606U1 double bootlace ferrules have been used but the wiring configuration differs between cabinets. Wiring should be the same format across the DOO cabinets with only a single crimp used in each terminal
| 05SY - Systemwide | Cxxx-NCR-000308 | NCR | Slow progress with returns of asset labelling information |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-11-30 | 2018-12-07 15:16 | 7 | 2018-06-26 17:54 | Communications and Control Systems - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper handling of material | Completed |  | Crossrail have requested the raising of an NCR as a result of slow progress in returning asset labeling information (i.e. confirmation via ADCS sheets that asset label has been installed).
| 05SY - Systemwide | Cxxx-NCR-000309 | NCR | DOO Leaky Feeder Cable - CUH |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-08-31 | 2018-08-31 14:04 | 0 | 2018-06-27 09:04 | Communications and Control Systems - Driver only Operation CCTV | 5000 |  | Material | Rework | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The Leaky Feeder cable that has been installed at Custom House Station is a cable designed for a section 12 (sub surface) station.
| 05SY - Systemwide | Cxxx-NCR-000310 | NCR | Missing cable entry blanks PMP |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-08-01 | 2018-07-27 08:45 | -5 | 2018-07-04 10:34 | Communications and Control Systems | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Error by manufacturer in shipping or marking | Completed |  | The cabs in the CER where we have no cables going into the top of the cab are missing the cable entry blanks. With this in mind we have the potential for dust ingress
| 05SY - Systemwide | Cxxx-NCR-000311 | NCR | Cabinet hardware missing. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-09-14 | 2018-09-14 14:33 | 0 | 2018-07-06 08:31 | Communications and Control Systems - General | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During site visits to CERs it was noted that Rittal Sealing Modules not installed to the top of __ cabinets. With the modules not being installed, the cabinet doesn't maintain its IP rating and there is potential for failure of equipment due to dust ingress.
| 05SY - Systemwide | Cxxx-NCR-000312 | NCR | Fan switches not located suitably to allow fan operation when door is closed |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-08-31 | 2018-08-24 16:18 | -7 | 2018-07-11 11:27 | Communications and Control Systems - General | 500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | It has been noted on three sites so far PAD-02-CAB-731U2, FAR-01-CAB-2731U9 and WOO-05-CAB-731U5 that one of the two door contacts are located in such a way that when the door is closed it appears the switch pin is going through the door frame spacing hole and not being activated.
| 05SY - Systemwide | Cxxx-NCR-000313 | NCR | VDP camera back plate corrosion |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-08-22 | 2018-08-31 13:56 | 9 | 2018-07-11 12:02 | Communications and Control Systems - CCTV | 500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On Inspection With the quality team it was spotted that the back plate the camera is fixed to at track level looks to have corrosion.
| 05SY - Systemwide | Cxxx-NCR-000314 | NCR | Incorrect labelling installed on CCTV at Victoria Dock Portal Trackside |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-08-31 | 2018-08-31 14:07 | 0 | 2018-07-17 08:55 | Communications and Control Systems - CCTV | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | At Victoria Dock Portal Track side, The white Asset label has been installed on the body on the Camera.Not as detailed within the CCTV Installation Guidance and Procedures Cxxx-SMN-R3-GPD-CR001-50010 Revision 3.0 Section 3.1.2 which states that White Asset tag label is fixed adjacent the equipment installed. it is noted that the Yellow Equipment Label had not been installed at the location.
| 05SY - Systemwide | Cxxx-NCR-000315 | NCR | Damaged __ Cable Asset IDs and Cable Ties not trimmed correctly at Victoria Dock portal Trackside FOSCs |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-08-31 | 2018-08-31 14:11 | 0 | 2018-07-17 08:59 | Communications and Control Systems - Fibre Optic Network | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | At Victoria Dock Portal Trackside it is noted at VDP-01-CAB- FOSCU1 and VDP-01-CAB- FOSCU2 there are a number of damaged and illegible Cable asset IDs installed at the cabinet entry point, and some cable ties have not been trimmed back correctly as detailed in Installation Procedures and Guidelines – Structured Cabling Document Number Cxxx-SMN-R3-GPD-CR001-50017 Revision 3.0 section 13 which states Cable ties shall be the necessary size as to secure the tag around the diameter of the cable. Cable ties shall not be over tightened resulting damage or distortion to the cable or sheath. Cable ties shall be trimmed flush following installation ensuring no protruding sharp edges remain
| 05SY - Systemwide | Cxxx-NCR-000316 | NCR | Incorrect Cable Asset ID fitted to SCADA Cable at VDP Trackside |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-09-22 | 2018-09-12 13:03 | -10 | 2018-07-17 09:10 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | At Cabinet VDP-TR-CAB-101NEU1, it was found that the 2 pair cable had the incorrect cable asset ID label attached, It reads CR503-RAD-00302, This should be CR503-RAD-00303 as detailed on SCADA I/O Cable and Wiring Schedule Cxxx-SMN-R3-LST-CR144_PT003-50009.Rev 10.0
| 05SY - Systemwide | Cxxx-NCR-000318 | NCR | Cable Asset IDs not installed to SCADA cabling exiting the high level cable ducts at VDP |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-08-14 | 2018-08-17 15:56 | 3 | 2018-07-17 09:24 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | At VDP Trackside SCADA cabling exits cable ducts at highlevel to supply trackside systems. At the transition point between the cable ducting and the trackside CMS cable asset IDs have not been installed as detailed in Installation Procedures and Guidelines-Structural cabling Cxxx-SMN-R3-GPD-CR001-50017 Rev 2.0 Section 13 which states that Asset Tag Labels will be installed on cables On either side of any bulkhead or wall that the cable passes through;(Within 500mm entry/exit)
| 05SY - Systemwide | Cxxx-NCR-000319 | NCR | PLP Radio Cable damaged |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-10-15 | 2018-10-16 08:30 | 1 | 2018-07-16 09:05 | Communications and Control Systems - Radio | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Whist installing cables at PLP we have came across two damaged Radio cables. FD001,FD028 these cables have been damaged by the CMS lip on an internal bend
| 05SY - Systemwide | Cxxx-NCR-000320 | NCR | Earth Bonding of Type 6C enclosures |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-12-28 | 2019-04-08 13:09 | 101 | 2018-07-17 09:51 | Communications and Control Systems - General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | At VDP the Type 6C enclosures have been bonded from the internal back plate to the local containment using 10mm2 earth cable and not 35mm2 to an earth bar. The Type 6C enclosure also requires an external earth lug as the earth bond must be visible without opening the enclosure.
| 05SY - Systemwide | Cxxx-NCR-000321 | NCR | VDP cabinet CR503-CAB-00016 asset label barcode unreadable when scanned. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-09-30 | 2018-10-03 12:08 | 3 | 2018-07-18 07:09 | Communications and Control Systems - General | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | CR503-CAB-00016 located near trackside was found to have the barcode unreadable when scanned. The label isn't compliant with Asset Identification Standard CRL1-XRL-O6-STD-CR001-00031
| 05SY - Systemwide | Cxxx-NCR-000322 | NCR | Damaged door contact junction box at North Woolwich Portal |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-08-01 | 2018-08-07 10:43 | 6 | 2018-07-18 13:12 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | It has been noted that the Door Contact Junction Box for Main Entrance Door MD03 is damaged, this has resulted in the IP rating of the JB being compromised and has resulted in water ingress.
| 05SY - Systemwide | Cxxx-NCR-000323 | NCR | Fan casing touching finger trunking when Door is closed |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-11-29 | 2018-11-28 10:27 | -1 | 2018-07-19 11:33 | Communications and Control Systems - General | 500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | As a result of the fan being turned around in WHI-04-CAB-731U5 to suck hot air out some of the case mouldings now touch the finger trunking below the main consumer unit when the door is closed
| 05SY - Systemwide | Cxxx-NCR-000324 | NCR | Incorrect SCADA cable asset ID's at Victoria Dock Portal. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-09-06 | 2018-09-14 11:09 | 8 | 2018-07-23 11:04 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | At Mile End park 6 x SCADA Cable asset IDs were found to have the incorrect or incomplete asset information on their associated label after checks were carried out to SCADA I/O Cable and Wiring Schedule Cxxx-SMN-R3-LST-CR094_SH006-50014 current Rev 10.0. On Cables CR513-CCC-00085, 00090 & 00134 asset line 2 differed from that shown on the current Cable and Wiring Schedule On Cables CR513-CCC-00055, 00065, & 00074 asset line 2 had incomplete information which is detailed on the current Cable and Wiring Schedule
| 05SY - Systemwide | Cxxx-NCR-000325 | NCR | Flaking paint on telephone bases PLU-ABW |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-10-19 | 2018-11-09 07:20 | 21 | 2018-07-20 08:04 | Communications and Control Systems - Telephony | 500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | During a survey 19th July by __ and Crossrail it was noted that the paint on the Passcomm bases of the telephones has flaked off. Attached are photos of RTL-50101, RTL-5099, and RTL-50097
| 05SY - Systemwide | Cxxx-NCR-000326 | NCR | MEP - Incorrect asset labels installed on earth cables installed between earth bar & cabinets in CER. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-09-06 | 2018-09-14 11:10 | 8 | 2018-07-23 14:06 | Communications and Control Systems - Power Supplies | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Within the CER Room there are 5 x 10mm Earth conductors on the Earth bar which bond to Cabinets 005BU1, U2, U3, U4, & U5. The Cable Asset labels have the incorrect asset information, they should be a 4 line Asset Label as detailed in Cxxx-SMN-R3-LST-CR094_SH006-50012 current Rev 2.0. Also awaiting detail for the 230v mains isolators to label 230v cables between isolator and cabinets within the CER.
| 05SY - Systemwide | Cxxx-NCR-000327 | NCR | Mile End Park asset labels not readable on cabinets MEP.005BU3 & MEP.005BU5 |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-09-30 | 2018-10-03 12:12 | 3 | 2018-07-24 11:10 | Communications and Control Systems - General | 500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During desktop exercise for surveillance report QS72 Mile End Park Asset Labelling (Cxxx-SMN-R3-RGN-CR094_SH006-50017) it was found that cabinets MEP.005BU3 & MEP.005BU5 asset label barcodes are unreadable when scanned with I-nigma.
| 05SY - Systemwide | Cxxx-NCR-000328 | NCR | Temporary Earth connections for radio cables within tunnels |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-12-14 | 2018-12-12 11:16 | -2 | 2018-07-26 14:46 | Communications and Control Systems - Radio | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Within the Cxxx earthing design there are insufficient earth connections provided for the radio leaky feeder. To enable earthing of the radio cables [for safety during HV energisation] the Cxxx installed earth cables have been temporarily connected to either spare or insulator lugs on Cxxx earth bars, in many cases there are multiple connections to one lug. Cxxx have received Cxxx-PMI-00546 to install additional earth bars at specified locations in Zones 1 & 2 to provide the extra connectivity required.
| 05SY - Systemwide | Cxxx-NCR-000329 | NCR | NWP Damaged radio cable |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-08-23 | 2018-08-07 10:45 | -16 | 2018-07-26 06:39 | Communications and Control Systems - Radio | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | When installing the 7/8" from CER down to track our sub contractor damaged one of them going down to the West Bound FD2604
| 05SY - Systemwide | Cxxx-NCR-000330 | NCR | TCR DOO incorrect bolt type |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-10-30 | 2018-10-31 13:49 | 1 | 2018-07-30 12:58 | Communications and Control Systems - Driver only Operation CCTV | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | DOO cables installed along the track have the incorrect bolts fitted. The bolt heads protrude out of the clip preventing it from closing fully
| 05SY - Systemwide | Cxxx-NCR-000331 | NCR | Fisher St RTU cabinet energised without going through IRN process. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-09-10 | 2018-09-11 10:12 | 1 | 2018-07-31 12:05 | Communications and Control Systems - Power Supplies | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | FIS-03-CAB-3731U4 RTU 230v cabinet has been energised without going through the IRN process. The cabinet was excluded from the last IRN and was supposed to be on the outstanding works register, it wasn't included. This doesn't comply with Works Information Volume 2B – Part 28 – Testing and Commissioning Process CRL1-XRL-V3-XWI-CR001-50131 28.2.2.2.1 Phase 2.1 Intermediate Static Tests per Sub-System Satisfactory completion of this phase of testing by the Contractor results in the issue of the IRN for the individual Commissioning Lot.
| 05SY - Systemwide | Cxxx-NCR-000332 | NCR | Fisher St - Rittal Sealing Modules not installed in top of cabinets in CER. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-10-15 | 2018-10-17 10:32 | 2 | 2018-07-31 12:09 | Communications and Control Systems - General | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During IRN visit to Fisher St it was noted that Rittal Sealing Modules not installed in top of cabinets in CER 1. With the modules not being installed, the cabinet doesn't maintain its IP rating and there is potential for failure of equipment due to dust ingress.
| 05SY - Systemwide | Cxxx-NCR-000333 | NCR | Fisher St RTU - Incorrect orientation of red blade crimps. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-10-15 | 2018-10-10 14:35 | -5 | 2018-07-31 13:33 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | During IRN visit for SCADA cabling it was found that red blade crimps had been installed in different orientations at RTU cabinet FIS-03-CAB-3731U4.
| 05SY - Systemwide | Cxxx-NCR-000334 | NCR | Fisher St - Insufficient capacity within cable trunking for associated SCADA cables into |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-10-15 | 2018-10-10 12:01 | -5 | 2018-07-31 16:15 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | There is insufficient capacity within the cable trunking that is installed as the primary route for RTU cabinet FIS-03-CAB-3731U4.
| 05SY - Systemwide | Cxxx-NCR-000335 | NCR | Limmo - Rittal Sealing Modules not installed in top of cabinets in CER. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-10-15 | 2018-10-09 11:47 | -6 | 2018-07-31 14:18 | Communications and Control Systems - General | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Inadequate/insufficient tooling. | Completed |  | During IRN visit to Limmo it was noted that Rittal Sealing Modules not installed in top of cabinets in the CER. With the modules not being installed, the cabinet doesn't maintain its IP rating and there is potential for failure of equipment due to dust ingress.
| 05SY - Systemwide | Cxxx-NCR-000336 | NCR | Limmo - RADIO cables installed and terminated in front of fibre patch panels within the cabinet. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-12-15 | 2018-12-18 09:32 | 3 | 2018-07-31 15:53 | Communications and Control Systems - Radio | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | At Limmo Shaft within cabinet LIP-01-CAB-B19EU3 the radio cabling has been dressed and terminated; the cables have been installed in front of the __ patch panel impeding future access to the cassette.
| 05SY - Systemwide | Cxxx-NCR-000337 | NCR | Plumstead Portal Damaged Cat 6a Camera cable |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-12-31 | 2018-10-22 12:16 | -70 | 2018-07-31 10:36 | Communications and Control Systems - CCTV | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During camera cable testing it has been noted at Plumstead Portal that the Cat 6a cable to camera PLP-00-CAM-9203 was damaged 13.9M from the CER. The damage was located within the trunking.
| 05SY - Systemwide | Cxxx-NCR-000338 | NCR | Cxxx Unmonitored doors at Whitechapel station |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-12-31 | 2018-11-30 12:49 | -31 | 2018-08-01 13:13 | Communications and Control Systems - Station Management System | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | Omission / exclusion of monitored doors for __ operations at Whitechapel station
| 05SY - Systemwide | Cxxx-NCR-000339 | NCR | Un-protected Radio connector at VDP Cabinet VDP-00-CAB-1733U2 |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-09-17 | 2018-09-20 06:57 | 3 | 2018-08-07 16:31 | Communications and Control Systems - Radio | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | During a site visit to Victoria Dock Portal CER it was noted that within Cabinet VDP-00-CAB-1733U2 Radio cable CR503-RAD-00016 had been disconnected from its termination point and was left with the cable end lying unprotected without a protection cap fitted as detailed Installation Procedures and Guidelines - Private Mobile Radio Radiating Infrastructure Document Number Cxxx-SMN-R3-GPD-CR001-50023 Revision 4.0 Appendix C
| 05SY - Systemwide | Cxxx-NCR-000340 | NCR | FIS Radio Labels Not Installed At IRN |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-10-22 | 2018-10-26 14:59 | 4 | 2018-08-03 12:57 | Communications and Control Systems - Radio | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper storage of material | Completed |  | Permanent radio asset and cable labels not installed at time of IRN of GSM-R Part A. Temporary labels installed at all required locations in the interim.
| 05SY - Systemwide | Cxxx-NCR-000341 | NCR | Damaged DOO Cable at CUH |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-09-03 | 2018-09-10 12:04 | 7 | 2018-08-06 11:34 | Communications and Control Systems - Driver only Operation CCTV | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | DOO leaky feeder cable at Custom House has been damaged on the drum/while being drummed. The EB cable has a small kink approximately 4m from the start and a larger dent (attached) approximate 5m from the start. The WB cable has a small kink either end of the cable. Both cables have multiple scuff marks. Damage to the cable was not visible until the cable had been pulled from the drum. Cables have been installed awaiting testing on site.
| 05SY - Systemwide | Cxxx-NCR-000342 | NCR | At WPA Incorrect Information has been issued on 6 x Minor Electrical Installation Works Certificates |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-09-17 | 2018-09-17 14:22 | 0 | 2018-08-07 16:15 | Communications and Control Systems - Power Supplies | 500 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Minor Electrical Installation work certificate Nos IMN4/0911142, 43, 44, 45, 46, & 47 have been issued by Coral with the following issues. 1). Part 1 details the date minor works completed as 31/07/2018. Part 4 details the results of the inspection and testing was reviewed by the Qualified Supervisor on 30.05.2018 2). Part 2 provides details of RCD BN EN 61008 RCD with I^n 100mA. The installation covered in these Certificates does not have this RCD installed. 3). Part 2 gives the detail of the Maximum Zs permittedby BS 7671 as 500 Ohms, this is not consistent with the information provided on the Tier 1 Electrical Installation Certificate ICN4/0552047 which states 10.93 Ohms for 2Amp Type C BS EN 60898 __ 4). Part 3 details the calculated value of Zs when the Information provided by the Tier 1 Electrical Installation Certificate ICN4/0552047 is added to the circuit measured R1 + R2 value. In each instance the calculated value is excessive for the information provided. 5).The supply circuit way detail and Cabinet ID provided in Part 1 is not aligned with the information provided by the Tier 1 Electrical Installation Certificate ICN4/0552047
| 05SY - Systemwide | Cxxx-NCR-000343 | NCR | At Connaught CER Cabinet COT-00-CAB-1731U1 there are broken MD45 Modules |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-11-30 | 2018-12-03 13:16 | 3 | 2018-08-14 15:03 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Within Cabinet COT-00-CAB-1731U1 there are 4 No damaged MD45 Modules. Serial Nos SN-00087, SN-00073, SN-00059, SN-00075. Quality Spotter 107 (attached) has been raised.
| 05SY - Systemwide | Cxxx-NCR-000344 | NCR | PLP Incorrect Information Provided On a Minor Works NIC Cert |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-10-15 | 2018-10-03 10:13 | -12 | 2018-08-10 08:31 | Communications and Control Systems - Power Supplies | 500 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | On Inspect of an NIC Cert been filled out by our subcontractor we highlighted that that the R1+R2 value provided was way to high for the length and the spec of the cable and was not inline with the maximum ZS value.
| 05SY - Systemwide | Cxxx-NCR-000345 | NCR | Plumstead Portal - Internal 230v Distribution Board cover plate found to be removed whilst live. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-09-17 | 2018-08-30 15:41 | -18 | 2018-08-14 15:52 | Communications and Control Systems - Power Supplies | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | At Plumstead Portal CER within Cabinet PLP-01-CAB-1731U1 the internal cabinet distribution board cover was found to be removed with the earth fly lead disconnected from the DB cover plate. The Distribution Board was in a live state with the internal live components exposed to possible Electric Shock.
| 05SY - Systemwide | Cxxx-NCR-000346 | NCR | Custom House DOO Leaky Feeder Clips installed trackside are expanding when the temperature rises. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-11-08 | 2018-11-09 10:15 | 1 | 2018-08-15 17:40 | Communications and Control Systems - Driver only Operation CCTV | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | At CUH Trackside east and West bounds the DOO platform leaky feeder cable has been installed along the platform edge position fixed with Clic 28 type cable clips. On the West Bound side which is predominately within the Sun all day the cable clip locking mechanism is failing possibly due to heat exposure and allowing in some cases the cable to drop when fully opened and in other cases allowing the cable to twist from its intended fixed plane when partially opened.
| 05SY - Systemwide | Cxxx-NCR-000347 | NCR | TCR PSD SCADA cable incorrectly routed to PSD Header Switch |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-10-26 | 2018-10-24 12:22 | -2 | 2018-08-16 10:42 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | One SCADA CAT6a cable between Cxxx PSD Controller and Cxxx CDN is incorrectly routed to a PSD Header switch, this cable bridges Station and Traction Earth systems which does not comply with the Earthing and Bonding Strategy. One PSD cable is routed into Hydrant cabinet CDN switches and overfilling the switch to not leave the required 20% spare to comply with the works information.
| 05SY - Systemwide | Cxxx-NCR-000348 | NCR | Inadequate process for definition of above ground radio coverage |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-03-31 | 2019-03-27 18:08 | -4 | 2018-08-16 10:12 | Communications and Control Systems - Radio | 500 |  | Planning | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | This NCR is raised further to Cxxx-PMC-07084 and Cxxx-CCM-10578. It is apparent there is an inadequate process to determine the coverage requirements for above ground areas. This has resulted in areas which may require coverage not being included within the current design.
| 05SY - Systemwide | Cxxx-NCR-000349 | NCR | Radio OMU Faulty/Damaged Card |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-09-30 | 2018-08-31 13:35 | -30 | 2018-08-16 12:34 | Communications and Control Systems - Radio | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | OMU card found with dirty fibre port and unable to successfully clean.
| 05SY - Systemwide | Cxxx-NCR-000350 | NCR | CUH PHP Installation - Damaged Panel |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-11-16 | 2018-11-19 09:01 | 3 | 2018-08-22 16:58 | Communications and Control Systems - Telephony | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | PHP Ref: CUH-11-PHP-01102 was installed to a pre-fabricated glass panel in the concourse area. Standard 10mm fixings where used to affix the PHP to the panel and upon installing the 3rd fixing the screen shattered in situ. The PHP was then removed and reported directly to Cxxx. (Note: the screen remained intact as a laminate type material retained the glass) A picture of the damaged panel with PHP removed and initial email correspondence with Cxxx attached for reference.
| 05SY - Systemwide | Cxxx-NCR-000351 | NCR | Isolation of earth connections at earth zone boundaries |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-11-30 | 2019-12-09 17:45 | 9 | 2018-08-24 14:25 | Communications and Control Systems | 500 |  | Planning | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Feedback from site has highlighted that installations are going ahead not in conformance with the Cxxx Earthing and Bonding Specification. In parallel, discussions are on-going to relax the requirements for isolation as this will make the installation more "standard" and therefore familiar to maintainers. This NCR will be used to track the outcome of these discussions.
| 05SY - Systemwide | Cxxx-NCR-000352 | NCR | Stepney Green Radio Cable Damage Found During Testing |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-09-22 | 2018-09-12 14:26 | -10 | 2018-08-29 11:33 | Communications and Control Systems - Radio | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | Damage found on radio cable FD2334 during testing
| 05SY - Systemwide | Cxxx-NCR-000353 | NCR | Plumstead Portal Cabinet Damage PLP-01-CAB-1731U1 |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-10-26 | 2018-10-29 14:25 | 3 | 2018-08-29 16:41 | Communications and Control Systems - General | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | PLP-01-CAB-1731U1 has 5 x missing fixings on the external side panel. The front cabinet door opening mechanism is loose and the internal document holder has been detached from the inside of the door. A length of finger trunking lid is of the incorrect type and was cable tied on, and where there has been a reduction in the left hand trunking vertical drop the trunking lid requires to be cut back to suit the revised trunking length.
| 05SY - Systemwide | Cxxx-NCR-000354 | NCR | Stepney Green Shaft - Radio schematic uncontrolled document. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-09-26 | 2018-10-04 07:00 | 8 | 2018-08-29 17:50 | Communications and Control Systems - Radio | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | IRN for GSM-R Feeder Cables ComLot RAD-__-RAD00-07001 Radio GSM-R (Part A) found that uncontrolled PMR-RI Design Schematic - Cxxx-SMN-R3-DWG-CRG03-50078 Rev 5.0 had been installed against. Rev 4.0 is the current version in eB.
| 05SY - Systemwide | Cxxx-NCR-000355 | NCR | CCTV NVR server delivered to Limmo with damage. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-09-21 | 2018-09-20 13:35 | -1 | 2018-08-30 16:21 | Communications and Control Systems - CCTV | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper handling of material | Completed |  | T&C took delivery at Limmo of multiple CCTV NVR servers which were transported in little to no protection. One server was found with its front panel totally buckled, possibly has been dropped or left unsecure in transit (Coral or Ashby).
| 05SY - Systemwide | Cxxx-NCR-000356 | NCR | Two Westbourne Park cabinets mounted in wrong locations |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-10-31 | 2018-09-26 12:15 | -35 | 2018-08-31 08:09 | Communications and Control Systems - SCADA/Central Management System | 1500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | cabinet 4810/34U1 type 6B3 and cabinet 4810/32U1 type 6B2 have been mounted the wrong way around. 4810/34U1 is where 4810/32U1 is mounted and visa versa
| 05SY - Systemwide | Cxxx-NCR-000357 | NCR | Fisher St Shaft - Antenna 10 has been installed in wrong location. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-11-17 | 2018-11-13 15:43 | -4 | 2018-09-05 11:59 | Communications and Control Systems - Radio | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Antenna 010 has been installed in wrong location due to the CMS finishing short of final design position at Level B-1.
| 05SY - Systemwide | Cxxx-NCR-000358 | NCR | Limmo - Antenna damage. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-12-15 | 2018-12-18 09:17 | 3 | 2018-09-10 11:18 | Communications and Control Systems - Radio | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | At LIMMO B1 south corridor it was noted that the Antenna was broken from its bracket mounting plate and was suspended on its cable.
| 05SY - Systemwide | Cxxx-NCR-000360 | NCR | COT Telephony over length cable |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-11-23 | 2018-11-29 14:45 | 6 | 2018-09-10 12:36 | Communications and Control Systems - Telephony | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | COT-00-RTL-10005 cable has been installed. Due to the routing of the cable the as installed length is 150m and the calculated design length was 85m. Reason being was the Ducting routes had been changed by the T1
| 05SY - Systemwide | Cxxx-NCR-000361 | NCR | Incorrect information on Cable schedule |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-10-16 | 2018-10-17 13:39 | 1 | 2018-09-13 13:19 | Communications and Control Systems - Telephony | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | Trackside telephone cables PZ1008A and PZ1009B have been pulled along the eastbound trace. It was not clear that the cables require terminating at Cab WWU1 which is on the west bound. Cables have been pulled short
| 05SY - Systemwide | Cxxx-NCR-000362 | NCR | Fisher St - Damaged Antenna -001 |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-11-03 | 2018-10-31 12:12 | -3 | 2018-09-17 12:27 | Communications and Control Systems - Radio | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | At Fisher Street Ground Floor corridor it was noted that Antenna 001 was broken from its bracket mounting plate and was suspended on its cable, it is suspected the cause was due to being struck by contractors moving tower/access equipment.
| 05SY - Systemwide | Cxxx-NCR-000363 | NCR | Anritsu Test Equipment Calibration |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-10-31 | 2018-10-31 16:58 | 0 | 2018-09-16 08:38 | Communications and Control Systems - Radio | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | An Item of Anritsu test equipment used to test Coaxial Cables in CP's 011 and 012 was out of date. Calibration Certs for ANS331E-M12 Ser No 1223015 have a gap from 04.01.2018 to 17.01.2018 The test Trace example shown in the SAF files was carried out 0n 11.01.2018
| 05SY - Systemwide | Cxxx-NCR-000364 | NCR | Limmo - SCADA Cxxx cabling in marshalling cabinet - Sleeve req on earth core and FCD to be raised. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-12-22 | 2018-12-20 09:06 | -2 | 2018-09-17 13:12 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Insufficient information made available to the worker. | Completed |  | At cabinet B19EU4 it has been noted that cable CR515-CCC-00023 which links to the Tier 1 marshalling cabinet has had its Green/Yellow core no C25 used as detailed in the current SCADA cable termination schedule Cxxx-SMN-R3-LST-CR144_SH011-50004 Rev 5.0 with core ID B1-C (Common).
| 05SY - Systemwide | Cxxx-NCR-000365 | NCR | CUH PHP Screw/ Casing Damage |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-11-30 | 2018-12-07 15:21 | 7 | 2018-09-18 17:09 | Communications and Control Systems - Telephony | 500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | PHP CUH-11-PHP-01101 security pins have been damaged and also the casing around the pins.
| 05SY - Systemwide | Cxxx-NCR-000366 | NCR | Custom House Method Statement - Code 2 status Risk assessment dates haven't changed since Rev 6.0. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-11-12 | 2018-11-22 12:06 | 10 | 2018-09-21 07:36 | Communications and Control Systems - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | Custom House Method Statement Cxxx-SMN-R3-GMS-CR145-50001 Rev 7.0 has Code 2 decal status in eB whilst works have progressed. Risk assessment dates haven't changed since Rev 6.0.
| 05SY - Systemwide | Cxxx-NCR-000367 | NCR | TCR 2X Cat6 BMS AND PSD over 90m |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-01-18 | 2019-01-23 13:01 | 5 | 2018-09-20 12:44 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | We have 2 no cat6 cables that exceed the 90m rule 1 cable is part of BMS Com Lot __-TCR-__00-10020 , with the DAT number N105-DAT-03981 and we have 1 cable that's part of the PSD Com Lot __-TCR-__00-10019 and the DAT number is N105-DAT-03456.
| 05SY - Systemwide | Cxxx-NCR-000368 | NCR | __ - Rittal Sealing Modules not installed in top of cabinets in CER |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-12-21 | 2018-10-10 12:12 | -72 | 2018-09-21 16:09 | Communications and Control Systems - General | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | During IRN visit to Stepney Green it was noted that Rittal Sealing Modules not installed in top of cabinets in CER. With the modules not being installed, the cabinet doesn't maintain its IP rating and there is potential for failure of equipment due to dust ingress.
| 05SY - Systemwide | Cxxx-NCR-000369 | NCR | __ SCADA Conflicting Cable Number |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-10-19 | 2018-10-24 12:46 | 5 | 2018-09-21 17:25 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | It was highlighted that a cable is shown with a different cable number within two documents. 25 core cable CR512-CCC-00138 is correct in __ SCADA cable ad wiring schedule Cxxx-SMN-R3-LST-CR094_SH005-50012 Rev 5.0 but is shown as CR512-CCC-00139 in __ SCADA termination schedule Cxxx-SMN-R3-LST-CR094_SH005-50004 Rev 4.0
| 05SY - Systemwide | Cxxx-NCR-000370 | NCR | 3 x Type 1511Ba cabinets not compliant with BS7671 Requirements for Electrical Installations. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-12-28 | 2018-11-09 11:11 | -49 | 2018-09-25 15:37 | Communications and Control Systems - General | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | 3 No Type 1511Ba cabinets delivered to site haven't got adequate protection on 230v cabinets. Canary Wharf, Custom House and Woolwich. Cabinets should not be energised until the 230v cables have had remedial works carried out.
| 05SY - Systemwide | Cxxx-NCR-000371 | NCR | MD45 unit damaged at PAD-02-CAB-3732U2 |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-11-30 | 2018-12-07 14:37 | 7 | 2018-09-26 13:27 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | MD45 module damaged again after the 2 other modules where replaced back in June under Cxxx-NCR-000288
| 05SY - Systemwide | Cxxx-NCR-000372 | NCR | RVP radio coverage |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-06-30 | 2019-07-04 15:17 | 4 | 2018-10-04 13:05 | Communications and Control Systems - Radio | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | Rendezvous Points (RVPs) radio coverage is omitted from the radio design for Airwave and LFEPA radio systems.
| 05SY - Systemwide | Cxxx-NCR-000373 | NCR | No emergency evacuation routes radio coverage |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-06-30 | 2019-06-28 13:17 | -2 | 2018-10-04 13:15 | Communications and Control Systems - Radio | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Emergency evacuation routes (and the corresponding emergency ingress routes) are omitted from the radio design for Airwave and LFEPA radio systems at SSP locations.
| 05SY - Systemwide | Cxxx-NCR-000374 | NCR | Cxxx Radio Combiners |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-01-15 | 2018-12-11 13:41 | -35 | 2018-10-08 10:50 | Communications and Control Systems - Radio | 2000 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | Incorrect information listed on Supplier data sheets/manuals resulting in poor UL on site.
| 05SY - Systemwide | Cxxx-NCR-000375 | NCR | Ashby - Gaps in HF testing |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-05-06 | 2019-09-15 17:07 | 132 | 2018-10-15 11:16 | Communications and Control Systems - SCADA/Central Management System | 10000 |  | Software | Rework | 2 (6-60k) | Complete | Verification Problems - Inspection points not adequate | Completed |  | During review of performance specification validation matrixes and software quality plan the gaps have been identified in relation to testing of HF factors by factory and site team.
| 05SY - Systemwide | Cxxx-NCR-000376 | NCR | Ashby - CFAT FOR's 3.1.3 |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-05-31 | 2019-08-16 11:56 | 77 | 2018-10-15 15:08 | Communications and Control Systems - SCADA/Central Management System | 5000 |  | Software | Rework | 3 (3-6k) | Complete | Verification Problems - Other | Completed |  | During cFAT for CMS Build 3.1.3 number of issues were identified not previously captured by the iFAT.
| 05SY - Systemwide | Cxxx-NCR-000377 | NCR | Ashby - CFAT FOR's 3.4 |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-05-31 | 2019-08-16 12:06 | 77 | 2018-10-16 16:45 | Communications and Control Systems - SCADA/Central Management System | 5000 |  | Software | Rework | 3 (3-6k) | Complete | Verification Problems - Other | Completed |  | During cFAT for CMS Build 3.4 number of issues were identified not previously captured by the iFAT.
| 05SY - Systemwide | Cxxx-NCR-000378 | NCR | Damaged door handle to __ cabinet FAR-01-CAB-2732U2 WTH CER L-1 |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-01-31 | 2019-12-19 15:38 | -43 | 2019-11-06 12:14 | Communications and Control Systems - Crossrail Data Network | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Damaged door handle to __ cabinet FAR-01-CAB-2732U2. WTH CER. Unable to open the rear cabinet door, Internal spindle lock only spins. Lock mechanism is faulty and will require replacing. See photos attached.
| 05SY - Systemwide | Cxxx-NCR-000379 | NCR | Custom House - Asset label positions not in compliance with install guidelines. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-12-10 | 2018-12-11 10:28 | 1 | 2018-10-17 16:53 | Communications and Control Systems - General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Insufficient information made available to the worker. | Completed |  | Yellow equipment labels have been installed on the camera housings rather than the camera.
| 05SY - Systemwide | Cxxx-NCR-000380 | NCR | Incorrect Asset Data Content at CUH |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-01-31 | 2019-01-08 10:48 | -23 | 2018-10-17 16:43 | Communications and Control Systems - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | An asset information VAP at Custom House station has revealed a number of assets (listed below) which have been allocated to the wrong location, as follows: CR145-CIN-00321 CR145-CIN-00284 CR145-CIN-00286 CR145-CIN-00272 CR145-CIN-00287 CR145-CIN-00318 CR145-CIN-00114 CR145-CIN-00322 CR145-CIN-00283 CR145-CIN-00308 CR145-CIN-00285 CR145-CIN-00319 CR145-CIN-00320 CR145-CAB-00071 CR145-CAB-00078 CR145-CAB-00089 CR145-CIN-00330 CR145-CIN-00294 CR145-CIN-00291
| 05SY - Systemwide | Cxxx-NCR-000381 | NCR | Ashby - Unimplemented __ requirements on software |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-01-07 | 2019-01-28 11:29 | 21 | 2018-10-19 12:23 | Communications and Control Systems - Station Management System | 15000 |  | Software | Rework | 2 (6-60k) | Complete | Design Problem - Other | Completed |  | It was recently identified by CRL that there are __ requirements which are currently not implemented on software. These requirements have been marked as compliant on the design. Examples below; __171 • Requirement stated as “not implemented” by CRL within __ version 3.4.8 (PD/SC) • Requirement marked as “compliant” within complypro • TT-003.2.9.4 does not validate __171 as detailed within complypro. DP stated that this requirement was validated under TT-004.2.45 SIM • SMN (DP) stated there is an open FOR and took an action to provide the number. PMN: no FOR as this requirement was validated. • Review status within complypro shown as “CRL Accepted”. • VV evidence column provides reference to FAC and FAT Report which are placeholders and marked obsolete within eB (captured within comment # 41 for Factory Acceptance Validation and Verification Matrix Cxxx-XRL-R3-XCS-CR001-50819) __093 • Requirement stated as “not implemented” by CRL within __ version 3.4.8 (PD/SC) • Requirement marked as “compliant” within complypro • SMN (JM) stated they required clarification on requirement __093 in that they required CRL to confirm which alarms were “consequential”. No RFI has been raised to date on this. • SMN (DP) stated there is an open FOR and took an action to provide the number. PMN: DP provided reference to [__-6110] stating: “At the minute there is no FOR as there is outstanding work, attached User Story is an example: with relations to existing FORs (5599, 6806, 6805) as an example” • VV evidence column provides reference to FAC and FAT Report which are placeholders and marked obsolete within eB. (captured within comment # 41 for Factory Acceptance Validation and Verification Matrix Cxxx-XRL-R3-XCS-CR001-50819) • CRL (PD) stated that TT-003.1.9 does not satisfy the validation of the requirement (PMN) • Review status within complypro shown as “CRL Accepted”. __095a • Requirement stated as “not compliant” by CRL within __ version 3.4.8 (PD/SC) • Requirement marked as “compliant” within complypro • SMN (JM)/ CRL (PD) discussed requirement. CRL (PD) stated this should read “partial compliance” at this stage as the requirement for hierarchical menu of systems and component items was not available. SMN spoke of the impact of changing the software at this stage of the programme. • VV evidence column provides reference to FAC and FAT Report which are placeholders and marked obsolete within eB. (captured within comment # 41 for Factory Acceptance Validation and Verification Matrix Cxxx-XRL-R3-XCS-CR001-50819) • CRL (PD) stated that TT-004.1.1 does not satisfy the validation of the requirement (PMN) • Review status within complypro shown as “CRL Accepted”.
| 05SY - Systemwide | Cxxx-NCR-000382 | NCR | Software Compliance of Requirements |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-04-29 | 2019-06-21 07:14 | 53 | 2018-10-19 12:28 | Communications and Control Systems - Station Management System | 15000 |  | Software | Rework | 2 (6-60k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Further to Cxxx-NCR-000381, it has recently been identified by CRL that the process that is currently in use within Cxxx for implementation of requirements are not robust enough to ensure that all requirements are designed and get implemented on the software.
| 05SY - Systemwide | Cxxx-NCR-000383 | NCR | Inadequate internal reviews and deficiencies on Test Scripts to satisfy requirements |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-01-17 | 2019-02-08 10:18 | 22 | 2018-10-19 12:31 | Communications and Control Systems - General | 15000 |  | Software | Rework | 2 (6-60k) | Complete | Design Problem - Other | Completed |  | Further to Cxxx-NCR000382, it is recently identified by CRL that the process that currently in use within Cxxx for verification of requirements are not robust enough to ensure the correct implementation of requirements on the software.
| 05SY - Systemwide | Cxxx-NCR-000384 | NCR | Inaccurate evidence on Verification and Validation (V&V) matrices |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-02-04 | 2019-02-22 14:15 | 18 | 2018-10-19 12:36 | Communications and Control Systems - Station Management System | 5000 |  | Software | Rework | 3 (3-6k) | Complete | Verification Problems - Other | Completed |  | Further to Cxxx-NCR-000383, it is recently identified by CRL that the process that currently in use within Cxxx for documenting V&V evidences are inaccurate and not robust enough.
| 05SY - Systemwide | Cxxx-NCR-000385 | NCR | Incorrect DOO Camera asset labelling. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-01-11 | 2019-01-31 09:07 | 20 | 2018-11-02 08:47 | Communications and Control Systems - Driver only Operation CCTV | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | During a recent IRN visit at CUH it was note that the Yellow DOO Camera Component Asset IDs had been fitted to the camera housing and not attached to their individual associated component.
| 05SY - Systemwide | Cxxx-NCR-000388 | NCR | FIS MS146 Rework |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-11-23 | 2018-11-29 08:38 | 6 | 2018-10-19 14:33 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | MS146 cabinets installed as per Fisher St design. When trackside team came to install 18c cable from the trace, it was highlighted that the two MS146 cabinets had different names to what was expected from the trace and therefore meant the eastbound and westbound earth switches were cabled back to the incorrect HV RTU's. Cables have been replaced to align with trace information and all works have now been completed.
| 05SY - Systemwide | Cxxx-NCR-000389 | NCR | FIS CCTV Labels Missing |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-11-23 | 2018-12-05 10:22 | 12 | 2018-10-19 15:03 | Communications and Control Systems - CCTV | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Labels previously supplied have either been misplaced or design information updated and so not installed at time of IRN
| 05SY - Systemwide | Cxxx-NCR-000390 | NCR | VDP 24V and 240V single cables grouped together Type 5A Cab |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-01-31 | 2019-02-01 10:21 | 1 | 2018-10-22 14:22 | Communications and Control Systems - General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Type 5A cabinet that operates the keypad entry have both the 24V cables and the 240V feed grouped together and not protected by any sheath. The 240 voltage will need to separated from the 24V. A new length of sheathed twin and earth will be required from the PDU/terminals to the PSU and will not be run with the 24v
| 05SY - Systemwide | Cxxx-NCR-000391 | NCR | Royal Oak Portal - __ cables haven't gone through the IRN process. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-12-10 | 2018-11-12 10:29 | -28 | 2018-10-24 11:44 | Communications and Control Systems - General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Not Defined | Completed |  | Royal Oak Portal - __ cables between FOSC 1 & 2 and CER haven't gone through the IRN process.
| 05SY - Systemwide | Cxxx-NCR-000392 | NCR | Earthing and Bonding |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-03-09 | 2019-03-25 12:10 | 16 | 2018-10-24 14:38 | Communications and Control Systems - General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The earth bond conductor between traction earth and cabinet PMP-02-CAB-3732U2 is shown in Cable & Wiring Schedule Cxxx-SMN-R3-LST-CR094_PT002-50002 Rev 3.0 as 6mm also appears in Cable & Wiring Schedule Cxxx-SMN-R3-LST-CR094_PT002-50004 Rev 2.0 as a 10mm. A 10mm csa earth cable has been installed and terminated from the cabinet to the adjacent containment as specified in Cxxx-SMN-R3-LST-CR094_PT002-50004 which is not in compliance with the Cxxx E&B strategy requirement of 35mm, the FOSCs are also incorrectly bonded to the adjacent containment. The requirement for bonding any Cxxx trackside cabinet to traction earth is a 35mm csa conductor and not 6mm csa as detailed on the Cable and Wiring Schedule.
| 05SY - Systemwide | Cxxx-NCR-000393 | NCR | PAVA Cables under length |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-11-21 | 2018-11-22 08:25 | 1 | 2018-10-24 15:04 | Communications and Control Systems - Public Address Systems | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | 2 No H1000 Cables CR145-RAD-00064, CR145-RAD-00065 for the whip Antennas down to the SAP at GL20 was found to be under length for the intended design route of the cables
| 05SY - Systemwide | Cxxx-NCR-000394 | NCR | PLP Damaged 25 core scada cable |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-11-21 | 2018-10-29 14:22 | -23 | 2018-10-24 16:08 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Site team came across a damaged 25 core scada cable which is for the EB TLPPs (CR505-CCC-00040)
| 05SY - Systemwide | Cxxx-NCR-000395 | NCR | CUH 12 core Fibre Damaged |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-12-11 | 2018-11-25 08:31 | -16 | 2018-11-04 21:55 | Communications and Control Systems - Fibre Optic Network | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Fibre team reported that 12 core fibre from SCER to the DC2 cab is showing as damaged once they tested the cable. Cable ID is CR145-DAT-01241
| 05SY - Systemwide | Cxxx-NCR-000396 | NCR | PLP Damaged Radio Cable |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-12-10 | 2018-11-20 08:40 | -20 | 2018-11-06 16:23 | Communications and Control Systems - Radio | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | FD2807B has failed on High Band test. The cable will have to be replaced.
| 05SY - Systemwide | Cxxx-NCR-000397 | NCR | Scada Reworks at PMP |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-12-04 | 2018-11-12 09:37 | -22 | 2018-11-06 16:52 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | On site inspection it was seen that scada works hadn't been completed as they had originally declared
| 05SY - Systemwide | Cxxx-NCR-000398 | NCR | BUCF Cable Schedule |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-02-23 | 2019-03-01 11:42 | 6 | 2018-11-07 18:06 | Communications and Control Systems - General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | Installation of CER Cabinet supplies progressed without an approved Cable schedule being available. The ComLot definition document for the CER cabinets has been redlined and attached detailing cables installed. This will also be submitted to support an FCD in the production of an as installed cable schedule.
| 05SY - Systemwide | Cxxx-NCR-000400 | NCR | ROP Marshalling terminations |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-12-31 | 2018-12-21 10:51 | -10 | 2018-11-09 08:26 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Use of two crimp lugs in one terminal instead of a single double crimp
| 05SY - Systemwide | Cxxx-NCR-000401 | NCR | Failed cable tests |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-12-31 | 2018-12-21 10:53 | -10 | 2018-11-09 08:30 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The following cables failed resistance tests: CR501-CCC-00073 CR501-CCC-00074 CR501-CCC-00076
| 05SY - Systemwide | Cxxx-NCR-000402 | NCR | Crosspassage 1 - Incomplete works signed off against ITP. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-11-26 | 2018-12-07 15:32 | 11 | 2018-11-12 13:23 | Communications and Control Systems - Power Supplies | 500 |  | Incomplete Works | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | A recent site visit for IRN at CP1 identified that 70m2 earth cable installation between earth bars was incomplete. It was found that one end of the 70m2 earth cable was coiled on the cable tray above the destination point. Inspections had been carried out as per the Site Inspection & Test Plan with the Earth Cable Installation Inspection and Test Checksheet being signed off as satisfactory. Inspections carried out failed to highlight that the cable installation was incomplete. In fact, the Checksheet was signed off for “Cable terminated correctly at source and destination and Lugs & Crimps secure”.
| 05SY - Systemwide | Cxxx-NCR-000403 | NCR | Custom House - DOO cable cleats installed without an approved MCR. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-12-21 | 2018-12-20 09:14 | -1 | 2018-11-14 17:44 | Communications and Control Systems - Driver only Operation CCTV | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | Custom House - DOO cable cleats installed without an approved MCR. New DOO cable cleats had to be installed due to previously installed clips (MCR approved) expanding on the west bound side which is predominately within the sun all day. Site Inspection and Test Plan - Equipment Installation Cxxx-SMN-R3-ITP-CR001-50023 Rev 3.0 Section 2.1 Equipment / Components Approval states that MCR has to be at Code 1 in eB prior to procurement.
| 05SY - Systemwide | Cxxx-NCR-000404 | NCR | PLP Telephony Cable over Length |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-12-17 | 2018-12-21 15:43 | 4 | 2018-11-19 14:19 | Communications and Control Systems - Radio | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Telephony cable CR505-TEL-00064 has failed due to the cable being over length measuring at 114.3 m
| 05SY - Systemwide | Cxxx-NCR-000406 | NCR | VERINT CAMERA HEATER/NON HEATER |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-02-28 | 2019-02-28 17:16 | 0 | 2018-11-20 13:08 | Communications and Control Systems - CCTV | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Material/Preservation Problems - Lack or improper material identification and traceability | Completed |  | It has been identified that Internal and external cameras (with and without heaters) have been installed incorrectly across several Sites which does not align within current site specific application designs and/or equipment schedules.
| 05SY - Systemwide | Cxxx-NCR-000407 | NCR | BUCF - CDN CABLE SCHEDULE |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-02-23 | 2019-03-01 11:46 | 6 | 2018-11-21 16:49 | Communications and Control Systems - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The CAT6a interconnecting cables installed @ the BUCF have been completed without an approved cable schedule. A site cable schedule has been created to capture As-Installed information and is attached for reference.
| 05SY - Systemwide | Cxxx-NCR-000408 | NCR | BUCF - SCADA DESIGN |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-01-13 | 2019-01-08 10:28 | -5 | 2018-11-21 17:00 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The SCADA installation has been completed at BUCF without an approved cable or termination schedule. A site termination schedule has been created to capture connections required inline with alarms presented at the BMS panel and cabinet fans. (A copy attached for reference)
| 05SY - Systemwide | Cxxx-NCR-000409 | NCR | Test & Commissioning Competency Matrix not up to date. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-02-19 | 2019-03-01 11:02 | 10 | 2018-11-29 12:58 | Communications and Control Systems - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Quality Surveillance Report QS75 – Test & Commissioning - Review of the Competency Matrix in eB & __ Cxxx server found that Teodor Cordtas hasn’t been included. This requires a refresh to include up to date T&C personnel as per requirements of Cxxx Test & Commissioning Plan Section 4.6 Competency.
| 05SY - Systemwide | Cxxx-NCR-000410 | NCR | PMP Failed Radio Cables |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-12-23 | 2018-11-28 08:41 | -25 | 2018-11-25 18:55 | Communications and Control Systems - Radio | 2000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Personnel Error - Other human error | Completed |  | After testing radio cables at PMP there has been 4 No Cables failed the test Fd-001 -21.1m Fd-007 - 4.4m Fd-015 - 12m Fd-046 - 2.8m
| 05SY - Systemwide | Cxxx-NCR-000411 | NCR | Plumstead Portal - Asset labels not reading when scanned. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-04-30 | 2019-06-07 07:42 | 38 | 2018-11-30 10:11 | Communications and Control Systems - General | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Lack or improper material identification and traceability | Completed |  | 2 No White asset labels barcodes are unreadable when scanned - Refuge Help Point & Induction Loop on Level -2 PLP-02-RHP-00201 & PLP-02-RIL-00201. White asset labels barcode is unreadable when scanned. Passive housing cabinet PLP-00-CAB-TRU1. The labels aren't compliant with Asset Identification Standard CRL1-XRL-O6-STD-CR001-00031.
| 05SY - Systemwide | Cxxx-NCR-000412 | NCR | General - 5 No Faulty Verint Cameras |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-02-07 | 2019-02-18 10:57 | 11 | 2018-12-03 15:56 | Communications and Control Systems - CCTV | 500 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Not Defined | Completed |  | 5 No Verint cameras have been returned from site faulty for one reason or another. Serial Numbers below: 15VS076862027 15VS016863807 15VS076862047 15VS076862039 15VS086860731
| 05SY - Systemwide | Cxxx-NCR-000413 | NCR | Royal Oak Portal - damaged adaptaflex at JB for CCTV. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-01-31 | 2019-01-16 11:04 | -15 | 2018-12-03 17:37 | Communications and Control Systems - CCTV | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During a recent IRN visit at ROP it was noted within the external room 901 that the adaptaflex exiting the high-level junction box within the room right side of doorway to supply the external camera was broken at its gland. The adaptable flex couldn’t be repaired on the day of the IRN, therefore Cxxx-NCR-000413 has been raised to capture the non-conformance.
| 05SY - Systemwide | Cxxx-NCR-000414 | NCR | Royal Oak Portal - Incomplete FOSC |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-03-04 | 2019-02-19 11:14 | -13 | 2018-12-03 17:59 | Communications and Control Systems - Fibre Optic Network | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During a recent IRN visit at ROP the following was noted at FOSC ROP-01-CAB-2668U5 • Cabinet has door fixing missing; • Cabinet has scuff/dirt marks; • Cabinet has unsealed glands; • Cable Asset IDs missing on yellow __ cables; and • Hasp missing from FOSC. There isn't any snag list available for the FOSC at Royal Oak Portal.
| 05SY - Systemwide | Cxxx-NCR-000415 | NCR | Royal Oak Portal - Incorrect sized crimps installed on cable within enclosure - ROP-01-CAB-WW.U1 |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-01-17 | 2019-02-01 16:07 | 15 | 2018-12-03 18:14 | Communications and Control Systems - Power Supplies | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During a recent IRN visit at ROP the following was noted at ROP-01-CAB-WW.U1 • Within the cabinet there is 2.5mm earth core bonding interlinks used with 4/6mm yellow earth lugs. • The main bond to the panel is a 35mm, this is terminated via a bolt in the gland plate and the earth size reduces inside the cabinet to a 2.5mm bonding conductor linked to the internal Main Cabinet Earth Stud. • Spare gland holes in the bottom gland plate and top section have plastic press in/out blanks inserted compromising the cabinet IP rating.
| 05SY - Systemwide | Cxxx-NCR-000416 | NCR | CP4A - Radio cabling incorrect labels, cold shrink & warning labels missing. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-02-22 | 2019-02-25 13:23 | 3 | 2018-12-03 18:27 | Communications and Control Systems - Radio | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Insufficient quantity of material to do the job | Completed |  | During a recent Radio IRN visit to cross passage 4A it was note that some labelling on the Radio system PMR cabling was incorrect and had been penned out. Cold shrink and Warning Labels were missing from the galvanic Isolators after cable testing was completed. Earth Bond cable IDs were missing.
| 05SY - Systemwide | Cxxx-NCR-000417 | NCR | Paddington PA VA Design |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-02-04 | 2019-03-01 11:16 | 25 | 2018-12-04 09:49 | Communications and Control Systems - Public Address Systems | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Drawing number Cxxx-SMN-R3-DDA-M171_3-40001 revision C01 has speaker number Z11B64 missing from the top right of the drawing, this speaker is shown on previous drawings, the asset schedule, and the wiring schedule. Consequently this speaker has not been incorporated into the integrated design and has not been installed on site.
| 05SY - Systemwide | Cxxx-NCR-000418 | NCR | __ IRN Process Not Followed |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-01-17 | 2019-01-30 09:52 | 13 | 2018-12-20 10:54 | Communications and Control Systems - Radio | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | IRN process not followed resulting in cabinet being energized to commence T&C works on BTS cabinet for NR integration works. It should be noted that the verification certification was reviewed by T&C representatives prior to energisation.
| 05SY - Systemwide | Cxxx-NCR-000419 | NCR | Cable Drum Tests Not Performed on Delivery |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-02-28 | 2019-02-25 09:36 | -3 | 2018-12-05 13:18 | Communications and Control Systems - General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Not Defined | Completed |  | Cable deliveries to Limmo Shaft site were carried out, complete with delivery notes. When the cable drums were received on site, no electrical continuity test was carried out to confirm that the cable was satisfactory. Cables not tested are: 2 x 500m CAT6A 10GXE92 2 x 500m 2C 1.00mm LF-329
| 05SY - Systemwide | Cxxx-NCR-000420 | NCR | ITP Process Not Followed - Paperwork Incomplete |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-02-28 | 2019-02-25 09:55 | -3 | 2018-12-05 13:27 | Communications and Control Systems - General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | ITP paperwork, including check sheets and test sheets have not been completed in line with the works on site at LIMMO.
| 05SY - Systemwide | Cxxx-NCR-000421 | NCR | Trace heating cable at NWP incorrect final position |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2018-12-20 | 2018-12-12 11:18 | -8 | 2018-12-06 14:25 | Communications and Control Systems - SCADA/Central Management System | 4000 |  | Workmanship | Rework | 3 (3-6k) | Complete | Personnel Error - Inattention to detail | Completed |  | Installation of the Fire mainTrace heating SCADA cables trackside at NWP have been pulled to the wrong final location
| 05SY - Systemwide | Cxxx-NCR-000422 | NCR | 2 damaged MD45 units at WHI-04-CAB-731U10 |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-03-31 | 2019-02-07 12:16 | -52 | 2018-12-07 12:05 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Design Problem - Approval of Design Change Notice (FCN/FCR) in CTI excessive | Completed |  | MD45s damaged plugs need replacing.
| 05SY - Systemwide | Cxxx-NCR-000424 | NCR | Cross-passage BS7671 Certificates have been issued with incorrect details. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-02-15 | 2019-03-01 11:26 | 14 | 2018-12-20 11:29 | Communications and Control Systems - Power Supplies | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | During a recent IRN Visit to cross passages 05, 05A and 06 it was noted that the Minor Electrical Installation Works Certificates have discrepancies within Part 4. In Part 4 declaration of each certificate it has been signed off by the Tester and Supervisor without any of the discrepancies being picked up.
| 05SY - Systemwide | Cxxx-NCR-000425 | NCR | __ Software Implementation against __095a |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-04-29 | 2019-07-22 09:30 | 84 | 2018-12-20 08:27 | Communications and Control Systems - Station Management System | 4500 |  | Software | Rework | 3 (3-6k) | Complete | Design Problem - NCR excessive closure due to design issue | Completed |  | During analysis of __ implementation against performance specification it was identified that __ software is not fully compliant against __095a. The __ HMI shall allow an operator to select the item of equipment whose status is to be determined by the following means: a From a hierarchical menu of systems and component items, and SMN is to issue an RFI to clarify its position and propose solution. NCR should be closed once the RFI is resolved and ComplyPro updated with an RFI number if change accepted.
| 05SY - Systemwide | Cxxx-NCR-000426 | NCR | __ Implementation Compliance against __113i and __283a6 |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-04-29 | 2019-05-22 10:27 | 23 | 2018-12-20 08:33 | Communications and Control Systems - Station Management System | 500 |  | Software | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | During analysis of __ implementation against performance specification it was identified that __ software is not fully compliant against __113i and __283a6 __113i The system maintenance terminal shall provide, as a minimum, the following maintenance functions: i Station SCADA Network monitoring and management __283a6: a Interfaces to other C&C Systems as provided by the Contractor and as described elsewhere within this specification: 6 Station LAN (part of Crossrail Data Network) SMN is to issue an RFI to clarify its position and propose solution. NCR should be closed once the RFI is resolved and ComplyPro updated with an RFI number if change accepted.
| 05SY - Systemwide | Cxxx-NCR-000427 | NCR | __ Software Implementation against requirement __139 |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-04-29 | 2019-06-21 07:19 | 53 | 2018-12-20 08:37 | Communications and Control Systems - Station Management System | 6000 |  | Software | Rework | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | During analysis of __ implementation against performance specification it was identified that __ software is not fully compliant against __139. __139 The __ HMI shall allow an operator to play back on a selected screen a recording from a selected camera starting at a selected point in time. SMN is to issue an RFI to clarify its position and propose solution. NCR should be closed once the RFI is resolved and ComplyPro updated with an RFI number if change accepted.
| 05SY - Systemwide | Cxxx-NCR-000428 | NCR | __ Software Implementation against requirement __113m and __114c |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-08-28 | 2019-08-13 17:10 | -15 | 2018-12-20 08:43 | Communications and Control Systems - Station Management System | 6000 |  | Software | Rework | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | During analysis of __ implementation against performance specification it was identified that __ software is not fully compliant against __113m and __114c. __113 The system maintenance terminal shall provide, as a minimum, the following maintenance functions: __113 m Creation of, and modifications to, graphical display objects __114 The __ HMI shall allow a system administrator to perform non-engineering system administration and system configuration tasks, including the following: __114 c Assignation of important actions to toolbar hot-keys __ to clarify its position on editing mimics and graphical objects – SMN to confirm CCM-10799 and update as required. NCR should be closed once the CCM is confirmed or amended and if agreed by CRL ComplyPro should be updated with an CCM (10799 or amended agreed between SMN and CRL)
| 05SY - Systemwide | Cxxx-NCR-000429 | NCR | __ Software Implementation against requirement __156, __169, __177, __ 177a |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-04-29 | 2019-06-21 14:46 | 53 | 2018-12-20 08:47 | Communications and Control Systems - Station Management System | 6000 |  | Software | Rework | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | During analysis of __ implementation against performance specification it was identified that __ software is not fully compliant against __156, __169, __177, __ 177a, All requirements mentioned above refer to 'type' of recorded announcement. RFI to be issued from __ to inform that the ‘type’ of the announcement is not part of the solution. RFI should propose alternative means of searching and sorting recorded announcements. Note: Proposed method if accepted needs to be captured in O&M manual and training materials NCR should be closed once the RFI is resolved and ComplyPro updated with an RFI number if change accepted.
| 05SY - Systemwide | Cxxx-NCR-000430 | NCR | __ Software Implementation against requirement __252 |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-04-29 | 2019-05-22 10:17 | 23 | 2018-12-20 08:50 | Communications and Control Systems - Station Management System | 500 |  | Software | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | During analysis of __ implementation against performance specification it was identified that __ software is not fully compliant against __252. __252 The __ shall include for future provision to remote start/stop escalators. SMN is to issue an RFI to clarify its position on escalators. NCR should be closed once the RFI is resolved and ComplyPro updated with an RFI number if change accepted.
| 05SY - Systemwide | Cxxx-NCR-000431 | NCR | __ Software Implementation against requirement __053 |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-09-20 | 2020-11-04 12:53 | 45 | 2018-12-20 08:54 | Communications and Control Systems - Station Management System | 12500 |  | Software | Rework | 2 (6-60k) | Complete | Design Problem - Inadequate or defective design | Completed |  | During analysis of __ implementation against performance specification it was identified that __ software is not fully compliant against __053. __053 Object identifiers shall be carefully selected to confer useful information to operators. For example, the numbering of cameras shall follow a logical sequence throughout the station in order to facilitate the rapid and seamless tracking of a subject's movement. SMN is to issue an RFI to clarify its position on mismatch between tag numbers and levels/locations and advise on the system use. NCR should be closed once the RFI is resolved and ComplyPro updated with an RFI number if change accepted.
| 05SY - Systemwide | Cxxx-NCR-000432 | NCR | CMS Implementation vs Requirements Compliance Check |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-04-29 | 2019-08-13 17:28 | 106 | 2018-12-20 09:10 | Communications and Control Systems - SCADA/Central Management System | 15000 |  | Software | Rework | 2 (6-60k) | Complete | Verification Problems - Inspection points not adequate | Completed |  | Further to Cxxx-NCR-000382, it has recently been identified by CRL that the process that is currently in use within Cxxx for implementation of requirements are not robust enough to ensure that all requirements are designed and get implemented on the software. as per Cxxx-NCR-000382 was carried out on __, same exercise is being carried out on CMS. The CMS compliance check will follow same procedure as __ and had to be excluded from the original NCR because of testing priorities that caused for the compliance check to be completed in the New Year on the CMS.
| 05SY - Systemwide | Cxxx-NCR-000433 | NCR | BTS CABINET SUPPLIES |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-03-05 | 2019-03-12 12:17 | 7 | 2018-12-20 10:31 | Communications and Control Systems - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | It has been identified that 3No BTS Cabinets have progressed into commissioning phase without following due IRN process @ the following sites; 1. Farringdon (Cab Ref: FAR-01-CAB-2731U12) 2. Paddington (Cab Ref: PAD-02-CAB-3731U9) 3. Whitechapel (Cab Ref: WHI-04-CAB-731U13)
| 05SY - Systemwide | Cxxx-NCR-000434 | NCR | CER CDN INTERCONNECTING CABLING |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-03-05 | 2019-03-25 14:13 | 20 | 2018-12-20 11:02 | Communications and Control Systems - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | It has been identified that 4No sites have progressed into commissioning phase using the CER CDN Interconnecting cable infrastructure without following due IRN process @ the following sites; 1. Bond Street 2. Farringdon 3. Paddington 4. Whitechapel
| 05SY - Systemwide | Cxxx-NCR-000435 | NCR | Custom House - Spare cores and screen not identified or terminated within cabinet. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-01-31 | 2019-02-01 10:27 | 1 | 2019-01-02 16:32 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | At Custom House it has been noted that within Cabinet CUH-00-CAB-731U4 the spare cores & the screen from cable Asset No CR145-CCC-00555 have been left loose/floating adjacent to operational components within the cabinet, unterminated and unidentified. The oversleeving used on the screen is excessive in size with no crimp fitted. The cable hasn’t any Cable Asset ID fitted at entry to Cabinet CUH-00-CAB-731U4, and when traced to the source device Cabinet CUH-00-CAB-731U2 it was noted that the incorrect Cable ID has been fitted, this reads CR145-CCC-00554 and should be CR145-CCC-00555 as detailed on current SCADA I/O Cable and Wiring schedule Cxxx-SMN-R3-LST-CR145-50016 Rev 9.0 Line item 59
| 05SY - Systemwide | Cxxx-NCR-000436 | NCR | Custom House - Yellow equipment labels peeling (CCTV) |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-01-31 | 2019-02-01 11:04 | 1 | 2019-01-03 16:34 | Communications and Control Systems - CCTV | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During a recent CCTV IRN at Custom House it has been noted that a quantity of the yellow equipment labels fitted to the body of some cameras are peeling off.
| 05SY - Systemwide | Cxxx-NCR-000437 | NCR | Limmo - Rittal Sealing Modules not installed on top of cabinets in CER. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-02-22 | 2019-03-01 13:40 | 7 | 2019-01-12 13:40 | Communications and Control Systems - General | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Rittal sealing modules haven’t been installed to maintain the IP rating of cabinets LIP-01-CAB-B19EU1, U2 & U3 in the CER. This reoccurring issue was raised in July 2018 and captured under Cxxx-NCR-000335, Quality Spotter 98 & Quality Bulletin 014.
| 05SY - Systemwide | Cxxx-NCR-000438 | NCR | MEP 24V and 240V single cables grouped together Type 5A Cab |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-02-28 | 2019-03-01 09:04 | 1 | 2019-01-14 11:31 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Approval of Design Change Notice (FCN/FCR) in CTI excessive | Completed |  | Type 5A cabinet that operates the keypad entry have both the 24V cables and the 240V feed grouped together and not protected by any sheath. The 240 voltage will need to separated from the 24V. A new length of sheathed twin and earth will be required from the PDU/terminals to the PSU and will not be run with the 24v
| 05SY - Systemwide | Cxxx-NCR-000439 | NCR | Custom House - Damaged __ monitor |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-02-08 | 2019-02-08 07:47 | 0 | 2019-01-15 11:53 | Communications and Control Systems - Station Management System | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | During a recent IRN visit to Custom House it has been noted that the __ monitor has a cracked screen.
| 05SY - Systemwide | Cxxx-NCR-000440 | NCR | Custom House Cabinets CUH-00-CAB-731U1 and CUH-00-CAB-731U3 share the same Asset Identification line 1 coding. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-04-08 | 2019-04-23 12:53 | 15 | 2019-01-15 12:16 | Communications and Control Systems - General | 500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | At Custom House within the CER room it has been noted that Cabinets CUH-00-CAB-731U1 and CUH-00-CAB-731U3 share the same Asset Identification line 1 coding.
| 05SY - Systemwide | Cxxx-NCR-000441 | NCR | Limmo - Site construction folders not up to date. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-02-04 | 2019-02-25 09:23 | 21 | 2019-01-21 13:40 | Communications and Control Systems - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Insufficient information made available to the worker. | Completed |  | Surveillance visit to site found that construction site folders haven't been kept up to date. The RIR that was found within the site folders was Rev 9.0 and all documentation found was aligned with that revision. The latest RIR in eB is Rev 22.0.
| 05SY - Systemwide | Cxxx-NCR-000442 | NCR | COT CCTV Over length cables |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-02-19 | 2019-02-28 17:41 | 9 | 2019-01-22 16:39 | Communications and Control Systems - CCTV | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | COT Cameras cables , COT-00-CAM-8101, COT-00-CAM-8102, COT-00-CAM-8103 are all over length designed length
| 05SY - Systemwide | Cxxx-NCR-000444 | NCR | PLP/CAB No Power |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-03-20 | 2019-02-05 12:56 | -43 | 2019-01-23 16:42 | Communications and Control Systems - General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | PLP Cab PLP-01-CAB-1668U1 has no power supply feeding the cab. This also includes no CMS installed for the Fuse Spur
| 05SY - Systemwide | Cxxx-NCR-000445 | NCR | Limmo - Incorrect sized clips installed for Galvanic Isolators |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-02-21 | 2019-02-25 09:19 | 4 | 2019-01-24 10:03 | Communications and Control Systems - Radio | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During a recent IRN visit to Limmo Shaft it was noted that the clips installed to retain the Galvanic Isolators (GI) were undersized and did not provide support to the cable or GI. Labels are also peeling from the GI’s. Cxxx-NCR-000445 has been raised to capture the non-conformance for the incorrect sized clip. See attached Quality Spotter 205.
| 05SY - Systemwide | Cxxx-NCR-000446 | NCR | Coral Communications - Electrical Certification Procedure not being followed. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-03-06 | 2019-03-12 09:36 | 6 | 2019-01-29 17:51 | Communications and Control Systems - Power Supplies | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | __Certification Procedure CCLPR22– Although the procedure captures sequence of events from cradle to grave, it doesn’t capture improvements that have been put in place for to ensure that there aren’t any repeats of previously identified discrepancies with signed BS7671 Electrical Certificates.
| 05SY - Systemwide | Cxxx-NCR-000447 | NCR | PLP CCTV Cables over length |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-02-26 | 2019-02-27 08:37 | 1 | 2019-01-29 18:18 | Communications and Control Systems - CCTV | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | CCTV camera cables for Cameras PLP-00-CAM-9206, PLP-00-CAM-9207 are over the designed length measuring over 120m. Long span extender will be need to ensure camera quality
| 05SY - Systemwide | Cxxx-NCR-000448 | NCR | Eleanor Street – Radio splitter installed near fire stop. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-02-28 | 2019-02-08 11:46 | -20 | 2019-01-31 16:53 | Communications and Control Systems - Radio | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | During a recent RfL visit to Eleanor Street it has been noted that the 4 - way splitter has been installed near the fire stop. Quality Spotter (attached) refers to the positioning.
| 05SY - Systemwide | Cxxx-NCR-000449 | NCR | NWP 24V and 240V single cables grouped together Type 5A Cab |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-02-28 | 2019-02-07 08:08 | -21 | 2019-02-01 12:25 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Type 5A cabinet that operates the keypad entry have both the 24V cables and the 240V feed grouped together and not protected by any sheath. The 240 voltage will need to separated from the 24V. A new length of sheathed twin and earth will be required from the PDU/terminals to the PSU and will not be run with the 24v
| 05SY - Systemwide | Cxxx-NCR-000452 | NCR | CUH PHP Transformer power supplies |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-03-31 | 2019-03-29 07:42 | -2 | 2019-02-05 08:47 | Communications and Control Systems - Power Supplies | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | PHP transformer power supplies cables that run from the Fuse spur to the Transformer itself are not on any design and cable schedule
| 05SY - Systemwide | Cxxx-NCR-000453 | NCR | CAW CIS BRACKETS |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-05-15 | 2019-06-21 14:59 | 37 | 2019-02-05 16:37 | Communications and Control Systems - Customer Information System | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | The following issues have been identified associated with the CIS Bracket installation at Canary Wharf Station. 1. The Screen height detailed within the Site specific Application design Ref: Cxxx-SMN-R3-RSP-CR143-50004 Rev 3.0 Section 5.2.1 is 2250mm above finished floor level to the bottom of the display. The current installation height is 3000mm. It is proposed that this is reviewed with RFL in attendance on site. 2. The orientation of the Displays on the layout drawings ref: Cxxx-SMN-R3-DDA-CR143_5-50002 C01 & Cxxx-SMN-R3-DDA-CR143_5-50003 C01 is horizontal with the wall e.g. between grid ref: S6 & S7 this section of wall runs at an angle as the Ticket Hall opens up. Due to the presence of rebar when scanning the ceiling structure a location was unable to be identified as to install at this angle. The brackets are therefore installed square with the ticket hall furniture and ceiling installations. It is proposed that this is reviewed with RFL in attendance on site. 3. The structural detail and fixing proposal was provided to CRL 6th June 2018 for submission to CEG for Structural calculation and approval. A copy of these calculations are required to be included with the Site Assurance file for the CIS handover. (CRL to provide to Cxxx) (Document attached for reference) 4. The Fixings for the Bracket are __ HUS HR type however the MCR Ref: CRL-MCR-005474 is currently approved for use within the tunnels only. A New MCR will be submitted to include Stations. (Cxxx Action) 5. The MCR for the Bracket ref: CRL-MCR-007627 is currently on eB awaiting CRL approval. MCR to be at Code 1 (Cxxx Action) 6. CRL have advised that further calculations are required to consider Bomb blast for the CIS brackets. CRL to progress and advise Cxxx of additional requirements once available. 7. The current design does not detail any earth connections to the SID or ESUB displays. A 10mm supplementary earth cable has been installed between the local CMS and bracket along with a 10mm earth cable from the bracket to the external 6mm stud on each display. Confirmation is to be provided that this is sufficient by design. (Measured value captured on minor works certificates) (Cxxx Action)
| 05SY - Systemwide | Cxxx-NCR-000454 | NCR | North Woolwich Portal damaged antenna. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-03-31 | 2019-03-25 12:43 | -6 | 2019-02-06 12:38 | Communications and Control Systems - Radio | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | During a recent IRN visit to Limmo Shaft it was noted that the Omni Ant006 fly lead has been damaged due to poor Installation.
| 05SY - Systemwide | Cxxx-NCR-000455 | NCR | Woolwich - Contamination of Radio Connectors |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-04-02 | 2019-03-12 08:20 | -21 | 2019-02-07 13:25 | Communications and Control Systems - Radio | 500 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | A recent visit to site found that testing had been carried out on the radio system and radio connectors had been left disconnected. This has left the connectors exposed to dust & water ingress. Coral Communications who noticed the issue have wrapped the ends with amalgamated tape as a temporary measure.
| 05SY - Systemwide | Cxxx-NCR-000456 | NCR | Radio Test Specifications - Testing being carried out against Test Scripts that have still to be reviewed and approved by Crossrail. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-04-02 | 2019-03-13 11:34 | -20 | 2019-02-07 14:32 | Communications and Control Systems - Radio | 500 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Phase 3.0 testing is being carried out against Test Scripts that have still to be reviewed and approved by Crossrail.
| 05SY - Systemwide | Cxxx-NCR-000457 | NCR | Infotec Bracket drawing issued to eB for Information Only. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-04-30 | 2019-04-15 14:58 | -15 | 2019-02-07 16:58 | Communications and Control Systems - Customer Information System | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Inspection and Test Plan - Infotec CIS Cxxx-SMN-R3-ITP-CR001-50017 Rev 2.0 references Cxxx-SMN-R3-XDS-CR001-50656 Rev 1.0 Infotec CIS Mounting Bracket. This was found to be a placeholder in eB. Further checks that the drawing had been issued under Cxxx-SMN-R3-XDS-CR143-50001, this was found to be issued for Information only - ITP states that the drawing should be at Code 1 status for Installation. Infotec Bracket drawing issued to eB for Information Only.
| 05SY - Systemwide | Cxxx-NCR-000458 | NCR | LIP 24V and 240V single cables grouped together Type 5A Cab |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-04-26 | 2019-04-15 11:34 | -11 | 2019-03-13 10:59 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Type 5A cabinet that operates the keypad entry have both the 24V cables and the 240V feed grouped together and not protected by any sheath. The 240 voltage will need to separated from the 24V. A new length of sheathed twin and earth will be required from the PDU/terminals to the PSU and will not be run with the 24v
| 05SY - Systemwide | Cxxx-NCR-000459 | NCR | __ 24V and 240V single cables grouped together Type 5A Cab |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-03-28 | 2019-02-15 14:14 | -41 | 2019-02-07 16:19 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | Type 5A cabinet that operates the keypad entry have both the 24V cables and the 240V feed grouped together and not protected by any sheath. The 240 voltage will need to separated from the 24V. A new length of sheathed twin and earth will be required from the PDU/terminals to the PSU and will not be run with the 24v
| 05SY - Systemwide | Cxxx-NCR-000460 | NCR | ROP 24V and 240V single cables grouped together Type 5A Cab |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-03-21 | 2019-03-13 11:29 | -8 | 2019-02-08 11:14 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Type 5A cabinet that operates the keypad entry have both the 24V cables and the 240V feed grouped together and not protected by any sheath. The 240 voltage will need to separated from the 24V. A new length of sheathed twin and earth will be required from the PDU/terminals to the PSU and will not be run with the 24v
| 05SY - Systemwide | Cxxx-NCR-000461 | NCR | CUH PHP-01102 Cable over length |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-03-07 | 2019-02-28 17:32 | -7 | 2019-02-07 17:07 | Communications and Control Systems - Telephony | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | CUH-11-PHP-01102 cable is over length at 95.2m, See attached document.
| 05SY - Systemwide | Cxxx-NCR-000462 | NCR | Inadequate Reviews of Test Scripts against Requirements |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-05-30 | 2019-07-30 17:23 | 61 | 2019-02-08 10:16 | Communications and Control Systems - SCADA/Central Management System | 6000 |  | Software | Rework | 3 (3-6k) | Complete | Verification Problems - Inspection points not adequate | Completed |  | __ Library review and process updates were carried out as part of the Cxxx-NCR-000383, this NCR is to track CMS changes and progress. CMS Library still undergoes the same procedure and due to size it is scheduled to run for some time. The process introduced on the __ library is the same on CMS and therefore this NCR.
| 05SY - Systemwide | Cxxx-NCR-000463 | NCR | ELS 24V and 240V single cables grouped together Type 5A Cab |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-03-28 | 2019-03-29 12:00 | 1 | 2019-02-08 11:30 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Type 5A cabinet that operates the keypad entry have both the 24V cables and the 240V feed grouped together and not protected by any sheath. The 240 voltage will need to separated from the 24V. A new length of sheathed twin and earth will be required from the PDU/terminals to the PSU and will not be run with the 24v
| 05SY - Systemwide | Cxxx-NCR-000464 | NCR | FIS 24V and 240V single cables grouped together Type 5A Cab |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-01-02 | 2019-02-16 13:23 | 45 | 2019-02-08 13:39 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Type 5A cabinet that operates the keypad entry have both the 24V cables and the 240V feed grouped together and not protected by any sheath. The 240 voltage will need to separated from the 24V. A new length of sheathed twin and earth will be required from the PDU/terminals to the PSU and will not be run with the 24v
| 05SY - Systemwide | Cxxx-NCR-000467 | NCR | Inaccurate evidence on Verification and Validation (V&V) matrices - CMS |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-05-30 | 2019-07-30 17:30 | 61 | 2019-02-12 11:02 | Communications and Control Systems - SCADA/Central Management System | 6000 |  | Software | Rework | 3 (3-6k) | Complete | Verification Problems - Other | Completed |  | Further to Cxxx-NCR-000384, it is recently identified by CRL that the process that currently in use within Cxxx for documenting V&V evidences are inaccurate and not robust enough. This NCR is to cover update to CMS.
| 05SY - Systemwide | Cxxx-NCR-000468 | NCR | Damage to Whitechapel SOR Operators Desk |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-05-30 | 2019-05-30 12:16 | 0 | 2019-02-14 14:40 | Communications and Control Systems - General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Design Problem - Approval of Design Change Notice (FCN/FCR) in CTI excessive | Completed |  | The Operators Workstation installed in the Whitechapel SOR has been damaged since completion by others. The damage consists of cracks to the worktop joints, the seal between worktop and wall has opened and there is substantial amounts of swarf under the protective cordex sheet. The damage to the joints and opening of the seal to the wall is commensurate with heavy weights being on the worktop, see attached photographs.
| 05SY - Systemwide | Cxxx-NCR-000469 | NCR | Test Equipment not calibrated for testing purposes on Radio system. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-11-26 | 2019-08-05 08:10 | -113 | 2019-02-27 16:49 | Communications and Control Systems - Radio | 500 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Phase 2.2 testing has been carried out at __, ROP, ELS, PLP, VDP, FIS & ELS by PanRF. There is no evidence of a calibration certificate on the test equipment that was used for testing purposes.
| 05SY - Systemwide | Cxxx-NCR-000470 | NCR | BUCF Power and Earthing Schedule Missing Asset IDs |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-06-25 | 2019-06-07 10:14 | -18 | 2019-03-01 12:05 | Communications and Control Systems - Power Supplies | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | BUCF Cable Schedule Cxxx-SMN-R3-LST-CRG03-50162 Rev 1.0 has missing Asset IDs therefore labels cannot be created
| 05SY - Systemwide | Cxxx-NCR-000471 | NCR | Incorrect barcodes on Asset Tag Labels. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-05-27 | 2019-04-18 07:53 | -39 | 2019-03-04 16:41 | Communications and Control Systems - General | 500 |  | Material | Repair | 4 (0.5-3k) | Complete | Verification Problems - Not Defined | Completed |  | During a recent IRN visit to TUCA it was noted that four of the cabinet labels had been printed in Quick Response (QR) Code rather than Data Matrix 2-D Barcode.
| 05SY - Systemwide | Cxxx-NCR-000473 | NCR | Limmo Peninsular Cabinet LIP-00-CAB-006DU1 energised without going through the IRN process. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-05-15 | 2019-05-24 10:02 | 9 | 2019-03-06 12:21 | Communications and Control Systems - Power Supplies | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Cabinet Ref; LIP-00-CAB-006DU1 is a 5C type cabinet for the lift interface connections with Cxxx. At the time of the IRN site visit on 27th Feb 2019 to sign off the relevant paperwork it was found to be energised.
| 05SY - Systemwide | Cxxx-NCR-000474 | NCR | Passcomm Ltd Box on Post IP rating |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-05-25 | 2019-03-25 14:07 | -61 | 2019-03-06 13:11 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | The Passcom Box on Post has an IP55 rating and been used in an external open track location (Westbourne Park Sidings) where the contractual requirement is for IP65
| 05SY - Systemwide | Cxxx-NCR-000475 | NCR | BOS Radio Drum Not Tested |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-04-05 | 2019-03-29 09:29 | -7 | 2019-03-08 10:01 | Communications and Control Systems - Radio | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | 7/8" radio drum wasn't tested and verified before the start of the installation
| 05SY - Systemwide | Cxxx-NCR-000476 | NCR | __ documentation not capturing changes at site. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-03-27 | 2019-03-28 08:34 | 1 | 2019-03-13 16:42 | Communications and Control Systems - Fibre Optic Network | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Office base check to ensure __ design documentation is being updated to reflect as built status of __ system in the field found anomalies at Eleanor Street. This is non compliant against Management of Redlines and As Builts Procedure CRL1-XRL-Z-GPD-CR001-50010. Observation CRL-OBS-26815 has also been raised by Russell Fletcher - Crossrail.
| 05SY - Systemwide | Cxxx-NCR-000477 | NCR | Stepney Green Shaft - Non duct quality cable installed within ducts - trackside. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-04-12 | 2019-03-18 10:37 | -25 | 2019-03-15 11:40 | Communications and Control Systems - Telephony | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Telephony System Cable and Wiring Schedule - Tunnels, CP's and Surface Stepney Green Document number Cxxx-SMN-R3-LST-CRG03-50053 Rev 4.0 References cables - CR094-TEL-00001 & CR094-TEL-00002 as internal grade __ cables. The cables have been installed in within ducts and chambers and sis not suitable for the environment.
| 05SY - Systemwide | Cxxx-NCR-000478 | NCR | Whitechapel - Non duct quality cable installed within ducts - trackside. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-08-23 | 2019-08-22 10:18 | -1 | 2019-03-18 11:30 | Communications and Control Systems - Telephony | 8000 |  | Incorrect Installation | Rework | 2 (6-60k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | Telephony System Cable and Wiring Schedule - Tunnels, CP's and Surface Stepney Green Document number Cxxx-SMN-R3-LST-CRG03-50053 Rev 4.0 References cables - CR092-TEL-00001 as internal grade __ cable. The cable had been installed within ducts and chambers and is not suitable for the environment.
| 05SY - Systemwide | Cxxx-NCR-000479 | NCR | Fisher Street - Non duct grade quality cables installed within ducts - trackside. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-08-23 | 2019-08-22 10:19 | -1 | 2019-03-18 11:44 | Communications and Control Systems - Telephony | 10000 |  | Incorrect Installation | Rework | 2 (6-60k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | Telephony System Cable and Wiring Schedule - Tunnels, CP's and Surface Stepney Green Document number Cxxx-SMN-R3-LST-CRG03-50053 Rev 4.0 References cables - CR086-TEL-00001 & CR086-TEL-00002 as internal grade __ cables. The cables have been installed within ducts and chambers, they are not suitable for the environment.
| 05SY - Systemwide | Cxxx-NCR-000480 | NCR | Stepney Green Shaft - Incorrect cable installed trackside for Telephony System. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-08-23 | 2019-08-22 10:16 | -1 | 2019-03-27 12:50 | Communications and Control Systems - Telephony | 10000 |  | Incorrect Installation | Rework | 2 (6-60k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Further to Cxxx-NCR-000477 that was raised to cover the non duct grade quality cable that was installed within ducts and chambers. This has been replaced with a Cat 6a type cable that is covered by CRL-MCR-004145. Review of the Material Compliance Record in eB found that the cable is intended for use in shaft/portal locations ONLY and not within tunnels nor stations. Its unknown who decided to install the Cat 6a type cable as a replacement.
| 05SY - Systemwide | Cxxx-NCR-000481 | NCR | Tracking concerns of internal alarm list definitions to closure |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-09-16 | 2020-04-30 16:47 | 227 | 2019-03-21 17:42 | Communications and Control Systems - SCADA/Central Management System | 47000 |  | Design | Rework | 2 (6-60k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Crossrail believe the re-issue of the internal alarm description is overdue, it also needs to include additional information, such as alarm sourcing information and test methodology.
| 05SY - Systemwide | Cxxx-NCR-000484 | NCR | TUCA Site Assurance Files not compliant with WI Vol 2B – Part 29 – Contractors Design, Assurance Records and Certification |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-06-28 | 2019-07-19 12:53 | 21 | 2019-04-02 16:43 | Communications and Control Systems - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | TUCA Site Assurance Files not compliant with WI Vol 2B – Part 29 – Contractors Design, Assurance Records and Certification. There are missing key items missing from Site Assurance Files that have been uploaded to eB. e.g. __ Desk Installation, 1 No BS7671 Electrical Certificate & checksheets for MS146 and conflicting cable sizes between BS7671 Certificate and associated check sheets. Due to the design not being complete at the time of Installation there are cable & equipment ID's and test results that make no reference to the current assigned ID's. This is proving difficult to align assurance records - ITP check sheets, BS7671 certificates and test results against the correct cable & equipment ID's. See attached Quality Surveillance Report QS78 Cxxx-SMN-R3-RGN-CR001-50485.
| 05SY - Systemwide | Cxxx-NCR-000485 | NCR | Water Ingress at ABW-00-CAM-9503 and ABW-00-CAM-9501 |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-01-21 | 2020-01-09 11:56 | -12 | 2019-11-22 10:44 | Communications and Control Systems - CCTV | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | Water has been sighted in the housing of cameras ABW-00-CAM-9503 and ABW-00-CAM-9501 on the external wall at Abbey Wood.
| 05SY - Systemwide | Cxxx-NCR-000487 | NCR | Water Ingress - Cam 9503 |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-04-14 | 2019-04-26 08:33 | 12 | 2019-03-31 08:21 | Communications and Control Systems - CCTV | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | ABW-00-CAM-9503 water ingress. Water was found in the camera and the junction box. All components to be replaced and red fibre washers to be installed instead of the rubber washers. See attached photos
| 05SY - Systemwide | Cxxx-NCR-000488 | NCR | __ Cables not glanded into Cabinet |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-05-14 | 2019-06-03 09:45 | 20 | 2019-03-31 08:32 | Communications and Control Systems - Fibre Optic Network | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Personnel Error - Not Defined | Completed |  | __ Armoured __ cable not glanded into ABW-00-CAB-SERU4.
| 05SY - Systemwide | Cxxx-NCR-000489 | NCR | GSM-R performance in the Routeway between Connaught tunnel east portal and North Woolwich portal |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-04-02 | 2021-04-27 15:01 | 25 | 2019-04-02 09:29 | Communications and Control Systems - Radio | 50000 |  | Design | Rework | 2 (6-60k) | Complete | Design Problem - Other | Completed |  | This issue, in this location relates to your design not conforming to the Works Information for the Contract Cxxx, Communications and Control Systems, for the following reasons: 1. Your Design shall provide for the use of GSM-R handportables from within the driving cabs and carriages of trains and currently does not, 2. Your Design shall provide GSM-R Radio System support for general purpose communication throughout the Central Section for handportables, including from the inside of trains and currently does not, Whilst the design achieves the EIRENE minimum values coverage levels of 41.5 dBmV/m (-95 dBm), the above requirements remain unfulfilled. It is worth noting that the EIRENE values are stated as minimum levels and do not preclude radiating a greater power to meet the above requirements. Nevertheless the levels require to be validated and reviewed after the first operational implementation as per 3.2.6 of the EIRENE specification. This is aligned with Performance Specification, GSM-R Radio System (Cxxx-PBF-R3-RSP-CRG03-00011) specifically GSR044, GSR052 and GSR071. There has been no change the spectral environment occupied by adjacent mobile network operators and respective noise floor – I have seen no evidence to the oppose that stance. Additionally, I believe no new antenna farms have been installed at London City Airport. Crossrail will consider closing this NCR when, GSM-R handportables can successfully communicate between Connaught tunnel east portal and North Woolwich portal on the routeway, from within the driving cabs and carriages of trains, and __ can demonstrate that GSM-R train radio will function and communicate correctly.
| 05SY - Systemwide | Cxxx-NCR-000490 | NCR | ABW Camera -ABW-00-CAM-9501 installed to wrong location |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-06-28 | 2019-05-25 08:14 | -34 | 2019-04-03 12:01 | Archaeology - General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | ABW-00-CAM-9501 installed approx. 800mm from proposed design position.
| 05SY - Systemwide | Cxxx-NCR-000491 | NCR | Connaught Cabinet COT-00-CAB-1731U1 undersized containment. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-05-28 | 2019-05-15 10:44 | -13 | 2019-04-03 16:27 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Previous Construction - Improper As Built | Completed |  | Connaught Cabinet COT-00-CAB-1731U1 has undersized containment to accommodate SCADA field cabling. This is non - conforming to Site Inspection and Test Plan - Cabling and Termination Cxxx-SMN-R3-ITP-CR001-50003 Rev 5.0 & Installation Procedures and Guidelines – Structured Cabling Document Number Cxxx-SMN-R3-GPD-CR001-50017 Revision 3.0 sections that are listed in Technical Requirements Section.
| 05SY - Systemwide | Cxxx-NCR-000492 | NCR | Mile End Park - Incorrect asset labelling on __ cables installed FOSC to FOSC trackside. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-11-12 | 2019-11-18 13:08 | 6 | 2019-04-08 15:06 | Communications and Control Systems - Fibre Optic Network | 5000 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | During a surveillance visit to Mile End Park it was highlighted that 96c __ asset cables labelling on cables installed to FOSC 1 & FOSC 2 at Mile End Park were incorrect. The cabinet source and destination details on the database, schedules and labelling are incorrect due to design change that was never captured via the NCR process. This is not compliant with Asset Identification Standard CRL1-XRL-O6-STD-CR001-00031.
| 05SY - Systemwide | Cxxx-NCR-000493 | NCR | Mile End Park - Incorrect asset data information in forms2mobile database for __ system. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-06-24 | 2019-05-16 09:43 | -39 | 2019-04-08 15:22 | Communications and Control Systems - General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Further to Cxxx-NCR-000492 being raised it was found that entries in the forms2mobile database were incorrect. The result of this is that the asset labels installed are incorrect. The change of FOSC's locations have never been entered into the asset database.
| 05SY - Systemwide | Cxxx-NCR-000494 | NCR | Paddington - Cxxx Site Folders not set up at site. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-05-26 | 2019-06-03 14:51 | 8 | 2019-04-12 10:06 | Communications and Control Systems - Radio | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Surveillance visit found that Cxxx site folder set up wasn’t available at site, this is non-compliant with the requirements of Cable Installation and Termination Document Number Cxxx-SMN-R3-ITP-CR001-50003 Revision 5.0 Section 4 Documentation. Due to folders not being available this has led to the 8Point8 team not being briefed at site on the requirements of the __ system cable installation and termination ITP and the associated referenced Installation Procedures and Guidelines (Radio) documentation required to complete the installation.
| 05SY - Systemwide | Cxxx-NCR-000495 | NCR | Paddington - Uncontrolled copies of wiring schedules at site. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-05-26 | 2019-06-05 13:28 | 10 | 2019-04-12 10:08 | Communications and Control Systems - Radio | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | PMR-RI System Cable and Wiring Schedule - Paddington Station - Cxxx-SMN-R3-LST-M171-50014 Rev 4.0 Code 1 since 20.02.2017 is the current approved version on eB. The site surveillance revealed that the site team were not using the current Wiring Schedule, they were referencing a print out of an uncontrolled extract of a cable schedule which had no documentation references.
| 05SY - Systemwide | Cxxx-NCR-000496 | NCR | Paddington - FCD Process not being followed at site. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-05-10 | 2019-06-05 13:29 | 26 | 2019-04-12 10:09 | Communications and Control Systems - Radio | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | The __ site Engineer had requested clarification from the __ radio design team regarding the LCF cables which supplied Antennas 28, 32, 58, & 76 being changed to SCF cables, this change was confirmed via email by Lee Parkin 04.12.2018. Checks were carried out to PMR-RI- Design Schematic – Paddtington Station Cxxx-SMN-R3-DWG-M171-50018 Code 1 since 09.02.2017 and PMR-RI System Cable and Wiring Schedule - Paddington Station - Cxxx-SMN-R3-LST-M171-50014 Rev 4.0 Code 1 since 20.02.2017. This revealed that the associated cables remain unchanged, type LCF on the schedule and schematic. There was no red lined documentation on site to reflect changes and the FCD process had not been followed.
| 05SY - Systemwide | Cxxx-NCR-000497 | NCR | Paddington - 8Point8 Test Equipment |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-05-26 | 2019-05-16 09:40 | -10 | 2019-04-12 11:07 | Communications and Control Systems - Radio | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Although there was a valid calibration certificate for the specialised equipment it was found that the testing house who have calibrated the test equipment don't hold UKAS accreditation as per the WI. No concession has been requested to Crossrail Project Manager to allow non UKAS test equipment for testing purposes.
| 05SY - Systemwide | Cxxx-NCR-000499 | NCR | PAD - Damaged Fibre Cable CR081-DAT-00211 |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-05-31 | 2019-06-05 13:32 | 5 | 2019-04-09 11:32 | Communications and Control Systems - Radio | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | During ongoing T&C activities @ Paddington station the following cable has been identified as damaged between DC3 & DC4. This cable will require replacing. Cable Ref: CR081-DAT-00211 (12-Core Fibre Cable) Length: Approx 150mtrs Damage: Kinked/broken within DC4 cabinet (Loop across hinged opening) This cable has previously been IRN'd by Cxxx. It is unkown who caused this damage.
| 05SY - Systemwide | Cxxx-NCR-000500 | NCR | PAD Damaged Fibre Cable CR081-DAT-03776 |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-05-31 | 2019-06-05 13:31 | 5 | 2019-04-09 11:24 | Communications and Control Systems - Fibre Optic Network | 2500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | During ongoing T&C activities @ Paddington station the following cable has been identified as damaged between CER 5 & FOSC 2 This cable will require replacing. Cable Ref: CR081-DAT-03776 (24-Core Fibre Cable) Length: Approx 250mtrs Damage: Kinked/broken within Trunking approx 30mts from CER. This cable has previously been IRN'd by Cxxx. It is unkown who caused this damage.
| 05SY - Systemwide | Cxxx-NCR-000502 | NCR | Canary Wharf PAM Brackets installed without an approved Material Compliance Record. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-06-23 | 2019-06-21 14:01 | -2 | 2019-04-09 11:37 | Communications and Control Systems - CCTV | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Information not detailed | Completed |  | During the IRN visit to Canary Wharf it was found that the 4 No PAM Brackets that had been installed on Level -4 at the gate lines for the CCTV system hadn't an approved MCR in place. This is non-compliant with Inspection & Test Plan __ Ltd PAM Brackets Document Number Cxxx-SMN-R3-ITP-CR143-50005 Rev 1.0.
| 05SY - Systemwide | Cxxx-NCR-000503 | NCR | RCC Cabinet internal patch lead installation |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-06-14 | 2019-07-11 07:43 | 27 | 2019-04-15 15:10 | Communications and Control Systems - Crossrail Data Network | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The internal patch leads in cabinets RCC-00-CAB-L031U7 and RCC-00-CAB-L031U8 have been changed to CAT6A shielded cables making bend radii much wider.The original cable management has been removed and 19" rack 2U 75mm x 75mm trunking sections installed, the CAT6A cables have been dressed over the top of this trunking which now impacts the closing of the door, the door has to be forced shut thereby pushing on the internal cables causing stress on the cable and connector with some cables already kinked. The installation is now such that the switch port operation indicators are no longer viewable and the RJ45 plug clips are not easily accessible without manhandling the surrounding connections. The lids of the 19" rack type trunking cannot be removed or replaced without disturbing the CAT6A cabling dressed over the top of it.
| 05SY - Systemwide | Cxxx-NCR-000504 | NCR | PML - CDN Partial Acceptance Certificate issued and signed off with outstanding Test Script. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-06-30 | 2019-07-19 07:30 | 19 | 2019-04-12 11:35 | Communications and Control Systems - Crossrail Data Network | 500 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | CDN - Cxxx-SMN-R3-CER-CR094_PT002-50030 PMP-CDN-PAC (Pudding Mill Lane Portal - CDN - PAC) Partial Acceptance Certificate has been issued and signed off with an outstanding Test Script for CDN Cabinet PMP-TR-CAB-00U1.
| 05SY - Systemwide | Cxxx-NCR-000505 | NCR | RCC CDN cabinet unauthorised modifications |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-06-14 | 2019-06-19 13:23 | 5 | 2019-05-13 11:10 | Communications and Control Systems - Crossrail Data Network | 500 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Contamination | Completed |  | Post the IRN and hand over of RCC-00-CAB-L029U7 and RCC-00-CAB-L029U8 the internal unshielded CAT6A cables, as per the port and node schedules, have been installed as shielded patch leads. The associated cable management systems to the front elevation of RCC-00-CAB-L029U7 & U8 have modified without consultation with the Cxxx cabinet design team and this has created access issued to the RJ45 connectors. Post modifications the Eplan drawings have not been uploaded at the next X0? status to show changes made.
| 05SY - Systemwide | Cxxx-NCR-000506 | NCR | Incorrect cables installed to trackside telephones |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-11-23 | 2019-08-22 12:31 | -93 | 2019-04-18 13:25 | Communications and Control Systems - Telephony | 0 |  | Material | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Cables installed to RTL - 50047 and RTL 50048 do not conform to LUL 1-085. NCR raised to confirm if portal is affected as the start and end of the cables run inside the cut and cover for 400m.
| 05SY - Systemwide | Cxxx-NCR-000507 | NCR | Installation of potentially incorrect cables to telephone |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-11-23 | 2019-08-22 12:33 | -93 | 2019-04-18 13:46 | Communications and Control Systems - Telephony | 0 |  | Material | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Cables installed to PLP-TR-RTL-50093 (CR505-TEL-00001)and PLP-TR-RTL-50094 (CR505-TEL-00002) are not LUL 1-085 approved but are installed approx. 250M inside the portal tunnel from the telephone track position. NCR raised to confirm if the cables are compliant to be installed this far into the tunnel area
| 05SY - Systemwide | Cxxx-NCR-000508 | NCR | Connaught COT-00-CAB-1731U1 Cabinet I/O card interlinking cables - missing asset labels and different colour code. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-06-14 | 2019-06-03 09:14 | -11 | 2019-04-25 14:41 | Communications and Control Systems - Power Supplies | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Insufficient information made available to the worker. | Completed |  | During a recent IRN visit to Connaught Head House for IRN it was noted that some Cabinet I/O card interlink cables have been installed with all cores the same colour (pink) and fitted without cable IDs. Whilst other cards are installed with the correct colour coding and cable ID's in place.
| 05SY - Systemwide | Cxxx-NCR-000509 | NCR | Custom House Incorrect Trackside Telephone Cable ID |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-06-14 | 2019-06-13 14:09 | -1 | 2019-04-25 14:47 | Communications and Control Systems - Telephony | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | During Trackside Telephony IRN it was noted at Custom House VX Cabinets CUH-01-JCN-GL3A-U6 had a cableasset ID which read CR146-TEL-00004. This should have read CR146-TEL-00003 and vice versa at CUH-01-JCN-GL4A-U5 has cable ID CR146-TEL-00003. This should read CR146-TEL-00004. The cable asset ID's couldn't be changed over in the shift therefore the NCR was raised.
| 05SY - Systemwide | Cxxx-NCR-000510 | NCR | Connaught Tunnel Trackside Telephone __ twisted around traction earth cable. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-06-14 | 2019-06-13 07:24 | -1 | 2019-04-25 14:55 | Communications and Control Systems - Telephony | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During a recent Trackside Telephony IRN at Connaught Tunnel it was noted that at Telephones CR1-TR-RTL-50075 the supply __ passes around the incorrect side of the installed black Traction Earth Cable which runs below the Telephone. This cable has been removed from its support hook.
| 05SY - Systemwide | Cxxx-NCR-000511 | NCR | Paddington Station Level -2 damaged Antenna by others. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-05-28 | 2019-06-03 14:52 | 6 | 2019-04-25 14:58 | Communications and Control Systems - Radio | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | ANT049. Level -2 Antenna damaged after installation was completed. The damage has been caused by others.
| 05SY - Systemwide | Cxxx-NCR-000512 | NCR | Paddington Station Level -1 Radio Cable FD131 damaged by others. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-05-28 | 2019-06-03 14:54 | 6 | 2019-04-26 14:28 | Communications and Control Systems - Radio | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | Cables that were previously installed on CMS by Tier 1 have been removed and left hanging loose due to a CMS re-design. Whilst left hanging loose Cable FD131 been damaged by others.
| 05SY - Systemwide | Cxxx-NCR-000513 | NCR | RTL Telephones installed with phones facing the wrong direction and clash with CMS Ladder racking |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-05-23 | 2019-05-15 10:16 | -8 | 2019-04-25 10:23 | Communications and Control Systems - Telephony | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | During IRN inspection noted that some of the phones have been installed with the phone facing the wrong direction. the affected Phones are CR1-TEL-50001 - phone should be facing east not west CR1-TEL-50002 - Phone should be facing North not east CR1-TEL-50004 - Phone installed against ramp wall conflicts with installed Ladder racking. Requires a position change and extend telephone out level with Ladder rack using power arms.
| 05SY - Systemwide | Cxxx-NCR-000514 | NCR | Abbey Wood - 2 No cables crimped within one crimp. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-05-14 | 2019-05-14 10:52 | 0 | 2019-04-25 13:13 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During a recent IRN site visit to Abbey Wood is was noted that in Cabinets ABW-00-CAB-SERU3 and ABW-00-CAB-SERU4 the SCADA fan termination at -X11 terminal 4 have 2 x 1.00mm2 cable cores crimped in 1 no red 1.5mm2 crimp.
| 05SY - Systemwide | Cxxx-NCR-000515 | NCR | Abbey Wood - Control cable not sufficiently glanded - cabinet CR149-SCC-00140 |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-05-14 | 2019-05-14 10:50 | 0 | 2019-04-25 13:55 | Communications and Control Systems - General | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During a recent IRN site visit to Abbey Wood is was noted at the 50V DC Section Cabinet CR149-SCC-00140 cabinet that a grey control cable has been installed to the cabinet through a plastic compression type gland with a steel lock ring. The cable also had no cable asset ID fitted along its visible run. This cable has been installed through the high-level compartmented CMS via a floating steel __ to the GRP traywork which runs above the cabinet. This cable appears not dressed to the GRP traywork.
| 05SY - Systemwide | Cxxx-NCR-000516 | NCR | Abbey Wood - Incorrect SCADA terminations for fan controllers within cabinet. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-05-31 | 2019-05-28 11:50 | -3 | 2019-04-26 15:45 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Desktop surveillance revealed that the SCADA termination card, Cxxx-SMN-R3-LST-CR149-50013 Rev 3.0, shows -X11 terminals 3 and 4 as connected together. Checking each cabinets Eplan wiring diagram for ABW-00-CAB-SERU3 and ABW-00-CAB-SERU4 it is evident that the two fan alarms cannot provided the single ‘cabinet fan fault alarm’ as the signals need to be wired in series, i.e. for ABW-00-CAB-SERU3 the terminations should be A1-11 to -X11-1, 2 and 3 link, A1-H to -X11-4. The SCADA termination schedule was found to have the incorrect termination detail.
| 05SY - Systemwide | Cxxx-NCR-000517 | NCR | Pudding Mill Lane - Faulty Cabinet Lock |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-07-29 | 2019-06-11 10:40 | -48 | 2019-04-26 16:02 | Communications and Control Systems - General | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | A recent site visit to Pudding Mile Lane found that the lock mechanism had failed on Cabinet PMP-00-CAB-1731U5. To hold the door closed a cone had been placed in front of the cabinet. This leaves the cabinet open for unauthorised access.
| 05SY - Systemwide | Cxxx-NCR-000518 | NCR | Pudding Mill Lane - Antenna cable bending radius. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-05-27 | 2019-06-12 10:41 | 16 | 2019-04-26 16:45 | Communications and Control Systems - Radio | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | Within the escape stairwell the cable at Antenna PMP-02-ANT-0014 was found to be excessively tight where it passes through the wall conduit to the Antenna. The manufacturers bending radius requirement hasn’t been achieved.
| 05SY - Systemwide | Cxxx-NCR-000519 | NCR | CUH CCTV Shrouds |  | Contr | __M | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-05-29 | 2019-05-21 10:23 | -8 | 2019-05-01 13:31 | Communications and Control Systems - CCTV | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Additional cameras have been added to the design but 2 No shrouds haven't been order by the T1
| 05SY - Systemwide | Cxxx-NCR-000520 | NCR | Westbourne Park REB - Incorrect Installation of cable gland. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-06-20 | 2019-05-15 11:00 | -36 | 2019-05-02 09:38 | Communications and Control Systems - Telephony | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | At Cabinet WRP-00-CAB-731U1 the cable shroud at the cable gland for CR076-TEL-00002 cannot be fitted correctly as the gland is tight to that of an adjacent gland.
| 05SY - Systemwide | Cxxx-NCR-000521 | NCR | PML - IP rated rubber washer failure. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-05-25 | 2019-05-15 11:21 | -10 | 2019-05-02 09:56 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Equipment Breakdown | Rework | 4 (0.5-3k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | At Pudding Mill Lane, the rubber washer fitted to the __ gland for external gate cable containment system was found to have signs of deterioration and had split and during the inspection had dislodged from the gland.
| 05SY - Systemwide | Cxxx-NCR-000522 | NCR | FIS Incorrect Door on Ext RTL |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-06-27 | 2019-06-24 16:16 | -3 | 2019-05-02 10:32 | Communications and Control Systems - Telephony | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | External ruggedised telephone FIS-00-RTL-10009 at Fisher Street Shaft level 0 should have rail lock door as per the equipment schedule. Layout drawing shows zero button ruggedised telephone with standard door.
| 05SY - Systemwide | Cxxx-NCR-000523 | NCR | __ Incorrect Door on Ext RTL |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-06-27 | 2019-05-20 12:03 | -38 | 2019-05-02 10:32 | Communications and Control Systems - Telephony | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | External ruggedised telephone __-00-RTL-10008 at Stepney Green Shaft level 0 should have rail lock door as per the equipment schedule. Layout drawing shows zero button ruggedised telephone with standard door.
| 05SY - Systemwide | Cxxx-NCR-000524 | NCR | LIM Incorrect Door on Ext RTL |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-06-27 | 2019-07-04 06:43 | 7 | 2019-05-02 10:32 | Communications and Control Systems - Telephony | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | External ruggedised telephone LIP-00-RTL-10008 at Limmo Peninsula Shaft level 0 should have rail lock door as per the equipment schedule. Layout drawing shows zero button ruggedised telephone with standard door.
| 05SY - Systemwide | Cxxx-NCR-000525 | NCR | __ Installation Guidlines Not Followed For CCTV JB's |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-06-27 | 2019-06-14 15:55 | -13 | 2019-05-02 10:35 | Communications and Control Systems - CCTV | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | It was identified on an inspection that flange couplers were missing on the CCTV side of the CCTV JB's at Stepney Green Shaft. This is not in line with the approved Installation Procedures and Guidelines document that should be followed.
| 05SY - Systemwide | Cxxx-NCR-000526 | NCR | Canary Wharf - Damaged Speaker |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-06-14 | 2019-06-11 13:35 | -3 | 2019-05-13 16:33 | Communications and Control Systems - Public Address Systems | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Not Defined | Completed |  | Whilst carrying out planned works labelling Comms Assets on Level -3 Back of house it was noticed by Cxxx __ that a PAVA speaker (Horn MHS20)Speaker had been damaged by others and was beyond repair and needs to be replaced.
| 05SY - Systemwide | Cxxx-NCR-000527 | NCR | Canary Wharf - MS146 Minituare Circuit Breaker ratings. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-12-31 | 2019-10-02 10:49 | -90 | 2019-05-02 10:52 | Communications and Control Systems - Power Supplies | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | At Canary Wharf it has been noted that cabinets CAW-04-CAB-4465U1 & CAW-04-CAB-4214U1 have 6A double pole __’s installed as the main incomer switch disconnector . Both ePlan drawings show that 2A __’s should be installed instead of 6A __’s.The change of 6A to 2A __ was on the Canary Wharf outstanding works list. Change Note CN533 was raised to capture the changes and is now closed. The Change note shouldn’t have been closed out until all works are complete.
| 05SY - Systemwide | Cxxx-NCR-000528 | NCR | RCC - Loose earth cables within cabinets in CER. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-05-23 | 2019-05-20 08:49 | -3 | 2019-05-02 16:01 | Communications and Control Systems - Power Supplies | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | During a site visit to RCC it was noted that there were various loose earth cables within the cabinets that are energised within the CER
| 05SY - Systemwide | Cxxx-NCR-000529 | NCR | PML - Insufficient capacity within finger trunking for field cables in cabinet. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-06-28 | 2019-06-10 09:16 | -18 | 2019-05-13 16:47 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | During a recent IRN visit to Pudding Mill Lane CER it was noted at cabinet PMP-00-CAB-1731U6 that the left hand front internal finger trunking was full to capacity with cabling and as a result the lidding could not be closed correctly, leaving no spare capacity for future cable installation. It was also noted that on the basket above the cabinet there are 2 x SCADA cables(1 x 5c and 1 x 12c) awaiting glanding and termination into the cabinet, these cables are due for termination to I/O cards on this same section of cabinet.
| 05SY - Systemwide | Cxxx-NCR-000530 | NCR | WOO SOR Power/Earthing Issues |  | Contr | __M | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-06-05 | 2019-05-15 11:03 | -21 | 2019-05-08 16:07 | Communications and Control Systems - Power Supplies | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On inspection of the WOO SOR desk it was found that no dedicated 10mm earth bond had not been installed but a cross bond between the CMS had been but its not acceptable. Also on inspection the spurs that had been installed which feed the PSU's was not in an accessible place and had been installed behind the 50mm basket.
| 05SY - Systemwide | Cxxx-NCR-000531 | NCR | Canary Wharf - Damaged Radio Omni Antenna 09. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-06-14 | 2019-05-24 10:17 | -21 | 2019-05-20 08:33 | Communications and Control Systems - Radio | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Whilst carry out above ground Radio works on Level -1 it was noticed by Bartosz Szarek that another Radio Omni Antenna 09 in Room 1206A had been damaged by others.
| 05SY - Systemwide | Cxxx-NCR-000532 | NCR | NWP Radiating cable fixing Spacing |  | Contr | __M | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-06-12 | 2019-06-13 11:19 | 1 | 2019-05-15 12:33 | Communications and Control Systems - Radio | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | NWP above ground radio cable installation has been installed with the cones at 1500mm apart when they should be installed maximum 1300mm apart
| 05SY - Systemwide | Cxxx-NCR-000533 | NCR | NWP Damaged radio cable |  | Contr | __M | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-12-06 | 2019-06-18 14:08 | -171 | 2019-05-15 13:15 | Communications and Control Systems - Radio | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | At NWP on the above ground radio there is potential damage to a leaky feeder cable (RA002) that has been installed on cones below the 100mm CMS provide to us by the T1 install team.
| 05SY - Systemwide | Cxxx-NCR-000534 | NCR | RTL Incorrectly Drilled |  | Contr | __M | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-06-12 | 2019-06-24 08:54 | 12 | 2019-05-15 15:12 | Communications and Control Systems - Telephony | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | RTL installed at NWP has been installed incorrectly. The back box has pre-made holes for fixing. Installers have drilled the Centre of the back box which is incorrect.
| 05SY - Systemwide | Cxxx-NCR-000535 | NCR | NWP Damaged 5B JB |  | Contr | __M | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-06-12 | 2019-06-03 09:12 | -9 | 2019-05-15 15:36 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Contamination | Completed |  | On a site visit we have highlighted that one of the screws on the JB has been cross threaded. Because of this we cannot open the JB without damaging the JB
| 05SY - Systemwide | Cxxx-NCR-000536 | NCR | Connaught Tunnel Telephone guage clash and other design issues |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-12-09 | 2019-11-05 14:57 | -34 | 2019-05-16 07:48 | Communications and Control Systems - Telephony | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Upon a recent IRN inspection it was noted trackside telephones COT-TRK-RTL-50073, COT-TRK-RTL-50074, COT-TRK-RTL-50075, COT-TRK-RTL-50076 are installed within 300mm of HV power cables and access for the operator is restricted by a water trough at foot level. Photo attached. Furthermore it has arisen that COT-TRK-RTL-50075, COT-TRK-RTL-50076 fail guage according to Cxxx guage checks.
| 05SY - Systemwide | Cxxx-NCR-000537 | NCR | FOSCs identified as Cabinets in Asset Database |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-07-20 | 2019-06-28 15:48 | -22 | 2019-05-21 11:11 | Communications and Control Systems - Fibre Optic Network | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | A review of asset classes has identified that a sub-class of cabinets L7681 has been created in AIMS for fibre cabinets. Cxxx have allocated all FOSCs to the primary equipment cabinet class L215611. Changing this allocation at this stage of the project would have significant impact in terms of creating new Asset IDs an re-labelling across the worksites. Following discussions with AIMS team is was proposed that an NCR should be used to formalise a request to keep the allocation of FOSCs to L215611 and "Use As-Is" to avoid unnecessary rework, since the maintenance requirements for FOSCs do not differ from other cabinets.
| 05SY - Systemwide | Cxxx-NCR-000538 | NCR | Earth cables not installed correctly at Limmo Penninsula Shaft |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-06-05 | 2019-06-06 07:53 | 1 | 2019-05-22 10:27 | Communications and Control Systems - Radio | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Previous Construction - Other | Completed |  | Two earth cables installed from the radio leaky feeder have been routed down the tunnel wall, fixed using P-clips and pass behind the case of the ruggedised telephone. It is not known if the cables or telephone was installed first.
| 05SY - Systemwide | Cxxx-NCR-000539 | NCR | PML - Incorrect gland type in cabinet. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-06-17 | 2019-06-19 15:32 | 2 | 2019-05-23 08:50 | Communications and Control Systems - Radio | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | At Cabinet PMP-00-CAB-1731U2 is noted at repeater TF3 a cable has been installed at the base of the unit without its associated compression gland and had no asset identification.
| 05SY - Systemwide | Cxxx-NCR-000540 | NCR | PML- Identical labels on different cables. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-06-06 | 2019-06-10 08:12 | 4 | 2019-05-23 09:04 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During SCADA cable IRN at Cabinet PMP-00-CAB-1731U6 is noted at SCADA Cables CR502-CCC-01443 and CR502-CCC-01444 that the wrap round label installed within the cabinet is incorrect. The wrap round labels both read CAB-1731U6-CMB-CP008. These should read CAB-1731U6-D__-001 at cable 01443 and CAB-1731U6-D__-002 at cable 01444. Cxxx-NCR-000540 has been raised to cover the non-conformance.
| 05SY - Systemwide | Cxxx-NCR-000541 | NCR | Westbourne Park REB cabinet asset label printed in QR Code rather than 2-D Barcode. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-06-28 | 2019-06-24 13:44 | -4 | 2019-05-23 11:26 | Communications and Control Systems - General | 500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | During a recent IRN visit to Westbourne Park REB it was noted that cabinet label for WRP-00-CAB-731U1 had been printed in Quick Response (QR) Code rather than Data Matrix 2-D Barcode. Cxxx-NCR-000 has been raised in eB to capture the non-conformance. Note that the label will scan ok with i-nigma app, therefore the new Forms2mobile App will have to be used to scan.
| 05SY - Systemwide | Cxxx-NCR-000542 | NCR | Liverpool St - Damaged Antenna by others |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-07-15 | 2019-06-06 12:12 | -39 | 2019-05-23 11:34 | Communications and Control Systems - Radio | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Omni antenna 046 has been damaged by others, there is a crack on the cover of the antenna. This NCR has been raised to track the replacement of the antenna.
| 05SY - Systemwide | Cxxx-NCR-000543 | NCR | NWP Radio cable Orientation |  | Contr | __M | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-06-20 | 2019-06-18 14:11 | -2 | 2019-05-23 14:43 | Communications and Control Systems - Radio | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On a IRN for NWP it was highlighted the Leaky feeder cable Orientation was off which was resulting in the Apertures facing away from the targeted coverage area
| 05SY - Systemwide | Cxxx-NCR-000544 | NCR | GSMR Radio Coverage Testing - DAS - walk test not followed route as described in Test Spec. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-07-26 | 2019-08-16 16:02 | 21 | 2019-06-03 14:47 | Communications and Control Systems - Radio | 500 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | GSMR Radio Coverage Testing - DAS - walk test not followed route as described in Test Spec.
| 05SY - Systemwide | Cxxx-NCR-000545 | NCR | DAS coverage testing has selected a detection type of ‘Peak’ and not ‘RMS / Avg’ as outlined in the Radio Technical Note |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-07-31 | 2019-08-16 15:56 | 16 | 2019-06-03 14:48 | Communications and Control Systems - Radio | 500 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | DAS coverage testing has selected a detection type of ‘Peak’ and not ‘RMS / Avg’ as outlined in the Radio Technical Note
| 05SY - Systemwide | Cxxx-NCR-000546 | NCR | incorrect information and Wrong cable labels at VDP |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-07-18 | 2019-07-17 15:08 | -1 | 2019-06-13 09:44 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | Cable labels from the VX boxes EBU1 and WBU1 to the MS146 boxes 101NEU1 and 102LEU1 are incorrect. FCD-000380 has been raised to explain in further detail the issue and to amend the schedules and labels. On the cables coming from the CER to the VX boxes the labels that have been attached are actual for Plumstead Portal ATS site. When checking PPA cables from the CER to the track cabinets VDPs label have been installed there. NCR-000547 has been raised for PPA to cover this New labels to be printed for both sites
| 05SY - Systemwide | Cxxx-NCR-000547 | NCR | Incorrect labels installed for MS146 cabinets |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-07-26 | 2019-08-16 11:17 | 21 | 2019-06-14 07:08 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | VDP labels have been installed at PPA. also see NCR 000546 which relates to this site
| 05SY - Systemwide | Cxxx-NCR-000548 | NCR | NWP Telephony RHP Cable over Length |  | Contr | __M | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-07-03 | 2019-06-20 14:40 | -13 | 2019-06-19 10:51 | Communications and Control Systems - Telephony | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | At NWP we have an over length cable which feeds the RHP NWP-01-00101 (CR504-TEL-00067). Its been tested and the cable measured 94.3m
| 05SY - Systemwide | Cxxx-NCR-000549 | NCR | Whitechapel - SOR Cabinet 7531U Creased Patch Leads |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-07-26 | 2019-07-29 10:53 | 3 | 2019-06-24 16:13 | Communications and Control Systems - General | 500 |  | Testing and Commissioning | Repair | 4 (0.5-3k) | Complete | Design Problem - Approval of Design Change Notice (FCN/FCR) in CTI excessive | Completed |  | During a recent IRN visit to Whitechapel SOR it was noted within Cabinet 7531U that some of the Green patching leads had been poorly installed resulting in them being left twisted and creased. Cxxx-NCR-000549 has been raised in eB to capture the non-conformance.
| 05SY - Systemwide | Cxxx-NCR-000550 | NCR | TCR- Non Compliant Radio Coverage. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-08-14 | 2019-09-13 15:31 | 30 | 2019-06-26 13:32 | Communications and Control Systems - Radio | 10000 |  | Testing and Commissioning | Rework | 2 (6-60k) | Complete | Material/Preservation Problems - Other | Completed |  | __ undertook DAS CW Spot testing at TCR at Phase 2.2 (see reference documents for reference). This was performed as per the request of CRL at 450MHz. However, these tests only proved the near field coverage and not the far field. Walk tests were descoped at risk by CRL, which would have given a true indication of system performance that are now being picked up by __. The root cause of the coverage failure has to be established by T&C manager.
| 05SY - Systemwide | Cxxx-NCR-000551 | NCR | VDP - Non duct grade cable installed within duct for Portal CCTV System |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-09-30 | 2019-10-01 16:13 | 1 | 2019-07-09 08:03 | Communications and Control Systems - CCTV | 20000 |  | Design | Rework | 2 (6-60k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | At Victoria Dock Portal the East Bound and West Bound trackside cabling installed for the Portal CCTV System is not duct grade cabling where it passes through the UTX. The ELV power and Comms cabling has been installed within a single metal __ running through the UTX ductwork. The UTX ducting is flooded with water. It has been noted that the cable and wiring schedule Cxxx-SMN-R3-LST-CR144_PT003-50004 Rev 5.0 does not detail the requirement for duct grade cables.
| 05SY - Systemwide | Cxxx-NCR-000552 | NCR | VDP Trackside incomplete earth connections at cabinet VDP-01-CAB-TRU1 |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-08-23 | 2019-08-22 13:46 | -1 | 2019-07-09 08:52 | Communications and Control Systems - General | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The earth bonding installed from the trackside earth bar has not been terminated at the cabinet.
| 05SY - Systemwide | Cxxx-NCR-000553 | NCR | Canary Wharf Station FORs |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-10-05 | 2019-11-11 08:18 | 37 | 2019-07-07 11:28 | Communications and Control Systems - SCADA/Central Management System | 3500 |  | Software | Rework | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | 2846 CWX - CMS to PID Integration Testing - CIS View Display Function 'No Text Displayed' 2602 CAW - CMS (CCTV) - Escalators got wrong CAM associations 2585 CAW - __ (CCTV) Camera Switching priority 2601 CAW - CMS (CCTV) Door camera association incorrect 2599 CAW - __ Incorrect Door Descriptions on CCTV Cameras 2598 CAW - CMS Incorrect Door Description on CCTV Cameras 2501 CAW - Door camera association incorrect 2473 CAW - __ CCTV icon need adjustments in the GUI mimic 2393 CAW - DOE associated alarms , incorrect to field status. 1902 CAW - __ to PIDs out of service function 2309 CAW - __ GUI has Door Icon in wrong place & 2 SID numbers incorrect 1226 CAW - __ Phase 3.0 Monitored Doors - IO schedule alarm descriptions 1878 CAW - Operator profile need to be add in the __ RCM 2562 CAW - __ (CCTV) - Escalators got wrong CAM associations
| 05SY - Systemwide | Cxxx-NCR-000554 | NCR | NWP Portal - NWP-01-CAB-TRU1 cabinet corrosion. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-08-22 | 2019-08-22 06:54 | 0 | 2019-07-09 10:43 | Communications and Control Systems - Telephony | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | Point Cabinet NWP-01-CAB-TRU1 that corrosion was present around the internal cabinet edge possibly caused by chipping to the paint surface.
| 05SY - Systemwide | Cxxx-NCR-000555 | NCR | Systemwide FORs |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-10-13 | 2019-10-04 17:16 | -9 | 2019-07-07 11:35 | Communications and Control Systems - SCADA/Central Management System | 1750 |  | System Defect | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | 2729 CAW - CCTV switching to working tile instead of Primary/Secondary Tile 2523 TCR-CMS-UPS Integration Testing-Fan Failure Inhibited Alarm 2434 CCTV in CUH and found that On Disconnection, RCM Lost image but No Alarm, Event or mimic change happened 2516 PDX-CMS-Truth Table Issue-IP In Use Events Not Triggered 2149 _FPIP tags alarming on the wrong state 1793 RCM - LV switchboard general issues 1700 MDA alarm text on CMS doesnâ€™t match the Crossrail IO Schedule v5.5
| 05SY - Systemwide | Cxxx-NCR-000556 | NCR | Cross Passage FORs |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-10-13 | 2019-10-04 17:17 | -9 | 2019-07-07 11:40 | Communications and Control Systems - SCADA/Central Management System | 500 |  | System Defect | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | 2489 Alarms appearing in the inhibit list instead of the main alarm list 2656 CP11 TDP Sump Pump Stop Command Control Inconsistency
| 05SY - Systemwide | Cxxx-NCR-000557 | NCR | Custom House FORs |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-10-13 | 2019-10-04 17:18 | -9 | 2019-07-07 11:49 | Communications and Control Systems - SCADA/Central Management System | 1250 |  | System Defect | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | 2168 Wrong location not as per layout drawing Cxxx-SN-R3-DDA-CR145_A-30001 2772 Cannot Create Monitor View Layouts 2524 DOO Camera layout and positioning 2451 Camera symbol position on mimic 2179 Help points not working
| 05SY - Systemwide | Cxxx-NCR-000558 | NCR | Farringdon Station FORs |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-10-13 | 2019-10-04 07:45 | -9 | 2019-07-07 11:52 | Communications and Control Systems - SCADA/Central Management System | 500 |  | System Defect | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | 2555 CMS-FDX-LV-Outgoing CB Tripped Alarms Incorrectly Shelved
| 05SY - Systemwide | Cxxx-NCR-000559 | NCR | Fisher Street Shaft FORs |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-10-13 | 2019-10-04 07:54 | -9 | 2019-07-07 12:01 | Communications and Control Systems - SCADA/Central Management System | 500 |  | System Defect | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | 2831 No change of Camera Status on RCM CCTV Page
| 05SY - Systemwide | Cxxx-NCR-000560 | NCR | North Woolwich Portal FORs |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-10-13 | 2019-10-04 17:12 | -9 | 2019-07-07 12:15 | Communications and Control Systems - SCADA/Central Management System | 500 |  | System Defect | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | 2335 No UPS Lost Comms
| 05SY - Systemwide | Cxxx-NCR-000561 | NCR | Pudding Mill Lane FORs |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-10-13 | 2019-10-04 17:19 | -9 | 2019-07-07 12:36 | Communications and Control Systems - SCADA/Central Management System | 500 |  | System Defect | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | 1875 No mimic symbol in operational state
| 05SY - Systemwide | Cxxx-NCR-000562 | NCR | Royal Oak Portal |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-10-13 | 2019-10-04 17:14 | -9 | 2019-07-07 12:43 | Communications and Control Systems - SCADA/Central Management System | 500 |  | System Defect | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | 2833 No change of Camera Status on RCM CCTV Page and associated Mimic
| 05SY - Systemwide | Cxxx-NCR-000563 | NCR | Whitechapel Station |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-10-13 | 2019-10-04 17:30 | -9 | 2019-07-07 12:55 | Communications and Control Systems - SCADA/Central Management System | 500 |  | System Defect | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | 1738 Auto / Remote Control outputs failed alarm
| 05SY - Systemwide | Cxxx-NCR-000564 | NCR | Woolwich Station FORs |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-10-13 | 2019-10-04 17:15 | -9 | 2019-07-07 12:59 | Communications and Control Systems - SCADA/Central Management System | 500 |  | System Defect | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | 2581 GUI functionality
| 05SY - Systemwide | Cxxx-NCR-000565 | NCR | Misc FORs |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-10-13 | 2019-10-04 17:28 | -9 | 2019-07-07 13:03 | Communications and Control Systems - SCADA/Central Management System | 500 |  | System Defect | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | 1772 Discrepancy between truth table and CMS SCADA
| 05SY - Systemwide | Cxxx-NCR-000567 | NCR | Failure of PAVA batteries across the project |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-08-01 | 2019-07-30 14:17 | -2 | 2019-07-11 12:46 | Communications and Control Systems - Public Address Systems | 3000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Battery Isolated by 3rd Party Contractors and not Re-instated once works completed. This caused the batteries to be left idle for extended periods of time, reducing the efficiency and shelf-life of the battery. This has resulted in batteries being unable to hold sufficient charge to complete 2.2 testing.
| 05SY - Systemwide | Cxxx-NCR-000568 | NCR | Faulty __ amplifier frames across the project |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-08-01 | 2019-07-30 14:21 | -2 | 2019-07-11 12:57 | Communications and Control Systems - Public Address Systems | 500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | __ identified a faulty batch of PSUs installed in Amplifier Frames, Resulting in low Voltage Outputs
| 05SY - Systemwide | Cxxx-NCR-000570 | NCR | CCTV Coverage MEP - MEP-00-CAM-7507 |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-09-15 | 2019-08-29 10:17 | -17 | 2019-07-11 15:05 | Communications and Control Systems - CCTV | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | MEP-00-CAM-7507 does not cover the entire door 'MEP-00-D0002-MD02'. The camera needs to be relocated on to the adjacent wall to provide coverage of the entire door.
| 05SY - Systemwide | Cxxx-NCR-000571 | NCR | Missing / Damaged telephony patch leads |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-09-30 | 2019-10-07 10:06 | 7 | 2019-07-12 07:35 | Communications and Control Systems - Telephony | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Patch leads have gone missing on 5 standard telephone`s, 1 on departure`s road and 4 on concourse level . There is also 1 damaged patch lead on Intermediate level -2. Quality spotter was raised by Siemen`s and distributed by email accordingly.
| 05SY - Systemwide | Cxxx-NCR-000572 | NCR | CCTV Coverage TCR - Missing coverage of ESS1 5/613 |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-10-26 | 2019-11-01 12:10 | 6 | 2019-07-12 14:26 | Communications and Control Systems - CCTV | 5000 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | CCTV Coverage of ESS1 5/613 has been missed during the development of the CCTV design.
| 05SY - Systemwide | Cxxx-NCR-000573 | NCR | CCTV Coverage TCR - Missing internal coverage of 2x FOH to BOH doors at platform level |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-11-22 | 2019-09-26 07:45 | -57 | 2019-07-12 14:45 | Communications and Control Systems - CCTV | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | Doors between public and non-public areas (LB-S 5/102) and (LB-S 5/095) do not have at least recognition level (25%R) on the non-public side.
| 05SY - Systemwide | Cxxx-NCR-000574 | NCR | Farringdon - Uncontrolled Cxxx Radio document at site. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-01-10 | 2019-12-16 07:14 | -25 | 2019-07-17 12:52 | Communications and Control Systems - Radio | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | During the surveillance visit to Farringdon Station on Radio Testing it was found that System Architecture Drawing - GSM-R Radio System Cxxx-SMN-R3-DWG-CR001-50011 Rev 4.0 was being held at site. Rev 4.0 has not been issued to eB for approval - Rev 3.0 is the current version in eB at Code 2.
| 05SY - Systemwide | Cxxx-NCR-000576 | NCR | VDP – Portal Entrance Intruder Detection – Application Design has uncotrolled drawing at P0 status. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-09-05 | 2019-08-15 09:32 | -21 | 2019-07-23 05:51 | Communications and Control Systems - CCTV | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | During a recent visit to Victoria Dock Portal trackside to view the Portal Entrance Intruder Detection installation it was noted that the Coral operatives were referencing uncontrolled documentation to assist with the installation works. Application Design - Portal Entrance Intruder Detection – Victoria dock Portal (CCTV) Cxxx-SMN-R3-RSP-CR144_PT003-50035 Revision 2.0 is Code 1 on eB.
| 05SY - Systemwide | Cxxx-NCR-000577 | NCR | VDP cabinet VDP-00-CAB-1733U5 requires cover for 230v terminals. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-10-31 | 2019-10-23 07:48 | -8 | 2019-07-23 05:30 | Communications and Control Systems - Power Supplies | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | During a recent site visit to VDP CER room it was noted at cabinet VDP-00-CAB-1733U5 that the 230v power supply terminal block did not have any terminal covers installed or any warning signage present.
| 05SY - Systemwide | Cxxx-NCR-000578 | NCR | VDP - CCTV cable schedule incorrect details. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-09-05 | 2019-09-05 15:01 | 0 | 2019-07-23 05:39 | Communications and Control Systems - CCTV | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | During a recent site visit to VDP Trackside CCTV it was noted that the CCTV Cable and Wiring Schedule Cxxx-SMN-R3-LST-CR144_PT003-50004 Rev 5.0 - code 1 since 31.01.19 current on eB states that the CAT6A - 8 - 32 - 62 – GRY and __ H124 - 7 - 70 - 52.5 – BLK cables installed to the portal CCTV Intruder system are installed from source cabinet VDP-00-CAB-1733U5. At site these cables are installed from source cabinet VDP-00-CAB-1733U1.
| 05SY - Systemwide | Cxxx-NCR-000579 | NCR | Plumstead Portal Cabinet PLP-00-CAB-1320U1 - 230v cover missing and broken document holder. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-09-06 | 2019-08-02 09:42 | -35 | 2019-07-29 06:34 | Communications and Control Systems - General | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | During a recent IRN site visit to Plumstead Portal Substation CER Room 320 the following issues were noted at Cabinet PLP-00-CAB-1320U1. · Extract door fan filters required cleaning. · Cabinet internal/components were dusty. · Materials were stored in base of cabinet. · I/O Cards A3 & B1 had no terminal rail IDs fitted. · Loose X27 power and earth lead. · Door document holder is broken. . Cover plate/barrier and associated warning label was missing from the 230V LVAC din rail supply terminals.
| 05SY - Systemwide | Cxxx-NCR-000580 | NCR | Plumstead Portal Cabinet Cable Transit Blocks Missing from cabinet PLP-01-CAB-1731U1 |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-09-06 | 2019-08-02 09:31 | -35 | 2019-07-29 07:04 | Communications and Control Systems - General | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Previous Construction - Interfacing issues | Completed |  | During a recent IRN site visit to Plumstead Portal CER it was noted at Cabinets PLP-01-CAB-1731U1 and PLP-01-CAB-1731U2 that an interlink cable had been installed at both cabinets without having Rittal cable transit blocks fitted giving rise to dust/debris ingress. Cable was not Identified with cable ID.
| 05SY - Systemwide | Cxxx-NCR-000581 | NCR | Plumstead Portal PLP-01-CAB-1731U4 LVAC 24V and 240V single cables grouped together. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-09-06 | 2019-08-15 09:45 | -22 | 2019-07-29 07:22 | Communications and Control Systems - General | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | During a recent IRN site visit to Plumstead Portal CER it was noted at Cabinet PLP-01-CAB-1731U4 that the LVAC power cable supplying the cabinet has been installed in single core cables, which have been zip tied direct to the cabinet framework and back plate with no mechanical protection Cxxx-NCR-000390 was previously raised for the same issue at VDP. The 240 voltage will need to separated from the 24V. A new length of sheathed twin and earth will be required from the PDU/terminals to the PSU and will not be run with the 24v
| 05SY - Systemwide | Cxxx-NCR-000582 | NCR | Plumstead Portal Trackside - Corrosion on CCTV System Support Plates. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-10-31 | 2019-11-01 11:51 | 1 | 2019-07-29 07:43 | Communications and Control Systems - CCTV | 3000 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper handling of material | Completed |  | During a pre IRN inspection at Plumstead Portal Trackside Intruder detection system it has been noted that the support plates installed for the Illuminators and Cameras are showing signs of corrosion on the edge of the plates. The plates appear to be of mild steel construction. The plates have also been installed at Connaught Tunnel, Victoria Dock Portal, Royal Oak Portal and Pudding Mill Lane. Possible cause could be bimetallic corrosion due to dissimilar metals being in contact with each other. THis NCR has been raised for Plumstead Portal only until it is established the cause of the corrosion, once established it may be prudent to raise individual NCR's for four other locations.
| 05SY - Systemwide | Cxxx-NCR-000583 | NCR | Paddington Station Damaged CCTV Camera |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-09-30 | 2019-09-20 09:34 | -10 | 2019-07-29 08:04 | Communications and Control Systems - CCTV | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper handling of material | Completed |  | At Paddington Station during a recent CCTV IRN it has been noted that at Cam-10427 the camera mount bracket has sheared off internally from the camera base rendering the camera loose on the circuit board. NCR has been raised to capture damage by others.
| 05SY - Systemwide | Cxxx-NCR-000585 | NCR | PLP Power supplies cables unprotected within cab 1731U4 |  | Contr | __M | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-09-15 | 2019-08-15 09:42 | -31 | 2019-07-29 09:28 | Communications and Control Systems - Power Supplies | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On a Site Walkout it was highlighted inside Cab 1731U1 sits the door entry Cab 1731U4 and the power supply that feeds that is a flex and the cable has been stripped to far back and the single insulted cable has been tie wrapped to the cabinet frame work.
| 05SY - Systemwide | Cxxx-NCR-000586 | NCR | PLP Cabinet Entry Blanks Removed |  | Contr | __M | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-09-15 | 2019-08-15 09:39 | -31 | 2019-07-29 09:50 | Communications and Control Systems - General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | On a site walkout it was highlighted that Patch leads had been installed between 1731U1 and 1731U2 via the cabinet entry points. However entry blanks had been removed for these cables to be installed but no entry blocks had been installed to support the cables and also to stop dust egressing into the Cabinets
| 05SY - Systemwide | Cxxx-NCR-000587 | NCR | PML - Four Span doors terminated to SCADA System Cable Termination Schedule .The schedule has incorrect termination details. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-09-30 | 2019-10-02 10:44 | 2 | 2019-07-29 15:42 | Communications and Control Systems - SCADA/Central Management System | 1000 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | Four Span doors terminated to SCADA System Cable Termination Schedule - Pudding Mill Portal Document Number .Cxxx-SMN-R3-LST-CR094_PT002-50008 Rev 9.0 of the termination schedule as this is the most up to date one on EB and was stated in the FCD. This is in fact not correct and the core IDs for the four span doors will need to be changed. Id information below: PMP-TR-JCN-D102 – Core IDs terminated as X2-1 to X2-6 but should be C1 and C2 for all three cables. PMP-00-JCN-D301 – Core IDs terminated as X2-1 and X2-2 but should be C1 and C2 PMP-00-JCN-D201 – Core IDs terminated as X2-3 and X2-4 but should be C1 and C2 PMP-00-JCN-D101 – Core IDs terminated as X2-5 and X2-6 but should be C1 and C2
| 05SY - Systemwide | Cxxx-NCR-000588 | NCR | PAD - Damaged 12 core Fibre DC6 to CER II |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-11-11 | 2019-10-03 10:12 | -39 | 2019-07-29 14:08 | Communications and Control Systems - Fibre Optic Network | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper handling of material | Completed |  | Damaged 12 core fibre optic cable between DC6 to CER II requires to be replaced. The damaged fibre cable that requires replacing within the UPD is: CR081-DAT-00213. It runs from DC 6 (PAD 5.179U1) on Platform Level to CER II - ODF 1 (PAD 3. 732.U1).
| 05SY - Systemwide | Cxxx-NCR-000589 | NCR | NWP Fibre Drum number/Test |  | Contr | __M | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-08-30 | 2019-08-15 09:35 | -15 | 2019-08-02 07:28 | Communications and Control Systems - Fibre Optic Network | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Insufficient surveillance of subcontractors | Completed |  | When installing the fibre cables at NWP CR504-DAT-00025, CR504-DAT-00026 we never recorded what drum the cables was taking off from
| 05SY - Systemwide | Cxxx-NCR-000590 | NCR | Connaught Tunnel radio infrastructure not compliant with requirement RAI044 |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-08-31 | 2020-09-04 10:23 | 4 | 2019-08-07 07:45 | Communications and Control Systems - Radio | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Requirement RAI044 requires "resilient and overlapping radio coverage such that the loss of a feed from a single location does not result in the total loss of coverage to a tunnel section or other area”. The current design does not meet this requirement as the Connaught Tunnel section is fed from the single location at the CER.
| 05SY - Systemwide | Cxxx-NCR-000591 | NCR | Paddington to Fisher Street tunnel radio infrastructure not compliant with requirement RAI044 |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-09-30 | 2020-03-30 12:39 | -184 | 2019-08-09 10:16 | Communications and Control Systems - Radio | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | Requirement RAI044 requires "resilient and overlapping radio coverage such that the loss of a feed from a single location does not result in the total loss of coverage to a tunnel section or other area”. The current design does not meet this requirement as the tunnel sections from PAD to FIS are all fed from one BTS located at Paddington Station. This situation arises as a result of
| 05SY - Systemwide | Cxxx-NCR-000592 | NCR | Westbourne Park REB - __ cable joint removed from cable tray. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-10-31 | 2019-11-08 11:38 | 8 | 2019-09-07 07:23 | Communications and Control Systems - Fibre Optic Network | 2000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | At Westbourne Park REB it has been noted that an __ cable joint has been removed from its support tray work and the support tray work provided has been utilised to support cable installation. The __ joint has been left lying on the floor and the cables are now prone to damage.
| 05SY - Systemwide | Cxxx-NCR-000593 | NCR | Plumstead Trackside Cabinet PPA-00-CAB-102/17U1 Corrosion. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-01-11 | 2019-12-19 15:57 | -23 | 2019-09-07 09:34 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Material | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | During a recent Trackside visit to Plumstead it was noted at Cabinet PPA-00-CAB-102/17U1 that corrosion was visible around the cabinet door lip and around the door hinge area. See attached Quality Spotter 398. This NCR has been raised and has been assigned to design to capture signs of rusting and can be closed out once corrective action is established. Another NCR will be raised for Construction to carry out the remedial works.
| 05SY - Systemwide | Cxxx-NCR-000594 | NCR | Plumstead Trackside Cabinet PPA-00-CAB-102/15RU1 Corrosion and Termination issue. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-01-11 | 2019-12-19 15:58 | -23 | 2019-09-07 10:02 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Material | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | During a recent Trackside visit to Plumstead the following issues were noted at Cabinet PPA-00-CAB- 102/15RU1, • Slight Corrosion was visible around the cabinet door lip. • Copper was visible at XZ2 Termination C1-2+ (Note that this is Tier 1 connection- Construction site team to liaise with Tier 1 to close out) See attached Quality Spotter 399. This NCR has been raised and has been assigned to design to capture signs of rusting and can be closed out once corrective action is established. Another NCR will be raised for Construction to carry out the remedial works.
| 05SY - Systemwide | Cxxx-NCR-000595 | NCR | Abbeywood Trackside Cabinet ABY-TR-CAB-101/17U1 Faulty Door Lock and labels peeling. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-10-31 | 2019-11-05 15:02 | 5 | 2019-09-07 10:19 | Communications and Control Systems - SCADA/Central Management System | 1000 |  | Equipment Breakdown | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Insufficient quantity of material to do the job | Completed |  | During a recent trackside visit to Abbey Wood the following issues were noted at Cabinet ABY-TR- CAB-101/17U1. • The battery backup section door lock was broken and inoperative. • The yellow warning labels are peeling off. See Quality Spotter QS400.
| 05SY - Systemwide | Cxxx-NCR-000596 | NCR | Abbeywood Trackside Cabinet ABY-TR-CAB-102/16U1 Door Lock issue and corrosion. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-12-21 | 2019-12-10 08:22 | -11 | 2019-09-07 10:27 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | During a recent Trackside visit to Abbeywood the following issues were noted at Cabinet ABY-TR- CAB-102/16U1 • Key type Locking mechanisms had not been installed. • The __ logo was faded. • Corrosion was visible at top section right hand fixing stud. • Corrosion was visible around the plastic door locking mechanism on the inside of door. • It was noted the cabinet label had been printed in Quick Response (QR) Code rather than DataMatrix 2-D Barcode. Cxxx-NCR-000471 was previously raised in eB to capture the non-conformance. Note that the label will scan ok with i-nigma app, therefore the new Forms2mobile App will have to be used to scan. This NCR has been raised and has been assigned to design to capture signs of rusting and can be closed out once corrective action is established. Another NCR will be raised for Construction to carry out the remedial works.
| 05SY - Systemwide | Cxxx-NCR-000597 | NCR | Abbey Wood Trackside Cabinet ABY-TR-CAB-102S/101TU1 Door Lock issue. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-10-31 | 2019-11-05 15:04 | 5 | 2019-09-07 10:31 | Communications and Control Systems - SCADA/Central Management System | 1000 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | During a recent Trackside visit to Abbey Wood the following issues were noted at Cabinet ABY-TR- CAB-102S/101TRU1 • The Battery Backup Section door lock was broken and inoperative. • The cabinet lower section did not have key lock mechanism fitted. • The __ logo was faded. • Asset label Line ID 3 isn’t correct ABW-TR-CAB-102S/101TU1 has an additional R. See attached Quality Spotter QS402
| 05SY - Systemwide | Cxxx-NCR-000598 | NCR | CCTV Coverage CUH - Camera CUH-11-CAM-1109 |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-03-15 | 2019-11-22 15:41 | -114 | 2019-09-05 14:07 | Communications and Control Systems - CCTV | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | CUH-11-CAM-1109 needs to cover the non public side of the door leading in to the stairwell as well as the staircase, this can be achieved by mounting the camera on to the opposite side of the stairwell.
| 05SY - Systemwide | Cxxx-NCR-000599 | NCR | CCTV Coverage CUH - Camera CUH-11-CAM-1113 & CUH-11-CAM-1125 |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-03-15 | 2020-03-30 10:00 | 15 | 2019-09-05 14:30 | Communications and Control Systems - CCTV | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The coverage from cameras CUH-11-CAM-1113 & CUH-11-CAM-1125 is obscured by signage and furniture that has been designed and installed by the T1 contractor.
| 05SY - Systemwide | Cxxx-NCR-000600 | NCR | CCTV Coverage CUH - Coverage of the three Escalators |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-03-15 | 2020-03-16 13:35 | 1 | 2019-09-05 14:39 | Communications and Control Systems - CCTV | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The current CCTV coverage being achieved of the three escalators at Custom House Station is 50% of each escalator which does not comply with the works information.
| 05SY - Systemwide | Cxxx-NCR-000601 | NCR | Help Points and Monitored Doors – CCTV Camera Association Issues |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-01-31 | 2020-02-07 10:11 | 7 | 2019-09-11 15:31 | Communications and Control Systems - SCADA/Central Management System | 5980 |  | Software | Rework | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | An NCR covering the following FORs was proposed to __ on 16/08/2019 with a request that the NCR should be raised by Close of Business on 21/08/2019. *** A ROOT CAUSE ANALYSIS IS REQUIRED FOR THIS NCR *** 3766 CAW - CCTV (Associated Cameras Removed from Monitored Doors) 3762 ELS-CMS-CCTV-Incorrect & Missing Camera Associations 3740 Discrepancy between IO Schedule and present RCM Configuration for CCTV Switching Test Door and Camera correlation 3623 WOO- __ CCTV associations did not switch when in alarm 3616 LIS-CMS- CCTV-Camera Switching and Recording 3606 PLP - CCTV Image Switching Test not working for mentioned CCTV for associated device 3604 WOO - __ LHP call switches wrong Camera 3590 FIS - CCTV - wrong camera switching 3589 FIS - CCTV - camera not switching 3562 CUS-CMS-CCTV-Camera Switching and Recording Issues 3550 WOO-CMS-CCTV-Camera Switching 3480 LIP-CMS-CCTV-Camera Switching and Recording
| 05SY - Systemwide | Cxxx-NCR-000602 | NCR | Potential Configuration Control or Regression Issues |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-01-31 | 2020-02-07 10:32 | 7 | 2019-09-11 15:39 | Communications and Control Systems - SCADA/Central Management System | 2000 |  | Software | Rework | 4 (0.5-3k) | Complete | Verification Problems - Inspection points not adequate | Completed |  | An NCR covering the following FORs was proposed to __ on 16/08/2019 with a request that the NCR should be raised by Close of Business on 21/08/2019. *** A ROOT CAUSE ANALYSIS IS REQUIRED FOR THIS NCR *** 3723 Camera Switching/Recording 3545 Spurious Red Dots appear on __ CCTV Monitor/Tile Destination screen 2361 CAW-__-Telephony Integration
| 05SY - Systemwide | Cxxx-NCR-000603 | NCR | Latest Documentation Not Followed |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-06-30 | 2020-07-21 21:39 | 21 | 2019-09-11 15:44 | Communications and Control Systems - SCADA/Central Management System | 2500 |  | Software | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | An NCR covering the following FORs was proposed to __ on 16/08/2019 with a request that the NCR should be raised by Close of Business on 21/08/2019. *** A ROOT CAUSE ANALYSIS IS REQUIRED FOR THIS NCR *** 3820 __ - TR1 and TR2 MDA wrong placement on graphic 3509 Discrepancy between PID Server Alarm Priority Configuration and Alarm Prioritisation Document 2503 Camera symbol position on mimic 2408 Camera Live Feed Descriptions
| 05SY - Systemwide | Cxxx-NCR-000604 | NCR | RTU Comms / IP Links / Processor Healthy / Dual Processor Comms Issues |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-11-15 | 2019-11-22 12:50 | 7 | 2019-09-11 15:47 | Communications and Control Systems - SCADA/Central Management System | 5000 |  | Software | Rework | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | An NCR covering the following FORs was proposed to __ on 16/08/2019 with a request that the NCR should be raised by Close of Business on 21/08/2019. *** A ROOT CAUSE ANALYSIS IS REQUIRED FOR THIS NCR *** 3720 CAW-CMS-RTU Internals 3719 PWR RTU - Spurious internal alarms 3718 Power RTU Net1 & Net2 lost comms alarms 3717 RTU Internal alarm class needs to be reviewed 3640 Lost Comms - Port X for RTU Internals not available in the CMS 3506 Persistent Alarm State 372 Incorrect Tag description
| 05SY - Systemwide | Cxxx-NCR-000605 | NCR | Lack of Coordination Between Comms Designs and SW Team |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-11-27 | 2020-01-31 00:19 | 65 | 2019-09-11 16:00 | Communications and Control Systems - SCADA/Central Management System | 33500 |  | Software | Rework | 2 (6-60k) | Complete | Design Problem - Inadequate or defective design | Completed |  | An NCR covering the following FOR was proposed to __ on 16/08/2019 with a request that the NCR should be raised by Close of Business on 21/08/2019. *** A ROOT CAUSE ANALYSIS IS REQUIRED FOR THIS NCR *** 3234 CMS-Telephony Integration-RHP and LHP Help Point Alarms
| 05SY - Systemwide | Cxxx-NCR-000606 | NCR | Alarms go to Inhibit List |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-11-27 | 2019-12-02 16:16 | 5 | 2019-09-11 16:15 | Communications and Control Systems - SCADA/Central Management System | 1500 |  | Software | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | An NCR covering the following FORs was proposed to __ on 16/08/2019 with a request that the NCR should be raised by Close of Business on 21/08/2019. *** A ROOT CAUSE ANALYSIS IS REQUIRED FOR THIS NCR *** 3806 Tag set in Out of Service appears in the inhibited alarms list 2384 Alarms appearing in the inhibit list instead of alarm list
| 05SY - Systemwide | Cxxx-NCR-000607 | NCR | Failover / Stability Issues |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-04-30 | 2020-04-30 18:13 | 0 | 2019-09-11 16:18 | Communications and Control Systems - SCADA/Central Management System | 4000 |  | Software | Rework | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | An NCR covering the following FORs was proposed to __ on 16/08/2019 with a request that the NCR should be raised by Close of Business on 21/08/2019. *** A ROOT CAUSE ANALYSIS IS REQUIRED FOR THIS NCR *** 3714 __ Script is not bringing up VIRTUAL MACHINES. Need to setup __ scripts to startup Virtual Machines 2312 UTL servers keep failing
| 05SY - Systemwide | Cxxx-NCR-000608 | NCR | CCTV Issues / CCTV Alarm Issues |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-06-30 | 2020-07-21 21:45 | 21 | 2019-09-11 16:22 | Communications and Control Systems - SCADA/Central Management System | 6000 |  | System Defect | Rework | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | An NCR covering the following FORs was proposed to __ on 16/08/2019 with a request that the NCR should be raised by Close of Business on 21/08/2019. 3784 Systemwide CCTV - RCM CCTV Integration - CCTV switching 3627 ELS - CCTV - OOS 3624 ELS - CCTV - Lost Comms 3618 WOO-CMS-CCTV-Camera Switching and Playback 3587 FIS - CCTV - alarm generated during "Out of Service" 3584 TCR - CCTV - camera switching after ack door open alarm 3549 WOO - __ CCTV Switching issues 3179 COT-CMS-CCTV-Camera Recording and Switching Issues 2159 CAW- __ Showing multiple Cameras as " Connection Lost " 1690 The functionality to assign cameras to LWOD and CID is not in the build
| 05SY - Systemwide | Cxxx-NCR-000609 | NCR | DOO Cameras - No Truth Table |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-11-26 | 2019-11-28 10:19 | 2 | 2019-09-11 16:24 | Communications and Control Systems - SCADA/Central Management System | 2000 |  | Software | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | An NCR covering the following FOR was proposed to __ on 16/08/2019 with a request that the NCR should be raised by Close of Business on 21/08/2019. 3813 Truth Tables are not implemented.
| 05SY - Systemwide | Cxxx-NCR-000610 | NCR | GUI / Display Derived Issues |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-11-27 | 2019-11-28 10:38 | 1 | 2019-09-11 16:25 | Communications and Control Systems - SCADA/Central Management System | 2000 |  | Software | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | An NCR covering the following FORs was proposed to __ on 16/08/2019 with a request that the NCR should be raised by Close of Business on 21/08/2019. 3817 Systemwide-RCM CMS to PID-NTI OOS Functionality 3602 View Display Mimic is displaying programming words 3586 WOO - UPS EASt and West ESR 1 Room SID on GUI dont match Xrail IO
| 05SY - Systemwide | Cxxx-NCR-000611 | NCR | General Alarm Issues |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-11-26 | 2019-11-28 10:57 | 2 | 2019-09-11 16:27 | Communications and Control Systems - SCADA/Central Management System | 2500 |  | Software | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | An NCR covering the following FORs was proposed to __ on 16/08/2019 with a request that the NCR should be raised by Close of Business on 21/08/2019. 3767 OoR alarms require deadband and max limit needs to be reduced 3695 RCM Software on 'Cxxx Controller' workstations 3568 __ - LV switchboards - outgoing CB - circuit no. missing from _KWHR tag 2335 No UPS Lost Comms
| 05SY - Systemwide | Cxxx-NCR-000612 | NCR | Cross passage 06 Cabinet X06-TR-CAB-CP6U1 water ingress due to failed IP blank on top of cabinet. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-12-13 | 2019-12-19 15:55 | 6 | 2019-09-14 10:03 | Communications and Control Systems - General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Not Defined | Completed |  | Water is seeping through the structure of CP06 onto the top ofcabinet X06-TR-CAB-CP6U1. The IP rated blank on top of the cabinet has failed, resulting in water ingress within the cabinet.
| 05SY - Systemwide | Cxxx-NCR-000615 | NCR | sheath damage to cable CR504-CCC-00354 |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-11-30 | 2019-10-03 07:01 | -58 | 2019-09-17 11:47 | Communications and Control Systems - SCADA/Central Management System | 1000 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | During post installation inspection of cable CR504-CCC-00354 from NWP to Connaught tunnel, it was noted that there was minor sheath damage at a section of cable at chainage 18491.
| 05SY - Systemwide | Cxxx-NCR-000616 | NCR | BOND ST DC CABS INSUFFICIENT CABLE ENTRIES |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-01-29 | 2020-01-31 09:57 | 2 | 2019-10-01 18:07 | Communications and Control Systems - General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | BOS-00-1411U1 (DC1) TOTAL TRANSIT ENTRIES REQUIRED 132 CURRENT TRANSIT ENTRIES 60 LID DOES NOT HAVE ENOUGH SPACE TO ADD ADDITIONAL TRANSITS REQUIRED BOS-00-1414U1 (DC2) TOTAL TRANSIT ENTRIES REQUIRED 78 CURRENT TRANSIT ENTRIES 60 LID HAS CAPACITY FOR ADDITIONAL TRANSITS/GLANDS
| 05SY - Systemwide | Cxxx-NCR-000618 | NCR | Royal Oak Portal Trackside CCTV System Corrosion on Support Plates. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-12-11 | 2019-12-19 14:38 | 8 | 2019-10-08 11:24 | Communications and Control Systems - CCTV | 3000 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Insufficient quantity of material to do the job | Completed |  | During a pre IRN inspection at Royal Oak Portal Trackside Intruder detection system it has been noted that the support plates installed for the Illuminators and Cameras are showing signs of corrosion on the edge of the plates. This issue was previously raised at Plumstead Portal when QS/334 and Cxxx-NCR-000582 was raised to capture the non-conformance. Cxxx-NCR-000618 has been raised to capture the non-conformance.
| 05SY - Systemwide | Cxxx-NCR-000619 | NCR | Royal Oak Portal Cabinet CCTVROP-00-CAB-1731U1 Cabinet - Missing Core IDs |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-12-19 | 2019-12-04 14:17 | -15 | 2019-10-08 16:34 | Communications and Control Systems - CCTV | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | During an IRN Inspection at Royal Oak Portal the following issues were noted on the Portal CCTV installation within Cabinet ROP-00-CAB-1731U1. 1. The field power supply cabling terminated at K3-X1 had no core identification installed on the Brown, Blue and Green/yellow cores. This had not been identified on the outstanding works list. 2. Terminals were missing identification tag K3-X1 as detailed on E/plan Cxxx-SMN-R3-DWG-CRG03-50189 X01 3. Green/Yellow terminals require terminal IDs
| 05SY - Systemwide | Cxxx-NCR-000620 | NCR | Installation of incorrect Temperature probes to trackside areas |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-10-31 | 2019-10-24 10:50 | -7 | 2019-10-08 13:05 | Communications and Control Systems - General | 3000 |  | Material | Rework | 4 (0.5-3k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | 5 off temperature probes have been installed with the incorrect temperature ranges. the spec requires a temp range of 25 - 90 Deg C, the incorrect ones have a temperature range of 70 - 150 deg C.
| 05SY - Systemwide | Cxxx-NCR-000621 | NCR | Paddington - 11 door omitted in original design. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-07-31 | 2020-07-09 08:30 | -22 | 2019-10-08 13:40 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | This NCR has been raised in response to RFI_RFI-004620(attached) raised by Tier 1 Contractor in regards to door monitoring additions. 11 monitored doors to be added: See attached marked up drawings & report.
| 05SY - Systemwide | Cxxx-NCR-000622 | NCR | WOO SOR desk Panels Damaged |  | Contr | __M | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-01-10 | 2020-01-09 09:46 | -1 | 2019-10-09 15:21 | Communications and Control Systems | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Two numbers SOR desk panels have been marked. Photos attached shows the damaged panels
| 05SY - Systemwide | Cxxx-NCR-000623 | NCR | ABW installation completed to non-approved design documentation |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-12-23 | 2019-12-12 11:44 | -11 | 2019-10-11 12:50 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | Abbey Wood SER SCADA system has been installed when documentation is not approved by Crossrail or on eB.
| 05SY - Systemwide | Cxxx-NCR-000624 | NCR | ABW Apollo interface module has no approved MCR |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-11-08 | 2019-10-31 11:35 | -8 | 2019-10-11 12:55 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | Abbey Wood fire alarm panel requires a Cxxx interface module of the Apollo brand. This interface module does not have an approved MCR.
| 05SY - Systemwide | Cxxx-NCR-000625 | NCR | PMR-RI Missing Results |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-01-10 | 2020-01-21 14:27 | 11 | 2019-10-16 12:49 | Communications and Control Systems - Radio | 500 |  | Incomplete Works | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | Trackside PMR-RI SAF has missing results.
| 05SY - Systemwide | Cxxx-NCR-000626 | NCR | Connaught East Compound Cabinet COT-00-CAB-ECU1 (Type 6G) Water Ingress |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-12-20 | 2019-11-29 14:03 | -21 | 2019-10-29 07:57 | Communications and Control Systems - CCTV | 500 |  | Equipment Breakdown | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | During Installation Inspection works for Connaught Tunnel portal CCTV it was noted at Cabinet COT-00-CAB-ECU1 that there was water within the base of the cabinet.
| 05SY - Systemwide | Cxxx-NCR-000627 | NCR | Mile End Park Cabinet MEP-00-CAB-005BU5- Missing Cable / Equipment ID's & inaccurate red lines in eB. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-12-20 | 2019-12-24 10:39 | 4 | 2019-10-28 18:34 | Communications and Control Systems - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Quality Surveillance Report QS/094 – Cabinet Test Specification Mile End Park Phase 2.2. found the following; Sample checks were carried out at Cabinet MEP-00-CAB-005BU5 installation against current approved E-Plan document Cxxx-SMN-R3-DWG-CR094_SH006-50008 Rev 2.0 & X01 the following issues were noted. • At Terminal block T2.X1.1 and T2.X1.2 it has been noted that 1 no cable on each block is missing its yellow cable core ID and terminal IDs are missing from block T2.X1.1 • At Terminal Block T1.X1 2 x cores are twisted in 1 x single type crimp, these cores are not identified. • New circuit hasn’t been captured on Rev 2.0 or X01 in eB. • At converter XZ6 the pink and Violet cores have no core idents installed • At Fastflex units FFA3, FFA4, and FFA5 the yellow equipment labels are not present, these should be provided and included on the cabinet equipment list Cxxx-SMN-R3-DWG-CR094_SH006-50008 Appendix 1. • The Cabinet Equipment List provided within the Cabinet referenced Cxxx-SMN-R3-DWG-CR094_SH006-50008 Appendix 1 is not detailed within the current EPLAN Drawing Pack for MEP-00-CAB-005BU5 Cxxx-SMN-R3-DWG-CR094_SH006-50008 Rev 2.0 or X01 on eB. This was noted as the old type and the new type equipment list should placed in the cabinet(s). • At Cabinet top Gland plate SZ sealing frames -UB1, -UB2, -UB10 and -UB11differ from those detailed on current E-Plan. Solid gland plates have replaced the sealing frames & modules.
| 05SY - Systemwide | Cxxx-NCR-000628 | NCR | Mile End Park - FOR 1592 closed out with outstanding works still to complete. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-12-20 | 2019-12-24 10:45 | 4 | 2019-10-28 18:35 | Communications and Control Systems - General | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 2.2.1-CAB-VIS-01 Testing to Cabinet MEP-00-CAB-005BU1 was carried out 06.03.2019. results detailed that test step 4 had failed and all other steps had passed. FOR 1592 had been raised against missing EQ, Danger and ID labels missing at RHP power supply units and signed off as complete on 13.03.2019. A Re-Test was carried out 08.03.2019 and test item 4 was passed. Sample checks during this surveillance revealed that items raised in FOR1592 were incomplete.
| 05SY - Systemwide | Cxxx-NCR-000629 | NCR | Telephony installation changes |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-12-20 | 2020-01-16 17:54 | 27 | 2019-10-24 09:42 | Communications and Control Systems - Telephony | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | During a recent trackside site visit it was noted at Connaught Tunnel that the post mounted telephones have had their supply cable glanded into a local conduit box prior to entry to the post and the cables inner sheath has been installed through a continuous stainless steel __ glanded to the base of the telephone. This method is not as detailed in the Installation Procedures and Guidelines – Telephony System Cxxx-SMN-R3-GPD-CR001-50025 rev 4.0 Section 9.3.4 & 9.4.2 Section 9.3.4 also details the use of Denzo tape at the post base fixing, this has not been carried out at any post mounted ruggedized telephones. Section 9.4.2 details: An earth wire is required to be connected to the telephone central earth terminal from a local earth. The conductor size shall be 1.5mm (0.5-2.5mm for flexible cable, 0.5-4.0mm solid cable). This has not been carried out to the post mounted ruggedized telephones.
| 05SY - Systemwide | Cxxx-NCR-000630 | NCR | Connaught Trackside Cabinets CUH-01-CAB-102P/EU1 and CUH-01-CAB-102P/12U2 corrosion. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-12-20 | 2019-11-29 14:06 | -21 | 2019-11-06 08:17 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Equipment Breakdown | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | During a recent site visit to Connaught West trackside it was noted at cabinets CUH-01-CAB-102P/EU1 and CUH-01-CAB-102P/12U2 that signs of corrosion are present on the cabinets as per the attached Quality Spotter 422.
| 05SY - Systemwide | Cxxx-NCR-000631 | NCR | Connaught West Compound Cabinet COT-00-CAB-WCU1 Corrosion and Damage. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-12-20 | 2019-11-29 14:09 | -21 | 2019-11-06 08:21 | Communications and Control Systems - CCTV | 500 |  | Equipment Breakdown | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | During a recent site visit to Connaught West compound it was noted at Cabinet COT-00-CAB-WCU1 that signs of corrosion and damage are present on the cabinet as per Quality Spotter 423.
| 05SY - Systemwide | Cxxx-NCR-000632 | NCR | Connaught Tunnel Intruder CCTV - No design available at presentation of IRN. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-12-20 | 2019-12-19 14:34 | -1 | 2019-11-06 08:34 | Communications and Control Systems - CCTV | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | During a recent IRN site visit to Connaught Tunnel to carry out the CCTV Intruder detection IRN the following issues were noted. • The application design documentation for the East and West Intruder CCTV was not available, advised that this was a work in progress and not approved on eB. • There were no LVAC design documentation available for the CCTV cabinets at East and West compounds. • LVAC cable asset IDs were not available, Temporary Yellow Asset IDs installed. • East and West CCTV Cabinet E/Plans required Redlines to be completed to reflect changes carried out within the cabinets. • There was no Outstanding Works List available. The IRN was not signed at this time.
| 05SY - Systemwide | Cxxx-NCR-000633 | NCR | Antenna Performance Verification |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-01-31 | 2020-04-24 14:03 | 84 | 2019-11-04 16:55 | Communications and Control Systems - Radio | 500 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During Radio system commissioning at TCR, Antenna performance was questioned and an investigation is required to determine performance against specification.
| 05SY - Systemwide | Cxxx-NCR-000634 | NCR | Trackside External Cabinet Inspections |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-07-23 | 2020-07-24 15:00 | 1 | 2019-11-01 12:02 | Communications and Control Systems - General | 10000 |  | Equipment Breakdown | Rework | 2 (6-60k) | Complete | Material/Preservation Problems - Other | Completed |  | During recent IRN's and general site visits, it has been identified that several external cabinets are showing signs of rust, faulty locks and water ingress. This has prompted the need for all external trackside cabinets be inspected, reports generated to determine a root cause or trend.
| 05SY - Systemwide | Cxxx-NCR-000636 | NCR | __ Cxxx LFEPA system with Routeway is not performing as per the Design |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-12-15 | 2021-01-08 17:01 | 24 | 2019-11-05 14:51 | Communications and Control Systems - Radio | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | NCR – __ Cxxx LFEPA system with Routeway is not performing as per the Design Crossrail have witnessed the Cxxx LFEPA system on several occasions not performing to the intend Design within the Routeway, with an adjacent LFEPA cell leaking considerably into the neighbouring cell. An example here has been the TCR LFEPA cell footprint seen significantly within the BOS cell on several different occasions, in these cases calls originating from the TCR LFEPA cell were heard clearly within the BOS station box. __ T&C team have since acknowledged a LFEPA Routeway issue with the Crossrail Cxxx Delivery Team. Whilst not limited to, the issue contravenes the flowing LFEPA Radio System Performance Specification (Cxxx-PBF-R3-RSP-CRG03-00014) clauses, LFE014, LFE017, LFE018, LFE019 and LFE020. Resolution closeout requirements __ are required to report on: i. In detail the root cause of the problem, any changes made or required to deliver the compliant Design by xx/xx/2019 ii. Prove through testing that all Crossrail LFEPA cell footprints are as Designed, this shall include testing throughout the Routeway at each station/SSP in conjunction with any adjacent neighbouring station/SSP iii. The Design is compliant with the clauses above ------------------------------------------------------------------------------------------------------------- NCR 636 – update wording 14082020 On initiation on this report __’ T&C team acknowledged a LFEPA Routeway cell breathing issue to Crossrail’s Cxxx Delivery Team, subsequently __’ extensive routeway testing has demonstrated the benefits of a direct fed arrangement in Zones 3 & 4. It is believed that a design incorporating a direct fed arrangement will allow cell breathing to be managed. CRL therefore issued Cxxx-PMI-01147, once these works have been completed CRL will review this NCR.
| 05SY - Systemwide | Cxxx-NCR-000637 | NCR | WPA EIS second fibre not connected |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-11-21 | 2019-11-22 09:44 | 1 | 2019-11-07 13:47 | Communications and Control Systems - Fibre Optic Network | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | During a visual survey of the Energisation Inhibit System (EIS) it was seen that the second (diversely routed) fibre pair was not connected to the Westermo 720-ODW-F2 Fibre Optic Modem
| 05SY - Systemwide | Cxxx-NCR-000638 | NCR | PMA EIS second fibre not connected |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-11-21 | 2019-11-22 09:45 | 1 | 2019-11-07 13:55 | Communications and Control Systems - Fibre Optic Network | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | During a visual survey of the Energisation Inhibit System (EIS) it was seen that the second (diversely routed) fibre pair was not connected to the Westermo 720-ODW-F2 Fibre Optic Modem
| 05SY - Systemwide | Cxxx-NCR-000639 | NCR | Qualification for pull testing of operative not available. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-12-20 | 2019-12-24 10:50 | 4 | 2019-11-11 16:32 | Communications and Control Systems - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not qualified | Completed |  | From sample competencies reviewed for Coral Communications operatives it was noted that Antonio Teruzzi is not recorded as having Pull Test certification on the coral Matrix held on the __ Cxxx server folder 13-010 or on Construction Certificates of competency currently on eB Cxxx-SMN-R3-HRR-CR001-50003 Rev 3.0. It has been noted on some Cxxx-14-0028 Pull Test ITP checksheets have been signed off by Antonio Teruzzi
| 05SY - Systemwide | Cxxx-NCR-000640 | NCR | Spare capacity within cabinets to meet GEN166. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-12-20 | 2019-12-19 16:37 | -1 | 2019-11-25 17:20 | Communications and Control Systems - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | A recent visit to the Route Control Centre at Romford found that cabinet CR521-CAB-00013 hasn't net the requirement of GEN 166 that states "GEN166 Equipment cabinets shall be equipped such that at least 20% of the cabinet height (in rack units) is spare, at Completion, to allow for future expansion"
| 05SY - Systemwide | Cxxx-NCR-000641 | NCR | WPA EIS RS232 cable fouled by enclosure door |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-11-29 | 2019-11-25 14:35 | -4 | 2019-11-15 12:53 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The EIS system XZ1 RS232 9-pin D plug hood is the straight style and the cable bend radius is under stress when the enclosure door is shut
| 05SY - Systemwide | Cxxx-NCR-000642 | NCR | PMA EIS RS232 cable fouled by enclosure door |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-11-29 | 2019-11-25 14:33 | -4 | 2019-11-15 12:54 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The EIS system XZ1 RS232 9-pin D plug hood is the straight style and the cable bend radius is under stress when the enclosure door is shut
| 05SY - Systemwide | Cxxx-NCR-000643 | NCR | PMA EIS MS146SIG Power supply cover missing |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-11-29 | 2019-11-27 12:05 | -2 | 2019-11-15 12:55 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Personnel Error - Other human error | Completed |  | During a survey it was noticed that the MS146SIG board in PMA-00-CAB-00U2 was missing the perspex cover from the 230Vac connection area.
| 05SY - Systemwide | Cxxx-NCR-000644 | NCR | PMA EIS Fibre Optic Convertor Status Alarm |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-12-21 | 2019-12-20 08:51 | -1 | 2019-11-15 12:56 | Communications and Control Systems - SCADA/Central Management System | 2000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | PMA EIS Fibre Optic Convertor Status is not monitored by the CMS, the facility is available on the Westermo 720-ODW-F2 module and should report the status to the CMS at the RCC.
| 05SY - Systemwide | Cxxx-NCR-000645 | NCR | WPA EIS Fibre Optic Convertor Status Alarm |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-12-21 | 2019-12-20 08:49 | -1 | 2019-11-15 12:58 | Communications and Control Systems - SCADA/Central Management System | 2000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | WPA EIS Fibre Optic Convertor Status is not monitored by the CMS, the facility is available on the Westermo 720-ODW-F2 module and should report the status to the CMS at the RCC.
| 05SY - Systemwide | Cxxx-NCR-000646 | NCR | Eleanor street - Asset labels peeling off equipment. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-02-14 | 2020-03-09 09:16 | 24 | 2019-11-25 18:12 | Communications and Control Systems - General | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | During a recent site walkdown to Eleanor street shaft the following issues were noted relation to CCTV asset labelling. 1. At Camera ELS-00-CAM-7407 the white asset label was peeling off the asset tag plate. 2. At Camera ELS-00-CAM-7407 the yellow equipment label did not have all the required information, the end of line 2 is missing the text BLK. The label is also peeling off the asset. 3. At Camera ELS-00-CAM-7403 the yellow equipment label was peeling off the asset. 4. At Camera ELS-00-CAM-7402 the white asset label was missing from the asset tag plate. 5. At Camera ELS-00-CAM-7404 the yellow equipment label was peeling off the asset.
| 05SY - Systemwide | Cxxx-NCR-000648 | NCR | Damaged Radio Cable at ROP FD2011 |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2019-12-20 | 2019-12-04 14:25 | -16 | 2019-11-29 08:49 | Communications and Control Systems - Radio | 2000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Testing of radio feeder cable FD2011 showed a short circuit fault at 11M. Fault visually found in duct route. Cable requires replacement. To facilitate removal Cxxx will require the site team to remove and replace Firestopping at the FOSC
| 05SY - Systemwide | Cxxx-NCR-000649 | NCR | Eleanor Street - Camera shot can't be achieved, different type camera lens is required with additional cabling for the heater within the housing. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-01-30 | 2020-01-25 09:29 | -5 | 2019-12-02 13:39 | Communications and Control Systems - CCTV | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | During a recent site walkdown to Eleanor street shaft it was noted that external camera doesn’t capture the required screen shot due to the distance away from the required shot.
| 05SY - Systemwide | Cxxx-NCR-000650 | NCR | Eleanor Street CER Cabinets ELS-00-CAB-001AFU1, U2, U3 & U4 issues not picked up for hand over. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-02-07 | 2020-02-24 14:41 | 17 | 2019-12-10 11:27 | Communications and Control Systems - General | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During a recent site walkdown at Eleanor Street Shaft the following generic issues 1, 2, & 3 were noted at cabinets ELS-00-CAB-001AFU1, U2, U3 & U4. 1. The internal Earth bond to each cabinet was missing its internal Earth Cable Asset ID. 2. The additional internal Earth bar support had not been fitted. 3. The equipment list installed to the inside of the cabinet door was not the electronic version. 4. At Cabinets ELS-00-CAB-001AFU2, & U3 it was noted that the gland banjo at the supply cable gland did not have earth fly leads fitted as cabinets U1 & U4. 5. At Cabinet ELS-00-CAB-001AFU4 the following issues were noted. · Internal Fast flex units FFA3, FFA4, FFA5 & FFA6 had no yellow equipment labels fitted. · The front cabinet door handle of Cabinet ELS-00-CAB-001AFU4 was found to be loose. · The current E/plan for Cabinet ELS-00-CAB-001AFU4 did not reflect the change to top gland plate entry layout and 1 x gland appears to have gap between gland and gland plate. 6. At Cabinet ELS-00-CAB-001AFU4 the bolts securing the solid type gland plates protrude excessively into the Cabinet. 7. At Cabinet ELS-00-CAB-001AFU2 it was noted that cable ties were not cut flush as detailed in Installation Procedures and Guidelines – Structured Cabling Cxxx-SMN-R3-GPD-CR001-50017 sections 5.1 and 13. 8. At the Cabinet isolators it was noted that the cabinet supply cabling was missing cable ties below the isolators and the tray work was missing grommet type edging strip.
| 05SY - Systemwide | Cxxx-NCR-000651 | NCR | Eleanor Street - Failed VAP against asset labelling. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-02-28 | 2020-03-31 08:02 | 32 | 2019-12-10 10:20 | Communications and Control Systems - General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | During a recent site walkdown at Eleanor street shaft it was noted at cabinets ELS-00-CAB-001AFU4 and at the Tier 1 SCADA Marshalling Cabinet that some SCADA Cable Asset IDs were incorrect & incomplete missing information and had ? txt on some labels. This issue had previously been raised under QS/055. The issue was not identified as an open snag on the site outstanding works list. Crossrail have also carried out VAP (Cxxx-XRL-Z3-RGN-CR094_SH007-50001) with 48% negative observations. Another VAP will be required at site once the observations and Quality Spotter has been addressed.
| 05SY - Systemwide | Cxxx-NCR-000652 | NCR | Eleanor Street - Cabinet ELS-00-CAB-001AFU5 Incomplete |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-01-31 | 2020-02-02 21:02 | 2 | 2019-12-10 11:14 | Communications and Control Systems - General | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | During a recent site walkdown at Eleanor street shaft it was noted that cabinet ELS-00-CAB-001AFU5 was incomplete and the following issues were noted: · Cable cores had been disconnected and ends tapped over at KT2 and X24+ · Green/yellow cable core links had been installed between KT1 (18) and KT2 (15) · Green/yellow cable core links had been installed at terminal rail X1 Cabinet ELS-00-CAB-001AFU5 supply __ F10 was in the off position with tape detailing –(To be energised once handed over to RFL)
| 05SY - Systemwide | Cxxx-NCR-000653 | NCR | Water in Cabinet COT-00-CAB-ECU1 |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-02-14 | 2020-01-31 11:35 | -14 | 2019-12-11 14:43 | Communications and Control Systems - General | 4000 |  | Manufacturing Defect | Rework | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Inspection of cabinet revealed water inside of the cabinet. THe water had evaporated and condensated in the cab therefore water has dripped from the top onto the components
| 05SY - Systemwide | Cxxx-NCR-000654 | NCR | ROP Intruder Detection Blind Spot |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-02-28 | 2020-01-31 11:21 | -28 | 2019-12-16 10:29 | Communications and Control Systems - CCTV | 20000 |  | Design | Rework | 2 (6-60k) | Complete | Design Problem - Other | Completed |  | During Testing and Commissioning of the Royal Oak Portal Tunnel Intruder Detection System, a blind spot has been identified due to a lamp post being installed adjacent to the Redscan Detectors mounted in the center of the platform. Devices affected: ROP-TR-ILD-6161 ROP-TR-ILD-6152
| 05SY - Systemwide | Cxxx-NCR-000655 | NCR | Lack of User Profile/HF Test Specifications and Testing |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-08-21 | 2020-09-27 20:10 | 37 | 2019-12-19 15:27 | Communications and Control Systems | 15000 |  | Testing and Commissioning | Rework | 2 (6-60k) | Complete | Verification Problems - Inspection points not adequate | Completed |  | In Oct 2018 an NCR (Cxxx-NCR-000375) was raised relating to HF Testing and the approach __ Cxxx were going to take in testing the User Profiles & HF elements of the Cxxx CMS/__ system. The approach detailed the following documents that would be used as part of the User Profiles & HF Testing and __ Cxxx would carry out the final HMI/HF validation prior to the formal Operability Evaluations. • Mimic and Symbol Document • Truth Tables • Operator Roles Matrix • Alarm Routing and Prioritisation Matrix • HMI and Alarm Consistency Guidelines • Intended Design Specification CRL were assured that the User Profile testing were complete. In the Pulse slides issued in April & May, two weeks (w/c 12th & 19th April 2019) were dedicated to CMS User Profile Testing and in the Pulse slide of the 10th May 2019 it clearly states "Note: 23 defects raised against ___User profile have been converted to a single HMI User Story for close-out with the development team (HF User profile testing will then be completed)." During the Operability Evaluations it was identified that the User Profile testing had not been completed, in fact this was confirmed within an email from the Cxxx Test Manager to CRL on the 17/12/19 (after the Operability Evaluations) that stated "This area of testing is yet to complete so no certificates/reports are available.....This week I’m working with both the Marks and Manjula to put together a plan to cover the test effort and review the enablers once more".
| 05SY - Systemwide | Cxxx-NCR-000656 | NCR | CUH -Cxxx-FCD-000508 still at initiate stage whilst works have been carried out. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-04-29 | 2020-04-28 08:53 | -1 | 2020-01-06 13:32 | Communications and Control Systems - CCTV | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | The FCD has no redlined documents attached and details the affected documents to be CCTV Equipment Setting out Drawings: Cxxx-SMN-R3-DDA-CR145_1-30052 Rev C02 Cxxx-SMN-R3-DDA-CR145_1-30053 Rev C01 Checks on eB have revealed that these documents have been redlined and detail additional cameras and relocated cameras, the documents have been referenced Cxxx-FCD-000508. Their status on eB is as follows: Cxxx-SMN-R3-DDA-CR145_1-30052 Rev X02 code 1 since 19.09.2019 Cxxx-SMN-R3-DDA-CR145_1-30053 Rev X02 code 1 since 19.09.2019 The changes detailed have not gone through the FCD process. It has also been noted that the following redlined drawings – CUH - CCTV Equipment Layout Drawings for Platform level currently on eB reference Cxxx-FCD-000508. Again the redlines detail additional cameras and relocated cameras. The changes detailed have not gone through the FCD process.
| 05SY - Systemwide | Cxxx-NCR-000657 | NCR | CUH - Release Note uncontrolled copy at site. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-03-27 | 2020-03-06 13:19 | -21 | 2020-01-06 13:38 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Copy of External Engineering Release Certificate CMS-__ Configuration Release Note 4.12.1.19 held at site found that there weren’t any names or signatures for prepared by, checked by, or approved by on the certificate resulting in uncontrolled copy at site.
| 05SY - Systemwide | Cxxx-NCR-000659 | NCR | Cable damage at PLU sidings building Room M1.10 |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-03-31 | 2020-01-31 09:11 | -60 | 2020-01-15 09:38 | Communications and Control Systems - Fibre Optic Network | 2000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | During installation of fibre cables from Rm M1.10 to the cleaners cab ( Cable no CR526-DAT-00910) damage was found to the existing fibres previously installed
| 05SY - Systemwide | Cxxx-NCR-000660 | NCR | Woolwich OHLE switch changed on RailCom Manager. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-05-04 | 2020-05-15 16:33 | 11 | 2020-01-20 16:36 | Communications and Control Systems - SCADA/Central Management System | 2075 |  | Software | Rework | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | Woolwich OHLE switch changed on RailCom Manager. Between build 4.15 and 4.16 a change was made that resulted in the mimic button for switch 102/13 will operate 101/14, and vice versa.
| 05SY - Systemwide | Cxxx-NCR-000661 | NCR | Incorrectly Terminated WOO DOO Coaxal Cables |  | Contr | __M | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-02-26 | 2020-02-12 09:25 | -14 | 2020-01-17 08:44 | Communications and Control Systems - Driver only Operation CCTV | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | On a site Inspection its been highlighted that some of the coxal cables have poorly been terminated. These cables terminate from the DOO Bombadier cab back to the CDN cabinet
| 05SY - Systemwide | Cxxx-NCR-000662 | NCR | Liverpool Street Station - Incorrect asset equipment labels delivered and installed at site. Correct labels delivered and not installed. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-09-14 | 2020-09-18 20:27 | 4 | 2020-01-28 09:01 | Information Management - Asset Information | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Description - Tier 1 contractor have been issued asset labels by Cxxx to install and verify on Cxxx assets installed at Liverpool Street Station. Difference to requirements - The yellow equipment labels have failed asset verification due to the asset equipment label barcode not including serial number. This was highlighted in December 2019 when Tier started scanning in asset labels via the forms2mobile app and failures were found via the app. New labels that included serial numbers had been issued to site in July 2018. The new labels weren't handed over to the Tier 1 to install, as these were held back by __ site manager awaiting an agreed method with Tier 1 to replace the affected labels and subsequently they have been found in a cupboard at site.
| 05SY - Systemwide | Cxxx-NCR-000663 | NCR | Systemwide - Repeat Cabinet Test Specifications Phase 2.2 found incomplete. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-04-30 | 2020-04-30 15:31 | 0 | 2020-02-06 16:40 | Communications and Control Systems - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | Due to11 No observations and 2 No NCR’s being raised on previous surveillances; another NCR has been raised to identify the root cause and put in place actions to prevent recurrence.
| 05SY - Systemwide | Cxxx-NCR-000664 | NCR | BOS DC1 and DC2 insuffient cable entries. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-02-15 | 2021-03-04 13:02 | 17 | 2020-02-06 15:46 | Communications and Control Systems - General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | NCR-000616 identified insufficient cable entries into the cabinet.The proposed option is to make DC1&2 larger 800x800 size cabinets. this requires going through the spacing footprint within the room. BOS-00-1411U1 (DC1) TOTAL TRANSIT ENTRIES REQUIRED 132 CURRENT TRANSIT ENTRIES 60 LID DOES NOT HAVE ENOUGH SPACE TO ADD ADDITIONAL TRANSITS REQUIRED BOS-00-1414U1 (DC2) TOTAL TRANSIT ENTRIES REQUIRED 78 CURRENT TRANSIT ENTRIES 60 LID HAS CAPACITY FOR ADDITIONAL TRANSITS/GLANDS
| 05SY - Systemwide | Cxxx-NCR-000665 | NCR | Abbey Wood Trackside Cabinets- incomplete snag items signed off as complete. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-06-30 | 2020-07-10 11:49 | 10 | 2020-02-11 08:50 | Communications and Control Systems - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | Quality Surveillance Report QS/097 – Abbey Wood Trackside Cabinet Snag Management found that snag items on Site Snag Register had been marked as complete. Inspection at site found that the snag items remain open.
| 05SY - Systemwide | Cxxx-NCR-000666 | NCR | Generic NCR to cover camera issues at site |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-12-31 | 2021-01-29 14:56 | -336 | 2020-02-13 17:51 | Communications and Control Systems - CCTV | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | This NCR will be used to cross reference any issues raised at camera coverage reviews
| 05SY - Systemwide | Cxxx-NCR-000667 | NCR | PMP Redline Scada termination Schedule Miss Alignment |  | Contr | __M | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-07-30 | 2020-06-30 09:02 | -30 | 2020-03-05 09:44 | Communications and Control Systems - SCADA/Central Management System | 2500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | On site inspection for final verification of redlines produced for scada terminations. It was highlighted how cables and where cables are terminated do not align with the lasted X0's available on EB inside the T1 marshalling cabinet.
| 05SY - Systemwide | Cxxx-NCR-000668 | NCR | VDP Redline Scada Termination Schedule Miss Alignment |  | Contr | __M | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-04-30 | 2020-03-25 15:46 | -36 | 2020-03-05 11:15 | Communications and Control Systems - SCADA/Central Management System | 2500 |  | Design | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | On Site Inspection for final verification of redlines produced for scada terminations. It was highlighted how cables and where cables are terminated do not align with the latest X0's available on EB inside the T1 Marshalling Cabinet.
| 05SY - Systemwide | Cxxx-NCR-000669 | NCR | ILD at NWP installation requires moving |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-03-20 | 2020-03-16 15:07 | -4 | 2020-03-06 08:42 | Communications and Control Systems - CCTV | 3500 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | ILD 9161 installed to design but does not operate to the correct standard. The laser does not capture the area around the existing CMS
| 05SY - Systemwide | Cxxx-NCR-000670 | NCR | Incorrect cable used for OHLE VT analogue signals at PPA (101/16 & 102/15) |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-06-25 | 2020-06-26 15:49 | 1 | 2020-03-09 15:33 | Communications and Control Systems - SCADA/Central Management System | 20000 |  | Design | Rework | 2 (6-60k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | Voltage Transducers in PPA-00-CAB-101/16U1 and PPA-00-CAB-102/15U1 have been found to be unstable when in operation, investigation has found that the cable installed is a 2pr x 0.9mm telecom cable that is overall twisted and not twisted pairs. This has been found to cause interference between the two analogue signals in the same cable. The solution is to install a 5pr x 0.9mm cable that has individually twisted pairs. The two 2pr cables to be replaced are CR505-DAT-00089 and CR505-DAT-00089, due to the lack of space for glanding additional cables in the enclosures(s) the most efficient way is to replace rather than add cables.
| 05SY - Systemwide | Cxxx-NCR-000671 | NCR | Required STI score not achieved |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-04-29 | 2020-04-15 14:04 | -14 | 2020-03-11 16:06 | Communications and Control Systems - Public Address Systems | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | Following STIPA testing as conducted by __, it has been highlighted two areas have fallen below the required 0.5 STI Speech intelligibility score. These are the Eastern Ticket Hall level -1 and the Western Ticket Hall escalators. Eastern Ticket hall level -1 has achieved 0.49 STI which is 0.01 below the requirement. This is considered marginal and a concession has been applied for with LU. Western Ticket hall escalators have achieved a score of 0.48 STI which is 0.02 below the requirement. This is considered marginal and a concession has been applied for with LU.
| 05SY - Systemwide | Cxxx-NCR-000672 | NCR | Lack of T&C Specifications prior to carrying out testing and maintaining Test Records (on elements that do not go to Cxxx's HMI, but to 3rd parties) |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-05-30 | 2020-05-28 08:18 | -2 | 2020-03-12 11:33 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | Following the discussions held between CRL (Prav Dissanayake) and __ (Pete W__), it was identified that __ Cxxx has carried out SCADA testing with 3rd parties/own interfaces without maintaining the appropriate ITPs (i.e. the necessary test specifications) accepted by CRL, for the purposes of recording the testing activities and test results. The appropriate ITPs for all configured and tested elements must be recorded and maintained as per the requirements in the Works Information Volume 2B – Part 20 – Quality Management CRL1-XRL-V3-XWI-CR001-50131. Next actions: - __ Cxxx to assess the elements that have been tested without the necessary ITPs and produce and maintain the appropriate ITPs - __ Cxxx to assess the elements that have not yet been tested and produce and maintain the appropriate ITPs Any rework required in order to make the 'informal' records 'formal' and/or any further testing required (as stated in Cxxx-EWN-00921) to make the test records acceptable to CRL will be assessed. If deemed appropriate __ Cxxx will incur disallowed costs to rectify this matter.
| 05SY - Systemwide | Cxxx-NCR-000673 | NCR | CUH scada |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-05-31 | 2020-05-21 13:58 | -10 | 2020-03-27 10:47 | Communications and Control Systems - SCADA/Central Management System | 2000 |  | Incorrect Installation | Reject | 4 (0.5-3k) | Complete | Personnel Error - Not Defined | Completed |  | While carrying out verification of scada documentation we found out that the install and documentation were incorrect
| 05SY - Systemwide | Cxxx-NCR-000674 | NCR | Systemwide DOO SCADA Terminations - FCD & Red Line process not being followed. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-06-30 | 2020-07-13 07:22 | 13 | 2020-03-27 12:05 | Communications and Control Systems - SCADA/Central Management System | 2500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Lack of procedure | Completed |  | At Liverpool St Station there was modifications carried out by the Test & Commissioning engineers on DOO SCADA Terminations. Although changes were captured under FOR1270, the changes haven't been captured through the FCD & Red Line Process.
| 05SY - Systemwide | Cxxx-NCR-000675 | NCR | CCTV Coverage of 2x PHPs at CUH & 1x RHP at FIS |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-09-30 | 2020-09-17 15:29 | -13 | 2020-04-01 14:51 | Communications and Control Systems - CCTV | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | Due to a limitation with the Verint VMS not being able to synchronise simultaneous audio feeds with one video stream (2 PHPs covered by 1 Camera), 2x additional cameras are required at Custom House Station and 1x additional camera is required at Fisher Street Shaft. The three additional cameras will ensure every PHP and RHP across the project is assigned a unique camera thus eliminating the need to associate multiple audio streams to a single video stream.
| 05SY - Systemwide | Cxxx-NCR-000676 | NCR | Mile End Park Cabinet MEP-00-CAB-0031BU1 & MEP-00-CAB-005BU1 Test Specifications has passed with notable defects. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-06-26 | 2020-06-26 15:13 | 0 | 2020-04-07 07:31 | Communications and Control Systems - General | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Cabinets test Specification – Mile End Park Shaft 2.2 – Visual Check Cxxx-SMN-R3-RSP-CR094_SH006-50016 Revision X01 code 1 since 02.09.2019 is the current version on eB and details the test specification for cabinet MEP-00-CAB-003BU1 as a Pass. Items found: • Cables entering Cabinet MEP-00-CAB-003BU1 through conduits do not reference Cabinet MEP-00-CAB-003BU1 in Cable Asset ID line 2. • Yellow supply information label peeling from front of Cabinet • Cable CR513-TEL-00105 Termination is of poor quality and requires re-termination • Cable Label CR513-TEL-00105 requires replacing as this details ??? on Line 2 of the cable asset label • Cabinet has an incorrect version of E/Plan and Asset Map installed C01. This should be version X01 as held on eB MEP-00-CAB-005BU1 • Cables cores terminated at T11.X1 to T14.X1 have no core identification installed as installed on similar field cores in other cabinets systemwide (To be confirmed if by Construction) • Yellow supply information label peeling from front of Cabinet This does not meet the requirements of Test and Commissioning Plan Cxxx-SMN-R3-STP-CR001-50031 Revision 5.0 Test Specifications will be created for each sub-system and will be used to validate the systems.
| 05SY - Systemwide | Cxxx-NCR-000677 | NCR | Royal Oak Portal - Camera moisture ingress and label(s) peeling. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-08-31 | 2020-07-24 16:23 | -38 | 2020-04-23 | Communications and Control Systems - CCTV | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During a recent site walkdown at Royal Oak Portal water/moisture was noted on the inside of external Camera ROP-00-CAM-6103 glass dome, it is unclear if this has penetrated to the camera lens. The cable entry is to the back of the camera. Possibility that the camera housing haven't been cleaned prior to yellow equipment labels being installed. All external labels at this site will have to be verified that they are fit for purpose.
| 05SY - Systemwide | Cxxx-NCR-000678 | NCR | Scope of GSM-R RSV Fringe Test Reports may not be acceptable to NoBo. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-07-27 | 2020-07-08 15:30 | -19 | 2020-05-07 15:40 | Communications and Control Systems - Radio | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Information not detailed | Completed |  | Crossrail have expressed concern that the scope of the fringe testing detailed in the Fringe Test reports may not be acceptable to NoBo.
| 05SY - Systemwide | Cxxx-NCR-000679 | NCR | Concerns regarding overlapping radio coverage |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-07-31 | 2020-08-14 09:56 | 14 | 2020-04-21 18:53 | Communications and Control Systems - Radio | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Crossrail have raised concerns regarding overlapping coverage at portals referring to clause RAI044. __ believe that the intent of the WI and subsequent PMIs has been met in full and this is supported by agreement of test results. This NCR has been raised to provide a mechanism for Crossrail to highlight the issues but also record that there is no further works required and the NCR will be closed with the disposition "Use As-Is".
| 05SY - Systemwide | Cxxx-NCR-000680 | NCR | Tracking concerns of internal alarm list definitions to closure. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-06-01 | 2020-11-13 17:27 | 165 | 2020-04-29 12:24 | Communications and Control Systems - SCADA/Central Management System | 25000 |  | Software | Rework | 2 (6-60k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Cxxx-NCR-000481 was originally raised on 21/03/2019 against alarm list descriptions that were overdue. Significant progress has been made to close out Cxxx-NCR-00481 and this NCR has been raised to capture the remaining items required for Trial Running. 1. Item 1: Overall list of Comms assets per location a. Radio assets will need to be incorporated into the main Comms Asset List b. The cross referencing between Comms Asset List and Cxxx Internal Alarms List 2. Item 2: Generic alarm list per Comms asset type a. Outstanding Assets types (e.g. ILD alarms) 3. SNMP/Other configuration details of the alarms from Asset Type a. Configuration details for other assets. Examples: i. PA/VA – we seem to get our PA RTU alarms from the VIPA Virtual Machine, how do we get these alarms and how are they mapped to PAV/PAN/PAR tags? ii. CDN – IP address of Prime Server? iii. PID Servers / CIS Alarms? iv. RTU Internal alarms? v. Cxxx Servers?
| 05SY - Systemwide | Cxxx-NCR-000681 | NCR | Fault Observation Reports related to CCTV System |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-01-31 | 2021-03-31 08:54 | 59 | 2020-05-05 16:52 | Communications and Control Systems - SCADA/Central Management System | 20000 |  | Software | Rework | 2 (6-60k) | Complete | Design Problem - Inadequate or defective design | Completed |  | There are 13 No Fault Observation Reports listed that are required to be closed out to issue RCC CMS IAC for trial running. 5791 __-13700 CAW - CCTV (Highlighted camera changes randomly) 5730 __-13554 Systemwide - "Time Unsynchronised" CCTV Alarm Issues 5794 __-13701 Systemwide CCTV - Verint VMS System Alert Issues 5627 __-13434 ABX-CMS-CCTV-DOO Video Streams Not available 5738 __-13586 Systemwide CCTV - "Alarm Recordings" Operator Confirmation Observation 5806 __-13703 Systemwide - __ CCTV - CMS & __ Failover with a Loss of a VMS 5764 __-13698 System wide - CCTV switching / Functionality issue 5971 __-13976 Systemwide - CMS CCTV - Live Streams become unavailable after a few hours (Interface Issue) 5973 __-13978 Systemwide - CMS CCTV - Recorded clip stuck in a "Recording" state following a Fail-over 3472 __-11427 Systemwide-RCM CCTV Integration-CCTV Driver: Camera Status 5972 __-13977 Systemwide - CMS CCTV - Unable to select position in recorded clip 5763 __-13697 Systemwide - CMS CCTV - Playback Functionality 5869 __-13785 LSX-CCTV -Door/ESC Alarm Mapping Discrepancy in Asset DB (23 Mar 20) and Build 19 Plastic Alarm Mapping Sheets The close out date for the NCR is to be set as 1st June 2020 when Mark Punglia proposes action.
| 05SY - Systemwide | Cxxx-NCR-000682 | NCR | Farrindon STIPA marginal failure |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-07-27 | 2020-07-29 13:45 | 2 | 2020-05-14 15:18 | Communications and Control Systems - Public Address Systems | 500 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Two areas have failed the required STIPA levels as set out in the works information. These are: Eastern Ticket Hall Level -1 which achieved 0.49 STI, 0.01 below the required 0.5 STI Western Ticket Hall escalators which achieved 0.48, 0.02 below the required 0.5 STI A Risk assessment has been carried out which details the situation
| 05SY - Systemwide | Cxxx-NCR-000684 | NCR | Lack of internal coordination for repeated software related fault observation reports. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-08-28 | 2020-11-13 18:14 | 77 | 2020-06-15 08:05 | Communications and Control Systems - Station Management System | 13500 |  | Software | Rework | 2 (6-60k) | Complete | Design Problem - Other | Completed |  | The following FORs have been raised and have been grouped as lack of internal coordination. FOR 6051 - ABX-CMS-CCTV-__ Decoder RCM Monitoring (SNMP Issues) FOR 5856 - System wide - TEL calls playback Audio keeps dropping in middle of call FOR 6088 - Systemwide CCTV - CCTV switching and playback available when a camera is in a "Failed" state FOR 6022 - Alarm Testing
| 05SY - Systemwide | Cxxx-NCR-000685 | NCR | Fisher Street Cabinet FIS-03-CAB-373U1 Eplan Issues |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-09-04 | 2020-09-18 15:14 | 14 | 2020-06-23 14:00 | Communications and Control Systems - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | During a recent site walkdown at Fisher Street Shaft the following issues were noted at cabinet FIS-03-CAB-373U1 Eplan Cxxx-SMN-R3-DWG-CRG03-50134 Rev X01.The cabinet had previously gone through Cabinet Test Specification phase 2.2 – Visual Check and it currently has a signed off Pass status on eB in document - Cabinet Test Specification Cxxx-SMN-R3-RSP-CR086_SH003-50014 Rev X01. Eplan Cxxx-SMN-R3-DWG-CRG03-50134 Rev X01 is the current version on eB and was signed off Code 1 25.09.2019. Cxxx-FCD-000489 has been raised for the redline drawing update 11.09.2019, this is currently not approved on eB, at initiate stage and the planned end date has passed. There is a Revision X01 version of the E/plan within the cabinet which differs from the X01 version currently held on eB, as detailed within the quality spotter (attached).
| 05SY - Systemwide | Cxxx-NCR-000686 | NCR | CP03, 04 & 08 Labels peeling on equipment |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-09-11 | 2020-08-14 13:08 | -28 | 2020-06-23 14:28 | Communications and Control Systems - General | 3000 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Not Defined | Completed |  | During a recent Pre VAP site visit to Cross Passages 03, 04 and 08 it was noted that yellowinformation/warning labels were not correctly adhered to the respective cabinets/Radio repeaters. It was also noted that at CP08 repeaters the label type and position differed, at CP04 the warning label was fitted to the top of repeater and not on the door. See attached Quality Spotter 519 for reference.
| 05SY - Systemwide | Cxxx-NCR-000687 | NCR | Abbey Wood Cabinet ABW-TR-CAB-102/16U1 Water Ingress |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-12-31 | 2020-12-04 13:48 | -27 | 2020-06-23 15:34 | Communications and Control Systems - General | 30000 |  | Equipment Breakdown | Rework | 2 (6-60k) | Complete | Design Problem - Inadequate or defective design | Completed |  | During a recent pre VAP trackside site visit to at Abbey Wood it was noted at MS146 Cabinet ABW-TR-CAB-102/16U1 that a small quantity of water was present within the cabinets top section, this has caused some corrosion along the inside of the top section. See attached Quality Spotter 522 for reference.
| 05SY - Systemwide | Cxxx-NCR-000688 | NCR | Test Specifications to be written after associated PAC & IACs have been issued. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-09-04 | 2020-09-18 10:34 | 14 | 2020-06-23 17:03 | Communications and Control Systems - General | 500 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | 26 No additional Test Specifications have been identified as required (see reference documents) after associated PACs and IACs have been issued to eB.
| 05SY - Systemwide | Cxxx-NCR-000689 | NCR | Delays in software release and internal software processes |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-07-31 | 2020-11-02 11:40 | 94 | 2020-06-23 18:33 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Software | Rework | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | Software Release was due to the change in the published release date for Software Build 22, concerns have been raised around the software release process. The concerns cover : 1. Communication process with Crossrail and T & C for notification of changes to release dates 2. Delays in communicating with all parties about possible show stoppers in a release 3. New IFAT testing and certification process 4. Internal Software processes and procedures
| 05SY - Systemwide | Cxxx-NCR-000690 | NCR | CP10,11 & 12 Labels peeling on equipment |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-09-11 | 2020-08-14 13:09 | -28 | 2020-07-07 12:43 | Communications and Control Systems - CCTV | 3000 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | During a recent Pre VAP site visit to Niche 03 and Cross Passages 10, 11 and 12 it was noted that yellow information/warning labels and White Asset Identification Labels were not correctly adhered to the respective cabinet doors. See attached Quality Spotter 528.
| 05SY - Systemwide | Cxxx-NCR-000691 | NCR | STIPA test marginal failure |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-08-31 | 2020-07-29 12:43 | -33 | 2020-06-29 14:21 | Communications and Control Systems - Public Address Systems | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | STIPA testing has concluded that two areas of the station fail to meet the 0.5 STI criteria as set out in BS5839 standard and the works information. These two areas are: Eastern Ticket Hall level -1 which achieved 0.49STI & the Western Ticket Hall escalators which achieved 0.48 STI. A Risk Assessment has been raised to detail the issues. (Cxxx-SMN-R3-__-N105-50001)
| 05SY - Systemwide | Cxxx-NCR-000692 | NCR | Concerns over Performance/Load Testing at Ashby. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-02-28 | 2021-02-25 22:36 | -3 | 2020-06-30 15:22 | Communications and Control Systems - General | 500 |  | Software | Rework | 4 (0.5-3k) | Complete | Verification Problems - Inspection points not adequate | Completed |  | Evidence of Performance / Load testing at Lab & Site of CMS & __ to be provided. Requirements are required against Performance Specifications & Designers System Requirements.
| 05SY - Systemwide | Cxxx-NCR-000693 | NCR | LCS Code for Plumstead ATS |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-10-31 | 2020-10-07 14:42 | -24 | 2020-07-01 17:16 | Information Management - Asset Information | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Previous AIMS asset coordinator advised CR505 was the correct LCS code to use for Plumstead ATS assets. All assets are therefore allocated to this LCS. Current Asset Coordinator is stating CR526 is the correct code.
| 05SY - Systemwide | Cxxx-NCR-000694 | NCR | Installed materials without MCR Approval |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-09-19 | 2020-10-06 14:06 | 17 | 2020-07-02 15:54 | Communications and Control Systems | 1000 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | Various materials have been installed whilst the MCRs are either not submitted or submitted but not approved. There are currently nine unapproved MCRs which are CRL-MCR-005335, 007506, 007627, 008018, 008021, 008123, 008531, 008022 and 008023
| 05SY - Systemwide | Cxxx-NCR-000695 | NCR | Connaught Cabinet ECU1 & WCU1 Equipment Asset Identification Issues |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-09-21 | 2020-10-01 12:25 | 10 | 2020-07-07 12:31 | Communications and Control Systems - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | At Connaught East and West compounds issues have been noted with the yellow equipment labels and associated equipment lists installed within Cabinets ECU1 & WCU1. Some labels are duplicated on both equipment lists; some labels have a different serial number detailed on the equipment list to that detailed on the database/ Asset Verification Report. The Equipment Lists and labels fitted are not aligned with the information detailed on the Devices Cabinet Export MAP (See attached Quality Spotter QS532).
| 05SY - Systemwide | Cxxx-NCR-000696 | NCR | Pre-STIPA fail |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-11-15 | 2020-12-11 10:02 | 26 | 2020-07-13 09:10 | Communications and Control Systems - Public Address Systems | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During the STIPA optimisation exercise, two areas of the station were found to have poor speaker coverage which in turn indicates a STIPA failure in those areas. Correspondence has been sent to the acoustic consultant (__) for advice on whether or not it is an issue. Area 1: Bottom of Escalator 1, PAVA Zone 22. Large expanse with high ceiling and no speakers. This is a transit area between Escalator 1 and Access Passage 2a (leading to zone 23) STI readings were 0.46 which will influence the final area STI scores as the deviation would be higher. Area 2: End of Access Passage 6, Zone 25. This is where the Northern Line Link meets CRL Platforms with a set of stairs. No speakers at the bottom landing of speakers. Readings at pre-checks 0.45 which will influence the final area STI scores as the deviation would be higher.
| 05SY - Systemwide | Cxxx-NCR-000697 | NCR | Connaught Trackside Intruder Detection Power Supply Issue |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-08-28 | 2020-07-27 14:16 | -32 | 2020-07-08 10:35 | Communications and Control Systems - CCTV | 15000 |  | Design | Rework | 2 (6-60k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Upon further investigation of FOR5522 it was discovered that the as installed cable lengths exceeded the original design estimates due to limitations on where cables were able to transition from Eastbound to Westbound and vica versa. The voltage drop over the extended cable lengths lead to a supply voltage that fell short of the required input voltage range for the original DC-DC convertors. The solution to rectify this issue is to replace the DC-DC convertors with an alternative type that is compatible with the lower input voltage.
| 05SY - Systemwide | Cxxx-NCR-000698 | NCR | LFEPA Train Testing |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-02-28 | 2021-02-19 15:04 | -9 | 2020-07-14 17:39 | Communications and Control Systems - Radio | 500 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | __ to confirm that LFEPA requirements related to the performance on Rolling stock are tested and documented.
| 05SY - Systemwide | Cxxx-NCR-000699 | NCR | Investigation for where FORs detected on site can be picked up at IFAT |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-09-30 | 2020-11-04 13:04 | 35 | 2020-07-10 12:09 | Communications and Control Systems - General | 11250 |  | Software | Rework | 2 (6-60k) | Complete | Verification Problems - Inspection points not adequate | Completed |  | he following FORs were raised on site. The question was raised as to if they could have been found in the lab in Ashby. Could the processes be improved so that these are found prior to getting to site? The FORs listed can be seen below. 6222 Systemwide - CMS to ATS - Train Alarms and Train Data OPC Observations 6228 Systemwide - Help Point "Incoming" Calls Stuck after Fail-over (affects Mimics, Statuses & Alarms/Events) 6210 RCM - Cxxx OPC tags generated from logic, do not change to unknown state 6209 Systemwide - CMS to ATS - OPC Radio Observations 5787 DOO Camera Encoder Incorrect Mapping 6236 CIS - Out of service message doesn't update correctly in the displays 5690 LU11 testing on hold due to CDN interfaces disconnected because of ongoing PAVA multicast issues. 6265 Systemwide - Missing notification text 6204 Systemwide CCTV - RCM Alarm Discrepancies 6103 RCC - All WKS do not emit distinctive ringtone from WKS for PHP/RHP/LHP Emergency call 5167 TVS - No alarms received on RCM when TVS servers are disconnected 5649 CIS - PID servers do not update the status of the displays from Faulty to Healthy 6055 ABX-CMS-CCTV-Verint Encoder RCM Monitoring (SNMP Issues) 6026 Systemwide - CCTV - Analogue Camera Alarms (CRL DB - CCTV MetaData Observation) 5020 Systemwide-CMS-Call Queue Display Area of Active call not visible 5973 Systemwide - CMS CCTV - Recorded clip stuck in a "Recording" state following a Fail-over 6055 ABX-CMS-CCTV-Verint Encoder RCM Monitoring (SNMP Issues) 6049 ABX-CMS-CCTV-ABX CCTV Cameras (Live Stream Conflicts) 6051 ABX-CMS-CCTV-__ Decoder RCM Monitoring (SNMP Issues) 6050 UTL Servers failing over due to "Ghost" Calls 4908 Systemwide - TEL - Help Point Alarms Resets With Lost Comms 5828 RCC-CMS-Optex Driver (Analytic Track Cameras) 5856 System wide - TEL calls playback Audio keeps dropping in middle of call 6088 Systemwide CCTV - CCTV switching and playback available when a camera is in a "Failed" state 6087 CCTV - Camera Stop Recording When the Alarm is Acknowledged 6089 CMS - CCTV sequence Dwell time issues 6002 Alarm testing 6114 SNMP alarms clear on failover
| 05SY - Systemwide | Cxxx-NCR-000700 | NCR | PAVA configuration accidentally loaded on to LU operational equipment |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-09-11 | 2020-09-17 15:34 | 6 | 2020-07-14 08:52 | Communications and Control Systems - Public Address Systems | 500 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | On 8 July 2020 a PAVA configuration was accidentally loaded onto operational PAVA routers in the LU side of Liverpool street station causing faults in the operational equipment. This was done uring STIPA pre-checks when routing audio to Crossrail zones.
| 05SY - Systemwide | Cxxx-NCR-000701 | NCR | BUCF confirm correct paperwork was in place to support testing activity. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-10-12 | 2020-11-10 11:42 | 29 | 2020-07-14 17:25 | Communications and Control Systems - Radio | 500 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | A concern has been raised that an approved ITP was not in place to support Dispatcher Testing at the BUCF.
| 05SY - Systemwide | Cxxx-NCR-000702 | NCR | Stations DAS Antenna Installation |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-02-26 | 2021-03-05 16:13 | 7 | 2020-07-14 17:32 | Communications and Control Systems - Radio | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Information not detailed | Completed |  | During the Radio T&C process it became apparent that the system perf of RFS antennas was affected by the positioning of the fly leads on the directional panel antennas. On review with the manufacturer a requirement was identified that the N-Type connectors needed to be taped up to ensure optimal performance.
| 05SY - Systemwide | Cxxx-NCR-000705 | NCR | Eleanor Street Gate Junction Box Water Ingress |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-10-30 | 2020-09-15 08:29 | -45 | 2020-07-30 08:57 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During a recent visit to Eleanor Street it was found that both Gate01 and 02 Junction Boxes which both separately supply the two sets of double gates have had considerable water ingress (See attached Quality Spotter 533). This was a third party install but could affect our internal cabling/terminations within the JBs.
| 05SY - Systemwide | Cxxx-NCR-000706 | NCR | Limmo - CCTV Encoder has been removed from cabinet without following the WAD process. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-10-09 | 2020-10-02 10:34 | -7 | 2020-08-04 16:47 | Communications and Control Systems - CCTV | 500 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | During a recent Pre VAP visit to LIMMO Shaft it was noted at Cabinet LIP-00-CAB-006DU1 that the 12V DC video input encoder TF1 had been removed and its associated cabling, including earth connection was left on plug terminations floating in the cabinet. The Cabinet E/plan Cxxx-SMN-R3-DWG-CRG03-50144 rev X02 is the current approved version on eB and this details requirement of Encoder TF1. The removal of the encoder hasn’t followed the WAD process- Following the release of the IRN, Phase 2.2 testing will begin; all works under the Phase 2.2 testing will be controlled via the Work Authorisation Document (WAD) procedure (See attached Quality Spotter 538).
| 05SY - Systemwide | Cxxx-NCR-000707 | NCR | Plumstead ATS - Labels peeling on cabinet cabinet PPA-00-CAB-00U1 |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-10-29 | 2020-10-28 12:02 | -1 | 2020-08-07 18:35 | Communications and Control Systems - General | 1500 |  | Material | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Labels had slight peeling/damage and the 2 x yellow label wording did not match that detailedwithin the E/plan (N02 & N03) for cabinet PPA-00-CAB-00U1. See attached Quality Spotter 536 for reference.
| 05SY - Systemwide | Cxxx-NCR-000708 | NCR | Limmo - Cabinet labels peeling. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-10-15 | 2020-09-10 11:53 | -35 | 2020-08-11 09:47 | Communications and Control Systems - General | 1000 |  | Material | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During a recent Pre VAP visit to LIMMO Shaft it was noted at Cabinet LIP-00-CAB-01-B19EU2 and B19EU3 that some of the Yellow 230V warning Labels were not adhered correctly to the door surface and would require replacements. See attached Quality Spotter 539
| 05SY - Systemwide | Cxxx-NCR-000709 | NCR | Eleanor Street - Asset labels incorrect details. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-10-30 | 2020-10-26 16:38 | -4 | 2020-08-11 12:42 | Information Management - Asset Information | 2500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | During a site walkdown at Eleanor street shaft on 27.07.2020 it was noted at cabinet ELS-00-CAB-001AFU4 that 3 SCADA Cable Asset IDs remained incorrect with incomplete missing information and had ? txt on the labels. This issue had previously been raised under QS/055 and QS/463. The issue was not identified as an open snag on the current site outstanding works list. Cxxx-NCR-000651 had previously been raised previously to cover the non- conformance and closed out complete 31.03.2020 with evidence of SCADA Cable CR514-CCC-00095 having been corrected. Similar issues were also noted by the CRL asset verification team during VAP2 carried out 12.11.2019, however Cables CR514-CCC-00141, 00142 and 00133 had not been corrected. When these cables were scanned on __ Forms2Mobile App there was no data available within the data base search and the Asset Verification Report download from 21.07.2020 did not detail these cables as unscanned or failed scan. The SCADA I/O Cable and Wiring Schedule – Eleanor Street Shaft Current on eB Cxxx-SMN-R3-LST-CR094_SH007-50004 Rev X04 does not detail cables 00141 or 00142. Cable CR514-CCC-00133 has Asset Data line 1 and line 3 errors. See attached Quality Spotter 540
| 05SY - Systemwide | Cxxx-NCR-000710 | NCR | Eleanor St - Incorrect asset ID's on earth cables |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-10-30 | 2020-09-10 12:19 | -50 | 2020-08-11 15:19 | Communications and Control Systems - General | 2000 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | During a site walkdown at Eleanor Street Shaft on 27.07.2020 it was noted at cabinets ELS-00-CAB-001AFU1, U2 U3 and U4 that the Cable Asset ID installed within the cabinets at the internal cabinet earth bars and where the cables enter the cabinet internal side of the cable gland were incorrect and had TBA txt on line 4 of the label where the Earth Bar number should be. Information on line 3 differs from that held on the cable and Wiring schedule. The Cable asset IDs fitted on the CER Comms Earth Bar and above the Cabinets held the correct earth bar data. When scanned with forms2mobile the cable source and destination data detailed TBA but the image captured detailed the correct Earth bar reference on line 4. Checks to the SCADA system power and earthing schedule Cxxx-SMN-R3-LST-CR094_SH007-50012 current approved revision X03 on eB detailed TBA in line 4 for all cables at Eleanor Street Shaft on the schedule.
| 05SY - Systemwide | Cxxx-NCR-000711 | NCR | Eleanor St - Incorrect equipmnent serial no's found at pre-vap |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-10-30 | 2020-09-10 12:23 | -50 | 2020-08-11 16:19 | Communications and Control Systems - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | Serial numbers differ for 2no. switches CR514-DAT-00021 and CR514-DAT- 00022. Equipment list details SN-00081 and SN-00068. Label on equipment details SN-00011 and SN-00012. See attached Quality Spotter 544.
| 05SY - Systemwide | Cxxx-NCR-000712 | NCR | Eleanor St - Incorrect Radio asset labels |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-12-17 | 2021-01-08 16:36 | 22 | 2020-08-11 17:06 | Communications and Control Systems - Radio | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | During a site walkdown at Eleanor Street Shaft on 27.07.2020 it was noted at cabinets ELS-00-CAB-001AFU2 and U3 that radio Cables FD001, 002, 003, 004, 005, 012, 2386 and 2391 had a different DPX number detailed on line 2 of the cable asset ID to that held on the cable and wiring schedule and thiswas also different again on the radio schematic & E/plan for the PMR-RI Combining Unit. This was not highlighted at the time of Asset verification, nor was this detailed in the Asset Verification Report. See attached Quality Spotter 542
| 05SY - Systemwide | Cxxx-NCR-000713 | NCR | Fisher Street - Cabinet red line deficiencies. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-10-30 | 2020-11-13 17:09 | 14 | 2020-08-11 17:45 | Communications and Control Systems - General | 2000 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Red line mark ups haven't captured changes carried out to cabinets FIS-01-CAB-1661U1, FIS-03-CAB-3731U1, FIS-03-CAB-3731U2 & FIS-03-CAB-3731U3. See attached Quality Spotter 546. Management of Redlines and As Builts Procedure CRL1-XRL-Z-GPD-CR001-50010 procedure hasn't been followed.
| 05SY - Systemwide | Cxxx-NCR-000714 | NCR | Tunnel PMR damaged cable Eastbound Ch22140 |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-10-30 | 2020-09-03 16:45 | -57 | 2020-08-12 10:11 | Communications and Control Systems - Radio | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | PMR cable was found to be damaged between CP18 & CP 19 - Chainage 2214 - See attached photo.
| 05SY - Systemwide | Cxxx-NCR-000715 | NCR | Woolwich Radio cable connectivity / labelling incorrect. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-11-27 | 2020-12-17 13:52 | 20 | 2020-08-12 13:50 | Communications and Control Systems - Radio | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | While undertaking Intermodulation testing at Woolwich it was identified that LFEPA and Airwave connections at the PMR-RI Combiner were incorrect. This was noted in CER 1 & CER 2.
| 05SY - Systemwide | Cxxx-NCR-000716 | NCR | Deviation from T&C Plan on raising Site FORs for defects identified on site. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-12-20 | 2021-01-08 16:39 | 19 | 2020-08-13 18:27 | Communications and Control Systems - SCADA/Central Management System | 0 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | FOR hasn't been raised by T&C against standby server failing. This should have been raised at site as per the requirements of Test and Commissioning Plan Cxxx-SMN-R3-STP-CR001-50031 Revision 5.0. Section 3.2.6 Bugzilla - __ will use the Bugzilla FOR management system to record faults, issues or observations identified at phase 2.2, 3, 4 & 5 testing.
| 05SY - Systemwide | Cxxx-NCR-000717 | NCR | Defective Server Failover mechanisms on software at site. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2023-04-07 | 2023-01-18 14:03 | -79 | 2020-08-13 20:23 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Testing at site against Build 23 found that there was Defective Server Failover mechanisms on software on all types of servers – e.g. CMS, __, CIS, etc. There were on both occasions some issues with the Utility Server Failovers, specifically re-establishing the OPC connections after the failovers.
| 05SY - Systemwide | Cxxx-NCR-000718 | NCR | Mile End Park - Cabinet Test Specification MEP-00-CAB-0031BU1 Issues |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-10-23 | 2020-10-30 13:10 | 7 | 2020-08-17 06:23 | Communications and Control Systems - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | During a Pre-VAP site visit to MEP 04.08.2020 the following issues were raised at Cabinet MEP-00-CAB-003BU1. Some issues noted had previously been raised under QS/514 and Cxxx-NCR-000676. The NCR was closed out as works complete 26.06.2020 with evidence of Cabinets Test Specification – Mile End Park Shaft Phase 2.2 – Visual Check Cxxx-SMN-R3-RSP-CR094_SH006-50016 having been retested and submitted to eB as revision X02
| 05SY - Systemwide | Cxxx-NCR-000719 | NCR | Mile End Park - Cabinet Test Specification Issues - CER. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-10-23 | 2020-11-13 22:05 | 21 | 2020-08-17 07:31 | Communications and Control Systems - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Sample quality checks carried out during Pre-VAP site visit CER Cabinets MEP-00-CAB-005BU1, U2, U3, U4, U5 and U6 found various issues. Phase 2 Cabinet Test Specification has passed when it should have failed due to the following; Red lines not as built, incorrect asset information detailed for equipment installed, asset labels not installed on designed cables, electrical assurance documentation not available for additional circuits. See attached Quality Spotter 550.
| 05SY - Systemwide | Cxxx-NCR-000720 | NCR | Software - Deviation from Design Requirements when implementing Events in RCM |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-10-30 | 2020-11-09 20:11 | 10 | 2020-08-17 12:38 | Communications and Control Systems - SCADA/Central Management System | 5250 |  | Software | Rework | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | FOR 6480 was raised to capture “Decoder " Device offline " has no Device healthy event when Decoder goes healthy”
| 05SY - Systemwide | Cxxx-NCR-000721 | NCR | Implementation of Monitored Doors into RCM without an instructed PMI from Crossrail |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-12-14 | 2021-01-08 10:35 | 25 | 2020-08-17 15:11 | Communications and Control Systems - General | 500 |  | Software | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Lack of procedure | Completed |  | WOO - RCM has been configured with the new WOO doors as per FOR 6590, which was instructed under Cxxx-PMI-01091. TCR - RCM has been configured with the new TCR doors despite the CRL instructed Cxxx-PMI-01077
| 05SY - Systemwide | Cxxx-NCR-000722 | NCR | Incomplete CMS/__ Development works for the Reporting Function |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-02-26 | 2021-03-31 13:45 | 33 | 2020-08-17 15:44 | Communications and Control Systems - SCADA/Central Management System | 15000 |  | Software | Rework | 2 (6-60k) | Complete | Design Problem - Inadequate or defective design | Completed |  | During a meeting held between CRL (Prav D.) and Software Team (Mark P.) to discuss the Report Functions progress/ actions, it was noted to CRL that all necessary development works has not been completed, although it has been previously confirmed as completed.
| 05SY - Systemwide | Cxxx-NCR-000723 | NCR | Mile End Park CER Room Cabinet Yellow Labels Peeling |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-10-15 | 2020-10-15 10:43 | 0 | 2020-08-21 06:48 | Communications and Control Systems - General | 1000 |  | Material | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During a Pre-VAP site visit to MEP 04.08.2020 it was noted at CER Cabinets MEP-00-CAB-005BU1, U2 & U3 that the yellow labels adhered to the doors were showing signs of peeling. See attached Quality Spotter 551.
| 05SY - Systemwide | Cxxx-NCR-000724 | NCR | MEP - Cxxx assets not labelled at site. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-10-30 | 2020-10-28 15:39 | -2 | 2020-08-27 09:40 | Communications and Control Systems - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Level -9 SCADA cables without cable asset IDs at Junction Boxes, Junction Boxes not detailed on layout drawings. See attached Quality Spotter 552.
| 05SY - Systemwide | Cxxx-NCR-000725 | NCR | Royal Oak Portal CER Room Cabinet Deficiencies. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-10-23 | 2020-11-10 15:12 | 18 | 2020-08-28 16:12 | Communications and Control Systems - General | 3000 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During a Pre-VAP site visit to ROP 05.08.2020 the following issues were raised from sample checks carried out at CER Cabinets ROP-00-CAB-1731U1, U2, U3, U4 and U5 (See attached Quality Spotter 553). Cabinets Test Specification – Royal Oak portal Phase 2.2 – Visual Check Cxxx-SMN-R3-RSPCR076_PT001-50016 had previously been completed with all associated cabinets having a Pass result and Test Specification uploaded to eB at code 1. The Test Spec should have failed based on the findings.
| 05SY - Systemwide | Cxxx-NCR-000726 | NCR | Connaught Head House CER Room Cabinet Yellow Labels Peeling |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-10-15 | 2020-10-08 17:22 | -7 | 2020-08-21 07:01 | Communications and Control Systems - General | 1000 |  | Material | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | During a VAP site visit to Connaught Head House 06.08.2020 it was noted at CER Cabinets COT-00-CAB-1731U1, U2, U3 & U4 that the yellow labels adhered to the doors were showing signs of peeling. See attached Quality Spotter 555.
| 05SY - Systemwide | Cxxx-NCR-000727 | NCR | Royal Oak Portal Issues Raised at Pre-VAP |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-10-30 | 2020-10-30 11:49 | 0 | 2020-08-28 16:18 | Communications and Control Systems - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | During a Pre-VAP site visit to Royal Oak Portal 05.08.2020 the following issues were noted from sample checks carried out within the shaft at Cxxx installed Assets. See attached Quality Spotter 554.
| 05SY - Systemwide | Cxxx-NCR-000728 | NCR | Connaught Head House CER Room Issues Raised at VAP |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-11-30 | 2020-11-12 15:04 | -18 | 2020-08-28 16:58 | Communications and Control Systems - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Not Defined | Completed |  | During a VAP site visit to Connaught Head House 06.08.2020 the following issues were raised. See attached Quality Spotter 556. Cabinet COT-00-CAB-1731U1 · The Cabinet E/Plan details Distribution Board Ways 6 & 7 being used, there is no test data on the cabinet conditioning report for ways 6 & 7. Cabinet COT-00-CAB-1731U2 - Radio cable asset IDs within cabinet U2, PMR-RI Cable and wiring schedule and Design Schematic detail combiner unit reference DPX-001, the Eplan references the combiner unit as DPX-003. JCN-0001 within CER are not detailed on Layout Drawing.
| 05SY - Systemwide | Cxxx-NCR-000729 | NCR | I/O Schedule Process Control Issue - __-14329 |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-10-30 | 2020-11-13 18:18 | 14 | 2020-09-03 15:24 | Communications and Control Systems - SCADA/Central Management System | 2750 |  | Software | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Changes carried out to Tier 1 section of I/O schedule without instruction by Crossrail. The alarming states of the Black/Brown/Grey phase supply signals were inconsistent across the SSP locations back in March 2019 and an exercise was carried out by CRL to verify the signals. The only sites found to have an issue were Farringdon and Mile End Park. Recent checks have found that changes have been carried out on I/O schedules at Royal Oak Portal and Tottenham Court Road without instruction from Crossrail. This has resulted in incorrect alarm state at both sites. FOR __-14329 was blocked for CRL review due to an I/O schedule update.
| 05SY - Systemwide | Cxxx-NCR-000730 | NCR | Lack of detailed design - Cxxx-PMI-00431 |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-01-31 | 2021-02-09 17:55 | 9 | 2020-09-09 11:50 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Insufficient design documentation produced in respect of Cxxx-PMI-00431 (train on fire SCADA interface).
| 05SY - Systemwide | Cxxx-NCR-000731 | NCR | Multiple Sources of Truths and Change Control between Software and other Comms disciplines |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-11-16 | 2020-12-11 18:15 | 25 | 2020-09-15 14:57 | Communications and Control Systems - General | 500 |  | Software | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | 1. Between the various design teams internal to Cxxx, there are multiple sources of truth (databases) that lead to configuration control issues. As a result, the released software becomes defective. 2. Change Control / Coordination between software team and other discipline teams – this is currently not being strictly controlled by an effective process. e.g. any change to Asset Database / VMS / etc… are not visible to software team prior to the change being made. As a result the released software becomes defective.
| 05SY - Systemwide | Cxxx-NCR-000732 | NCR | Fault Observation Reports - Review comments not added to JIRA. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-12-14 | 2021-01-04 14:28 | 21 | 2020-09-15 17:32 | Communications and Control Systems - General | 500 |  | Software | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | An audit carried out on Fault Observation Reports (FORs) raised on JIRA are non-compliant with the Software Quality Plan Cxxx-SMN-R3-STP-CR001-50032 Revision 8.0 Section 7.4.1 . FORs being rejected at Triage or without explanation will defer the issue of Test Specifications to release the certificate for the system.
| 05SY - Systemwide | Cxxx-NCR-000733 | NCR | Cables given LCS code of adjacent shaft rather than routeway (CR511, CR512) |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-10-24 | 2020-10-07 09:15 | -17 | 2020-09-17 10:30 | Information Management - Asset Information | 0 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | A number of cables have been given the LCS code of the adjcent shaft rather than the routeway.
| 05SY - Systemwide | Cxxx-NCR-000734 | NCR | Whitechapel Station Cabinet WHI-02-CAB-733U1 - Insufficient capacity for cables. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-11-30 | 2021-01-04 14:38 | -330 | 2020-10-06 17:25 | Communications and Control Systems - General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During site visit to Whitechapel Station Cabinet WHI-02-CAB-733U1 was Inspected and was found to have insufficient capacity within the cabinet for cables that had been installed. All cabinets should be designed to have sufficient capacity to accommodate cabling for the system. See attached Quality Spotter 563.
| 05SY - Systemwide | Cxxx-NCR-000735 | NCR | Software - RCM OPC Client stability issues |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-07-25 | 2021-09-28 14:56 | 65 | 2020-09-18 13:36 | Communications and Control Systems - General | 500 |  | Software | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Concerns regarding the stability of the OPC client contained within RCM software
| 05SY - Systemwide | Cxxx-NCR-000736 | NCR | Third party software - Concerns regarding the stability of __ software implementation |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-01-31 | 2021-03-05 18:34 | 33 | 2020-09-18 13:24 | Communications and Control Systems - General | 500 |  | Software | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Over a period of 6 months, there have been issues with receiving OPC data that is connecting through the __ funnels. Related FORs are : __-13211 - __ Tunneller/Funnel unstable connection (See attachment) After a period of time, the RCM OPC connection to the __ Tunnel / Funnel stops working resulting in NULL values being received.
| 05SY - Systemwide | Cxxx-NCR-000737 | NCR | System Administration Requirements CM154 |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-08-31 | 2021-09-07 13:01 | 7 | 2020-09-18 14:38 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Software | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Crossrail have raised concerns that the system requirements haven't been met as per CMS154: The CMS HMI shall allow a system administrator to perform routine system administration and system configuration tasks of a non-technical nature, including the following: a Management of user accounts, including creation of new user accounts and modifications to existing user accounts b Specification of frequency of password changes c Assignation of important actions to toolbar hot-keys d Manage the digital voice announcer (DVA) recorded announcements library e Manage the CIS text message library, including addition of new message segments and associated words, phrases and proper names f Manage pre-defined CCTV camera/monitor assignations g Entry of operational help text for alarms
| 05SY - Systemwide | Cxxx-NCR-000738 | NCR | Radio - Liverpool Street Station Back of House Platform coverage |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-03-13 | 2021-03-25 16:54 | 12 | 2020-09-21 14:11 | Communications and Control Systems - Radio | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | LU Connect coverage has been deemed as requiring coverage to the back of house 'corridors' at the four corners of the platform. Currently only LFEPA, Airwave and GSM-R is provided for.
| 05SY - Systemwide | Cxxx-NCR-000739 | NCR | Earthing arrangements at Pudding Mill Lane Portal to be reworked. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-12-10 | 2020-10-30 17:24 | -41 | 2020-10-13 14:38 | Communications and Control Systems - General | 4000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | With the introduction of an additional cabinet being installed, insufficient earth connections not available at the time of installation.
| 05SY - Systemwide | Cxxx-NCR-000740 | NCR | __s Titanex 11 cable for Radio Base Station power installed before MCR approved |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-03-31 | 2021-02-03 09:03 | -56 | 2020-10-08 11:18 | Communications and Control Systems | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | The __ 11 power cables supplied by __, the Radio Base Station manufacturer, have been installed prior to CRL-MCR-08123 submission being approved. As part of the MCR review it has been determined that the __ 11 cables are not compliant with LU Standard 1-085 A3:2011 and will not be allowed to permanently remain in place. Cxxx are to identify a 1-085 A3:2011 compliant replacement cable and replace the non-compliant cable. Note - Discussions with CEG have accepted that the cable can temporarily remain in place to support the Dynamic Testing Programme but is to be replaced at the earliest opportunity.
| 05SY - Systemwide | Cxxx-NCR-000741 | NCR | M310 Series Hydra Trunk fibre cables installed before MCR or concession approval |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-03-31 | 2021-01-07 14:34 | -83 | 2020-10-13 12:10 | Communications and Control Systems | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | The M310 Series Hydra Trunk fibre cables have been installed prior to CRL-MCR-007056 submission being approved. Four fire test reports for the Hydra Trunk cable properties have been submitted to support the MCR but three of the four reports have been verbally rejected by the CRL CEG Material Engineer and CRL CEG have requested that concessions for both LU and RfL locations are submitted for approval. Subsequently to support the MCR submission, 50 year concession applications have been prepared and submitted to Crossrail Cxxx. Both LU (SP00828) and RfL (SP0829) have not yet been approved. These concessions request that the cables are allowed to remain in place permanently as part of the Cxxx design. This NCR requires no installation works and can be closed once the concessions are approved.
| 05SY - Systemwide | Cxxx-NCR-000743 | NCR | CMS153 O requirement hasn't been delivered - Management of user profiles, including creation of new user profiles and modifications to existing user profiles. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-08-31 | 2021-09-07 13:02 | 7 | 2020-10-20 07:39 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Software | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Management of user profiles, including creation of new user profiles and modifications to existing user profiles have been delivered but don't give the ability of creating new or modifying existing profiles.
| 05SY - Systemwide | Cxxx-NCR-000744 | NCR | Whitechapel __ PAVA cabinet - failed capacitor on amplifier card. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-12-11 | 2021-02-05 15:28 | 56 | 2020-10-26 12:01 | Communications and Control Systems - Public Address Systems | 500 |  | Equipment Breakdown | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | During Pre STIPA testing on the PAVA system from CER 1 at CRL Whitechapel Station a smell of burning was coming from one of the PAVA Amplifiers installed within cabinet WHI-04-CAB-731U6. See attached Amplifier Heat Damage Report for detailed information. The incident has been reported as RIVO Entry:13692515 - Notify Entry: 37602
| 05SY - Systemwide | Cxxx-NCR-000745 | NCR | CUH - Incorrect polarity GSM-R BTS cabinet. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-11-30 | 2020-11-18 16:30 | -12 | 2020-10-27 21:58 | Communications and Control Systems - Power Supplies | 2000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Damage was noted to the BTS cabinet CUH-00-CAB-731U5 fan assembly unit when energized after replacing 35mm Titanex cables that were installed between CUH-00-CAB-731U5 & CUH-00-CAB-731U6 . See attached Quality Spotter 575 This was a recurrence of Cxxx-NCR-000271 that was raised in April 2017 with an identical issue.
| 05SY - Systemwide | Cxxx-NCR-000746 | NCR | Paddington SOR - __ Desk Lock Keys Damaged. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-12-24 | 2021-01-08 11:47 | 15 | 2020-11-05 15:36 | Communications and Control Systems - General | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Electrical or instrument noise | Completed |  | During Cabinet inspections within Paddington Station SOR room it has been noted that at cabinets PAD-02-CAB-3751U6 and PAD-02-CAB-3751U8 the keys were snapped within the locks, due to this Cabinet U6 is not presently accessible and cabinet U8 has its door open and cannot be closed in situ. See attached Quality Spotter 577
| 05SY - Systemwide | Cxxx-NCR-000747 | NCR | Repeated failure of 230v distribution board cover fixings within cabinets. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-02-28 | 2021-03-04 09:34 | 4 | 2020-11-24 15:10 | Communications and Control Systems - Crossrail Data Network | 3000 |  | Equipment Breakdown | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | During sample inspections carried out on Cabinets at Canary Wharf Station it has been noted at 5 cabinet distribution boards that some of their cover fixings were not attached or aligned to their captive back nut. See attached Quality Spotter 589.
| 05SY - Systemwide | Cxxx-NCR-000748 | NCR | Systemwide - Comms issues on data links between SCADA RTUs and Assets |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-08-31 | 2021-11-04 10:55 | 65 | 2020-11-26 18:04 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Intermittent Comms issues contributes towards spurious alarms and unnecessary alarm workload. Conclusion based on CMS log analysis and Site Survey - see attachments; 1. Systemwide Comms Loss Alarms CMS Logs analysis 2. PAD CMS Logs analysis summary 3. PAD Site Survey Summary
| 05SY - Systemwide | Cxxx-NCR-000749 | NCR | Connaught compond - design not approved for installation works associated with COT-00-CAB-ECU3 & COT-00-CAB-ECU4. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-02-08 | 2020-12-23 10:06 | -47 | 2020-12-03 18:14 | Communications and Control Systems - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | Review of site assurance files found that design documentation had not been uploaded to eB for installation works carried out at Connaught Compound. All design documentation should be on eB to allow installation works to commence. Cxxx-FCD-000994 was approved after the installation was carried out. The IRN was signed off on the basis that the FCD had been approved by CRL on eB.
| 05SY - Systemwide | Cxxx-NCR-000750 | NCR | AIMS Equipment Description Mismatches |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-04-30 | 2021-01-27 13:17 | -93 | 2020-12-02 19:07 | Information Management - Asset Information | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | A number of equipment types in use have historically had minor discrepancies between the AIMS description and the __ project database description. These anomalies, although long standing, have only recently been identified as a cause for concern due to a mismatch on the equipment label. The details/proposals/impacts are as follows. EQ00000017 WHARTON Q01912 Station Clock Proposal: Change __ database from "Q01912" to "WHARTON Q01912" to match AIMS. Impact: Existing labels will continue to indicate "Q01912", propose use as-is. EQ00000022 V4320FDW-DN-BLK CCTV Camera Proposal: Change __ database from "V4320FDx-DN - BLK" to "V4320FDW-DN-BLK" to match AIMS. Impact: Existing labels will continue to indicate "V4320FDx-DN - BLK", propose use as-is. EQ00000024 Sentry 6 Loudspeaker Proposal: Change __ database from "Sentry6" to "SENTRY 6" to match AIMS. Impact: Existing labels will continue to indicate "Sentry 6", propose use as-is. EQ00000025 CELL 10 BD Loudspeaker Proposal: Change __ database from "Cell10BD" to "CELL 10 BD" to match AIMS. Impact: Existing labels will continue to indicate "Cell10BD", propose use as-is. EQ00000036 AMPLICON IMPACT - R 4031RAIL Server Proposal: Change __ database from "Impact-R 4031" to "AMPLICON IMPACT - R 4031RAIL" to match AIMS. Impact: Existing labels will continue to indicate "Impact-R 4031", propose use as-is. EQ00000038 CISCO CP – 3905 Telephone Proposal: Change __ database from "3905" to "CISCO CP - 3905" to match AIMS. Impact: Existing labels will continue to indicate "3905", propose use as-is. EQ00000101 S1801E-R Decoder Proposal: Change __ database from "S1801e-R-HD (KBD)" to "S1801E-R" to match AIMS. Impact: Existing labels will continue to indicate "S1801e-R-HD (KBD)", propose use as-is. EQ00000110 PRIME-NCS-APL-K9 V02 Server Proposal: Change __ database from "PRIME NCS" to "PRIME-NCS-APL-K9 V02" to match AIMS. Impact: Existing labels will continue to indicate "PRIME NCS", propose use as-is. EQ00000132 BSF3604 Repeater Unit Proposal: Change __ database from "BSF3604-xxx" to "BSF3604" to match AIMS. Impact: Existing labels will continue to indicate “BSF3604-xxx", propose use as-is. EQ00000136 FASTFLEX FF015E-100 RTU Equipment Proposal: Change __ database from "FF015e-100" to "FASTFLEX FF015E-100" to match AIMS. Impact: Existing labels will continue to indicate "FF015e-100", propose use as-is. EQ00000137 MS146 RTU Equipment Proposal: Change __ database from "MS146xxxx" to "MS146" to match AIMS. Impact: Existing labels will continue to indicate "MS146xxxx", propose use as-is. EQ00000156 TITAN CB Telephone Proposal: Change __ database from "Titan CB xxx" to "TITAN CB" to match AIMS. Impact: Existing labels will continue to indicate "Titan CB xxx", propose use as-is. EQ00000383 RBRARC-BMIC-BMIC Microphone Proposal: Change __ database from "RBRARC-BMIC" to "RBRARC-BMIC-BMIC" to match AIMS. Impact: Existing labels will continue to indicate "RBRARC-BMIC", propose use as-is. EQ00001863 R230 Server Proposal: Change __ database from "PowerEdge R230" to "R230" to match AIMS. Impact: Existing labels will continue to indicate "PowerEdge R230", propose use as-is. EQ00004576 15216-FLC-CWDM-8 Interface Converter Proposal: Change __ database from "15216-FLC-CWDM-8=" to "15216-FLC-CWDM-8" to match AIMS. Impact: Existing labels will continue to indicate "15216-FLC-CWDM-8=", propose use as-is.
| 05SY - Systemwide | Cxxx-NCR-000751 | NCR | North Woolwich Portal Phase 3 - Cxxx HV Power Integration Testing - Incomplete Energisation Script |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2020-12-28 | 2021-01-07 14:05 | 10 | 2020-12-14 08:32 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Incomplete Works | Use As-Is | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | Incomplete testing during Cxxx - Communication & Control Systems Central Management System Test Specification – North Woolwich Portal Phase 3.0 – Cxxx HV Power Integration Testing CRL Document Number: Cxxx-SMN-R3-RSP-CR146_PT004-50031; script: 3.0.1-CMS-ENG-03 - Phase 3.0 - 11kV Energisation. Unable to fully complete this test as LIP 11kV permanently energised making the secondary injection detailed in the Test Script unavailable.
| 05SY - Systemwide | Cxxx-NCR-000753 | NCR | Custom House Camera 0033 water ingress |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-06-30 | 2021-06-24 16:50 | -6 | 2020-12-15 18:23 | Communications and Control Systems - CCTV | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | External Phenomenon - Weather or ambient condition | Completed |  | Following a site inspection at Custom House Station, it was noted that there was water within Camera 0033. See attached Quality Spotter 609.
| 05SY - Systemwide | Cxxx-NCR-000754 | NCR | WPR Telephone CAT6a Cables exceed 90mtrs |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-02-26 | 2020-12-23 09:49 | -65 | 2020-12-16 16:04 | Communications and Control Systems - Telephony | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The Following CAT6A cables have been installed at Westbourne Park to supply additional RTLs as per Cxxx-PMI-01133. The cables have exceed the 90mtrs length however are under the 120mtr exceptional rule. 1. CR1-TR-RTL-50104 - 119mtrs 2. CR1-TR-RTL-50105 - 95mtrs It is proposed these cables are "used as is" (See Related Contract Communications previous NCR’s raised/closed) ITP checksheets and Fluke test results attached for reference.
| 05SY - Systemwide | Cxxx-NCR-000755 | NCR | Systemwide failure of SD cards installed within Verint CCTV cameras. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-05-30 | 2021-08-09 07:50 | 71 | 2020-12-21 16:20 | Communications and Control Systems - CCTV | 500 |  | Equipment Breakdown | Rework | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | During recent site inspections at Canary Wharf Station, it has been noted that there are faulty SD cards in some cameras. The functionality of the SD card is for on board recording. The failure of SD cards is a system wide issue. There is a total of 97 No that have been listed as faulty at Canary Wharf. See attached Quality Spotter 611 for more details.
| 05SY - Systemwide | Cxxx-NCR-000756 | NCR | Canary Wharf Station CAW-04-CAB-4405U18 cabinet cable ID's glued on. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-02-05 | 2021-02-03 08:08 | -2 | 2020-12-22 06:24 | Communications and Control Systems - Crossrail Data Network | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Sleeved cable ID labels at cabinet CAW-04-CAB-4405U18 have been cut and glued, rather than installed by the correct method of sliding over the cable. Some have yellow dymo tape to identify the cables, these are receptive to peeling. See attached Quality Spotter 620.
| 05SY - Systemwide | Cxxx-NCR-000757 | NCR | Cananary Wharf Station SOR cable joints. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-02-05 | 2021-02-02 10:21 | -3 | 2020-12-23 07:23 | Communications and Control Systems - Crossrail Data Network | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The electrical cables that connect monitors 2 and 5 to the PDU were found jointed and the electrical cable that feeds PDU, located in cabinet CAW-04-CAB-4460U1 had also been jointed. Although proprietary joints have been used, JY61 LV Cables and Wiring Crossrail M&W Specification CRL1-XRL-M-RSP-CR001-50078 JY61.3102 Cable Jointing Section a) states “Cables may only be jointed where cable lengths make impractical to install a continuous conductor”.
| 05SY - Systemwide | Cxxx-NCR-000758 | NCR | Paddington Station Ticket hall failed STIPA |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-03-08 | 2021-03-22 14:49 | 14 | 2021-01-21 15:20 | Communications and Control Systems - Public Address Systems | 20000 |  | Incorrect Installation | Rework | 2 (6-60k) | Complete | Verification Problems - Inspection points not adequate | Completed |  | Ticket hall and escalator STIPA failure. This is believed to be due to misalignment of 13 speakers in the concourse area which according to the Acoustic Report should be facing the failed area, but are not aligned correctly at installation
| 05SY - Systemwide | Cxxx-NCR-000759 | NCR | Whitechapel - WHI APC/UPS alarm testing |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-08-31 | 2021-07-19 14:07 | -43 | 2021-01-22 12:27 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | The following can't be tested against current test spec - Central Management System Test Specification Whitechapel Station Phase 3 - Cxxx Internal IO Testing 1. Over Temperature: Not able to generate this alarm - Propose use as is - Leave alarm in and rely on manufacturer’s guarantee 2. Fan Fail: Not able to generate this alarm - Propose use as is - Leave alarm in and rely on manufacturer’s guarantee 3. Voltage Out of Range - Propose use as is - Leave alarm in and rely on manufacturer’s guarantee 4. Bypass Mode: Not able to generate this alarm – UPS not able to support Bypass functionality – Propose remove signal 5. Overload: Not able to generate this alarm - Propose use as is - Leave alarm in and rely on manufacturer’s guarantee
| 05SY - Systemwide | Cxxx-NCR-000760 | NCR | Liverpool St Radio - unprotected connectors & components |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-03-08 | 2021-03-01 12:47 | -7 | 2021-01-28 16:05 | Communications and Control Systems - Radio | 500 |  | Testing and Commissioning | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During recent cabinet inspections carried out at Liverpool Street Station, it has been noted at within CER 1 and CER 2 that some radio cables and components were disconnected and unprotected from dust ingress and possible touch potential. The cable ends were not labelled detailing why they were disconnected. In some instances, it appears that replacement cables have been installed, these were identified by temporary hand marked labels. See attached Quality Spotter 612.
| 05SY - Systemwide | Cxxx-NCR-000761 | NCR | RCC - Condition of cabinets within the CER. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-02-28 | 2021-03-05 13:54 | 5 | 2021-02-02 15:40 | Communications and Control Systems - General | 500 |  | Testing and Commissioning | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Quality Inspections at the RCC found various issues within cabinets installed within the CER. Maintaining IP rating of bayed cabinets. General Housekeeping. Unterminated earth cables. Installation not aligned against eplans. Misalignment against eplans, BS7671 Electrical Certificates Extension power leads and adapters plugged in for temporary equipment D Type plugs loose at converters interface Earth fly leads not installed to equipment as per eplans Servers installed on top of each other within cabinets Temporary works, red lines, changes and assurance documentation have not been captured via PTR See attached Quality Spotters 623 to 629.
| 05SY - Systemwide | Cxxx-NCR-000762 | NCR | Intruder Laser Detection - intermittent lost comms. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-07-31 | 2021-10-25 09:22 | 86 | 2021-02-08 12:18 | Communications and Control Systems - General | 500 |  | Testing and Commissioning | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Intermittent lost comms associated with Intruder Laser Detectors installed at portal mouth locations. It is unknown what is causing the lost comms issue, further investigation is required to establish the reasons why.
| 05SY - Systemwide | Cxxx-NCR-000763 | NCR | Bond St Station - Cabinets IP rating not maintained |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-03-26 | 2021-03-31 13:26 | 5 | 2021-02-11 05:14 | Communications and Control Systems - General | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 7 No Cxxx cabinets within CER 1 have missing Rittal cable entry blanking modules on top of the cabinets resulting in the IP rating not being maintained. Rittal Sealing Modules form an integral part of the cabinet designs and their omission will invalidate their Ingress Protection (IP) rating and the subsequent certification that they are supplied with.
| 05SY - Systemwide | Cxxx-NCR-000764 | NCR | Low signal levels have been observed in LIS cells that is causing poor on-train LFEPA voice quality |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-09-01 | 2021-06-21 14:36 | -72 | 2021-02-12 19:20 | Communications and Control Systems - Radio | 500 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Poor voice quality was observed during testing on board train at Liverpool St Station cell. The cause of the poor voice quality is unknown at this time.
| 05SY - Systemwide | Cxxx-NCR-000765 | NCR | Stepney Green - poor Radio voice quality |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-09-01 | 2021-06-21 14:33 | -72 | 2021-02-15 12:29 | Communications and Control Systems - Radio | 5000 |  | Testing and Commissioning | Rework | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | There is poor voice quality throughout the train in the Stepney Green cell at the cell edge towards Canary Wharf Station, although it was poor on both bounds it was definitely worse on the west. FOR 8365 has been raised - see attached.
| 05SY - Systemwide | Cxxx-NCR-000766 | NCR | Tottenham Court Road - poor Radio voice quality |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-09-01 | 2021-06-21 14:30 | -72 | 2021-02-15 12:36 | Communications and Control Systems - Radio | 5000 |  | Testing and Commissioning | Rework | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | There is poor voice quality throughout the train in the Tottenham Court Road cell at the cell edge towards Bond Street Station. FOR 8366 has been raised - see attached.
| 05SY - Systemwide | Cxxx-NCR-000767 | NCR | CMS - events recorded with the same timestamp on OHLE VT OOR & Cxxx Track Access Doors events. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-06-30 | 2021-10-14 10:44 | 106 | 2021-02-15 18:19 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Software | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Ongoing issues since early December 2020 with identical timestamps on OHLE VT OOR & Cxxx Track Access Doors events. The first timestamp issue was raised with OHLE VT OOR events - timestamps were the same for both the alarm event and the cleared event. Latest findings are on Cxxx Track Access Doors
| 05SY - Systemwide | Cxxx-NCR-000768 | NCR | LIS-05-CAB-771U1 - No evidence of cabinet assurance. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-05-05 | 2021-04-29 08:50 | -6 | 2021-02-18 18:11 | Communications and Control Systems - Crossrail Data Network | 500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Information not detailed | Completed |  | The Surveillance Report had found that changes had been carried out at site since the cabinet had been delivered to site. Evidence provided was CN711 dated 27th November 2017. Title – Change cabinet type from S2 to 6D due to space and access restrictions. The change note was signed off by Alex Cupachin and James Morrisey 12th March 2018.
| 05SY - Systemwide | Cxxx-NCR-000769 | NCR | LIS-06-CAB-9771U1 - No evidence of cabinet assurance |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-05-05 | 2021-05-04 13:24 | -1 | 2021-02-18 18:26 | Communications and Control Systems - Crossrail Data Network | 500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The Surveillance Report had found that changes had been carried out at site since the cabinet had been delivered to site. No evidence could be provided for who had carried out the changes at site or any evidence of any assurance paperwork.
| 05SY - Systemwide | Cxxx-NCR-000770 | NCR | CAW radio implementation causing : Lifts 2/3 inadequate coverage and Radio overspill into adjacent LUL Jubilee line station |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-11-20 | 2021-11-09 15:03 | -11 | 2021-02-17 18:57 | Communications and Control Systems - Radio | 500 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | 1. Lifts 2/3 inadequate coverage - Airwave testing results for Lift 2 showed satisfactory RSSI levels and MOS scores only when the lift doors remain open per floor. When the lift doors are closed however, there is no service on the majority of floors. When taking a single lift ride between the top floor (Level 0) and the bottom floor (Level -5), the call is only maintained between Levels -1 and -5, with an average RSSI of -90dBm and MOS of 4/5 . The call drops when approaching or leaving Level 0. 2. Radio overspill into adjacent LUL Jubilee line station - On 15 July 2021 reciprocal cell spillage was witnessed between the LFEPA radio systems at CRL CAW RVP west and the LUL Jubilee line west at Jubilee Plaza, see attached image in this observation’s ‘Attach Photographs’. NB CRL, __ and LUL were in attendance for this observation. Radio calls showed that when walking away from CRL CAW RVP west that reasonable comms can be established until the South Colonnade, when reaching Reuters Plaza and Jubilee Plaza call quality is no better than a MOS 3/5, however when using the handset outside the LUL Jubilee line west at Jubilee Plaza, it would experience ‘busy channel’ when trying to make a call on the LUL LFEPA radio system, whilst the handset at the CRL CAW RVP west was keyed. The equivalent outcomes were witnessed at the CRL CAW RVP west when trying to make a call on the CRL LFEPA radio system it would experience ‘busy channel’, when a handset outside the LUL Jubilee line west was keyed.
| 05SY - Systemwide | Cxxx-NCR-000771 | NCR | Low signal levels have been observed in FAR cells that is causing poor on-train LFEPA voice quality |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-09-24 | 2021-06-21 14:27 | -95 | 2021-02-22 11:13 | Communications and Control Systems - Radio | 5000 |  | Testing and Commissioning | Rework | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | Poor voice quality was observed during testing on board train at Farringdon Station cell. The cause of the poor voice quality is unknown at this time. FOR 8367 (attached) has been raised on Bugzilla.
| 05SY - Systemwide | Cxxx-NCR-000772 | NCR | Custom House - 2 No PAVA issues - LLPA & roving mic broadcast and intermittent roving mic. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-03-26 | 2021-03-23 14:42 | -3 | 2021-03-02 11:26 | Communications and Control Systems - Public Address Systems | 0 |  | Testing and Commissioning | Reject | 4 (0.5-3k) | Complete | Personnel Error - Other human error | Completed |  | “During the recent BIU conducted by CRL T&C with support from __ Cxxx, the following items were identified: Both LLPA and Roving microphone announcements were broadcast together whereas the roving mic should have taken priority. Roving Mic unstable, did not operate on the platform and concourse use was intermittent” FOR 8427 & 8428 (attached) have been raised on Bugzilla.
| 05SY - Systemwide | Cxxx-NCR-000773 | NCR | Multiple alarms related to Cabinet Fans Speed Controllers at various sites - not set at correct temperatures & speeds. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2022-04-18 | 2022-05-27 14:26 | 39 | 2021-03-02 14:25 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Multiple alarms related Cabinet Fan/Room Temperature at various sites. See attached CMS Logs AW-UTL-Cxxx-013.xlsx. The set points were not set at 25 deg C to alarm at 35 deg C during cabinet FAT or 2.2 testing.
| 05SY - Systemwide | Cxxx-NCR-000774 | NCR | CCTV Encoder/Decoder hardware issues causing monitor blanking and high number of alarms. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-06-30 | 2022-02-24 10:44 | 239 | 2021-03-03 16:02 | Communications and Control Systems - CCTV | 10000 |  | Testing and Commissioning | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Other | Completed |  | High number of CCTV equipment failure alarms were being raised to the operator, this is increasing the operators workload. CCTV monitors going blank several times a day which are preventing the operators from using the equipment correctly. This issue is reported on the RFL issues list as issue 660-71
| 05SY - Systemwide | Cxxx-NCR-000775 | NCR | CDN Comms failure issues between RTU and Software - AW-UTL-Cxxx-015 |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-05-28 | 2022-03-04 12:12 | 280 | 2021-03-03 16:07 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | It has been highlighted by CRL that there are CDN Comms failure issues between RTU and Software that requires further investigation- See attached CMS Log AW-UTL-Cxxx-015
| 05SY - Systemwide | Cxxx-NCR-000776 | NCR | Spurious alarms on DOO Hardwired signals |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-05-31 | 2021-07-19 12:14 | 49 | 2021-03-03 16:17 | Communications and Control Systems - Driver only Operation CCTV | 500 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Not Defined | Completed |  | It has been highlighted by CRL that there are spurious alarms on DOO Hardwired signals - See attached CMS Logs AW-UTL-Cxxx-024.xlsx
| 05SY - Systemwide | Cxxx-NCR-000777 | NCR | Missing entries (alarm raised and reinstated events) in archived CMS event logs - AW-PWR-Cxxx-007 |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2023-04-05 | 2022-10-28 10:57 | -159 | 2021-03-08 11:58 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Software | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | CRL have raised concerns that there are missing entries (alarm raised and reinstated events) in archived event logs - AW-PWR-Cxxx-007. There are several instances where we have the alarm cleared events but there are no signs of the alarm raised or reinstated event.
| 05SY - Systemwide | Cxxx-NCR-000778 | NCR | Possible incorrect values are shown on Alarm Description of "out-of-range" Analogue signals - AW-PWR-Cxxx-008 |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-06-30 | 2021-11-16 13:44 | 139 | 2021-03-08 11:22 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | CRL have raised concerns that there may be possible incorrect values shown on Alarm Description of "out-of-range" Analogue signals - AW-PWR-Cxxx-008 (see attached). When current on Cxxx devices (CT1A, CT2A, CT3A) goes out of range, the value displayed in the alarm description seems to be that of the voltage instead of the current (around 26k is shown but the range defined in the I/O is 0 – 3000).
| 05SY - Systemwide | Cxxx-NCR-000779 | NCR | Incorrect categorisation of Alarm/Event types - likely on the archived event logs - AW-PWR-Cxxx-009 |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2023-05-31 | 2023-01-27 16:15 | -124 | 2021-03-08 11:40 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Software | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | CRL have raised concerns that there are incorrect categorisation of Alarm/Event types - likely on the archived event logs - AW-PWR-Cxxx-009 (see attached). There are two issues here: • There is inconsistency between how alarms are presented e.g. rows 344-347 shows we get 4 events in total for the raising and clearing of a primitive alarm however rows 348-350 shows we get 3 events in total for the raising and clearing of a primitive alarm • For rows 348-350, we do not seem to get the ‘Alarm_Raised’ or ‘Alarm_Reinstated’ event (however we do get the ‘Alarm State Cleared’ event suggesting an alarm was raised) – the first event on row 348 seems like it should be the ‘Alarm_Raised’ or ‘Alarm_Reinstated’ event but we are missing the appropriate text at the end of the alarm description and the ‘Cause_Of_Event’ column says it is an event
| 05SY - Systemwide | Cxxx-NCR-000780 | NCR | Outstanding works related to User Tag workstream and User Tag / Tag number inconsistencies - AW-PWR-Cxxx-010 |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-06-29 | 2022-03-04 12:05 | 248 | 2021-03-08 12:16 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Software | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | CRL have raised concerns that there are Outstanding works related to User Tag workstream and User Tag / Tag number inconsistencies - AW-PWR-Cxxx-010 (see attached). There are two issues here: • Some signals have the old Class Tag Number for the ‘User Tag’ • Some signals have the User Tag for the ‘Class Tag Number’ We are expecting the ‘User Tag’ column to have only the new user tags while the ‘Tag Number’ column to have only the old class tag numbers
| 05SY - Systemwide | Cxxx-NCR-000781 | NCR | Bulk camera Unknown Events without a VMS Offline Alarm - AW-UTL-Cxxx-007 |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-05-04 | 2021-05-20 14:00 | 16 | 2021-03-08 14:12 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | CRL have raised concerns that there are bulk camera Unknown Events without a VMS Offline Alarm - CMS Log refers AW-UTL-Cxxx-007 (see attached notes).
| 05SY - Systemwide | Cxxx-NCR-000782 | NCR | RTU Inaccessible alarms - AW-UTL-Cxxx-023 |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-10-24 | 2021-11-23 14:09 | 30 | 2021-03-08 15:55 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Software | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | CRL have raised concerns that there are RTU Inaccessible alarms - See attached CMS Log AW-UTL-Cxxx-023
| 05SY - Systemwide | Cxxx-NCR-000783 | NCR | PID server stability issues - AW-UTL-Cxxx-017 |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-06-28 | 2021-09-23 09:47 | 87 | 2021-03-08 16:11 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Software | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | CRL have raised concerns that there are PID server stability issues - AW-UTL-Cxxx-017 (see attached CMS Log).
| 05SY - Systemwide | Cxxx-NCR-000784 | NCR | Potential spurious RCM internal alarms - AW-UTL-Cxxx-019 |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2023-05-09 | 2023-01-27 17:37 | -102 | 2021-03-08 15:29 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Software | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | CRL have raised concerns that there are potential spurious RCM internal alarms - AW-UTL-Cxxx-019 (see attached CMS Log).
| 05SY - Systemwide | Cxxx-NCR-000785 | NCR | Spurious DOO Internal alarms - AW-UTL-Cxxx-021 |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-06-30 | 2021-12-08 15:34 | 161 | 2021-03-08 15:36 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Software | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | CRL have raised concerns that there are spurious DOO Internal alarms - AW-UTL-Cxxx-021 (see attached CMS Log).
| 05SY - Systemwide | Cxxx-NCR-000786 | NCR | Lost Comms issues on PIDs - AW-UTL-Cxxx-025 |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2023-05-15 | 2023-01-27 12:14 | -108 | 2021-03-08 19:44 | Communications and Control Systems - SCADA/Central Management System | 20000 |  | Software | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Electrical or instrument noise | Completed |  | CRL have raised concerns that there are reported Lost Comms issues on PIDs - see attached AW-UTL-Cxxx-025 (CMS Log).
| 05SY - Systemwide | Cxxx-NCR-000788 | NCR | Systemwide transient faults on PAVA system lasting a few seconds |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2023-01-10 | 2022-11-10 14:39 | -61 | 2021-03-05 14:33 | Communications and Control Systems - Public Address Systems | 10000 |  | Testing and Commissioning | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Other | Completed |  | Transient faults on the PAVA vnet card have been identified systemwide. This is resulting with the Vnet cards rebooting causing the long line announcement to be temporary unavailable for 4 -5 seconds until the vnet card is back online. There is no impact to safe operations for the operators. See attached FOR8445
| 05SY - Systemwide | Cxxx-NCR-000790 | NCR | Bond St - DC2 cabinet BOS-00-CAB-1414U1 recently delivered to site - Build not aligned against application design and eplan. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-04-30 | 2021-04-29 15:41 | -1 | 2021-03-16 15:35 | Communications and Control Systems - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | Surveillance carried out at Bond Street Station on DC2 cabinet BOS-00-CAB-1414U1 has found that the application design and eplans do not align with the cabinet build. The C01 eplan drawing held within the cabinet at site is uncontrolled and has not been uploaded to eB and the application design does not reflect the build. See referenced Quality Surveillance Report QS119 – Bond Street Station Cabinet DC2 Inspection for detailed report.
| 05SY - Systemwide | Cxxx-NCR-000791 | NCR | Bond St - CER1 & CER2 cabinet documents & records deficiencies |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-10-30 | 2021-08-17 10:01 | -74 | 2021-03-16 18:30 | Communications and Control Systems - General | 5000 |  | Documentation and Records | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | Surveillance visit to site has picked up various issues with sample checks of cabinets in CER 1 & 2. There are discrepancies between eplan drawings and electrical certificates as per the attached Quality Surveillance Report QS120 – Bond Street Station Cabinet Electrical Test Certificate Inspections
| 05SY - Systemwide | Cxxx-NCR-000792 | NCR | Camera Connection Lost Issue List - mainly Routeway to Image freezing on screens upon SCADA alarm triggering CCTV switching e.g. Doors/PHPs - in turn causing lost comms on CCTV cameras |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-08-25 | 2022-02-04 16:32 | 163 | 2021-03-23 20:59 | Communications and Control Systems - CCTV | 50000 |  | Testing and Commissioning | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | CRL have gone through the CMS events log from the __ period last week (12th March - 15th March) and have identified several cameras going in and out of connection lost state systemwide. The reasons why are currently under investigation. Alarms listed:- COT - 43 CUH - 1883 - Note that that 1869 alarm logs are from one faulty camera (CUS-CAM-0014) ELS -2 FDX-39 FIS - 1 MEP-11 NWP-1 __-1 VDP-3 XLS-10 XPL-74
| 05SY - Systemwide | Cxxx-NCR-000793 | NCR | Third party software - __ Funnel failures |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-07-05 | 2022-05-03 10:45 | 302 | 2021-03-23 21:31 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Software | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | There are still active __ issues (funnel failures) in the live system. The latest findings are from the 10th March (see attached spreadsheet filtered out for Funnel failures AW-UTL-Cxxx-033 - __ Funnel Failures - 9th-11th March).
| 05SY - Systemwide | Cxxx-NCR-000794 | NCR | Portal mouth ILD's reporting high number of intruder alerts to CMS |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-07-21 | 2021-08-04 22:12 | 14 | 2021-03-24 14:30 | Communications and Control Systems - CCTV | 5000 |  | Testing and Commissioning | Rework | 3 (3-6k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | A large volume of false Intruder Alarms are being reported from the Portal ILD's by the CMS.
| 05SY - Systemwide | Cxxx-NCR-000795 | NCR | CCTV Memory Leak - lack of CCTV switching ability for operations |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-06-25 | 2021-07-19 11:04 | 24 | 2021-03-30 07:50 | Communications and Control Systems - CCTV | 500 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | When switching cameras over multisite from stations to the RCC, there is no video stream present however cameras are online and showing healthy and still recording.
| 05SY - Systemwide | Cxxx-NCR-000796 | NCR | Paddington STIPA Failures |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-05-14 | 2021-05-24 15:01 | 10 | 2021-03-29 12:05 | Communications and Control Systems - Public Address Systems | 6000 |  | Design | Use As-Is | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Several areas did not achieve the required speech intelligibility 0.5 STI. Ticket Hall, Entrance escalators, Platform escalators and the Bakerloo Link stairs all achieved between 0.45 STI and 0.5 STI. RfL Have attended site to listen to the system and feedback is that they are happy with it.
| 05SY - Systemwide | Cxxx-NCR-000797 | NCR | Bond St - BOS-05-CAB-6734U2 damaged D-Type Plug at A2 |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-05-28 | 2021-05-21 23:40 | -7 | 2021-04-06 13:02 | Communications and Control Systems - Crossrail Data Network | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During a recent site visit to Bond Street Station cabinets it has been noted at cabinet BOS-05-CAB-6734U2 that the modular cable D-Type plug at Interface Module A2 is damaged and not sitting correctly at its termination point. The damaged D-Type plug could result in intermittent lost communications.
| 05SY - Systemwide | Cxxx-NCR-000798 | NCR | TUCA - Cabinet TUCA-11-CAB-109U1 missing equipment earth bonds |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-06-04 | 2021-05-26 17:37 | -9 | 2021-04-06 14:20 | Communications and Control Systems - Crossrail Data Network | 500 |  | Incomplete Works | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During a recent site inspection of TUCA cabinets it has been noted at cabinet TUCA-11-CAB-109U1 that the required 10mm2 Earth Bonds for __ equipment -XF1 and -XF2 detailed on the current Eplan Cxxx-SMN-R3-DWG-CR527-50007 revision X01 had not been installed.
| 05SY - Systemwide | Cxxx-NCR-000799 | NCR | TUCA SOR Cabinet TUCA-00-CAB-G01U3 exceeding bending radius of Cat 6 patch leads |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-06-04 | 2021-05-26 17:38 | -9 | 2021-04-07 10:42 | Communications and Control Systems - Crossrail Data Network | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During a recent site inspection of TUCA SOR cabinets it has been noted at cabinet TUCA-00-CAB-G01U3 that when the door is closed it is clashing with 2 x grey cat 6 patch leads terminating at Access switch -XF1. The cables are exceeding the manufactures guidance for bending radius with further potential for data loss on the system.
| 05SY - Systemwide | Cxxx-NCR-000800 | NCR | TUCA - Cabinet TUCA-11-CAB-109U3 - PDU 3 not tested on electrical certificate. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-05-31 | 2021-06-03 07:07 | 3 | 2021-04-20 13:14 | Communications and Control Systems - General | 500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During a recent site inspection of TUCA cabinets it has been noted at cabinet TUCA-11-CAB-109U3 that the cabinet test certificate held within the Cabinet and on __ server was incomplete and did not detail and circuit or test result data for the Cabinets PDU 3 Way 4. It was also noted that the way 4 devise -TF4 was plugged into way 1 on the PDU, not way 4, the plug was also incorrectly dyno label marked. See attached Quality Spotter 656.
| 05SY - Systemwide | Cxxx-NCR-000801 | NCR | CRL-MCR-008531 – Radio RFS Ser 5 antenna installed without an approved MCR. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-05-30 | 2021-05-07 11:31 | -23 | 2021-04-08 20:58 | Communications and Control Systems - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Radio RFS Multiband Indoor Antenna 380-2700MHz. I-ATO5-380_2700 Omni varient and I-ATP5-380_2700 Directional variant has been installed without an approved MCR. This is non - compliant against Site Inspection and Test Plan - Equipment Installation Cxxx-SMN-R3-ITP-CR001-50005 Rev 7.0 Section 2.2 Equipment Approval - Material Compliance Record has to be Code 1 on eB.
| 05SY - Systemwide | Cxxx-NCR-000802 | NCR | CRL-MCR-009176 - 70mm² Single Core LSOH Black Cable installed without an approved MCR |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-05-30 | 2021-04-29 10:24 | -31 | 2021-04-08 20:58 | Communications and Control Systems - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | 70mm² Single Core LSOH Black Cable installed without an approved MCR has been installed without an approved MCR. This is non - compliant against Site Inspection and Test Plan - Equipment Installation Cxxx-SMN-R3-ITP-CR001-50005 Rev 7.0 Section 2.2 Equipment Approval - Material Compliance Record has to be Code 1 on eB.
| 05SY - Systemwide | Cxxx-NCR-000803 | NCR | CRL-MCR-009240 - T-SIM Controller Interface Module installed without an approved MCR. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-05-30 | 2021-05-19 08:56 | -11 | 2021-04-08 20:59 | Communications and Control Systems - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | CRL-MCR-009240 - T-SIM Controller Interface Module has been installed without an approved MCR. This is non - compliant against Site Inspection and Test Plan - Equipment Installation Cxxx-SMN-R3-ITP-CR001-50005 Rev 7.0 Section 2.2 Equipment Approval - Material Compliance Record has to be Code 1 on eB.
| 05SY - Systemwide | Cxxx-NCR-000804 | NCR | CRL-MCR-009264 - Modbus/TCP to RTU/ASCII Gateway installed without an approved MCR. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-05-30 | 2021-05-18 16:10 | -12 | 2021-04-08 20:59 | Communications and Control Systems - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Modbus/TCP to RTU/ASCII Gateway has been installed without an approved MCR. This is non - compliant against Site Inspection and Test Plan - Equipment Installation Cxxx-SMN-R3-ITP-CR001-50005 Rev 7.0 Section 2.2 Equipment Approval - Material Compliance Record has to be Code 1 on eB.
| 05SY - Systemwide | Cxxx-NCR-000805 | NCR | CRL-MCR-009266 - 230Vac to 57Vdc 800ma Power Supply Unit installed without an approved MCR. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-05-30 | 2021-04-29 13:46 | -31 | 2021-04-08 20:59 | Communications and Control Systems - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | 230Vac to 57Vdc 800ma Power Supply Unit installed without an approved MCR has been installed without an approved MCR. This is non - compliant against Site Inspection and Test Plan - Equipment Installation Cxxx-SMN-R3-ITP-CR001-50005 Rev 7.0 Section 2.2 Equipment Approval - Material Compliance Record has to be Code 1 on eB.
| 05SY - Systemwide | Cxxx-NCR-000806 | NCR | Paddington Station - Cabinet PAD-02-CAB-3731U3 - design change process not followed. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-05-23 | 2021-05-25 10:22 | 2 | 2021-04-08 21:48 | Communications and Control Systems - Crossrail Data Network | 2000 |  | Design | Repair | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | Additional __ equipment has been installed within cabinet PAD-02-CAB-3731U3 without going through a formal change note. Cxxx-PMI-00748 was issued by Crossrail on 17th February 2019 to install 6 No additional power sockets within the CCTV/TEL cabinet. Because no change note was raised the cabinet assessment has not been fully assessed for heat calculations or spacing for air flow within the cabinet. See attached photo of equipment installed.
| 05SY - Systemwide | Cxxx-NCR-000807 | NCR | Bond St - DC1 cabinet BOS-00-CAB-1411U1 recently delivered to site - Build not aligned against application design and eplan. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-05-04 | 2021-05-13 15:03 | 9 | 2021-04-20 13:59 | Communications and Control Systems - Crossrail Data Network | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | Surveillance carried out at Bond Street Station on DC1 cabinet BOS-00-CAB-1411U1 has found that the application design and eplans do not align with the cabinet build.
| 05SY - Systemwide | Cxxx-NCR-000808 | NCR | Failure on Operator Handover Functionality |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-07-31 | 2021-08-06 16:07 | 6 | 2021-04-22 13:56 | Communications and Control Systems - SCADA/Central Management System | 5000 |  | Software | Rework | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | During shift handover, operator's use the "handover" button to do a shift handover. The operator's are presented with a popup screen asking the current operator and the new operator to put their passwords. On completion of this, RCM should do a seamless handover of AOR's from the operator leaving shift and the new operator taking over. This functionality does not appear to work consistently as the new operator has been left with no AOR's allocated and the new operator has not realized this. Resulting in the possible lack of cover for the expected alarms. Transfer of control - not all alarms and controls transfer with the user. (FOR 8610 refers 8513 also). Initially functionality was available after 30 mins transferred to alternative W/S. See attached FORs 8513 & 8610.
| 05SY - Systemwide | Cxxx-NCR-000809 | NCR | Lack of alarm activation on unallocated Area of Responsibility (AORs). |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-09-20 | 2021-10-01 15:34 | 11 | 2021-04-22 19:11 | Communications and Control Systems - General | 500 |  | Software | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | During shift handover, operator's use the "handover" button to do a shift handover. The operator's are presented with a popup screen asking the current operator and the new operator to put their passwords. On completion of this, RCM should do a seamless handover of AOR's from the operator leaving shift and the new operator taking over. This functionality does not appear to work consistently as the new operator has been left with no AOR's allocated and the new operator has not realized this. Resulting in the possible lack of cover for the expected alarms. When the handover failed, no alarms were generated to indicate lack of cover.
| 05SY - Systemwide | Cxxx-NCR-000811 | NCR | Stuck Alarms in Inhibit Alarms list |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-09-30 | 2021-11-02 10:38 | 33 | 2021-04-26 14:47 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | High/Critical alarms - indications seen but alarm detail not sent to TM2 alarm list. Critical Alarm - Farringdon 22kV site. Possible UCOS fault but alarm not on TM2 SCADA alarm screen despite alarm indication (a "C" in a red box) High Alarm - Pudding Mill Lane. Site reporting as "energised". Also not on TM2 alarm screen despite alarm indication (a "H" in a red box). IRM's have gone to site and doors were seen to be shut. There have been previous issues with door contact alignment. Investigation currently underway.
| 05SY - Systemwide | Cxxx-NCR-000813 | NCR | RCC - CMS screen intermittently losing signal and another flickering |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-09-24 | 2022-02-02 14:19 | 131 | 2021-04-27 19:53 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Equipment Breakdown | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Not Defined | Completed |  | Left hand CMS screen intermittently losing signal and middle Screen on WS2 flickering lighter and dimmer than the other screens. The issue captured within this defect has now been observed on all WKS's in the RCC including RCC-WKS-12 (CE desk). See attached FOR 7858
| 05SY - Systemwide | Cxxx-NCR-000814 | NCR | Route Control Centre - CUH PAVA inhibit at RCC |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-08-31 | 2021-08-16 11:12 | -15 | 2021-04-27 20:17 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Software | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | RCC Workstation - All PAVA zones had a cross next to them on the left hand side of the screen for Custom House. To clear the current fault the operator has to highlight the affected zones and select inhibit all and then highlight the affected zone again and then select enable all, this then clears the fault.
| 05SY - Systemwide | Cxxx-NCR-000815 | NCR | Liverpool St Station - Rejected Redlines |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-06-25 | 2021-06-22 11:09 | -3 | 2021-05-18 21:27 | Communications and Control Systems - Crossrail Data Network | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | Changes carried out at site on cabinets Cabinets LIS-01-CAB-731U10 & LIS-03-CAB-731U11 have not met the requirements of Management of Redlines and As-Builts Procedure CRL1-XRL-Z-GPD-CR001-50010 and do not reflect the as-constructed condition at site. Cxxx-Communications & Control Systems CDN Patch Wiring Schedule – Liverpool Street Station – Cxxx-SMN-R3-LST-C101-50020 rev X02 did not align with Cxxx-Communications & Control Systems CDN Cable & Port Schedule – Liverpool Street Station – Cxxx-SMN-R3-LST-C101-50003 rev X02. Both schedules had been signed off by 3 No individual persons as prepared, checked and approved.
| 05SY - Systemwide | Cxxx-NCR-000816 | NCR | __ Damaged Tel Cable (__-01-TEL-10102) |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-07-25 | 2021-07-05 14:31 | -20 | 2021-05-13 08:22 | Communications and Control Systems - Telephony | 4000 |  | Damaged | Rework | 3 (3-6k) | Complete | Personnel Error - Inattention to detail | Completed |  | FOR 6855 Raised to investigate faulty telephone __-01-TEL-10102. Terminations in CER & at device checked with no issue found, further tests identified a damaged cable 3.5 mtrs away from the Tel RJ45 outlet. I t is unclear how this has occurred however the cable is to be replaced to resolve. Note: __ Tel IRN 08/11/2018
| 05SY - Systemwide | Cxxx-NCR-000817 | NCR | Traction Power switching - Device Plant Control issues at ATS sites, Paddington & Whitechapel. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-08-31 | 2021-08-31 12:42 | 0 | 2021-05-17 19:32 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | Device Plant Control for Traction Power switching has been found at various locations with different scenarios. Issue Type 1&3- Device Control issues at WEPA/SYGA/PLUA (likely a generic issue related to Secure Authentication, across all sites) Issue Type 4 - Device Control issue at PAD 102/6 and 101/6 a. A site investigation is required be required by RFL/Cxxx/Cxxx SAP b. RFL to support access to switch room via maintenance c. RFL to support a provision of a switching schedule and execution of switching via Traffic Managers d. Cxxx PAD access is also to be arranged Issue Type 5 - Device Control Issues at Whitechapel 102G/E, 101C/E and 102/1 a. offsite investigation is ongoing b. site visit may be required following the investigation by RFL/Cxxx/Cxxx SAP Issue Type 6 - SYGA 102K/A – Failed to open. a. However, open control was successful once multiple commands were issued in the sequence: Open, Close, Open b. off-site investigation is ongoing Cxxx
| 05SY - Systemwide | Cxxx-NCR-000818 | NCR | Plumstead Sidings - Uncontrolled documents being used at site. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-06-04 | 2021-06-09 17:51 | 5 | 2021-05-21 13:45 | Communications and Control Systems - General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | Whilst carrying out a review of Plumstead Sidings Telephony Site Assurance File Cxxx-XPG SAF 002 Cxxx-SMN-R3-CER-CR526-50004 rev 3.0 it was noted that Cxxx-SMN-R3-DDA-CR526_1-60004 P01.1 version had been marked up for a red line drawing for cabinets trackside. This is not complaint against Management of Redlines and As Builts Procedure CRL1-XRL-Z-GPD-CR001-50010 Rev 7.0 Section 3.4 CAD Standards - A Revision of P0x indicates that the CAD Model or CAD Drawing is preliminary. It also doesn't meet the requirements of Site Inspection and Test Plan Equipment Installation – Cxxx-SMN-R3-ITP-CR001-50005 Rev 7.0 - Issued for Construction Drawings at Code 1 on eB.
| 05SY - Systemwide | Cxxx-NCR-000819 | NCR | Liverpool Street SOR Speaker Feedback |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-07-16 | 2021-07-16 10:12 | 0 | 2021-05-24 13:39 | Communications and Control Systems - Public Address Systems | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Feedback has been observed when making an announcement in the SOR using the SOR microphone/s.
| 05SY - Systemwide | Cxxx-NCR-000821 | NCR | Verint No recordings available message |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-07-31 | 2021-12-24 09:31 | 146 | 2021-05-28 10:56 | Communications and Control Systems - CCTV | 10000 |  | System Defect | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | When requesting video streams in a multisite environment via SDK connected devices (CMS, LU __). A 'No Recordings Available' message is displayed on the associated CCTV monitor and no video stream is present.
| 05SY - Systemwide | Cxxx-NCR-000822 | NCR | CCTV Cameras losing focus |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-08-16 | 2021-08-20 15:10 | 4 | 2021-05-28 11:40 | Communications and Control Systems - CCTV | 500 |  | System Defect | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Camera views are losing focus after being set up. Even when manual focus is selected, issues are being experienced.
| 05SY - Systemwide | Cxxx-NCR-000825 | NCR | Whitechapel Station SOR Speaker Feedback |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-07-30 | 2021-08-06 14:19 | 7 | 2021-06-15 19:57 | Communications and Control Systems - Public Address Systems | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Two speakers in the SOR at Whitechapel are causing feedback issues when making an announcement in the SOR using the SOR microphone/s.
| 05SY - Systemwide | Cxxx-NCR-000826 | NCR | TUCA Cabinet TUCA-00-CAB-G04U3 Showing Signs of Corrosion and Moisture Ingress |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-08-30 | 2021-09-07 09:32 | 8 | 2021-06-16 21:54 | Communications and Control Systems - General | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | At TUCA Site during Phase 2.2 test spec visual checks it has been noted at trackside Cabinet TUCA-00-CAB-G04U3 that there is evidence of some moisture ingress and signs of corrosion around the enclosure. Corrosion noted around the cabinet has previously been raised under Cxxx-PWK-01352. See attached Quality Spotter 669
| 05SY - Systemwide | Cxxx-NCR-000827 | NCR | LEFPA radio unacceptable call quality recorded at the RVP in the Whitechapel cell east bound |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-09-19 | 2021-08-27 14:51 | -23 | 2021-06-17 14:45 | Communications and Control Systems - Radio | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | Following routeway LFEPA onboard train testing 28 & 29 May 2021 the WHI cell, east bound still has issues with the uplink (UL) call quality to the RVP, with the RVP having a MOS score of ‘3’ and the RVP reporting the quality as ‘breaking up badly and a robotic noise’.
| 05SY - Systemwide | Cxxx-NCR-000828 | NCR | Route Control Centre - Slow CCTV switching at RCC for Paddington Station |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-09-19 | 2021-09-09 11:41 | -10 | 2021-06-23 15:02 | Communications and Control Systems - CCTV | 500 |  | Software | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Not Defined | Completed |  | Camera switching at the RCC for Paddington Station is excessively slow - approx. 15 seconds. The camera switching would normally expected to be around be around 1 -2 seconds to complete.
| 05SY - Systemwide | Cxxx-NCR-000829 | NCR | Canary Wharf - damaged Cat 6 cable |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-08-31 | 2021-08-05 09:37 | -26 | 2021-06-25 13:08 | Communications and Control Systems - Crossrail Data Network | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | Damaged Cat 6a cable sheath within the cable trunking route supplying and adjacent to __ Cabinet CAW-06-CAB-6303U1 on Level -6. See attached Quality Spotter
| 05SY - Systemwide | Cxxx-NCR-000830 | NCR | CMS standby Power Server (RCC-PWR-01) indicating an issue with the repository - Service Request 3866 |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-09-20 | 2021-09-21 13:05 | 1 | 2021-07-06 15:48 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Software | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | During a routine system health check by the __ Cxxx SCADA Floorwalking team we notice the CMS standby Power Server (RCC-PWR-01) was indicating an issue with the repository. See attached Picture 1. RCC-PWR-01 Operational Mode indicating Offline This means if there was an issue with the main server, at the time RCC-PWR-02, there would not have been a standby server to failover to. Thus no redundancy to the Power SCADA system was in place.
| 05SY - Systemwide | Cxxx-NCR-000831 | NCR | Whitechapel Station - PAVA speakers in concourse showing signs of rust. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-11-30 | 2022-02-03 10:03 | 65 | 2021-07-16 09:44 | Communications and Control Systems - Public Address Systems | 6000 |  | Manufacturing Defect | Rework | 3 (3-6k) | Complete | Material/Preservation Problems - Other | Completed |  | At Whitechapel Station it has been noted that the new ceiling speakers installed on the LUL upper concourse are showing signs of corrosion on the speaker grill, a Tier 1 survey carried out details thisto be affecting 32no. speaker grills. The speakers are mounted at high level to the underside of the concourse canopy which has its sides open and exposed to weather and environmental elements. The following speakers have been identified by the tier 1 with corrosion issues on the grill as sample image below. Z20/B4, Z20/B2, Z20/A1, Z8/B18, Z16B22, Z16/A19, Z16/B20, Z16/A17, Z16/B18, Z16A15, Z8/B82, Z8/A81 Z8/A111, Z8/B110, Z8/B80, Z8/A79, Z8/B78, Z8/A77, Z8/B76, Z8/A75, Z8/B74, Z8/A73, Z8/B72, Z8/A87, Z8/A85, Z8/A103, Z8/B86, Z8/B104, Z8/A89, Z8/B102, Z8/A105 & Z8/B88 See attached Quality Spotter 664 and marked up the Layout drawings of the Rusted speakers on the concourse (highlighted green)
| 05SY - Systemwide | Cxxx-NCR-000832 | NCR | Punchwork (Cxxx-PWK-01352) was closed out on eB without sufficient evidence. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-09-16 | 2021-09-22 14:01 | 6 | 2021-07-22 22:30 | Communications and Control Systems - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Quality surveillance at TUCA for cabinet Inspections had picked up 38 No snag items and these had been captured by Cxxx-PWK-01351. Although the PWK has been closed eB there was insufficient evidence to close the PWK out and there are still outstanding works to be completed. In some instances there have been Fault Observation Reports raised on Bugzilla, labels to be ordered and installed, electrical certificates pending (See attached Cxxx_PWK_01352 evidence.docx). Closing out PWKs in this manner does not follow Snagging and Outstanding Works (Punchworks) Procedure CRL1-XRL-O4-GPD-CR001-50010 Rev 3.0 Section 10 Appendices 10.1 Appendix A : Defect Item Process Step 1.13 - Has defect item been completed as per contract requirements.
| 05SY - Systemwide | Cxxx-NCR-000833 | NCR | Failure on Operator (TM2) Log in/Log out Functionality |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-09-27 | 2021-09-21 08:16 | -6 | 2021-07-16 15:11 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Software | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | On handover of the CMS system an issue was experienced with logon, the TM2 after logging on was requested to change password. This then resulted in all screens going blank and the TM2 having to utilise the WS2 spare desk. This is a known issue that has 2 No FORs associated with it. See attached FOR8868 & FOR8968
| 05SY - Systemwide | Cxxx-NCR-000834 | NCR | __ Turret was deployed to site and issues found at site weren't picked up at iFAT. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-08-31 | 2021-08-17 12:57 | -14 | 2021-07-21 14:58 | Communications and Control Systems - Telephony | 500 |  | Software | Rework | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | During Integration of __ Turret on Friday 9th July 2021 at approx 02:00hrs the call forwarding/transfer functionality was found to be not working. The GUI (visual indication) was showing that the call was forwarding when it wasn't. Call forwarding functionality was not in the iFAT scope for testing.
| 05SY - Systemwide | Cxxx-NCR-000835 | NCR | Systemwide - Scaling issues on analogue values |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-09-30 | 2021-11-04 11:02 | 35 | 2021-07-22 21:31 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Software | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | An issue has been identified at the RCC on the LV Incoming circuit breakers at BDS, LSX, FDX, PDX, XPL, XRY, TCR, WHX and CUS.The frequency reading (HRTZ) for these breakers in not showing the correct value on the CMS HMI. An investigation into the CMS database highlighted that each frequency analogue inputs which displayed the issue had a scaling factor not equal to 1.The scaling factor is set when the CMS/__ is built using a calculation based on the analogues engineering range (eng max/min) and the raw input range (min/max). The general rule for analogue configuration is that the engineering range and raw input range are the same so the scaling factor is always 1.This allows the CMS will simply display the value received from the RTU without manipulating or data adjustment.
| 05SY - Systemwide | Cxxx-NCR-000836 | NCR | CCTV images dropping frames over CDN network from multi-site locations. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-09-17 | 2021-12-21 14:06 | 95 | 2021-07-21 15:36 | Communications and Control Systems - CCTV | 500 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | CCTV images are dropping frames due to high network jitter in a multisite environment when viewing from the BUCF or RCC. The frame dropping does not occur when they are viewed locally.
| 05SY - Systemwide | Cxxx-NCR-000837 | NCR | Custom House - Failed LED tiles on 6 No Infotec CH-MF1 Customer Information System displays. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-11-02 | 2021-10-13 14:04 | -20 | 2021-08-09 20:33 | Communications and Control Systems - Customer Information System | 8000 |  | Manufacturing Defect | Rework | 2 (6-60k) | Complete | Material/Preservation Problems - Other | Completed |  | 6 No Infotec CH-MF1 Double sided, Full Matrix Bright White LED Display NTI (Next Train Indicator) have various failed LED tiles between them (approximately 150 No LED tiles in total). The double sided displays have 80 No LED tiles per display(40 either side - total over 6 No displays is 480 LED tiles).
| 05SY - Systemwide | Cxxx-NCR-000838 | NCR | RCC - Loss of workstation connectivity causing loss of alarms for the operator. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-11-20 | 2021-10-01 11:00 | -50 | 2021-08-13 16:53 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Software | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | On Tuesday 10th August at the RCC there was a report of loss of comms with SCADA resulting in no alarm messages incoming. This results in bringing trains safely to a stand in order to assess exact status (see attached jpg). The Workstation to server mailbox’s have been overflowing under load of late, due to a limitation in the toolset that is being exposed by the quantity of changing data in the cms and the number of workstations. The mailbox overflows have caused the connection between workstation and server to be dropped and then reset, when this happens all the data from the server is requested again. On this occasion a large amount of data was requested by a workstation that had the test mimic open, this addition load put the system into a unrecoverable sate where it could no longer service the connected workstations in a timely manger and they gradually reset their list connections and could not recover them.
| 05SY - Systemwide | Cxxx-NCR-000839 | NCR | Plumstead ATS MS146 Cabinets PPA-00-CAB-102/15RU1, 101/16U1 & 102/17U1 - Red Lines not reflective of what has been installed at site. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-10-18 | 2021-10-20 12:36 | 2 | 2021-08-24 17:12 | Communications and Control Systems - SCADA/Central Management System | 3000 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | Following the recent failure of VT102Q & VT102R at Plumstead, RfLI have been investigating the wiring between Motorised OHLE Switch MSS-102/15R cabinet and MS146 Cabinet PPA-00-CAB-102/15RU1. Part of the investigation found that there were anomalies with terminations of CR505-CCC-00579 (Formally CR505-TEL-00384) against the current schematics & schedules. Surveillance has been carried out and found there are a few anomalies between schematics, schedules eplans and termination cards.
| 05SY - Systemwide | Cxxx-NCR-000840 | NCR | Requested changes to LFEPA optimisation in the trace |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2022-07-21 | 2022-07-12 08:05 | -9 | 2021-09-07 13:00 | Communications and Control Systems - Radio | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | The revised campaign 3 configuration of the LFEPA system maximises on train coverage with the known side effects of box to box (trace) coverage and noise within the overlap areas adjacent to band stops within the trace (WB to EB, CP to WB/EB). Details of relevant specification clauses not met are identified below. This NCR is used to track this change and close out any outstanding NCRs/observations. Note that the instruction Cxxx-PMI-01340 mandates reversing certain signal attenuation measures implemented to close Cxxx-NCR-000636.
| 05SY - Systemwide | Cxxx-NCR-000841 | NCR | Bond Street Radio - on site test equipment calibration overdue. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2021-11-20 | 2021-10-21 15:50 | -30 | 2021-09-15 20:03 | Communications and Control Systems - Radio | 2000 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | Whilst carrying out surveillance at Bond Street Radio terminating and testing it was noted that test equipment Anritsu Open/Short Load OSLN50A-8 calibration kits SN:1813597 was out of calibration. The surveillance visit was 2nd August 2021 and the calibration date on the test equipment was 24th June 2021.
| 05SY - Systemwide | Cxxx-NCR-000842 | NCR | Portal mouth Intruder Laser Detector (ILD's) reporting high number of intruder alerts to Central Management System (CMS). There are 5 No areas of concerns that contribute to the alerts - see NCR details. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2022-01-10 | 2022-02-18 16:24 | 39 | 2021-09-29 22:22 | Communications and Control Systems - CCTV | 500 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Contamination | Completed |  | A large volume of false Intruder Alarms are still being reported from the Portal ILD's by the CMS. Cxxx-NCR-000794 was raised previously 24/03/2021 and closed out 04/08/2021 with evidence of logs between 09/07/2021 to 01/08/2021. Further to the NCR being closed out there have been further false positive alarms being reported back every day. There are 5 No areas of concerns 1. North Woolwich Portal there has been an oil spill causing false positives. 2. Connaught Tunnel has faulty ILD unit. 3. Pudding Mill Lane requires fox fix & firmware upgrades 4. ROP has historic UDP comms connectivity. 5. Timing needs adjusted between zone remote activity on ILD.
| 05SY - Systemwide | Cxxx-NCR-000843 | NCR | Westbourne Park MS146 cabinet WPA-00-CAB-4810/34U1 assurance documentation not available in SAF and inaccurate redline/as-built documentation against cabinets WPA-00-CAB-4810/32U1, WPA-00-CAB-4810/34U1 & WPA-00-CAB-101/10U1. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2022-02-11 | 2022-02-07 17:13 | -4 | 2021-11-01 21:20 | Communications and Control Systems - SCADA/Central Management System | 2000 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | Surveillance carried out on 3 No MS146 cabinets at Westbourne Park (Cabinets WPA-00-CAB-4810/32U1, WPA-00-CAB-4810/34U1 & WPA-00-CAB-101/10U1) have found discrepancies between schematics, eplans & schedules. The site assurance file associated with WPA-00-CAB-4810/34U1 hasn't been uploaded to eB. For detail refer to the following; 1. Quality Surveillance Report QS144 - Westbourne Park MS146 Cabinet WPA-00-CAB-4810/32U1 2. Quality Surveillance Report QS145 - Westbourne Park MS146 Cabinet WPA-00-CAB-4810/34U1 3. Quality Surveillance Report QS146 - Westbourne Park MS146 Cabinet WPA-00-CAB-101/10U1
| 05SY - Systemwide | Cxxx-NCR-000844 | NCR | Systemwide Help Point Intermittent Lost Comms Alarms |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2022-01-31 | 2022-04-13 21:31 | 72 | 2021-11-06 10:14 | Communications and Control Systems - Telephony | 500 |  | Software | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | We have noticed a considerable number of instances where we are getting lost comms alarms from Passenger Help Points/Refuge Help Points across all sites. The cause of the lost comms alarms are unknown at this time and further investigation is required - refer to the attached spreadsheet (AW-UTL-Cxxx-010_24Sep-31Oct.xlsx ) for details of lost comms. Also attached are 2 No email with timeline of events for lost comms.
| 05SY - Systemwide | Cxxx-NCR-000845 | NCR | Incorrect power cable label format |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2022-02-24 | 2022-01-21 13:11 | -34 | 2021-11-26 16:20 | Information Management - Asset Information | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | During a VAP it was observed that three power cables had been fitted with asset labels which were in the wrong format. Although the labels' asset data and source/destination information was correct, it had been printed in the wrong format (3 line instead of 4 line). A review of verification records revealed a further 16 affected assets, all of which are referenced below.
| 05SY - Systemwide | Cxxx-NCR-000846 | NCR | Portal Mouth Intruder Laser Detectors(ILD) - TCP/UDP issues causing lost comms on ILDs at VDP and PML. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2022-09-20 | 2022-03-31 15:57 | -173 | 2022-01-11 22:11 | Communications and Control Systems - CCTV | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | User Datagram Protocol (UDP) communications with the Central Management System (CMS) server occasionally drops out leading to lost comms with CMS Utility Server 2. Upon failover from CMS Utility Server 1 to Server 2, the ILDs which had lost comms will now be in alarm and not functioning. VDP & PML have stopped transmitting UDP packets on ILD devices over the festive period - TBC if any other ILD's have similar issues.
| 05SY - Systemwide | Cxxx-NCR-000847 | NCR | Plumstead (XPG) - mimic symbols applicable for the substation building are missing and navigation is non intuitive through the menu. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2022-12-24 | 2022-11-03 11:18 | -51 | 2022-01-14 16:22 | Communications and Control Systems - Station Management System | 500 |  | Software | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Mimic for XPG substation CER is missing GUI symbols for the substation building for a number of monitored assets present in the latest IO schedule - Cxxx-XRL-R3-LST-CR148_SD013-50001 Rev 3.0. 2 No Tickets raised __-15229 XPG - Missing SID No for the Plant Items (SHV, MRA and UPS) & __-17597 XPG: Level 1 Ground Level Detail Section 3 & 5 Mimic Observation. Navigation is also non intuitive through the menu.
| 05SY - Systemwide | Cxxx-NCR-000848 | NCR | __ Turret - Terminated Help Point calls not clearing the Tel_Active table (1) and inability to make a new call using the same Help Point (2). |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2022-03-07 | 2022-01-27 11:37 | -39 | 2022-01-24 21:02 | Communications and Control Systems - Telephony | 500 |  | Software | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | There are two issues: Terminated Help Point calls not clearing the Tel_Active table (1) and inability to make a new call using the same Help Point (2). Both do not meet the requirements of Central Management System Test Specification - Route Control Centre - __ Turret Handset Integration Testing Rev 2.0.
| 05SY - Systemwide | Cxxx-NCR-000849 | NCR | Video Management System(VMS) load balancing at the RCC |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2022-12-23 | 2022-09-02 12:17 | -112 | 2022-04-08 14:26 | Communications and Control Systems - CCTV | 50000 |  | Testing and Commissioning | Rework | 2 (6-60k) | Complete | Design Problem - Other | Completed |  | Site implementation is in-line with design, however, more recently __ sent information through with regard to maximum number of decoders the VMS should have subscribed; under the current HW/SW configuration we should have a maximum number of 30, whilst the VMS currently has 43 decoders assigned. 2016 upgrade was FAT tested before implementing on site and no issues were found - on site, it is found to be using more server resources and slowing down the system; impacting the operator. Immediate action on this is to delete 2012 VM (rollback mitigation for 2016 upgrade) and increase server RAM.
| 05SY - Systemwide | Cxxx-NCR-000850 | NCR | HDMI extenders overheating and affecting screens performance at the RCC. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2022-05-30 | 2022-04-21 11:29 | -39 | 2022-04-01 07:43 | Communications and Control Systems - CCTV | 5000 |  | Equipment Breakdown | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Electrical or instrument noise | Completed |  | RFL have reported various issues of blank and frozen screens at the RCC. The extenders do not allow the screens to meet the requirements of Performance Specification, CCTV System Cxxx-PBF-R3-RSP-CRG03-00007 Rev 15.0 Section 4.10 CCTV Workstation Performance Requirements.
| 05SY - Systemwide | Cxxx-NCR-000851 | NCR | BUCF/RCC - Out of Range - Alarms raised for below 0 analogue values - |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2022-10-05 | 2022-07-28 09:35 | -69 | 2022-04-27 10:29 | Communications and Control Systems - SCADA/Central Management System | 5000 |  | Software | Rework | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | After the latest software drop Central Management System Test Specification – Route Control Centre Build Specific Operations Testing – Release 4.28.4 Test Script & Step: 3.0.1-CMS-SYS-14 had been tested at site and failed. The test objective is to ensure the correct reporting of Specific Traction Voltage levels from VT’s. This is a repeat of FOR 4161(attached) which was rectified within Build 4.14.1.19 Patch 3 (raised 04/09/2019 and closed 28/11/2019).
| 05SY - Systemwide | Cxxx-NCR-000852 | NCR | Systemwide - Mismatch between the Cxxx IO schedule and CCTV metadata |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2023-04-14 |  | -67 | 2022-05-03 15:45 | Communications and Control Systems - Station Management System | 5000 |  | Design | Rework | 3 (3-6k) | Open |  | IMPLEMENTATION |  | During CMS/__ testing onsite the T&C team have identified a misalignment between the Door labels onsite, the Cxxx IO schedule and Cxxx CCTV Metadata. Issue 1: In some instances the door label matches the Cxxx IO schedule but does not match the CCTV Metadata. Issue 2: In some instances the door label does not match the Cxxx IO schedule and CCTV Metadata. Historically the door IDs have been provided by others via Crossrail issued marked up Cxxx IO schedules attached to FCDs.
| 05SY - Systemwide | Cxxx-NCR-000853 | NCR | Bond St Station - Unfused PDU's installed in 2 No cabinets - the design is for fused PDU's. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2023-02-27 | 2022-08-19 11:55 | -192 | 2022-05-14 07:35 | Communications and Control Systems - Power Supplies | 2000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 2 No cabinets (BOS-00-CAB-1411U1 & BOS-00-CAB-1414U1) at Bond St Station have the incorrect type (PDU) power distribution units installed. The units installed are non fused part number __EIC10H-C14, the units should be individually fused and the correct part number should be __IEC10HFNC14 as per design and listed on the Eplan drawings. See attached photos.
| 05SY - Systemwide | Cxxx-NCR-000854 | NCR | Abbey Wood CCTV camera switching issues |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2023-02-28 | 2022-09-01 09:17 | -180 | 2022-05-14 09:52 | Communications and Control Systems - CCTV | 20000 |  | Testing and Commissioning | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | 1.Frame rate on cameras is low, sluggish image being shown with some cameras leaving trails (ghosting) as a object person is moving. 2.When assigning an ABX camera on a tile, sometimes the camera displayed is not the camera that has been actually selected. It is either the previously assigned camera or a random one. 3. cctv_nice_decoder table will not clear the FK_camera and other fields after a while 4. Blue screen/grey screen displayed after switching– 5. cctv_nice_decoder FK_camera and other columns are not cleared if a decoder encoder goes to unknown or lost comms 6. When assigning a camera, this should land on an unique encoder, but it is not.
| 05SY - Systemwide | Cxxx-NCR-000855 | NCR | RCC - Intermittent non-responsive workstations after PID failover |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2023-05-19 | 2023-01-18 14:05 | -121 | 2022-05-23 14:23 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Software | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Workstation(s) at the RCC stop responding for the user causing operational disruption for them but then recovers. This happens after a failover of the PID servers and subsequent high data throughput into Cromos.
| 05SY - Systemwide | Cxxx-NCR-000856 | NCR | Systemwide failure of Camera to raise Edge Storage Alarm |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2022-12-06 | 2022-10-28 22:00 | -39 | 2022-05-23 15:40 | Communications and Control Systems - SCADA/Central Management System | 2000 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The camera SD card recording serves two functions. Firstly, when recording at 25 fps, any recorded event can be enhanced with a period of pre-event footage at the higher frame rate so any investigation can include high quality footage before any incident is noticed. All help point calls, Door events, escalator stop events and operator manual recording events have the advantage of 30 seconds of 25fps footage available to assist in any investigations. Secondly, the SD card streams video to the NVR’s in the event of a failover where normally a few minutes of footage would be lost. CRL has lowered the requirement to 3FPS sometime ago, but now RFL are expecting 25 FPS as a deliverable. This issue has been esclated with Verint/Cognyte for resolution.
| 05SY - Systemwide | Cxxx-NCR-000857 | NCR | RCC - Digital Voice Announcer Method failure [Causing UTL Failover] - SR 33398 |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2023-03-03 | 2022-06-24 14:16 | -252 | 2022-05-23 20:52 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Software | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Failover from UTL-01 to UTL-02 due to DVA method failure. WKS-5 operator said he was editing PA message and trying to preview it in fragment builder when the failover occurred. Prevents user from starting a second PA Message Builder task, removing a message or cancelling from the Manage Messages mimic if a PA Message Builder task is running on the workstation
| 05SY - Systemwide | Cxxx-NCR-000858 | NCR | Bond St Station - Gap in Public Address / Voice Alarm coverage |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2023-03-04 | 2022-09-02 15:17 | -183 | 2022-05-24 04:17 | Communications and Control Systems - Public Address Systems | 5000 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | A number of areas at BOS have been identified as potentially not having sufficient PAVA coverage, as follows: A/901 Mezzanine Air Intake Plenum A/776 Mezzanine Station Plant Room A/041 Mezzanine Circulation Area 6/904 Services Void 6/942 Void 6/943 Void
| 05SY - Systemwide | Cxxx-NCR-000859 | NCR | Systemwide - Some cameras are raising offline alarms in the VMS for short durations. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2022-10-28 | 2022-09-09 09:50 | -49 | 2022-05-30 22:19 | Communications and Control Systems - CCTV | 5000 |  | Testing and Commissioning | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | Some cameras are raising offline alarms in the VMS for short durations. Resolution of this issue has been communicated from Verint to be upgrading the camera firmware. However, 20% of cams on site are not accepting the latest firmware (v49).
| 05SY - Systemwide | Cxxx-NCR-000860 | NCR | Systemwide - CEC Microphone remains open for 'In Use' PA zones. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2022-06-24 | 2022-06-24 07:42 | 0 | 2022-06-08 22:56 | Communications and Control Systems - Public Address Systems | 500 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Fault identified where CEC Microphone remains open for 'In Use' PA zones and cannot be closed for 5 minutes.
| 05SY - Systemwide | Cxxx-NCR-000861 | NCR | Systemwide - UTL Server failover following service request submission |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2023-03-09 | 2022-10-27 09:26 | -133 | 2022-07-15 11:35 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Software | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Around 8.07am on 8 July 2022, the UTL server failed over to the standby server. At the time of the incident, the operators were making a service request to Maximo.
| 05SY - Systemwide | Cxxx-NCR-000862 | NCR | Whitechapel PAVA Vipedia is out of sync |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2022-08-31 | 2022-07-29 09:08 | -33 | 2022-07-15 12:36 | Communications and Control Systems - Public Address Systems | 500 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Verification Problems - Inspection points not adequate | Completed |  | Site works were carried out to correct the time, however, there is also a setting change that needs to be made to the Vipedias to ensure all are synced to the correct time. Due to go back to site on 27/07 to address this.
| 05SY - Systemwide | Cxxx-NCR-000863 | NCR | Cxxx-PMI-01393 - Maglock testing carried out without an approved test specification. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2022-08-25 | 2022-08-22 10:55 | -3 | 2022-08-11 14:16 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Management Problem - Other management problem | Completed |  | Testing & Commissioning had progressed without an approved test spec (Central Management System Test Specification - Systemwide - Phase 3 - Maglock Testing for PMI-1393) being signed off by Crossrail after the installation works had been completed against Cxxx-PMI-01393 : Provision of Maglock Remote Door Release at XLS and __. The difference to requirements is that Section 3.6, subsection 3.6.1 of the Test and Commissioning Plan Cxxx-SMN-R3-STP-CR001-50031 Revision 6.0 states; Test Specifications will be created for each sub-system and will be used to validate the systems. Each of the Tests Specifications will be built up from a number of Test Scripts & Test Data Sheets that will be completed with Test Results.
| 05SY - Systemwide | Cxxx-NCR-000864 | NCR | Multiple Comms loss alarms are observed at Connaught Tunnel on the RTU which has 2 x Modbus TCP Slaves configured (s1 & s2). |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2023-05-19 |  | -102 | 2022-08-30 15:08 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Design | Rework | 4 (0.5-3k) | Open |  | IMPLEMENTATION |  | Two UPSs at Connaught Tunnel COT-01-UPS-00004 and COT-01-UPS-00005 are connected to RTU NWP-11-RTC-0101 via Modbus TCP/IP link. Multiple comms loss alarms are observed for these UPSs.
| 05SY - Systemwide | Cxxx-NCR-000865 | NCR | Systemwide PAVA stuttering on CMS scheduled and recorded announcements |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2023-05-31 |  | -114 | 2022-11-24 09:52 | Communications and Control Systems - Public Address Systems | 8000 |  | System Defect | Rework | 2 (6-60k) | Open |  | IMPLEMENTATION |  | There is an impact to the end user resulting in stuttering on CMS scheduled and recorded announcements from the RCC.
| 05SY - Systemwide | Cxxx-NCR-000866 | NCR | Systemwide various PAVA announcements at different noise levels across stations. |  | Contr | SMN | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2023-05-31 |  | -114 | 2022-11-24 09:53 | Communications and Control Systems - Public Address Systems | 10000 |  | System Defect | Rework | 2 (6-60k) | Open |  | IMPLEMENTATION |  | 3 No issues have been grouped under this NCR. 1. RCC Live Mic and CMS Recorded announcement audio levels being different (recorded is lower level than live mic) 2. All Live (CMS, RCC) and Recorded announcements at some stations Ticket halls are too quiet (recently observed at PAD) 3. Live Train announcements are too loud at all station Platforms (observed at CWX and CUH)
| 05SY - Systemwide | Cxxx-NCR-000001 | NCR | No cubes taken for manhole 135 base slab |  | Contr | ARP |  |  | 2017-12-07 | 2017-12-07 17:00 | 0 | 2017-10-10 15:52 | Civil - Drainage | 1000 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Supervision - Supervisor not familiar with the work | Completed |  | On 9/10/2017 the concrete base slab to MH135 was poured. No slump test or concrete cubes were taken for the concrete pour. There was also no trained or competent person on site to sample the concrete or an approved on-site facility to store the cubes.
| 05SY - Systemwide | Cxxx-NCR-000002 | NCR | Accommodation Building Lift Pit Blinding- Out of Tolerance |  | Contr | __ |  |  | 2017-12-31 | 2017-11-27 10:21 | -34 | 2017-10-24 12:53 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | The blinding to the lift pit of the accommodation building is out of tolerance between +3-10mm. The levels range from 103.403 to 103.407. Design level is 103.400 as shown on Cxxx-OVE-S-DDA-CR148_SD013_1-41100.
| 05SY - Systemwide | Cxxx-NCR-000003 | NCR | Drainage marker tape not installed |  | Contr | ARP |  |  | 2017-12-30 | 2017-11-27 13:04 | -33 | 2017-10-30 09:57 | Civil - Drainage | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | Following the backfilling of drainage run S1.021 it was noted that the marker tape required under 5/2.2 (h) of Cxxx-OVE-C-RSP-CR148-50010 had not been installed.
| 05SY - Systemwide | Cxxx-NCR-000004 | NCR | Deviation from MCR (Cxxx-__-C-MCR-CR526-50061) |  | Contr | __ |  |  | 2018-02-01 | 2018-01-29 17:47 | -3 | 2017-11-15 16:50 | Civil - Civil Engineering General | 0 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Lack or improper material identification and traceability | Completed |  | The imported Type 1 material used within the permanent works for the accommodation building was not the supplier specified in the MCR (Cxxx-__-C-MCR-CR526-50061). The aforementioned material was from a supplier that is ISO-9001 approved, however it is certified by a non-UKAS accredited organisation.
| 05SY - Systemwide | Cxxx-NCR-000005 | NCR | Damage to MH135 |  | Contr | ARP |  |  | 2018-03-21 | 2018-02-05 10:58 | -44 | 2017-12-13 12:31 | Civil - Drainage | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | During the excavation for drainage pipe S1.020, a small section of the manhole ring on MH135 was struck and chipped by the excavator bucket.
| 05SY - Systemwide | Cxxx-NCR-000006 | NCR | Concrete Surround to MH135 cast within 150mm of Biscuit |  | Contr | COS |  |  | 2018-03-29 | 2018-02-02 09:56 | -55 | 2018-01-05 12:09 | Civil - Drainage | 1000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Supervision - Other | Completed |  | Concrete was poured to the top of the manhole ring MH 135 within 150 mm of the biscuit against the requirements of Civils specification 5.16 precast concrete manholes note 4, which states that each construction joint shall break joint with precast sections by at least 150mm.
| 05SY - Systemwide | Cxxx-NCR-000007 | NCR | Water Ingress into MH-136 |  | Contr | COS |  |  | 2018-10-31 | 2018-10-16 13:35 | -15 | 2018-01-19 08:37 | Civil - Drainage | 3000 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Water ingress into the base of MH136 through semi dry GEN 3 concrete base. The base of sump chamber has not had a granolithic screed applied.
| 05SY - Systemwide | Cxxx-NCR-000008 | NCR | Construction of Works to Non Construction Issue Drawings |  | Contr | __ |  |  | 2018-06-28 | 2018-03-27 13:49 | -93 | 2018-01-18 08:33 | Civil - Sewage/Water services | 0 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Under slab drainage for the Accommodation Building is being installed to Non Construction issue drawings provided by the Employers Designer and instructed under Cxxx-PMI-00142.
| 05SY - Systemwide | Cxxx-NCR-000009 | NCR | MH46 - Incorrect manhole ring installed |  | Contr | COS |  |  | 2018-05-31 | 2018-05-30 16:44 | -1 | 2018-01-29 11:21 | Civil - Drainage | 6000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Supervision - Insufficient supervision | Completed |  | 1800mm manhole ring was installed in MH46 and set 100mm into the S1 GEN 3 base pour. This was left overnight and cast in. The correct ring size was 2100mm. In addition to this the base as poured too small for a 2100mm manhole ring.
| 05SY - Systemwide | Cxxx-NCR-000010 | NCR | Defective Gully pots |  | Contr | COS |  |  | 2018-05-31 | 2018-03-16 17:35 | -76 | 2018-01-30 14:57 | Civil - Drainage | 0 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Defective gully pots delivered to site and not inspected until placement in S1 GEN 3 concrete. Gullies were agreed to be removed and swapped.
| 05SY - Systemwide | Cxxx-NCR-000011 | NCR | Accommodation building slab concrete |  | Contr | __ |  |  | 2018-05-31 | 2018-04-24 15:08 | -37 | 2018-02-12 14:02 | Civil - Civil Engineering General | 0 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | 3No. loads of concrete were placed within the slab despite failing the slump test.
| 05SY - Systemwide | Cxxx-NCR-000012 | NCR | Accommodation Building slab level out of tolerance |  | Contr | __ |  |  | 2018-08-31 | 2018-06-29 13:33 | -63 | 2018-02-13 13:09 | Civil - Civil Engineering General | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Accommodation building slab level does not meet the vertical tolerance requirements as set out in the Inspection Test Plan.
| 05SY - Systemwide | Cxxx-NCR-000013 | NCR | Accommodation Building- Finish to Slab |  | Contr | __ |  |  | 2018-06-28 | 2018-06-29 11:08 | 1 | 2018-02-13 13:04 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | The current finish to the Accommodation Building doesn't meet the quality requirements set out in the Cxxx - Materials & Workmanship Specification - Section KF11 - In Situ Concrete for Buildings.
| 05SY - Systemwide | Cxxx-NCR-000014 | NCR | Accommodation building - Construction joint between beams and slab |  | Contr | __ |  |  | 2018-05-31 | 2018-05-24 07:11 | -7 | 2018-02-13 13:24 | Civil - Civil Engineering General | 7500 |  | Workmanship | Repair | 2 (6-60k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | There was multiple imperfections on the vertical concrete face, mainly along the construction joint, once the formwork was removed from the perimeter of the Accommodation building slab.
| 05SY - Systemwide | Cxxx-NCR-000015 | NCR | The Contractor has not followed the ITP and method Statement for back filling drainage trench. |  | Crossrail | XRL |  |  | 2018-05-16 | 2018-03-14 11:53 | -63 | 2018-02-16 10:44 | Civil - Drainage | 5500 |  | Supervision/Management | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Insufficient information made available to the worker. | Completed |  | The granular fill around the drainage pipe and the 6N back fill have not been completed prior to the trench box being moved forward, as per the ITP Cxxx-__-D-ITP-CR526-50001 Rev 4.0 item B2.6 states; under frequency “ For every pipe prior to moving onto next activity”, Under Activity;” Backfill of trench to line and level of pipe invert”. Photograph attached. As a consequence to the back fill not being completed as stated in the ITP and Method Statement there is a high risk of damage to the drainage pipe whilst re-excavating the area to complete the backfill activity.
| 05SY - Systemwide | Cxxx-NCR-000016 | NCR | The Contractor are carry out Air Leakage Testing in lieu of UKAS Accreditation. |  | Crossrail | XRL |  |  | 2018-05-16 | 2018-03-14 12:14 | -63 | 2018-02-16 10:53 | Civil - Drainage | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | A planned surveillance was carried on drainage at the Plumstead Maintenance Facility, On discussion it was found that no Project Managers Acceptance is in place for __ to undertake Air Leakage Testing in lieu of UKAS Accreditation.
| 05SY - Systemwide | Cxxx-NCR-000017 | NCR | The Benching in Manhole has not been installed as per the ITP and Specification |  | Crossrail | XRL |  |  | 2018-05-16 | 2018-03-14 12:12 | -63 | 2018-02-16 11:04 | Civil - Drainage | 8500 |  | Supervision/Management | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Insufficient information made available to the worker. | Completed |  | A planned surveillance of drainage at Plumstead Maintenance Facility found on inspection the Contractor incorrectly installed the benching in manhole 46 using only sand and cement instead of 1 part cement, 1 part natural sand, and 2 parts single as stated in the ITP and Specification.
| 05SY - Systemwide | Cxxx-NCR-000018 | NCR | Accommodation Building - Clash Between Perimeter Upstand and Secondary Posts |  | Contr | __ |  |  | 2018-05-31 | 2018-05-31 11:54 | 0 | 2018-02-22 12:30 | Structural Engineering - Structural Engineering - General | 6000 |  | Design | Repair | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | The contractor identifies a clash in 17 locations between the secondary steelwork posts on the Accommodation Building Elevations and the ground floor concrete upstand around the perimeter of the Building. See attached photos and 'Clash Locations'.
| 05SY - Systemwide | Cxxx-NCR-000019 | NCR | Maintenance building gas membrane verification |  | Contr | __ |  |  | 2018-06-29 | 2018-06-19 12:49 | -10 | 2018-02-21 15:28 | Civil - Civil Engineering General | 0 |  | Material | Rework | 4 (0.5-3k) | Complete | Verification Problems - Inspection points not adequate | Completed |  | Gas membrane verification on a section of Maintenance building works was not carried out as per the current ITP revision.
| 05SY - Systemwide | Cxxx-NCR-000020 | NCR | Accommodation Building - Clash Between Perimeter Upstand and Cladding Rails |  | Contr | __ |  |  | 2018-05-31 | 2018-05-31 12:13 | 0 | 2018-02-22 14:11 | Structural Engineering - Structural Engineering - General | 6000 |  | Design | Repair | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | The contractor identifies a clash in 27 locations between the bottom of the secondary steelwork cladding rails, on the Accommodation Building Elevations, and the ground floor concrete upstand around the perimeter of the Building. See attached photos and 'Clash Locations'.
| 05SY - Systemwide | Cxxx-NCR-000021 | NCR | Unnapproved product (retarder) used on construction joint |  | Contr | __ |  |  | 2018-05-29 | 2018-05-29 17:06 | 0 | 2018-04-03 16:40 | Civil - Civil Engineering General | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | The retarder used to aid the formation of construction joint on the under-cover stores retaining wall is not approved by Crossrail by means of MCR.
| 05SY - Systemwide | Cxxx-NCR-000023 | NCR | Shutter Oil- unapproved material in works |  | Contr | __ |  |  | 2018-06-28 | 2018-05-25 07:51 | -34 | 2018-04-09 15:07 | Civil - Civil Engineering General | 0 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | The product being used to oil shutters prior to concrete (Adomast Safestrike XL) did not have an approved MCR in place prior to use.
| 05SY - Systemwide | Cxxx-NCR-000024 | NCR | Accommodation Building - Incorrect Paint Finishes to Primary Steelwork |  | Contr | __ |  |  | 2018-08-06 | 2018-08-07 10:47 | 1 | 2018-04-17 14:25 | Architectural - Finishes | 0 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Following a review of the Accommodation Building's decorative finish to primary steelwork, the contractor confirms the following: 1. Columns on GLs C7, D7 and D8 need to be high decorative (FPS-201) @1st floor level, in line with Cxxx-__-S-DDL-CR148_SD013_C-10106 2. Column C2 needs to be high decorative (FPS-201), full height, in line with Cxxx-__-S-DDL-CR148_SD013_C-10106 3. The high level rafter to GL 1 needs to be normal decorative (FPS-203), in line with Cxxx-__-S-DDL-CR148_SD013_C-10106 4. The bracing in the atrium area (Grids 1 & 2) has arrived to site with normal decorative (FPS-203) finish. Although not shown on any drawing, the braces and RHSs need to be high decorative (FPS-201) finish, to keep in line with the architectural intent of the exposed atrium steelwork. NB: This clarification to the scope for the NCR is not related to performance requirements; it relates only to architectural finish. Please find attached RFI response from the contractor's designer confirming the above.
| 05SY - Systemwide | Cxxx-NCR-000025 | NCR | Train wash slab - Silt trap reinforcement |  | Contr | __ |  |  | 2018-06-08 | 2018-05-24 06:55 | -15 | 2018-04-24 08:32 | Civil - Civil Engineering General | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The reinforcement that is required in the silt trap surround, shown on drawing Cxxx-OVE-D-DDD-CR148_SD013_1-37542 Rev C01, was installed incorrectly and as a result are now loose, with some being removed fully.
| 05SY - Systemwide | Cxxx-NCR-000027 | NCR | Contractor has not complied with the requirements of the Intumescent Paint specification |  | Crossrail | XRL |  |  | 2018-08-22 | 2018-08-22 15:50 | 0 | 2018-04-26 12:32 | Civil - Structural Engineering | 3000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | A planned Crossrail surveillance was undertaken on 5th April 2018. This looked at fabrication and installation of primary and secondary steelwork (including coatings) at Plumstead Maintenance Facility – Accommodation Building. On request the Contractor was unable to produce a report from __ regarding a visit to inspect the initial application of the Firetex FX6000 Intumescent system to the Accommodation Building Structural Steelwork, as required in the Architectural Specification Cxxx-__-A-RSP-CR526-50001 JM61.
| 05SY - Systemwide | Cxxx-NCR-000029 | NCR | Incorrect Gloss Finish on the paint sample (Red high decorative finish) |  | Contr | __ |  |  | 2018-07-02 | 2018-07-02 07:29 | 0 | 2018-06-04 09:07 | Civil - Structural Engineering | 0 |  | Material | Rework | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | __ invited Crossrail’s Architecture on the 05-03-18 to attend Cxxx Plumstead to review the high decorative paint (FPS-201) sample provided by __'s Subcontractor (__). During the sample review, it was noted there is a discrepancy between the gloss content applied to the sample and the onsite high decorative finish applied to the steel frame. After __ conducting a full review, __ have raised an NCR to their Subcontractor (__) clarifying the incorrect paint (C137 with a sheen gloss content) was applied to the high decorative (FPS-201) sample presented to __/CRL
| 05SY - Systemwide | Cxxx-NCR-000030 | NCR | Saddle connection in S8.003 to gully G23 not installed correctly |  | Contr | COS |  |  | 2018-08-03 | 2018-07-13 09:30 | -21 | 2018-05-08 23:37 | Civil - Drainage | 3750 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A saddle connection was incorrectly installed on pipe run S8.003 to gully G23. The concrete pipe was scabbled so the clay saddle connection could fit (see photo file-21). This should have been bedded on the mortar before being surrounded in concrete as per the manufacturers instructions (see attachments).
| 05SY - Systemwide | Cxxx-NCR-000031 | NCR | Accommodation building 1st floor slab levels |  | Contr | __ |  |  | 2018-08-03 | 2018-07-11 09:51 | -23 | 2018-05-12 14:47 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | accommodation building 1st floor slab is not within vertical level tolerance
| 05SY - Systemwide | Cxxx-NCR-000032 | NCR | Accommodation building lower roof slab not within vertical level tolerance |  | Contr | __ |  |  | 2018-09-07 | 2018-07-11 09:46 | -58 | 2018-05-12 14:50 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Accommodation building lower roof slab not within vertical level tolerance
| 05SY - Systemwide | Cxxx-NCR-000033 | NCR | Undercover stores Retaining Wall - Cover to reinforcement on front of Retaining wall base |  | Contr | __ |  |  | 2018-08-06 | 2018-06-12 15:42 | -55 | 2018-05-22 08:07 | Civil - Civil Engineering General | 0 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | FCD 00046 was raised regarding the requirement for an additional 25mm cover to the front of the retaining wall bases. This meant that cover increased from 75mm to 100mm. RFI 407 was also raised regarding this issue.
| 05SY - Systemwide | Cxxx-NCR-000034 | NCR | Contractor progressing Cladding works using un-accepted drawings |  | Crossrail | XRL |  |  | 2018-08-31 | 2018-07-19 09:32 | -43 | 2018-06-01 09:02 | Architectural - General | 0 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | A planned Crossrail surveillance was undertaken on 30th May 2018. This looked at the Cladding installation at Plumstead Maintenance Facility – Accommodation Building. On checking the drawings for the Cladding, it was found that the drawings in use were at P status; ‘Accommodation Building Envelope Detail’ Cxxx-__-A-DDD-CRCR148_SD013_Z-51501 (Rev P03) and ‘Accommodation Building Envelope Detail’ Cxxx-__-A-DDD-CRCR148_SD013_Z-51503 (Rev P04). In discussion with the Contractor it was stated that ‘By Exception’ was in place for the buildings envelop design. The Contractor was requested to provide evidence of this by supplying the follow documents; By Exception Risk Assessment and NCR as required in the ‘By Exception Procedure’. The Contractor was unable to provide the evidence and as such is progressing works using un-accepted drawings. As the surveillance was based on a sample, other drawings should be checked and confirmed as part of closure to this NCR.
| 05SY - Systemwide | Cxxx-NCR-000035 | NCR | Level inverts at SP SW MH26 |  | Contr | COS |  |  | 2018-09-28 | 2018-07-23 09:33 | -67 | 2018-06-27 16:02 | Civil - Drainage | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | Pipe run S1.011 stub into SP-SW-MH-26 was installed at the incorrect downstream invert level (103.054) as to what is stated on Cxxx-OVE-D-DDJ-CR148_SD013_Z-37901 (103.20).
| 05SY - Systemwide | Cxxx-NCR-000037 | NCR | Construction of Works to Non Construction Issue Drawings - Maintenance Building under slab utilities |  | Contr | __ |  |  | 2018-09-30 | 2018-09-03 11:35 | -27 | 2018-06-28 07:19 | Civil - Utilities Engineering | 0 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | Under slab drainage and utilities for the Maintenance Building has been installed to Non Construction issue drawings provided by the Employers Manager via email on 25/04/18- drawings attached
| 05SY - Systemwide | Cxxx-NCR-000038 | NCR | Accommodation Building - External Cladding Panel Finish |  | Contr | __ |  |  | 2019-03-01 | 2019-02-02 19:53 | -27 | 2018-06-29 15:47 | Architectural - Finishes | 50000 |  | Manufacturing Defect | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | After carrying out an onsite survey the external cladding panels to the Accommodation Building, it was found; 1. Variation in shading between the 1000 and 1200 module RAL 7012 cladding panels 2. Variation in horizontal joint thicknesses - up to 30% of horizontal joint thicknesses do not comply with manufacturer's own specification 3. Damaged panels requiring replacement or repair 4. Some of the corner panels have significant stepping, in places, vertically from corner panel to corner panel
| 05SY - Systemwide | Cxxx-NCR-000039 | NCR | Works Being Progressed via the "By Exception" process |  | Crossrail | XRL |  |  | 2018-10-31 | 2018-10-12 11:45 | -19 | 2018-07-16 08:50 | Architectural - Brickworks/Blockworks | 0 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | This NCR has been issued in accordance with CRL's "by exception construction prior to gate acceptance" CRL1-XRL-O7-GPD-CR001-50023
| 05SY - Systemwide | Cxxx-NCR-000040 | NCR | S3.007 downstream invert incorrect |  | Contr | COS |  |  | 2019-01-31 | 2019-01-13 21:54 | -18 | 2018-07-19 08:54 | Civil - Drainage | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The design level downstream invert of pipe run S3.007 from SW-MH-22 to SW-MH-23 is 103.83 as shown in Cxxx-OVE-D-DDJ-CR148_SD013_Z-37901. The pipe run was installed as per design levels and gradient. Following the base pour of the manhole and surrounding of the pipe it was found that the invert level of the downstream invert into SW-MH-23 had dropped to 103.792.
| 05SY - Systemwide | Cxxx-NCR-000041 | NCR | FW11 cracks in top ring |  | Contr | COS |  |  | 2018-11-30 | 2018-11-30 16:05 | 0 | 2018-07-24 09:36 | Civil - Drainage | 1000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | There are a number of cracks in the top manhole ring of FW11 which exceed the .3mm allowance for crack width.
| 05SY - Systemwide | Cxxx-NCR-000042 | NCR | Maintenance Lower Roof Slab - Cracks |  | Contr | __ |  |  | 2018-11-20 | 2018-10-11 20:58 | -40 | 2018-07-25 16:06 | Civil - Civil Engineering General | 1000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | There are four locations on the Maintenance building lower roof slab where the cracks are 0.5mm and approximately 1.5m in length. The acceptable allowance as per the National Structural Concrete Specification is 0.3mm.
| 05SY - Systemwide | Cxxx-NCR-000043 | NCR | Conduit Material Approval |  | Contr | __ |  |  | 2018-10-11 | 2018-09-19 11:33 | -22 | 2018-08-30 11:47 | Electrical - Cable Management | 0 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | Conduit is being installed without an approved MCR. The MCR has been submitted but Crossrail approval has not been received at present.
| 05SY - Systemwide | Cxxx-NCR-000044 | NCR | Screed Insulation damaged by water ingress |  | Contr | __ |  |  | 2018-10-31 | 2018-11-02 20:10 | 2 | 2018-08-22 15:05 | Architectural - Flooring | 3000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Supervision - Other | Completed |  | The floor screed within the female change room (A1.22) of the Accommodation building, had to be removed and re-installed due to saturated/damaged insulation under the screed. Consequently, the screed has failed its testing.
| 05SY - Systemwide | Cxxx-NCR-000045 | NCR | Accommodation Building - Low DFT Readings to Structural Steelwork |  | Contr | __ |  |  | 2018-11-30 | 2018-10-31 14:47 | -30 | 2018-08-15 13:21 | Structural Engineering - Surface Treatment | 6000 |  | Manufacturing Defect | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | As part of the quality assurance provided for the Accommodation Building’s structural steel work, the intumescent paint manufacturer Sherwin-Williams checked factory applied paint depths on site and gave DFT readings for members in accordance with the Architectural Specification Cxxx-__-A-RSP-CR526-50001, clause JM61. This action was in response to Cxxx-NCR-000027. The __ report issued on 15/05/18 (attached) stated that the following structural members have isolated areas of insufficient paint thickness: Ground Level Columns C9 & B9 - Low DFT readings were obtained to the inner flanges Bracing between Gridline (6-7) A – Low readings were obtained throughout resulting in a low average 1st Floor Columns C9 & B9 – Low DFT readings were obtained on the inner flanges Bracing between Gridline (B-C) 8 – Lower section of the bracing in a 2m area low DFT readings were obtained Columns B5 and A5 – Low DFT readings were obtained on the inner flanges
| 05SY - Systemwide | Cxxx-NCR-000046 | NCR | Accommodation Building - Damaged Gutter Outlet |  | Contr | __ |  |  | 2018-10-31 | 2018-09-25 11:21 | -36 | 2018-09-03 07:28 | Architectural - Roofing & Exterior Treatment | 1000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper handling of material | Completed |  | One outlet to the Accommodation Building's pitched roof gutter has a crack to it
| 05SY - Systemwide | Cxxx-NCR-000047 | NCR | Attenuation Tank - Commencing works without an approved ITP |  | Contr | __ |  |  | 2018-10-29 | 2018-10-24 15:43 | -5 | 2018-09-04 10:12 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | Works on Attenuation tank 2 commenced without an approved ITP in place.
| 05SY - Systemwide | Cxxx-NCR-000048 | NCR | Maintenance Building - Grout Cubes Not Stored Correctly |  | Contr | __ |  |  | 2018-10-31 | 2018-10-23 09:18 | -8 | 2018-09-05 10:45 | Structural Engineering - Grouting | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper storage of material | Completed |  | As per Crossrail observation CRL-OBS-23250, one batch of grout cubes taken for the Maintenance Building's baseplates were left out overnight. This is not in line with the British Standard.
| 05SY - Systemwide | Cxxx-NCR-000049 | NCR | Accomodation Building - Glazing; Packing to Window Straps |  | Contr | __ |  |  | 2018-11-30 | 2018-10-23 09:08 | -38 | 2018-09-07 12:07 | Architectural - Glazing | 3000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Please refer to attached F2 Dwgs, 'window jamb detail', where it can be seen that an adjustable strap with minimal packing is required to the window openings. Windows have been installed to some openings of the Accommodation Building using straps in a straight application with up to 40mm packing. It was observed that: the window strap is not installed as per the IFC - this should be used in a 'Z' application with minimal packing, rather than in a straight application with excessive packing, please see photos attached. The remainder of the window installation was found to be as per the design: - 40mm Aperture - Correct dimensions for window frame and window jamb post
| 05SY - Systemwide | Cxxx-NCR-000050 | NCR | Maintenance Building Pit Conrete |  | Contr | __ |  |  | 2019-06-30 | 2019-06-28 11:02 | -2 | 2018-09-06 12:33 | Civil - Civil Engineering General | 6000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The concrete surface finish in the Maintenance building pit requires remedial action. The issues include; 1) Blow holes and honeycombing the full length of the pit 2) Wood chippings and plywood seen present in the underside of the recess 3) Cold joint 4) Medium to large concrete repairs where insufficient compaction occurred, with reinforcement exposed.
| 05SY - Systemwide | Cxxx-NCR-000051 | NCR | S7.00A change in size and level |  | Contr | COS |  |  | 2019-05-31 | 2019-05-28 13:50 | -3 | 2018-09-06 15:55 | Civil - Drainage | 2000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | S7.00A has been installed approximately 200mm lower than design level. Currently 10m of pipe has been installed with the upstream invert of 104.486 and downstream invert of 104.347. This will mean a fall of 1:72 across the run. Design levels are 104.8 to 1.04.33 (1:25 fall) S7.00A and S7.00B have been installed with the incorrect size pipe (150mm). The pipe run should go from a 100mm diameter pipe (S7.00A) into SW-AC-01 and 100mm diameter coming from SW-AC-01 for the rest of the run along the north of the accommodation building.
| 05SY - Systemwide | Cxxx-NCR-000052 | NCR | Intumescent Coatings of Connections – Visual Requirements |  | Contr | __ |  |  | 2019-02-28 | 2019-02-08 21:51 | -20 | 2018-09-07 12:55 | Structural Engineering - Surface Treatment | 6000 |  | Supervision/Management | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | As per JM61.1403 and JM61.1202i of the Architectural Specification, the intumescent coating to some steel member connections in the Accommodation and Maintenance Buildings do not match the factory applied finish on the members themselves. These sections of the specification directly relate to the visual aesthetics of painted members.
| 05SY - Systemwide | Cxxx-NCR-000053 | NCR | Maintenance Building Slab Delamination |  | Contr | __ |  |  | 2019-06-30 | 2019-06-28 10:15 | -2 | 2018-09-08 15:32 | Civil - Civil Engineering General | 6000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Local spots of delamination present on the Maintenance building slab. Primarily on the south side of the Maintenance pit. See attached photos and survey.
| 05SY - Systemwide | Cxxx-NCR-000054 | NCR | Maintenance Building Slab Repair |  | Contr | __ |  |  | 2019-05-31 | 2019-06-11 15:28 | 11 | 2018-09-07 15:12 | Civil - Civil Engineering General | 3000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | Remedial Works to Maintenance Building Slab commenced prior to authorised repair method by CEG.
| 05SY - Systemwide | Cxxx-NCR-000055 | NCR | Train Wash Slab - Coring clash with rebar |  | Contr | __ |  |  | 2018-11-04 | 2018-10-31 12:16 | -4 | 2018-09-17 14:30 | Civil - Civil Engineering General | 3000 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Supervision - Other | Completed |  | Whilst coring for the rail base plate fixings on the Train Wash slab, there have been a number of clashes with reinforcement on the most southerly row (see attached). There currently has been 10 clashes, with 5 going fully through the bar and 5 partially through it. Out of the remaining cores which remain, a further 6 will be partially caught.
| 05SY - Systemwide | Cxxx-NCR-000057 | NCR | Accommodation Building, Glazing, GLP101 104 Specification |  | Contr | __ |  |  | 2018-12-28 | 2019-01-02 12:03 | 5 | 2018-09-19 14:08 | Architectural - Glazing | 6000 |  | Material | Rework | 3 (3-6k) | Complete | Management Problem - Inadequate administrative control | Completed |  | The schedule 'Accommodation Bldg GLP101-104 installed", attached, shows the windows/door sets, that have been installed to date, in the Accommodation Building, requiring compliance with glazing specification GLP101, GLP102, GLP103 and GLP104 (42 windows are affected by this NCR). Each installed window bears a sticker which does not match specifications GLP101, GLP102, GLP103 or GLP104. There are no other marks on the glazing or documentation to positively identify the specification applied.
| 05SY - Systemwide | Cxxx-NCR-000058 | NCR | CMS location |  | Contr | __ |  |  | 2019-06-12 | 2019-03-14 15:24 | -90 | 2018-09-24 16:12 | Electrical - General | 3000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | CMS on the 1st floor in the Accommodation Building has been installed in a different location to that shown on the F1 drawings.
| 05SY - Systemwide | Cxxx-NCR-000060 | NCR | Fencing - Coping Stone Omission |  | Contr | __ |  |  | 2020-05-31 | 2020-03-25 16:06 | -67 | 2018-10-02 13:36 | Civil - Civil Engineering General | 6000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Drawing Cxxx-OVE-C-DDD-CR148_SD013_1-37541 C01 shows a coping stone to be installed as in Detail 2; in terms of constructability the coping profile should have been installed before the 1.5m fencing panels on top of the brick work wall - this has not been done.
| 05SY - Systemwide | Cxxx-NCR-000061 | NCR | Removal of EX-MH-SW-24 |  | Contr | __ |  |  | 2019-03-31 | 2019-02-19 21:21 | -40 | 2018-10-02 13:15 | Civil - Civil Engineering General | 6000 |  | Damaged | Rework | 3 (3-6k) | Complete | Management Problem - Other management problem | Completed |  | Existing surface water manhole EX-MH-SW-24 was demolished and replaced prior to Crossrail accepting the proposal.
| 05SY - Systemwide | Cxxx-NCR-000062 | NCR | Maintenance building slab and pit concrete cover |  | Contr | __ |  |  | 2019-07-31 | 2019-07-12 08:15 | -19 | 2018-10-03 08:42 | Civil - Civil Engineering General | 6000 |  | Workmanship | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The cover to reinforcement on the Maintenance building slab and pit walls, is out of tolerance. Please see attached.
| 05SY - Systemwide | Cxxx-NCR-000063 | NCR | Incorrect ring installed for SW-MH-37 |  | Contr | COS |  |  | 2018-11-19 | 2018-11-19 16:00 | 0 | 2018-10-10 15:46 | Civil - Drainage | 1750 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the construction of the base and embedment of the first 1200mm diameter ring, a 750mm high precast ring was installed. This height of ring is too high to achieve the correct build up to cover level.
| 05SY - Systemwide | Cxxx-NCR-000064 | NCR | Acc Bldg: Internal staircase colour |  | Contr | __ |  |  | 2019-02-28 | 2019-03-05 16:47 | 5 | 2018-10-17 13:57 | Architectural - General | 6000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | The staircase was delivered to site, installation commenced on the same day - on 10/10/2018; it has since been observed that the colour of the staircase is RAL 9016 as per the subcontractor's drawing Cxxx-__-A-DWG-CR526-50118-C02 (attached) rather than RAL 7016 as per the architectural specification Cxxx-__-A-RSP-CR526-50001 Rev 6.
| 05SY - Systemwide | Cxxx-NCR-000065 | NCR | Accommodation Building Ventilation changes |  | Contr | __ |  |  | 2019-09-30 | 2019-07-02 14:03 | -90 | 2018-10-19 11:39 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Changes to the ventilation design and plant room have been made changing the “gated” design intent without agreement from CRL. The changes to the ducting have already be incorporated in the installation.
| 05SY - Systemwide | Cxxx-NCR-000066 | NCR | CMS - Tray Transitions between 2 flat sections at different levels |  | Contr | __ |  |  | 2019-02-01 | 2019-01-25 16:18 | -7 | 2018-10-19 15:03 | Electrical - Cable Management | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | In a number of location within the Accommodation Building the transitions between two flat sections of cable tray at different levels have been installed incorrectly (i.e. not in accordance with the manufacturers detail). See attached photographs. The proposed solution is to complete the installation using a 45deg inside riser, straight section and 45deg outside riser. REWORKED: 18/12/2018 - Attached is a photograph showing the completed rework
| 05SY - Systemwide | Cxxx-NCR-000067 | NCR | Undercover Stores - Excess cover to reinforcement |  | Contr | __ |  |  | 2019-03-31 | 2019-02-07 20:34 | -52 | 2018-11-07 13:32 | Civil - Civil Engineering General | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Cover to the top of reinforcement for the Undercover Stores should be 65mm, as shown in note 8 on drawing Cxxx-OVE-S-DDL-CCR148_SD013_1-43501. A pre-pour as-built of the cover has shown that on site, this ranges between 75mm and 110mm. CND-00020 raised on this matter. Cover survey with photos attached.
| 05SY - Systemwide | Cxxx-NCR-000068 | NCR | Gantry crane rails installed out of tolerance |  | Contr | ARP |  |  | 2019-01-31 | 2019-01-13 22:01 | -18 | 2018-11-12 16:40 | Structural Engineering - Steel Member | 1000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | ISO 12488, gives a gantry crane rail span tolerance of +/-5mm for class 2, medium duty cranes. See attached. The Cxxx gantry crane rails were found to be out of tolerance at the following locations: - GL7: -6mm (-1mm out of tolerance) - GL3: -8mm (-3mm out of tolerance)
| 05SY - Systemwide | Cxxx-NCR-000069 | NCR | QS695-04 - Material Installed on site without accepted MCR |  | Crossrail | XRL |  |  | 2019-02-28 | 2019-03-05 16:49 | 5 | 2018-11-16 15:15 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | A Crossrail Quality Surveillance took place at Cxxx looking at Ductwork Installation. It was found that Galvamate Sealant had been installed between ductwork flanges. On checking the related MCR (CRL-MCR-006783), it was found as not approved on eB at the time. Therefore as materials have been installed without prior approval of the MCR there has been a breakdown in the ITP procedure; MCR approval is a hold point preceding site installation.
| 05SY - Systemwide | Cxxx-NCR-000070 | NCR | Manhole Water Egress |  | Contr | COS |  |  | 2019-03-31 | 2019-03-07 15:11 | -24 | 2018-11-17 14:37 | Civil - Drainage | 6000 |  | Testing and Commissioning | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Interim water testing of manholes has been carried out prior to final completion to check for signs of water ingress and egress. During this testing the water level dropped beyond the parameters specified in the ITP (see technical requirements).
| 05SY - Systemwide | Cxxx-NCR-000072 | NCR | Gantry crane T&C without IRN |  | Contr | ARP |  |  | 2019-02-28 | 2019-03-06 14:43 | 6 | 2018-11-26 08:25 | Mechanical - Lifts | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Inspector not familiar with inspection methods | Completed |  | The Cxxx gantry crane was energised and Tested and Commissioned without a signed IRN. Other subcontractors were working around the crane without it being isolated.
| 05SY - Systemwide | Cxxx-NCR-000073 | NCR | Roller Shutter Doors; Paint Finish |  | Contr | __ |  |  | 2019-03-29 | 2019-03-05 17:12 | -24 | 2018-11-28 12:22 | Architectural - Doors | 3000 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Please see photo attached-'Hag Roller shutter paint NCR 1': On site, there is a total of six roller shutter doors to be installed. On visual inspection, both of the larger type (RAL1021) of shutter door to the gable ends of the Maintenance Building were found to be defective. Please see photo attached-'Hag Roller shutter paint NCR 1'; the depth/appearance of the yellow powder coating was found to vary from slat to slat, giving the paintwork a non uniform finish.
| 05SY - Systemwide | Cxxx-NCR-000074 | NCR | MEP - Rainwater Pipe - Deviation of Specification Material. |  | Contr | __ |  |  | 2019-03-29 | 2019-03-05 16:52 | -24 | 2018-12-03 08:24 | Mechanical - Mechanical Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | The installation of the Rainwater pipes commenced with a material that is not listed within the MEP Specification under Rainwater Pipe Materials ( See Technical Requirement Below). The material used is Geberit Silent PP and has an approved MCR (See MCR ref: CRL-MCR-006853). We propose the use of the material for the following reason: - OFFSETS - minimum offset that can be achieved by the use of HDPE Electrofusion would be approximately 200mm, by using Silent PP push Fit and joining the same two 45 degree elbows, the m/f connection offers you a minimum of 130mm. - ADDITIONAL FITTINGS - The Silent PP range also offers additional angled bends that are not available with HDPE. You create smaller offsets with the use of 15 and 30 degree bends. The attached table gives you and breakdown of the achievable offsets with Silent PP. This will significantly improve the installation with the holes in their current incorrect positions. - WHITE INNER PIPE - The white inner pipe has considerable advantages, for example, if the discharge pipe becomes clogged and needs investigation with a camera. Deposits are more easily visible than with your normal dark inner. - SOUND OPTIMISED - Hydraulically optimised fittings ensure a higher discharge capacity and less noise in the discharge pipe. This mean the Geberit Silent PP drainage plug in system is ideally suited for fast, sound optimised stack connections. - LOW LINEAR EXPANSION - The low linear expansion of the Geberit Silent PP three-layer pipes allows the entire system to be installed without expansion sockets. This removes an area of potential failure over the specified system. - HIGH RING STIFFNESS - The high ring stiffness of the Silent PP pipes and the fittings, which have been reinforced with ribs, enable easy and safe processing. The EPDM lip seals guarantee reliable and permanent tightness of the system. The use of this material has been reviewed by the Contractors Designer and have provided no objection. REWORKED: The Contractor has now received acceptance of the material from the contractor's F1 designer. Please see attached letter confirming.
| 05SY - Systemwide | Cxxx-NCR-000075 | NCR | Gantry crane hook height |  | Contr | ARP |  |  | 2019-03-29 | 2019-01-22 12:45 | -66 | 2018-12-11 16:54 | Mechanical - Lifts | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The gantry crane hook lowest height has been set 120mm higher than that shown on design drawing (Cxxx-__-M1-DWG-CR526-50004).
| 05SY - Systemwide | Cxxx-NCR-000076 | NCR | Maintenance Building- LV Room Layout |  | Contr | __ |  |  | 2019-03-31 | 2019-03-06 19:26 | -25 | 2019-01-03 15:55 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Ducts within the Maintenance Building LV Room were cast into the slab out of position, leading to a clash with the block-work walls.
| 05SY - Systemwide | Cxxx-NCR-000077 | NCR | S24.002 rocker orientation |  | Contr | COS |  |  | 2019-06-30 | 2019-05-22 09:32 | -39 | 2019-01-08 10:33 | Civil - Drainage | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The rocker pipe from SW-MH-39 for pipe run S24.002 into EXP-PL 2.02 MH has been orientated incorrectly. As agreed in Cxxx-FCD-000158 a bend is required to re-align the pipe run into EXP-PL 2.02 MH. Note also that the rocker of existing manhole EXP-PL 2.02 MH. was also incorrectly orientated.
| 05SY - Systemwide | Cxxx-NCR-000078 | NCR | Cxxx PLU Track - Geotextile overlap underneath RRAP between maintenance siding MS10 and MS11 |  | Contr | __ |  |  | 2019-05-31 | 2019-06-04 13:21 | 4 | 2019-01-09 14:07 | Track - Track General | 2000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | In preparation for the installation of the RRAP concrete base, the ballast between sidings 10 and 11 was removed. To remove the ballast, an excavator bucket was used. During these works, the pressure and motion of the bucket and ballast lead to some of the underlying geotextile to damage. Subsequently, the geotextile was cut around the extents of the RRAP concrete base to remove the damaged geotextile and replace with new. However, the dimensions cut did not allow for an overlap of 500mm with the adjacent geotextile layers as per ITP requirement. This occurred between chainages 23075 and 23113.
| 05SY - Systemwide | Cxxx-NCR-000079 | NCR | REB Slab - PSP concrete level out of tolerance |  | Contr | __ |  |  | 2019-05-31 | 2019-04-30 15:22 | -31 | 2019-02-13 13:09 | Civil - Civil Engineering General | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The level for the top of concrete in the recess (where troughs are situated) in the PSP slab has raised up to a maximum of 25mm and is out of tolerance. Survey attached.
| 05SY - Systemwide | Cxxx-NCR-000080 | NCR | Installation of lighting support system without an approved MCR - Accommodation Building |  | Contr | __ |  |  | 2019-06-12 | 2019-03-14 17:15 | -90 | 2019-02-18 12:04 | Electrical - Lighting | 3000 |  | Material | Repair | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | __ have installed the lighting suspension system for the Accommodation Building open plan office, mess and task hub areas utilising Gripple branded wire rope, fixings and accessories without having submitted an MCR for the products used MCR referenced CRL-MCR-007646 has now been initiated and awaiting approval
| 05SY - Systemwide | Cxxx-NCR-000081 | NCR | Radiators were install without a sample been submitted for approval |  | Contr | __ |  |  | 2019-05-31 | 2019-05-23 08:57 | -8 | 2019-02-18 14:50 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | __ installed 2 number Radiators in the PPE Store room on the Ground Floor in the Accommodation Building without submitting a sample for approval
| 05SY - Systemwide | Cxxx-NCR-000082 | NCR | The Sizes of Heating Pipes installed are not as per LTHW schematic in isolated locations – Accommodation Building |  | Contr | __ |  |  | 2019-05-31 | 2019-06-07 16:22 | 7 | 2019-02-18 17:32 | Mechanical - Hot & Cold Water Supplies | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | The Sizes of Heating Pipes installed at high level ground floor to serve up the first floor are smaller in areas than what is shown on the LTHW schematic Cxxx-__-M-DDE-CR148_SD013_Z-61601 C01 The schematic shows the pipe starting at 25dia then 20dia most of the way and then 15dia for the last three rads.
| 05SY - Systemwide | Cxxx-NCR-000083 | NCR | Rail baseplate core hole locations |  | Contr | __ |  |  | 2019-05-31 | 2019-04-25 11:08 | -36 | 2019-02-19 11:11 | Civil - Track | 6000 |  | Design | Repair | 3 (3-6k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | 650 no. core holes in the reinforced concrete track slabs, at a design diameter of 55mm and 140mm depth, are required to affix the rail plate fixings in sidings 11/12 – see drawing attached Cxxx-OVE-R4-DDD-CR148_SD013_1-27501 C01. The drilled holes have been surveyed on site, and found to be set out incorrectly. See attached as-built schedule- Maintenance Building Holes_As-Built Report; the table shows the error between the designed baseplate hole centre line and the actual drilled hole centre line (see column Q titled Hole Offsets; Delta from Original Design) Further information to consider: The location of rebar in the Maintenance Building Slab has been ferro scanned & surveyed. The results show that Bar Mark 212 (12mm longitudinal bar) will not be compromised by drilling the base plate hole in the correct place. See attached IMG_2577 and surveys Track base plate cores vs re-bar position 1 of 2 and 2 of 2. The attachment ‘Design and Current configurations’ illustrate: a) the design configuration and the as built configuration c) the resultant grout clearance around the dowel in both cases.
| 05SY - Systemwide | Cxxx-NCR-000084 | NCR | Accomodation Building - Mortar Testing |  | Contr | __ |  |  | 2019-05-31 | 2019-02-27 11:09 | -93 | 2019-02-21 12:43 | Architectural - Brickworks/Blockworks | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | The Mortar prism test results for the Accommodation Building are missing. The subcontractor __ (__) and the testing facility are unable to locate the correct records. Additional Information to consider: See MCR attached Cxxx-__-A-MCR-CR526-50012 attached; the base requirement in the Architectural Specification is grade M6, strength 6N/mm2 , Designation ii). All of the mortar has come from the same silo and same supplier-CPI __. The same mix has been used on all buildings. They have tested their product, see attached CPI Mortar Strength Testing. __ Prism test results for the mortar in the Undercover stores, and Maintenance Building prove compressive strength to 6N/mm2 at 7 days and significantly greater than 6N/ mm2 at 28 days. See attachments Maintenance Bldg Mortar Test Cast 09072018 and UC Stores Mortar Test Cast 31012019. In light of __'s missing prism results for the Accommodation Building, __ requested they take samples from there and carry out testing to positively identify the prescribed mortar specification/strength/designation from what has been installed: 2 samples were taken, see attachments SOCOTEC Mortar Analysis Report RS180243 and SOCOTEC Mortar Analysis Report RS180244 . The results show that the BS 5268-3 designation is "(i)", on BCA Factsheet 13 attached, this to translates to M12.
| 05SY - Systemwide | Cxxx-NCR-000085 | NCR | Kerbs out of tolerance (Right Channel in Road String 1) due to concrete pour for laydown slab behind |  | Contr | COS |  |  | 2019-09-30 | 2019-09-11 12:35 | -19 | 2019-04-17 09:44 | Architectural - Urban Realm | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Currently 1 joint of the kerb at chainage 45m on kerb string Right Channel on Road String 1 (see drawings Cxxx-OVE-C-DDA-CR148_SD013_1-37163) is out of tolerance (see attached as-built). This was knocked out of tolerance during the pour of the laydown slab behind the kerb as the poker was too close/hit the kerb.
| 05SY - Systemwide | Cxxx-NCR-000086 | NCR | FW21A clash with bollard |  | Contr | COS |  |  | 2019-08-30 | 2019-09-12 12:03 | 13 | 2019-03-05 16:03 | Architectural - Urban Realm | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | FWMH21A was relocated 300mm east of its design location as part of the proposal in Cxxx-RFI-000657 to avoid clashing with the TW Maramadon Sewer and bollards. Following the initial RFI proposal to move the manhole 300mm east it was found that the manhole also needed to move 300m south and the RFI was updated. Due to a communication error the manhole was only moved east and there is now a clash with a bollard and the surround of FWMH21A.
| 05SY - Systemwide | Cxxx-NCR-000088 | NCR | AsBuilt Levels to Flat Roof Paving Slabs |  | Contr | __ |  |  | 2019-05-31 | 2019-03-07 15:00 | -85 | 2019-03-06 11:18 | Architectural - Roofing & Exterior Treatment | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The contractor advises that the +/- 6mm from designed level tolerance for flatness (ref: Cxxx-__-A-RSP-CR526-50001, Clause JJ41.3223) to the paving slabs to the flat roofs of both the Accommodation and Maintenance Buildings was not achieved.
| 05SY - Systemwide | Cxxx-NCR-000089 | NCR | Over-torque to lift shaft bolts |  | Contr | ARP |  |  | 2019-06-30 | 2019-04-18 09:51 | -73 | 2019-03-07 14:16 | Mechanical - Lifts | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During the stage 1 inspection of the Cxxx lift installation, a discrepancy between the ITP stated torque values and actual torque measured on site was identified. The ITP states hand torque to 90 N.m and measurements on site show up to 180 N.m.
| 05SY - Systemwide | Cxxx-NCR-000090 | NCR | Damage to Cxxx concrete lay down slab |  | Contr | __ |  |  | 2019-06-30 | 2019-05-14 16:29 | -47 | 2019-03-14 14:08 | Civil - Concrete Pavement | 3000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Cxxx operatives have "trimmed back" bottom of Cxxx lay down concrete slab by approx 30-50mm. Only bottom pat of slab was trimmed - top 200mm of slab are not disturbed - see pictures attached
| 05SY - Systemwide | Cxxx-NCR-000091 | NCR | Train Loading Slab- below strength 28-day cube test |  | Contr | __ |  |  | 2019-07-31 | 2019-05-22 14:56 | -70 | 2019-03-18 16:52 | Civil - Concrete Pavement | 2000 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Improper resource allocation | Completed |  | 1 of 3No. 28-day cube test results for 1st pour of the train refuelling slab achieved a strength of 25.9N/mm2. This is below the target strength of 40N/mm2.
| 05SY - Systemwide | Cxxx-NCR-000092 | NCR | Maintenance Building- Installing Electrical Panels Without Approved Design |  | Contr | __ |  |  | 2019-06-30 | 2019-06-07 09:07 | -23 | 2019-03-19 15:19 | Electrical - LV Equipment | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | Electricians from __ were working installing Distribution Boards and Lighting panels in Maintenance Building LV Switchroom M1.12 without approved design/drawing.
| 05SY - Systemwide | Cxxx-NCR-000093 | NCR | As-Built location of masonry walls - Undercover stores |  | Contr | __ |  |  | 2019-06-30 | 2019-04-04 12:44 | -87 | 2019-03-20 19:30 | Architectural - Brickworks/Blockworks | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The As-built survey of the blockwork walls in the undercover stores has indicated that the walls spanning on the North-South direction near Gridline 2 and Gridline 7, are located at an offset greater than 10mm from the intended design line. The offset varies from 13mm to 27mm.
| 05SY - Systemwide | Cxxx-NCR-000094 | NCR | Dry Lining and Parition Deviations |  | Contr | __ |  |  | 2019-06-30 | 2019-05-09 09:19 | -52 | 2019-03-20 20:17 | Architectural - Partitions | 0 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On Various locations within the Accommodation Building, the partition walls and the lining built with studwork and plasterboard, have exceeded the allowable deviation of +/-2mm, as this is described in the Architectural Specification and subsequent ITP. The typical deviation noted upon survey is usually 5mm.
| 05SY - Systemwide | Cxxx-NCR-000095 | NCR | Partition Wall and Window mullion interface - PPE Store A2.16 |  | Contr | __ |  |  | 2019-07-31 | 2019-07-22 09:27 | -9 | 2019-03-20 20:57 | Architectural - Partitions | 6000 |  | Design | Repair | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The Partition wall between Rooms A2.09 and A2.16 on the first flor of the Accommodation Building is by design set to terminate against the window mullion. The detail proposed does not work as designed since the size of the mullion is different to the one on the Partition Details. The current proposed solution would turn 1 of the 5 windows in the office (A2.09) from openable to fixed and would most likely change the handing of the single window in the PPE store (A2.16). The Setting out of the partition is also affected. A complete solution proposal is not yet in place.
| 05SY - Systemwide | Cxxx-NCR-000096 | NCR | Materials installed without MCR approval |  | Crossrail | XRL |  |  | 2019-07-31 | 2019-06-05 10:18 | -56 | 2019-03-26 09:09 | Electrical - Cable Management | 3000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | A planned surveillance of CMS installed on the 1st floor of the Maintenance Building was carried out; On checking the MCRs for materials installed on site; Gripple Suspension System CRL-MCR-007646, Wire Basket CRL-MCR-007797 and Heavy-Duty Cable Ladder and Tray CRL-MCR-006052 it was found that MCRs had not been approved at the time of the Surveillance.
| 05SY - Systemwide | Cxxx-NCR-000097 | NCR | The checksheets that have been generated, is not in line with ‘Maintenance Facility' Cxxx-__-E-ITP-CR526-50010 |  | Crossrail | XRL |  |  | 2019-07-31 | 2019-05-29 11:58 | -63 | 2019-03-26 09:55 | Electrical - Cable Management | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | during a planned surveillance of CMS installed on the 1st floor of the maintenance building, check sheets were requested to be submitted for review. On review of the check sheets supplied it was found that the generation of check sheets was not in line with ITP ‘Maintenance Facility Anchors and CMS’ Cxxx-__-E-ITP-CR526-50010 (Rev 1). Inspection numbers 4.2- 4.8 state inspection including snagging to be carried out for each completed section of works. The Contractor has generated only five 1st fix check sheets for the near complete installation, it was also found check sheets had been completed and dated after the surveillance had taken place.
| 05SY - Systemwide | Cxxx-NCR-000098 | NCR | Manhole build up too high for final cover level |  | Contr | COS |  |  | 2019-07-31 | 2019-06-14 08:36 | -47 | 2019-03-28 13:49 | Civil - Drainage | 6000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Verification Problems - Inspector not properly qualified | Completed |  | It has been found that the build up to biscuit level of 3 manholes is currently too high to achieve the correct build up to cover level. As can be seen from the attached survey the current levels of the manholes do not allow sufficient space for 2 course of brick and a manhole cover as per Cxxx-OVE-D-DDD-CR148_SD013_1-37538 Type C manhole detail. The manholes in question are SP-SW-MH-25, SP-SW-MH-26 and SP-SW-MH-38
| 05SY - Systemwide | Cxxx-NCR-000099 | NCR | Cleaners' socket omitted |  | Contr | __ |  |  | 2019-07-31 | 2019-06-26 14:20 | -35 | 2019-03-28 12:08 | Electrical - General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A 13A switched socket designated for cleaners has been omitted from the installation in the Accommodation Building first floor corridor A2.07.
| 05SY - Systemwide | Cxxx-NCR-000100 | NCR | Incorrectly positioned fire dampers |  | Contr | ARP |  |  | 2019-06-30 | 2019-05-28 16:03 | -33 | 2019-03-28 12:21 | Fire - Suppression | 6000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During a site check of installed fire dampers, a number of dampers were noted as not being compliant with the positional detail provided by the manufacturer. 7 No. dampers were noted as out of position 2 No. openings were noted as too big for the damper
| 05SY - Systemwide | Cxxx-NCR-000101 | NCR | Damage to S7.000 |  | Contr | COS |  |  | 2019-07-31 | 2019-05-28 13:45 | -64 | 2019-03-28 15:34 | Civil - Drainage | 3000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During a CCTV survey of Accommodation Building drainage, a crack was found in the side of pipe run S7.000. The crack is located approximately 3m along the length of the pipe measuring from SWAC01.
| 05SY - Systemwide | Cxxx-NCR-000103 | NCR | Incorrect installation of Cement Bound Material in the Staff Car Park |  | Contr | COS |  |  | 2019-07-31 | 2019-06-14 08:32 | -47 | 2019-03-29 08:06 | Architectural - Urban Realm | 30000 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The Cement Bound Layer in the Car Park has been incorrectly installed in the Staff Car Park as part of the permeable paving build-up. See attached photos of poorly compacted cement bound material
| 05SY - Systemwide | Cxxx-NCR-000104 | NCR | SSE Substation retaining wall - Waterproof coating level |  | Contr | __ |  |  | 2019-07-31 | 2019-05-22 07:57 | -70 | 2019-03-29 14:30 | Civil - Civil Engineering General | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Supervision - Other | Completed |  | The level of the waterproof coating applied to the SSE retaining wall is too high and is now visible above ground level.
| 05SY - Systemwide | Cxxx-NCR-000105 | NCR | Contractor has recorded changes to the F1 design using FCDs without PM's acceptance |  | Crossrail | XRL |  |  | 2019-07-31 | 2019-06-04 13:37 | -57 | 2019-04-01 13:32 | Electrical - Cable Management | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The Contractor has used FCDs to record changes made to the F1 design for the installation of CMS in the Accommodation Building. The Contractor raised a Contractors Communication (CCM) Cxxx-CCM-01161, to explain inconsistencies between the gated F1 design and __'s F2 design and seeking acceptance to complete FCD's identifying the changes from F1 to F2 and issue these to the Employer as an FCD per package. The PM replied to the CCM by way of Project Managers Communication (PMC) Cxxx-PMC-00907 stating; “the Project Manager has not accepted a change to the Works Information requirements in respect of the M&E installation, the Contractor is proceeding with works at their own risk.”
| 05SY - Systemwide | Cxxx-NCR-000106 | NCR | Installation of Fire Detection and Alarm System with Code 3 ITP |  | Contr | __ |  |  | 2019-07-31 | 2019-05-29 14:31 | -63 | 2019-04-16 10:56 | Fire - Detection | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | Installation of Fire Detection and Alarm System commenced with Code 3 ITP Cxxx-__-E3-ITP-CR526-50001
| 05SY - Systemwide | Cxxx-NCR-000107 | NCR | Unauthorised modification of 2 Compartment Trunking to one Compartment - Underfloor CMS - 1st Floor - Accommodation Building |  | Contr | __ |  |  | 2019-07-31 | 2019-06-14 08:39 | -47 | 2019-04-25 15:16 | Electrical - Cable Management | 6000 |  | Material | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During an inspection of the underfloor CMS of the 1st Floor Accommodation Building, it was observed that there has been an unauthorised modification of 2 Compartment Trunking to one Compartment
| 05SY - Systemwide | Cxxx-NCR-000108 | NCR | High utility chambers compared to finished paving level in the Staff Car Park |  | Contr | COS |  |  | 2019-07-31 | 2019-06-05 13:23 | -56 | 2019-05-10 10:55 | Architectural - Urban Realm | 1000 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | LV17 is currently poured 70mm too high in the staff car park (see attached sketch of the levels). Design Cover level:103.790 Current cover level:103.836 Permeable paving level:103.776 Cover + bedding thickness:120mm
| 05SY - Systemwide | Cxxx-NCR-000109 | NCR | Omission of Power Factor Correction |  | Contr | __ |  |  | 2019-10-31 | 2019-11-13 21:02 | 13 | 2019-07-30 15:10 | Electrical - Electrical Engineering General | 1000 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Power factor correction is specified as a requirement in MEP specification Cxxx-__-M-RSP-CR526-50001, clauses 3.2.1, 3.2.4, 3.2.6, 3.3, 3.3.4, 3.3.6 and 3.4.5. Electrical schematics Cxxx-__-E-DWG-CR526-50013 and Cxxx-__-E-DWG-CR526-50026 show power factor correction for each building. Power factor correction equipment has not been included in the equipment schedules, is not integral in the LV panels and has not been shown in room layouts for either building. The specification states that power factor should be corrected to 0.95 or above. It is shown as 0.924 on the load schedule for the Accommodation Building and 0.936 for the Maintenance Building within doc Cxxx-__-E-XCL-CR526-50001 Rev 9
| 05SY - Systemwide | Cxxx-NCR-000110 | NCR | Laydown Slabs- Failed 28-day cube strength |  | Contr | __ |  |  | 2019-07-31 | 2019-05-28 16:05 | -64 | 2019-05-20 16:41 | Civil - Civil Engineering General | 2000 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Inspector not familiar with inspection methods | Completed |  | Please see attached cube results which failed the required strength (40N/mm2) on laydown slab D: ref 25388762 and 25388763 28 day result made on 14/02/19; ref 25398284 and 25398285 28 day result made on 19/03/19; ref 25398288 and 25398289 28 day result made on 21/03/19
| 05SY - Systemwide | Cxxx-NCR-000111 | NCR | MEP- Lack of Coordination F2 Design for PA Speaker Locations- Accommodation Building Drying Room A1.13 |  | Contr | __ |  |  | 2019-07-31 | 2019-07-22 10:48 | -9 | 2019-05-28 15:57 | Communications and Control Systems - Public Address Systems | 1000 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | There is a clash between Supply Ductwork Access Panels and P.A. speakers in A1.13 Drying room, on the Ground Floor of the Accommodation Building.
| 05SY - Systemwide | Cxxx-NCR-000112 | NCR | MEP- Light Fittings Incompatible with Ceiling Type |  | Contr | __ |  |  | 2019-08-31 | 2019-06-18 12:53 | -74 | 2019-05-30 08:48 | Electrical - Lighting | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | Thorn Omega LED 3300-840 HFIX Q597 procured to be installed in the Male Change Room A1.19 are not compatible with __150 ceiling type.
| 05SY - Systemwide | Cxxx-NCR-000113 | NCR | MEP- Installing Drainage Channels Without Approved MCR |  | Contr | __ |  |  | 2019-09-30 | 2019-07-24 08:34 | -68 | 2019-07-08 11:00 | Mechanical - Public Health Engineering | 0 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | Contractor on site installed Drainage channels without approved MCR.
| 05SY - Systemwide | Cxxx-NCR-000114 | NCR | Incorrect line marking in the Staff Car Park |  | Contr | COS |  |  | 2019-11-30 | 2019-11-12 14:28 | -18 | 2019-05-30 12:50 | Architectural - Urban Realm | 6000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | The line marking has been installed incorrectly in the following areas (see attached photo) including bays an arrows. The line marking material used was one class lower in respect to the retroflectivity than defined in the Works Information (as agreed between the Contractor and Clients Engineering Manager) prior to works commencing. The paving blocks underneath the incorrect arrow will be replaced and the line marking will be redone in this area. The noncompliant material was used in the Staff Car Park originally (See attached 'MCR Thermoplastic Road Marking RevD.docx').
| 05SY - Systemwide | Cxxx-NCR-000115 | NCR | MEP- Installation of Access Control Break Glass Without Approved MCR |  | Contr | __ |  |  | 2019-08-31 | 2019-08-19 15:25 | -12 | 2019-06-06 09:13 | Communications and Control Systems | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Installation of access control break glass boxes has commenced without an approved MCR.
| 05SY - Systemwide | Cxxx-NCR-000117 | NCR | Emergency lighting is not compliant with BS 5266 - Emergency Lighting |  | Contr | __ |  |  | 2019-10-31 | 2019-09-17 22:26 | -44 | 2019-06-07 15:03 | Electrical - Lighting | 15000 |  | Design | Repair | 2 (6-60k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The Emergency Lighting circuits do not provide circuit integrity required by BS5266. 4 areas of non-conformance have been identified: 1. Emergency cabling & associated products installation to the following accommodation building areas (typically within Plant Rooms, Stores and open Plan office Areas) -Ground floor areas A1.27, A1.26, A1.25, A1.24, A1.23, A1.03 & A1.34 -First floor areas A2.10, A2.18 & A2.19 2. Emergency cabling & associated products installation to the first floor Low Bay lighting Room A2.08 and the Atrium (Task Hub) 3. Emergency cabling to the following accommodation building areas (typically within CMS risers, Roof and Stairs Well areas) 4. ELCM-Thorn DUA (Typically installed within ceiling voids Areas) -Ground floor areas A1.02, A1.04, A1.07 to A1.10, A1.12, A1.13, A1.19 and A1.22 -First floor areas A2.01 to A2.04, A2.07, A2.09, A2.14 to A2.20
| 05SY - Systemwide | Cxxx-NCR-000118 | NCR | MEP- Non-Conformance to 25% Spare Cable Capacity of Underfloor Comms Basket |  | Contr | __ |  |  | 2019-08-31 | 2019-06-14 13:45 | -78 | 2019-06-11 09:56 | Electrical - Cable Management | 0 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Some sections of Comms basket on the First Floor of the Accommodation Building, predominantly in Open Office A2.10 does not comply to MEP Specification.
| 05SY - Systemwide | Cxxx-NCR-000120 | NCR | High fence within the northen section of Accomodation Building |  | Contr | __ |  |  | 2019-09-30 | 2019-09-23 10:56 | -7 | 2019-06-12 14:50 | Architectural - Urban Realm | 6000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Personnel Error - Inattention to detail | Completed |  | Fencing has been installed to the incorrect level from setting out points 28 and 29 . Works need to be dismantled and reinstalled to the correct levels as per design drawing
| 05SY - Systemwide | Cxxx-NCR-000122 | NCR | Escape Stairs - Baseplate Items |  | Contr | __ |  |  | 2019-09-30 | 2019-07-17 09:32 | -75 | 2019-06-17 10:17 | Structural Engineering - Bolted Connections | 3000 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | __'s subcontractor did not implement the requirements of their ITP for both external staircases, as follows: 1. No provision of pull out test records for baseplates. 2. No provision of cube test results for the pre-mix grout installed to the staircases' baseplates.
| 05SY - Systemwide | Cxxx-NCR-000124 | NCR | Drainage gully installed to the wrong position |  | Contr | __ |  |  | 2019-09-30 | 2019-09-12 11:39 | -18 | 2019-07-02 10:22 | Civil - Drainage | 1000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Gully27 (G27) was installed to the incorrect setting out position ,which clashes with position of the kerb line. Incorrectly installed gully is to be broken out and installed as per design position as per drawing Cxxx-OVE-D-DDJ-CR148_SD013_Z-37902 REV 6
| 05SY - Systemwide | Cxxx-NCR-000125 | NCR | Extra Holes Drilled into Track Slab West |  | Contr | __ |  |  | 2019-09-08 | 2019-09-13 20:20 | 5 | 2019-07-10 12:31 | Civil - Track | 1000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | Holes have been drilled into the Track Slab West and surface scabbled in preparation for the installation of the Rail Baseplates. This has been carried out on the whole length of the slab from the Maintenance Building up to the West end of the slab (as per attached picture). The track installation is actually stopping 3 baseplates location short of the end of the slab (as per attached mark-up drawing).
| 05SY - Systemwide | Cxxx-NCR-000126 | NCR | Inadequate formation of cable bend |  | Contr | __ |  |  | 2019-10-31 | 2019-08-07 10:25 | -85 | 2019-07-04 13:34 | Electrical - LV Equipment | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The termination of power supply cables (95mm, 4C SWA) from SB-M-LV-01 to DB-M-P-01 to the Maintenance Building have been formed in such a manner where the cable insulation is resting on the thread of the SWA gland. Due to the space constraints within the trunking, this pressure will have a detrimental effect on the lifespan of the cable. See attached photos.
| 05SY - Systemwide | Cxxx-NCR-000127 | NCR | Incorrect curing of road slab |  | Contr | COS |  |  | 2019-10-31 | 2019-09-28 09:48 | -33 | 2019-07-05 09:15 | Civil - Concrete Pavement | 6000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A section of the reinforced concrete road slab on the Access Road North (PV1b) was not cured in line with the requirements in the ITP as curing agent was not applied and the slab was not protected.
| 05SY - Systemwide | Cxxx-NCR-000128 | NCR | FW19A location |  | Contr | COS |  |  | 2019-09-10 | 2019-09-11 12:47 | 1 | 2019-07-22 16:15 | Civil - Drainage | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The position of FW19A was moved but not communicated to CRL through a PTR. This was moved to accommodate the oil interceptor pipes.
| 05SY - Systemwide | Cxxx-NCR-000130 | NCR | Lighting Columns Acces Issue 1 |  | Contr | __ |  |  | 2019-01-31 | 2019-12-09 19:49 | 312 | 2019-07-19 12:51 | Electrical - General | 6000 |  | Design | Repair | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Maintainability issues identified with lighting column SOP75: Given the orientation of the lighting column, the counterbalance unit (jack) cannot access the column to lower it for maintenance. This is due to insufficient clearance between the column and fence.
| 05SY - Systemwide | Cxxx-NCR-000131 | NCR | Lighting columns Access Issues (2) |  | Contr | __ |  |  | 2019-11-30 | 2019-11-12 14:10 | -18 | 2019-07-19 14:17 | Electrical - General | 6000 |  | Design | Repair | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Maintainability issues identified for 27 no. lighting columns: Counterbalance unit (jack) cannot access the columns due to clash with permanent works vertically and horizontally, as per attached mark-up and pictures. - Clash with Cxxx bollard design - Clash with paving - Clash with fence line/soft landscaping when lowered
| 05SY - Systemwide | Cxxx-NCR-000132 | NCR | Cracking of laydown slab B5 over movement joint |  | Contr | __ |  |  | 2019-10-31 | 2019-10-25 15:26 | -6 | 2019-07-19 16:19 | Civil - Structural Engineering | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | It has been discovered that a section of laydown slab over by area B5 has accumulated cracks over by the contraction joint . The design illustrates that there is a 250mm spacing between the reinforcement and the contraction joint . The attached photos illustrate that the cracks are no longer than 100mm which is up to reinforcement .
| 05SY - Systemwide | Cxxx-NCR-000133 | NCR | Incorrect installation of levels for Accommodation External Ramp |  | Contr | __ |  |  | 2019-10-31 | 2019-09-20 11:18 | -41 | 2019-07-22 16:41 | Civil - Landscaping | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Refer to drawing Footpath Cxxx-OVE-D-DDD-CR148_SD013_1-37551 REv2 ; The FFL for the ramp slope is installed to the incorrect levels-See as built attachment
| 05SY - Systemwide | Cxxx-NCR-000134 | NCR | Damage to Cold Water Tank in the Mechanical Plant room A1.27 - Accommodation Building |  | Contr | __ |  |  | 2019-11-29 | 2019-09-29 09:01 | -61 | 2019-08-09 15:51 | Mechanical - Hot & Cold Water Supplies | 0 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Damage to Cold Water Tank in the Mechanical Plant room A1.27 - Accommodation Building resulting to leakage
| 05SY - Systemwide | Cxxx-NCR-000135 | NCR | Energisation of LTHW Pumps without a signed IRN |  | Contr | __ |  |  | 2019-10-31 | 2019-09-12 11:09 | -49 | 2019-08-13 14:20 | Mechanical - Mechanical Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | The LTHW Pumps were energised prior to signing of IRN
| 05SY - Systemwide | Cxxx-NCR-000136 | NCR | Lipping in drainage pipes |  | Contr | COS |  |  | 2019-12-31 | 2019-12-18 14:52 | -13 | 2019-08-27 09:26 | Civil - Drainage | 10000 |  | System Defect | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | There are lippings over 4mm (as per the manufacturer's guidance) have been identified in the drainage pipes when carrying out the CCTV survey of the drainage runs. Attached is the summary spreadsheet "CCTV Lipping report" and marked up drawings.
| 05SY - Systemwide | Cxxx-NCR-000137 | NCR | Failed air test to Maintenance Building |  | Contr | ARP |  |  | 2020-08-31 | 2020-08-21 08:06 | -10 | 2019-08-23 09:18 | Environmental - Environmental General | 6000 |  | Design | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | In accordance with Cxxx-OVE-S-XST-CR148-50001 and part L of the 2013 Building Regulations, and Cxxx-OVE-MRSP-CR148-50001 Rev 4.0, clause 2.3.2.3, __ have now conducted an air test to the Maintenance building. As noted within Cxxx-RFI-000465, Cxxx-CCM-00966, Cxxx-CCM-00912, Cxxx-EWN-424 and Cxxx-EWN-00415 we can confirm that the air test has failed. Furthermore, we note that we were unable to reach the pressure required to even commence the test. This will prevent us from lowering the requirement to 10m3/hr.m2. Further to the previous communications regarding this issue, __'s specialist subcontractor attended site on 30/7/19, in advance of the test, to assess the works. We were advised on the day, and by follow-up email, that the Maintenance Building should not need to be tested and was highly likely to fail in the event of the test being undertaken. See attached. __ note that best reasonable endeavours were taken to test the building. This included: - Sealing all openings and service penetrations - Sealing all external doors - Sealing below roller shutter doors - Completing an inspection prior to works commencing - Utilising a full exclusion zone during testing - Conducting testing for different zones
| 05SY - Systemwide | Cxxx-NCR-000138 | NCR | High fence return to the North of the Accommodation Building |  | Contr | __ |  |  | 2020-03-31 | 2020-02-04 13:45 | -56 | 2019-08-29 07:47 | Architectural - Urban Realm | 6000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 5 Number posts which return and close off the north of the accommodation building were installed to the wrong foundation depth . This has created a 150mm gap from the finished ground level to the bottom of the fence line . The required gap distance is supposed to be maximum 25mm as per manufactures instruction. Additional 2 number panels that were installed were supposed to be insulated panels to GRP dug in post rather than steel dug in post as per attached NCR sketch
| 05SY - Systemwide | Cxxx-NCR-000139 | NCR | Accomodation Building - Plasterboard/Partitioning Alignment |  | Contr | __ |  |  | 2019-11-30 | 2019-12-02 10:22 | 2 | 2019-09-06 14:15 | Architectural - Partitions | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The partitions to the south east and south west of the ground floor male WC are out of alignment by approximately 12mm, which is greater than the allowable tolerance (+ - 5mm). See drawing Cxxx-__-A-DDA-CR148_SD013_1-51100 attached which shows exact location of defect.
| 05SY - Systemwide | Cxxx-NCR-000140 | NCR | MEP- 25% Spare Capacity Distribution Board DB-M-P-01 |  | Contr | __ |  |  | 2019-11-30 | 2019-09-19 16:21 | -72 | 2019-09-17 14:15 | Electrical - Power Distribution | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | Distribution board DB-M-P-01 in the Maintenance Building was installed without the required 25% spare ways.
| 05SY - Systemwide | Cxxx-NCR-000141 | NCR | MEP- Omission of BMS and DALI LAN from Design |  | Contr | __ |  |  | 2019-11-30 | 2019-10-09 12:16 | -52 | 2019-09-17 15:55 | Communications and Control Systems | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | BMS and DALI LAN was installed on site without approved FCD or gated design.
| 05SY - Systemwide | Cxxx-NCR-000142 | NCR | Isolation joints in the ACO surround |  | Contr | COS |  |  | 2019-12-24 | 2019-11-11 18:50 | -43 | 2019-10-01 10:05 | Civil - Drainage | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Isolation joints have not been installed in the ACO channel surround in line with the slab isolation joints which is against the manufactures guidance.
| 05SY - Systemwide | Cxxx-NCR-000143 | NCR | Kerbs in ramp damaged outside of Accomodation Building in the Access Road |  | Contr | COS |  |  | 2019-11-30 | 2019-12-03 15:40 | 3 | 2019-09-18 13:27 | Architectural - Urban Realm | 2000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | Kerbs have been damaged due to tarmacking activities (see attached photo and marked up drawing)
| 05SY - Systemwide | Cxxx-NCR-000144 | NCR | Undercover stores Walkway - incorrect width (double kerb detail) |  | Contr | COS |  |  | 2020-03-31 | 2020-01-22 14:22 | -69 | 2019-09-18 16:46 | Architectural - Urban Realm | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The walkway has been installed to a 2m width for the whole length of the undercover stores walkway, however this should have reduced to 1.85m as per drawing Cxxx-OVE-C-DDA-CR148_SD013_1-37144.
| 05SY - Systemwide | Cxxx-NCR-000145 | NCR | Flaking Away of Slip Resistant Floor Paint Over Delamination Repairs in Maintenance Building |  | Contr | __ |  |  | 2020-06-30 | 2020-10-02 15:39 | 94 | 2019-10-01 20:46 | Architectural - Flooring | 20000 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Flaking away of floor paint in the Maintenance Building has appeared in areas around the Maintenance Area. See attached survey and photos of these currently observed in the south slab of maintenance shed area
| 05SY - Systemwide | Cxxx-NCR-000146 | NCR | Undercover Store - UCS Rainwater Downpipe |  | Contr | __ |  |  | 2020-01-31 | 2019-12-16 13:41 | -46 | 2019-09-23 10:07 | Mechanical - Piping | 3000 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Currently the rainwater down pipes in the undercover stores, require testing and inspection using ITP Cxxx-__-M-ITP-CR525-50020, this ITP is in the main being applied to rainwater pipes in the ac bldg. (plastic and fused together) for air tightness. The u/c stores pipe is not of the same material as the remainder of pipes which the ITP refers to in the accommodation bldg - these are of metal connection/fitting-and will not pass for air tightness.
| 05SY - Systemwide | Cxxx-NCR-000147 | NCR | Accommodation & Maintenance Building Kitchen Design not compliant with the DDA regulations |  | Contr | __ |  |  | 2020-08-23 | 2020-09-23 13:31 | 31 | 2019-09-24 10:56 | Architectural - General | 25000 |  | Design | Repair | 2 (6-60k) | Complete | Design Problem - Not Defined | Completed |  | Accommodation Building: Worktop height needs to be decrease to be fully compliant with the ADD regulations. The zip tap need to be accessible at 850mm and have knee access. Maintenance Building: Kitchen units are not compliant with DDA requirement.
| 05SY - Systemwide | Cxxx-NCR-000148 | NCR | Failed cube results in Laydown Slab B |  | Contr | COS |  |  | 2019-11-30 | 2019-11-12 14:18 | -18 | 2019-09-25 09:28 | Architectural - Urban Realm | 3000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Currently __ have had 2no. 28 day cube results fail for Pour 9 and 11. The 56 day cube results for pour 11 has also failed. __ have attached the cube register (Laydown Area B Concrete Test Cube Report Register 25.09.19.xlsx) and associated test cube reports __ have provided their sets of cubes for the mix "257WP436pdf" & "257WP437.pdf" which show the mix passing. The contractor attaches the core results
| 05SY - Systemwide | Cxxx-NCR-000149 | NCR | Failed 28 day cube results in utilty RC chambers and lighting column bases |  | Contr | COS |  |  | 2019-12-31 | 2019-11-12 18:12 | -49 | 2019-10-10 15:18 | Civil - Utilities Engineering | 1000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The 28 day cubes have failed however all of the 56 days have passed (see attached register for a full list of areas).
| 05SY - Systemwide | Cxxx-NCR-000151 | NCR | As built for trapped gullies PF3 and PF4 in the undercover stores |  | Contr | COS |  |  | 2020-05-31 | 2020-01-30 14:23 | -122 | 2019-10-10 08:33 | Civil - Drainage | 0 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | This NCR is required to close out Cxxx-RFI-000651. The works were not constructed as per the design intent and amended on site prior to approval of an FCD.
| 05SY - Systemwide | Cxxx-NCR-000152 | NCR | Patches in Blacktop Around the Accommodation Building |  | Contr | __ |  |  | 2021-03-31 | 2021-01-20 13:00 | -70 | 2019-12-13 17:47 | Civil - Civil Engineering General | 2000 |  | Material | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Patches have been identified in blacktop around the Accommodation Building along the access road and footpath.
| 05SY - Systemwide | Cxxx-NCR-000154 | NCR | Longitudinal Crack in Laydown Slab D |  | Contr | __ |  |  | 2020-02-29 | 2020-02-10 18:01 | -19 | 2019-12-13 12:18 | Civil - Civil Engineering General | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Supervision - Other | Completed |  | A longitudinal crack was found in Laydown slab D
| 05SY - Systemwide | Cxxx-NCR-000155 | NCR | Crack Beneath Existing Cabins to Eastern End of Laydown D |  | Contr | __ |  |  | 2020-11-30 | 2020-09-07 15:50 | -84 | 2019-12-13 17:43 | Civil - Civil Engineering General | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A crack has been identified running under cabins stored on Laydown Slab D
| 05SY - Systemwide | Cxxx-NCR-000156 | NCR | Cut Rebar in Refuse Area Slab for the Due to Install of Drainage Channel |  | Contr | __ |  |  | 2020-02-29 | 2020-01-22 15:26 | -38 | 2019-12-13 17:30 | Civil - Civil Engineering General | 3000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Supervision - Other | Completed |  | Reinforcement was cut during the install of the Drainage Channel in the Refuse Store (Undercover Stores)
| 05SY - Systemwide | Cxxx-NCR-000157 | NCR | Ponding in Access Road Near Gully G45 |  | Contr | __ |  |  | 2020-08-24 | 2020-06-12 09:13 | -73 | 2019-12-13 17:39 | Civil - Civil Engineering General | 6000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Ponding has been identified near the main access gate to Cxxx (currently Gate 4) near gully G45.
| 05SY - Systemwide | Cxxx-NCR-000159 | NCR | Power Factor Correction Commissioning without a code 1 Test Procedure |  | Contr | __ |  |  | 2020-03-31 | 2020-02-11 16:03 | -49 | 2019-12-03 16:31 | Electrical - General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Lack of procedure | Completed |  | The Power Factor Correction devices in both Accommodation and Maintenance Buildings have been commissioned by __ following the attached Procedure (Crossrail Plumstead Method Statement LV PFC 25-11-19.doc) which has not been approved by __/Crossrail.
| 05SY - Systemwide | Cxxx-NCR-000160 | NCR | Civils- Out Of Tolerance Bin Store Slab |  | Contr | __ |  |  | 2020-09-30 | 2020-08-19 09:18 | -42 | 2019-12-13 16:03 | Civil - Civil Engineering General | 6000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Bin store slab is out of tolerance in areas which is causing excessive ponding to occur.
| 05SY - Systemwide | Cxxx-NCR-000161 | NCR | MEP- Incorrect Installation of Valves in LTHW System |  | Contr | __ |  |  | 2020-05-31 | 2020-02-10 17:58 | -111 | 2019-12-09 16:59 | Mechanical - Piping | 6000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | LTHW system at the top of the Mechanical Riser causing a bypass loop in the system to the First Floor of the Accommodation Building
| 05SY - Systemwide | Cxxx-NCR-000162 | NCR | Civil - SR3 fence at east side of site sliding gate |  | Contr | __ |  |  | 2020-04-30 | 2020-03-05 10:12 | -56 | 2019-12-11 13:28 | Civil - Civil Engineering General | 6000 |  | Incorrect Installation | Use As-Is | 3 (3-6k) | Complete | Supervision - Other | Completed |  | During Sliding Gate installation by Cxxxa Contractor, it was identified that the SR3 fence installed by Cxxx at the north of the sliding gate is out of it's design position by approx. 100mm southwards. This makes the sliding gate installation in current design location impossible due to the clash between the two structures.
| 05SY - Systemwide | Cxxx-NCR-000164 | NCR | Aesthetc Damage to ACO Channels- Maintenance building North Road |  | Contr | __ |  |  | 2020-06-30 | 2020-04-14 17:23 | -77 | 2020-01-23 09:35 | Civil - Civil Engineering General | 6000 |  | Damaged | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Aesthetic damage has been caused to the ACO channels along the road North of the Maintenance Building due to heavy plant movement when the tarmac was being laid.
| 05SY - Systemwide | Cxxx-NCR-000165 | NCR | MEP - Site water main - wrong level at the transition to Cxxx |  | Contr | __ |  |  | 2020-05-31 | 2020-03-12 11:39 | -80 | 2020-01-23 08:50 | Mechanical - Hot & Cold Water Supplies | 6000 |  | Incorrect Installation | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | At the location where the site water main has been transferred from Cxxx to Cxxx, it has been detected a variation on the pipe level. The alignment is correct but the level is 130mm lower that the stated by design. As discussed and agreed with CRL, Cxxx will accommodate the 130mm difference in level. This is to be done between the transition point and 18101-W-04 (look at "Figure 1" attached). More information attached as "Survey 11-10-2019 water pipe existing level.pdf ", "Cxxx-OVE-U-DDA-CR148_SD013_2-18101 C02 Mark-up.pdf ", and "Cxxx-OVE-U-DDJ-CR148_SD013_Z-00003 - schedule - Transition mark-up.pdf ". Please find also attached "TSP Response - Cxxx-NCR-000165 - MEP - Site water main - wrong level at the transition to Cxxx", where TSP confirm that the variation in levels doesn't impact the pressure levels in the water main.
| 05SY - Systemwide | Cxxx-NCR-000166 | NCR | ARC- Failed Slip Resistance Test- Accommodation Building Atrium Staircase Vinyl |  | Contr | __ |  |  | 2020-08-23 | 2020-07-09 15:32 | -45 | 2020-02-05 09:08 | Architectural - Flooring | 0 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Slip resistance test on the Accommodation Building Atrium Staircase vinyl did not meet requirements specified in the ITP under wet conditions.
| 05SY - Systemwide | Cxxx-NCR-000167 | NCR | Cladding Repairs - Commencing work without accepted MCRs |  | Contr | __ |  |  | 2020-08-31 | 2020-07-23 07:24 | -39 | 2020-02-27 17:14 | Architectural - Roofing & Exterior Treatment | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | On request, during the CRAF Site Tour, the Contractor was unable to provide MCRs for the cladding and louvre repairs as referenced in Cxxx-__-A-ITP-CR526-50018 item number 12.3 2-Pack Polyester Filler, Selemix Primer and Selemix Topcoat.
| 05SY - Systemwide | Cxxx-NCR-000169 | NCR | Surge Protection Installed without accepted MCR |  | Contr | __ |  |  | 2020-09-30 | 2020-06-12 09:14 | -110 | 2020-04-03 11:37 | Electrical - General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | It has been identified on site that the Surge Protection installed is not matching the approved MCR (CRL-MCR-006050). The MCR is for a __ product. The one installed is Raycap. Extent of this issue to be assessed.
| 05SY - Systemwide | Cxxx-NCR-000173 | NCR | MEP- Gaps in Back-to-Back Conduit Boxes Used for Emergency Lighting Connector Blocks |  | Contr | __ |  |  | 2020-09-30 | 2020-08-27 12:30 | -34 | 2020-07-01 07:57 | Electrical - General | 6000 |  | Design | Repair | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Back-to-back conduit boxes have been installed to incorporate the porcelain connector blocks as part of the Emergency Lighting installation. These have gaps between the boxes that leave the connector blocks exposed.
| 05SY - Systemwide | Cxxx-NCR-000174 | NCR | MEP- Redundant FCU for EACS in Accommodation and Maintenance Building |  | Contr | __ |  |  | 2020-09-30 | 2020-09-14 15:13 | -16 | 2020-07-06 11:55 | Electrical - Power Distribution | 3000 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | FCU's that have been installed for EACS system are redundant.
| 05SY - Systemwide | Cxxx-NCR-000175 | NCR | Undercover stores Walkway - incorrect width (double kerb detail) |  | Contr | __ |  |  | 2020-09-29 | 2020-09-25 11:33 | -4 | 2020-07-01 20:39 | Architectural - Urban Realm | 6000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The walkway has been installed to a 2m width for the whole length of the undercover stores walkway, however this should have been reduced to 1.85m as per drawing Cxxx-OVE-C-DDA-CR148_SD013_1-37144.
| 05SY - Systemwide | Cxxx-NCR-000176 | NCR | Civil - Gap underneath SR3 fence exceeds 25mm Exmesh requirement to the South of Accommodation Building |  | Contr | __ |  |  | 2020-09-30 | 2020-08-28 13:29 | -33 | 2020-07-15 16:17 | Civil - Civil Engineering General | 3000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The gap underneath the SR3 fence bays between SOP 19-20 and SOP 23-24 exceeds the 25mm Exmesh requirement (see pictures in attachment). The gaps have been measured and are as follow: - SOP 19 to 20 = 95mm - SOP 23 to 24 = 50mm
| 05SY - Systemwide | Cxxx-NCR-000178 | NCR | Fencing - Lack of supporting calculations provided for angle plates of insulated panel between SOP 11 and 12 |  | Contr | __ |  |  | 2020-12-31 | 2020-11-30 12:48 | -31 | 2020-08-17 20:12 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | On insulated panel installed between SOP 11 and 12, since Cxxx-FCD-000210, __ never provided calculations to support the angle plates. However the baseplates have already been installed on site.
| 05SY - Systemwide | Cxxx-NCR-000179 | NCR | Fencing - SR3 Fence twisted panels |  | Contr | __ |  |  | 2020-12-31 | 2020-11-03 15:36 | -58 | 2020-08-20 12:49 | Civil - Civil Engineering General | 6000 |  | Damaged | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | There are 3 SR3 fence twisted panels which have been raised as snags following a joint walkout with CRL and __ (see attached pictures 'Twisted panels.pdf' and 'Twisted panels - 1.pdf').
| 05SY - Systemwide | Cxxx-NCR-000180 | NCR | Asset information- Incorrect naming conventions used |  | Contr | __ |  |  | 2020-01-31 | 2021-01-12 14:02 | 347 | 2020-09-01 13:52 | Information Management - Asset Information | 3000 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Supervision - Other | Completed |  | During a quality report review it has been identified that the contractor has used an incorrect naming convention whilst labeling. Instead of using the name convention of "asset xxx" shown in CRL1-XRL-Z3-ADDSD-CR001-50413- Asset naming and labeling convention; they have used "asset xx" instead. It was also identified during VAP 3 that the word "compressed" has been printed on the labels in front of assets using the L Classes L7176, L7177 and L7178 which also does not follow naming conventions specified in CRL1-XRL-Z3-ADDSD-CR001-50413. There are a total of 159 tags that have been identified in the quality report that have been identified as not following this naming convention. A full list has been added as an attachment plus 4 examples of the instances.
| 05SY - Systemwide | Cxxx-NCR-000181 | NCR | Asset Labelling VAP Failures |  | Contr | __ |  |  | 2021-09-30 | 2021-04-21 13:38 | -162 | 2020-09-30 09:57 | Information Management - Asset Information | 6000 |  | Documentation and Records | Rework | 3 (3-6k) | Complete | Management Problem - Other | Completed |  | This NCR outlines the non-conformances with Asset Labelling/Information found during the VAPs conducted by CRL at Cxxx Plumstead Depot and Sidings. VAP 1: 22/01/2020 VAP 2: 05/03/2020 VAP 3: 11/08/2020 VAP 4: 16/09/2020 VAP 5: 03/11/2020 VAP 6: 03/12/2020 VAP 7: 05/01/2021 The VAPs highlighted various issues with Asset labelling/information mainly along the themes of: 1. Labels virtually allocated to incorrect space 2. Incorrect Equipment numbers allocated to assets 3. Incorrect system function codes on labels 4. Incorrect/inadequate virtual descriptions on tags 5. Incorrect asset information on the labels 6. Incorrect allocation of asset to PFU/FU 7. In correct asset naming (assets not named according to CRL requirements 8. Poor label positioning
| 05SY - Systemwide | Cxxx-NCR-000182 | NCR | MEP - Fire Alarm Ceiling Void Detectors Identification |  | Contr | __ |  |  | 2021-03-31 | 2021-01-14 11:35 | -76 | 2020-10-12 10:15 | Fire - Fire Systems & General | 500 |  | Incomplete Works | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | This NCR relates to query raised by Crossrail re remote indicators required for ceiling void detectors installed in Accommodation and Maintenance building at Plumstead Sidings. According to the F1 and F2 design (approved by Crossrail), there is no requirement of C/V remote indicators, and BS 5839 section 13.1 commentary states the below: "If a detector is concealed in a relatively inaccessible area (such as a floor or ceiling void), it is normally desirable to provide a remote indication of its operation. In an addressable system, the provision of an individual remote indicator might not be necessary provided that the location of each fire detector is clearly indicated at the control and indicating equipment". Whilst remote indicators are desirable and provision of the remote indicators might not be necessary, __ acknowledges the importance of identification of C/V detectors and therefore proposes the following: Installation of red identification discs with the following information 1. Type of Device (e.g. SD - Smoke Detector) 2. Device ID (e.g 001)
| 05SY - Systemwide | Cxxx-NCR-000183 | NCR | CIV- Redundant Drainage Connection SW-MH-32 to SW-MH-31 |  | Contr | __ |  |  | 2021-02-28 | 2021-01-07 12:12 | -52 | 2020-11-18 11:15 | Civil - Drainage | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | __ unable to achieve successful air test on drainage run between SW-MH 32 and SW-MH 31.
| 05SY - Systemwide | Cxxx-NCR-000185 | NCR | MEP- Accommodation Building Fire Alarm Pitched Roof Detection |  | Contr | __ |  |  | 2021-02-28 | 2021-01-12 14:41 | -47 | 2020-11-17 11:42 | Fire - Detection | 6000 |  | Design | Repair | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | Cxxx Fire Alarm installation is not compliant with BS 5839.
| 05SY - Systemwide | Cxxx-NCR-000186 | NCR | Non compliant Walking Route Marking |  | Contr | __ |  |  | 2021-03-31 | 2021-01-26 13:59 | -64 | 2021-01-12 17:30 | Civil - Civil Engineering General | 3000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The Contractor is required to provide Designate Walking Route Markings across site. The details of which can be found within Cxxx-OVE-C-DDD-CR148_SD013_1-37571. The Contractor instead installed non-compliant markings. See details in attached photographs.
| 05SY - Systemwide | Cxxx-NCR-000187 | NCR | CIV- Sitewide Issues with Road __ |  | Contr | __ |  |  | 2021-05-31 | 2021-03-09 16:52 | -83 | 2021-01-25 09:30 | Civil - Roadworks Formation | 3000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | It has been noted that there has been some damage to the tarmac at various locations throughout the access road through the Maintenance Facility.
| 05SY - Systemwide | Cxxx-NCR-000188 | NCR | CIV- Cracks in M&P Plant Room Screed (A1.27) |  | Contr | __ |  |  | 2021-05-31 | 2021-02-26 14:10 | -94 | 2021-01-25 17:51 | Civil - Civil Engineering General | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A number of cracks have been identified in screed within the M&P Plant room in the Accommodation Building (A1.27)
| 05SY - Systemwide | Cxxx-NCR-000189 | NCR | Under Cover Stores Steel Grating Missing Fixings and Brackets |  | Contr | __ |  |  | 2021-06-30 | 2021-07-28 10:11 | 28 | 2021-01-28 14:46 | Architectural - General | 500 |  | Incomplete Works | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | There is missing fixings and brackets from the steel grating surrounding the UCS and Refuse Area. __ proposes to rectify this issue by undertaking works to install the missing bracketry and fixings where required. See photos attached that show issues. Please confirm acceptance of proposal.
| 05SY - Systemwide | Cxxx-NCR-000190 | NCR | Missing Drainage Gullys in M1.09 and M1.15 |  | Contr | __ |  |  | 2021-06-30 | 2021-05-18 15:53 | -43 | 2021-03-24 09:48 | Civil - Civil Engineering General | 3000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In the Maintenance Building Rooms M1.15 and M1.09 there is supposed to be a drainage gullys to for condensate pipework drainage from the DX units in adjacent rooms. It has been noticed that the Contractor has not installed these during the Public Health installation.
| 05SY - Systemwide | Cxxx-NCR-000191 | NCR | Cxxx - Staff Car Park Remedial Works |  | Contr | __ |  |  | 2021-06-30 | 2021-05-18 21:37 | -43 | 2021-03-25 17:13 | Civil - Civil Engineering General | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the review of the CCTV Report for the NE Corner, drainage runs S26.000A and S26.000B had been identified to contain debris inside the filter pipes and it was requested the pipes were to be cleaned and capped off (See drawing Cxxx-OVE-D-DDA-CR148_SD013_1-37133). See attached snapshots from the CCTV Report.
| 05SY - Systemwide | Cxxx-NCR-000192 | NCR | Fire Hydrants- No Anti-Backflow Valve Installed |  | Contr | __ |  |  | 2021-11-30 | 2021-09-23 14:25 | -68 | 2021-04-08 09:21 | Civil - Sewage/Water services | 6000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The Contractor has failed to install anti backflow valves on the fire hydrants within Cxxx Site.
| 05SY - Systemwide | Cxxx-NCR-000193 | NCR | Asset Labelling - Valve DAAID labelling |  | Contr | __ |  |  | 2021-06-30 | 2021-04-30 12:25 | -61 | 2021-04-08 10:58 | Information Management - Asset Information | 3000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Information not detailed | Completed |  | Cxxx have existing asset labels installed that do not contain a Design Alternative Asset ID (DAAID), as such an ID was not present in the design documentation. Since installation, a request has been made to the Site engineering team that functional labels are required for assets identified as critical to maintenance. It is now understood that these functional ID numbers that feature upon the new functional dog tag labels installed on site, are to be used as the DAAID within the asset information. Cxxx Are raising this NCR to inform CRL that they will be updating the Asset Data to hold the new Functional IDs as DAAIDs against the relevant assets, however they do not intend to replace the affected asset labels on site. This is because the functional dog tag labels will display this DAAID and are also installed adjacent to the assets, meaning identification via both the Asset ID and/or the DAAID is possible. There is also an estimated time and cost impact that Cxxx would like to avoid in the interest of handing over the project; Relabelling of approx. 150 valves: - Duration : approx. 1.5days (most of valves are in ceiling void) + 1week for delivery of the labels on site (approx. 9.5 days total) - Manpower: 1 site engineer + 1 supervisor + 2operatives - Cost of the labels : approx. £120 (VAT included)
| 05SY - Systemwide | Cxxx-NCR-000194 | NCR | Asset Data Attributes |  | Contr | __ |  |  | 2021-07-31 | 2021-05-20 11:38 | -72 | 2021-05-12 07:16 | Information Management - Asset Information | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Cxxx are unable to determine the following attribute values for the Fan Coil Units installed on site. Cooling Return Air Humidity (Degrees Celsius) The wet bulb temperature of the return air for design maximum cooling load Cooling Return Air Temperature (Degrees Celsius) The dry bulb temperature of the return air for design maximum cooling load Cooling Supply Air Temperature (Degrees Celsius) The dry bulb temperature of the supply air for the design maximum cooling load External Static Pressure (Pa) The external operating air pressure of the unit Heating Return air temperature (Degrees Celsius) The dry bulb temperature of the return air for design maximum heating load Heating Supply air temperature (Degrees Celsius) The dry bulb temperature of the supply air for the design maximum heating load As these values are not readily available within the equipment datasheets (supporting documents attached), and could well refer to variable values, Cxxx will treat these attributes as not applicable within the ADCS templates. The affected tags are: Class Tag Name EQ number EQ Description Support file L75145 - Fan Coil Unit CR526-HVA-02612 FAN COIL UNIT 013 EQ00011346 Nortek Global HVAC (UK) Ltd - Electric Air Curtain - AB175A-2 AB_industrial_air_curtain_EN_2018-011 L75145 - Fan Coil Unit CR526-HVA-02613 FAN COIL UNIT 014 EQ00011346 Nortek Global HVAC (UK) Ltd - Electric Air Curtain - AB175A-2 AB_industrial_air_curtain_EN_2018-011 L75145 - Fan Coil Unit CR526-HVA-02498 FAN COIL UNIT 005 EQ00009844 Biddle Air Systems Ltd - Air Curtain (Invisidor) - CITY 200-E biddle-city-brochure-uk L75145 - Fan Coil Unit CR526-HVA-02499 FAN COIL UNIT 006 EQ00009844 Biddle Air Systems Ltd - Air Curtain (Invisidor) - CITY 200-E biddle-city-brochure-uk L75145 - Fan Coil Unit CR526-HVA-02069 FAN COIL UNIT 001 EQ00006898 __ Electric Europe BV - Air Conditioning, Power Inverter Heat Pump Wall Mounted System - PKA-M60KA __ Electric Europe BV L75145 - Fan Coil Unit CR526-HVA-02070 FAN COIL UNIT 002 EQ00006898 __ Electric Europe BV - Air Conditioning, Power Inverter Heat Pump Wall Mounted System - PKA-M60KA __ Electric Europe BV L75145 - Fan Coil Unit CR526-HVA-02071 FAN COIL UNIT 003 EQ00008940 __ Electric Europe BV - Heat Pump - PKA-M35HA __ Electric Europe BV L75145 - Fan Coil Unit CR526-HVA-02072 FAN COIL UNIT 004 EQ00008940 __ Electric Europe BV - Heat Pump - PKA-M35HA __ Electric Europe BV L75145 - Fan Coil Unit CR526-HVA-02500 FAN COIL UNIT 007 EQ00008940 __ Electric Europe BV - Heat Pump - PKA-M35HA __ Electric Europe BV L75145 - Fan Coil Unit CR526-HVA-02501 FAN COIL UNIT 008 EQ00008940 __ Electric Europe BV - Heat Pump - PKA-M35HA __ Electric Europe BV L75145 - Fan Coil Unit CR526-HVA-02502 FAN COIL UNIT 009 EQ00010331 __ Electric Europe BV - Air Conditioning, Power Inverter Heat Pump Wall Mounted System - PKA-M100KA __ Electric Europe BV L75145 - Fan Coil Unit CR526-HVA-02503 FAN COIL UNIT 010 EQ00010331 __ Electric Europe BV - Air Conditioning, Power Inverter Heat Pump Wall Mounted System - PKA-M100KA __ Electric Europe BV L75145 - Fan Coil Unit CR526-HVA-02504 FAN COIL UNIT 011 EQ00008940 __ Electric Europe BV - Heat Pump - PKA-M35HA __ Electric Europe BV L75145 - Fan Coil Unit CR526-HVA-02505 FAN COIL UNIT 012 EQ00008940 __ Electric Europe BV - Heat Pump - PKA-M35HA __ Electric Europe BV
| 05SY - Systemwide | Cxxx-NCR-000195 | NCR | Maintenance Building Switchboard Compartment 2 Door Colour |  | Contr | __ |  |  | 2021-07-31 | 2021-06-03 10:00 | -58 | 2021-05-17 08:59 | Electrical - Switchgear | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Compartment 2 door on maintenance building switchboard is red in contradiction to design.
| 05SY - Systemwide | Cxxx-NCR-000196 | NCR | Comms: SCADA Interface with CCTV and PIDS/EACS |  | Contr | __ |  |  | 2022-04-18 | 2022-05-23 13:16 | 35 | 2021-07-20 09:03 | Communications and Control Systems - General | 500 |  | Incomplete Works | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The Contractor has failed to provide an interface between the Maintenance Facility EACS/PIDS system and the Systemwide SCADA system in accordance with the Works Information.
| 05SY - Systemwide | Cxxx-NCR-000197 | NCR | MEP- Correctons to Functional Labelling |  | Contr | __ |  |  | 2021-11-30 | 2021-10-20 09:59 | -41 | 2021-09-28 07:50 | Mechanical - Mechanical Engineering General | 3000 |  | Incomplete Works | Repair | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | A small number of changes need to be made to the MEP functional labelling on Cxxx site, where labels are either missing, or contain ambiguous information.
| 05SY - Systemwide | Cxxx-NCR-000198 | NCR | Road Safety Audit Non conformities - No tactile paving at dropped kerb crossing & Hazardous signpost in footway |  | Contr | __ |  |  | 2022-04-28 | 2022-05-10 13:03 | 12 | 2022-03-09 13:42 | Civil - Kerbs | 1000 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | __'s Issues are as follows: 1. There is no tactile paving across the flush kerbs on either side of the uncontrolled pedestrian crossing over the bell-mouth of the main site access. 2. the report stated "there is a signpost (site speed limit) in the middle of the footway on the east side of the junction bell-mouth which presents a hazard to pedestrians, especially those with sight impairment." this was found to be within the parameters of BS8300 and therefore compliant. It was found that the signs themselves were located within 450mm of the edge of the kerb which was non-compliant.
| 05SY - Systemwide | Cxxx-NCR-000001 | NCR | Civil - Drainage - TDE pipe has been delivered and installed out of tolerance |  | Contr | __ | PLU - Plumstead Stabling Facility |  | 2019-01-31 | 2019-02-28 15:52 | 28 | 2018-10-09 17:42 | Civil - Drainage | 6000 |  | Material | Repair | 3 (3-6k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | While inspecting SW TR 83, it was noticed that the TDE pipe has been delivered and installed out of tolerance. Currently the pipes are not straight and have a 90mm bend in the pipe (see attached photos).
| 05SY - Systemwide | Cxxx-NCR-000002 | NCR | Civil - Drainage - Damaged Impermeable Membrane |  | Contr | __ | PLU - Plumstead Stabling Facility |  | 2019-01-31 | 2019-03-05 11:51 | 33 | 2018-10-29 17:09 | Civil - Drainage | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Impermeable membrane on drainage run S22.011, between catchpits SW TR82 and SW TR 83, has been damaged and some holes are now present in a small area. See attached picture.
| 05SY - Systemwide | Cxxx-NCR-000003 | NCR | OHLE Pad Foundation works started without IFC drawings |  | Contr | __ | PLU - Plumstead Stabling Facility |  | 2019-02-01 15:13 | 2019-01-31 13:10 | -1 | 2018-11-13 14:16 | Over Head Line Electrification - Catenary Masts | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Work on the 9no. OHLE Pad Foundations: XRS-22-041, XRS-22-044, XRS-23-003, XRS-23-006, XRS-23-009, XRS-23-012, XRS-23-015, XRS-23-018 & XRS-23-021 has started without the design being IFC. The following drawings are at Pxx status but code 1: - Cxxx-__-R6-DDA-CR148_Z-00206 P06 - Cxxx-__-R6-DDD-CR148_Z-00930 P01 - Cxxx-__-R6-DDA-CR148_Z-00313 P01
| 05SY - Systemwide | Cxxx-NCR-000004 | NCR | By Exception Gate Risk Assessment for Train access platforms, reinforced concrete foundations and steel platforms |  | Contr | __ | PLU - Plumstead Stabling Facility |  | 2019-08-17 14:21 | 2019-05-30 13:02 | -79 | 2019-02-15 17:04 | Civil - Civil Engineering General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | In order to start work on site, "By Exception Gate Risk Assessment" for Train access platforms, reinforced concrete foundations and steel platforms has been requested.
| 05SY - Systemwide | Cxxx-NCR-000005 | NCR | Drainage run S16.013 - Failure of final air test |  | Contr | __ | PLU - Plumstead Stabling Facility |  | 2019-05-24 17:23 | 2019-04-04 15:52 | -50 | 2019-02-28 10:27 | Civil - Drainage | 6000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Final air test of run S16.013 has failed
| 05SY - Systemwide | Cxxx-NCR-000006 | NCR | Cxxx OHLE - Piling Works - Piles Installed Out of Tolerance |  | Contr | __ | PLU - Plumstead Stabling Facility |  | 2019-07-17 14:28 | 2019-04-23 16:20 | -85 | 2019-03-28 15:53 | Over Head Line Electrification - Over Head Line Electrification General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The following six steel bossed piles have been installed marginally outside of the 75mm tolerance on installation: XRS/22/023 out of tolerance in Z plane by 41.6mm (117mm from design position) XRS/22/029A out of tolerance in XY plane by 16.7mm (92mm from design position) XRS/22/036 out of tolerance in XY plane by 15.7mm (91mm from design position) XRS/22/038 out of tolerance in XY plane by 41.9mm and Z plane by 44.0mm (117mm and 119mm from design position respectively) XRS/22/042 out of tolerance in XY plane by 26.0mm (101mm from design position) XRS/23/020 out of tolerance in XY plane by 3.9mm (79mm from design position)
| 05SY - Systemwide | Cxxx-NCR-000007 | NCR | Track RRAP - Concrete cube sample production and storage |  | Contr | __ | PLU - Plumstead Stabling Facility |  | 2019-08-14 10:55 | 2019-05-16 15:29 | -90 | 2019-04-18 16:46 | Track - Track General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Supervision - Other | Completed |  | The first concrete pour for the Road Rail Access Point (RRAP) consisted of three batches of concrete on 04/04/2019. The concrete testing subcontractor did not bring the requested number of concrete moulds for the pour (4 cube samples per batch, 3 batches, total of 12 moulds required) - they brought 4 moulds. A compliant set of 4 concrete cube samples were taken for batch 1 (Ticket number 2200161270) by the UKAS accredited concrete technician from the testing subcontractor (compliant as per ITP). To prevent wasting the concrete, __ made 4 cube samples for both batch 2 and 3 (Ticket 2200161331 and 2200161420) on site using __ moulds by non-UKAS accredited personnel. The samples were not kept in controlled conditions prior to collection by the testing company 6 days later.
| 05SY - Systemwide | Cxxx-NCR-000008 | NCR | PD4,PD6 and PD8 Track Horizontal Alignment Deviation. |  | Contr | __ | PLU - Plumstead Stabling Facility |  | 2019-09-30 | 2019-10-01 12:46 | 1 | 2019-06-28 15:04 | Track - Turnouts | 6000 |  | Design | Use As-Is | 3 (3-6k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | __jv has set the track from PD2 to back of PD8 according to IFC Drawing “ Cxxx-__-R4-DDA-CR148_SD013_1-25100 C01 – Permanent Way Layout general arrangement” and the RIBA F Track Alignment developed by Cxxx, “Cxxx-OVE-R4-DDA-CR148_SD013_1-25100 C01 - Permanent Way Layout general arrangement”. PD4, PD6 and PD8 Turnouts TOE position have been set according to Cxxx Chainages, however it has been noticed during the tamping works, that there are some Horizontal deviations. Summary below: PD4 TOE set at CH 22815.223, rather than the right one 22814.692, inducting a displacement to the east of 533mm PD6 TOE set at CH 22861.903, rather than the right one 22861.508, inducting a displacement to the east of 395mm PD8 TOE set at CH 22905.843, rather than the right one 22905.304, inducting a displacement to the east of 543mm
| 05SY - Systemwide | Cxxx-NCR-000009 | NCR | Track - Damaged RH Switch Blades of PD2 & PD3 |  | Contr | __ | PLU - Plumstead Stabling Facility |  | 2019-11-30 | 2019-10-17 10:37 | -44 | 2019-06-20 17:29 | Track - Turnouts | 6000 |  | Damaged | Repair | 3 (3-6k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | The right hand Switch blades of left-hand Crossings PD2 and PD3 have been hit, causing damage to the top of the blade.
| 05SY - Systemwide | Cxxx-NCR-000010 | NCR | Track - Damaged/Chipped Bearers on Crossings |  | Contr | __ | PLU - Plumstead Stabling Facility |  | 2019-10-16 16:39 | 2019-10-26 11:13 | 10 | 2019-07-11 15:45 | Track - Turnouts | 3000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During the tamping of the Sidings, the tamping head has hit some bearers, causing chipping of the bearer surface (no reinforcement is exposed): - PD1 (Bearer no. 127 and 114) - PD2 (Bearer VL203 and VR204) - PD3 (Bearer no. 320) - PD4 (Bearer no. 429) - PD7 (Bearer no. 711 and 706) See 'Sketch of Damaged bearers locations' attached for further details.
| 05SY - Systemwide | Cxxx-NCR-000011 | NCR | OHLE/Civil - Insufficient Thread exposed above pad foundation to install top lock nut of Mast XRS22+001 |  | Contr | __ | PLU - Plumstead Stabling Facility |  | 2019-10-30 16:19 | 2019-08-23 11:19 | -68 | 2019-07-17 16:28 | Over Head Line Electrification - Catenary Masts | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | There is insufficient thread exposed above the top of concrete level to install all components for the XRS22+001 Mast to Pad Foundation connection (two nuts, one locking nut, two washers, two threads).
| 05SY - Systemwide | Cxxx-NCR-000012 | NCR | Track - Damaged PD8 Points due to run through |  | Contr | __ | PLU - Plumstead Stabling Facility |  | 2019-11-24 | 2019-12-09 11:43 | 15 | 2019-08-19 16:31 | Track - Turnouts | 6000 |  | Damaged | Repair | 3 (3-6k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | On 13th August 2019 at Plumstead Sidings, there was a machine run through of PD8 points. As a result, both RH and LH switch blades of PD8 and some of the POE components (2no. E6 Lock Arms , 1no. Tie bar, 2no. Green Rams , 1no. Adjustable Stretcher ) were damaged. Points Maintenance Inspection Report is attached with photos.
| 05SY - Systemwide | Cxxx-NCR-000013 | NCR | Track - Incorrect Sleeper Spacing in Pedestrian Crossing Locations |  | Contr | __ | PLU - Plumstead Stabling Facility |  | 2019-11-21 | 2019-12-09 11:39 | 18 | 2019-08-23 10:30 | Track - Rails and Sleepers | 25000 |  | Incorrect Installation | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The sleepers in the locations of the pedestrian crossings of the plain line on maintenance Sidings 1-8 were spaced at 760mm (+/- 15mm) instead of 600mm (+/- 15mm) which is required for the baseplate connection to the rubber pedestrian crossing panels.
| 05SY - Systemwide | Cxxx-NCR-000014 | NCR | OHLE - Damaged Aerial Earth Wire midspan between structures XRS/23/019 and XRS/23/024A |  | Contr | __ | PLU - Plumstead Stabling Facility |  | 2019-11-21 | 2019-10-03 11:21 | -49 | 2019-08-23 14:07 | Over Head Line Electrification - Over Head Line Electrification General | 6000 |  | Damaged | Repair | 3 (3-6k) | Complete | Subcontractor Problems - Interfacing problems | Completed |  | On the morning of 23rd August 2019, an excavator hit the Aerial Earth Wire (AEW), midspan between structures XRS/23/019 and XRS/23/024A, damaging the AEW. The AEW was made safe with a securing rig over the damaged/frayed section of wire by the OHLE team.
| 05SY - Systemwide | Cxxx-NCR-000015 | NCR | NR Separation Fence - Limited Clearance at SOP19 |  | Contr | __ | PLU - Plumstead Stabling Facility |  | 2019-12-31 | 2019-12-02 16:49 | -29 | 2019-09-17 16:30 | Civil - Civil Engineering General | 0 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Crossrail Head Shunt Separation Fence – Limited clearance at SOP 19 for Down North __ Line Place of Safety (1.774m instead of 2m minimum). The use of the PW_ NR Track design data instead of the As-built NR Track to do the design of the NR Fence UTX design led to a limited clearance between the Down North __ Line running edge and the SOP 19 fence post because the position of the DNKL is slightly different on the as built than the initial design.
| 05SY - Systemwide | Cxxx-NCR-000016 | NCR | Surface Luminaire Installation Works have commenced without a code 1 ITP |  | Contr | __ | PLU - Plumstead Stabling Facility |  | 2019-12-08 | 2019-11-04 16:17 | -34 | 2019-10-09 21:39 | Electrical - Lighting | 0 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Glanding, terminating of cables and installation of lights/bollards has commenced without an approved code 1 ITP on the Plumstead sidings.
| 05SY - Systemwide | Cxxx-NCR-000017 | NCR | Civils - concrete strength in Chain link fence foundation |  | Contr | __ | PLU - Plumstead Stabling Facility |  | 2019-12-31 | 2020-03-30 10:02 | 90 | 2019-10-14 15:22 | Civil - Civil Engineering General | 6000 |  | Material | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Chain link fence foundations - 28 days concrete strength has not reached specified 40MPa compressive strength with results at 28 days being: - 7.5 and 7.7 MPa from concrete cast on 16 Sept 2019 - 17.7 and 18.1MPa from concrete cast on 17 Sept 2019
| 05SY - Systemwide | Cxxx-NCR-000018 | NCR | Track/OHLE - Part Drilled Bond Holes on MS2, PD4 & PD7 Crossings |  | Contr | __ | PLU - Plumstead Stabling Facility |  | 2019-12-31 | 2019-12-28 13:18 | -3 | 2019-11-01 18:16 | Track - Rails and Sleepers | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Additional holes have been part-drilled in the rail and the spacing between these part-drilled holes and the bond holes in these locations do not satisfy the __ standards for spacing between bond holes. NR standards show minimum 75mm interval between bond holes, according to drawings RE/PW/596. The locations concerned are: - MS2 - the rail adjacent to the fishplates between the check rail of MS204-RAIL and joint MS206-JT (see crossing drawing Cxxx-__-R4-DWG-CR526-50010 for details). There is a spacing of 60mm and 50mm between holes. - PD4 - the rail in between the nose of the crossing and joint 410-JT (see crossing drawing Cxxx-__-R4-DWG-CR526-50008 for details) - see photo for further details. - PD7 - the rail in between the nose of the crossing and joint 710-JT (see crossing drawing Cxxx-__-R4-DWG-CR526-50009 for details) - see photo for further details.
| 05SY - Systemwide | Cxxx-NCR-000020 | NCR | Train Access Platforms - Incompatible holes in steel work for handrail K-clamp fixing connection |  | Contr | __ | PLU - Plumstead Stabling Facility |  | 2019-12-26 22:59 | 2020-03-02 10:42 | 67 | 2019-11-08 11:00 | Structural Engineering - Bolted Connections | 6000 |  | Manufacturing Defect | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The holes drilled in the deck beam for the K-clamp fixing between the handrails and deck of the Train Access Platforms are correct to manufacturing design drawings. However, the design is not compatible with the K-clamp fixing. See photo attached.
| 05SY - Systemwide | Cxxx-NCR-000021 | NCR | Civils - Crossfall on east end walkway |  | Contr | __ | PLU - Plumstead Stabling Facility |  | 2020-03-26 11:33 | 2020-02-13 11:40 | -42 | 2019-11-08 10:47 | Civil - Civil Engineering General | 3000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Walkway's crossfall exceeds designed 2% crossfall. as-built survey shows 3-5% crossfall of east end walkway in area between Lighting columns SOP1 (across end of siding 2) and SOP2 (across end of siding 4)
| 05SY - Systemwide | Cxxx-NCR-000022 | NCR | Civils - LVC27 concrete chamber |  | Contr | __ | PLU - Plumstead Stabling Facility |  | 2019-12-22 | 2020-01-09 14:09 | 18 | 2019-11-12 16:58 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Chamber LVC 27 was built on 11/11/2019 in location shown on Cxxx-FCD-000133. Subsequent Cxxx-FCD-000138 and Cxxx-FCD-000142 have provided different coordinates for LVC27 chamber making original location being incorrect therefore LVC27 is now in incorrect location 2.163m away from lately scheduled position.
| 05SY - Systemwide | Cxxx-NCR-000025 | NCR | LVC 22, 23, 25, 27 and 28 chambers covers |  | Contr | __ | PLU - Plumstead Stabling Facility |  | 2020-01-31 | 2020-03-04 15:11 | 33 | 2019-12-02 11:40 | Civil - Civil Engineering General | 15000 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Concrete LVC chambers were built with 300mm thick concrete cover slab in mind as shown Cxxx-OVE-U-DDD-CR148_SD013_Z-37515 (Detail 1 and 2). According to Answer to Cxxx-RFI-000238 this is incorrect and Chambers were meant to be built with wall built up to finish road levels with a recess for the E900 iron covers to be grouted in. LVC 22, 23, 25, 27 and 28 chamber's walls built to following levels • LVC 25-27-28 – Current level of walls – 105.250 – Cxxx design cover level 105.550 - Cxxx-OVE-U-DDJ-CR148_SD013_Z-00001. Please note LVC 26 is not built yet. • LVC 22 – Current level of walls – 105.180 - Cxxx design cover level 105.480 • LVC 23 – Current level of walls – 105.230 – Cxxx design cover level 105.530 Contractor believes design levels of chambers are not aligned with pavement levels as shown on Cxxx-OVE-C-DDA-CR148_SD013_1-37151 e.g.: LVC 28 - design 105.550 Pavement approx. 105.700-105.725 - Cxxx-OVE-C-DDA-CR148_SD013_1-37151 LVC 27 - design 105.550 Pavement approx. 105.700-105.725 LVC 25 - design 105.550 Pavement approx. 105.525-105.550 LVC 23 - design 105.390 Pavement approx. 105.550-105.575 - LVC design shown on Cxxx-OVE-U-DDJ-CR148_SD013_Z-18000 LVC 22 - design 105.400 Pavement approx. 105.450-105.475 - LVC design shown on Cxxx-OVE-U-DDJ-CR148_SD013_Z-18000
| 05SY - Systemwide | Cxxx-NCR-000026 | NCR | No overlap on Semi-permeable geotextile between S8/9 |  | Contr | __ | PLU - Plumstead Stabling Facility |  | 2020-04-03 17:58 | 2020-02-24 10:26 | -39 | 2019-12-03 18:23 | Civil - Track | 3000 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During excavation and installation of CAT 5 water supply from Cleaners Building to Train Access Platforms located between Siding 8 and 9 semi-permeable geotextile (terram T1500) has been cut/ damaged. Due to proximity of the sidings track and ballast it is not achievable to reinstate the min. 300mm overlap.
| 05SY - Systemwide | Cxxx-NCR-000027 | NCR | Train Access Platforms - Incompatable holes in steelwork for stair stringer flanges |  | Contr | __ | PLU - Plumstead Stabling Facility |  | 2020-01-10 16:58 | 2020-03-02 12:30 | 52 | 2019-12-09 17:13 | Structural Engineering - Bolted Connections | 6000 |  | Manufacturing Defect | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The design dimensions shown between the holes intended to accept the fixings for the stringer flanges do not suit the dimensions of the procured stringer flanges. Therefore, the holes drilled in the stringer during fabrication are not compatible with the flanges procured by __.
| 05SY - Systemwide | Cxxx-NCR-000029 | NCR | Drainage Pipe Material between SW-MH-3A and EXT-SW-MH-05 |  | Contr | __ | PLU - Plumstead Stabling Facility |  | 2020-03-14 12:37 | 2020-01-14 12:38 | -60 | 2019-12-11 18:33 | Civil - Drainage | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | Cxxx-OVE-D-DDJ-CR148_SD013_Z-37907 C05 Drainage Surface Water Pipeline Schedule states vitrified clay to be installed on run S2.001 (from SW-TR-03 to SW-TR-3A) and S2.002 (from SW-TR-3A to EXT-SW-TR-05) however Cxxx-FCD-000001 accepted change from clay to HDPE pipe then response to Cxxx-FCD-000040 accepted change from TDE to TDK twin wall caveat being to maintain clay connections when feeding in to existing drainage installed by C298. Subsequently __ have installed twin wall HDPE on runs S2.001 and S.2002 due to proximity of adjacent structures in order to minimize the likelihood of damage from excavations adjacent.
| 05SY - Systemwide | Cxxx-NCR-000030 | NCR | Civils - Laydown Slab 3 in area "D" - concrete slab surface defects |  | Contr | __ | PLU - Plumstead Stabling Facility |  | 2020-05-31 | 2020-07-24 09:01 | 54 | 2019-12-23 12:58 | Civil - Concrete Pavement | 6000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Concrete surface of slab 3 in lay-down slabs area "D" has some surface flaking.
| 05SY - Systemwide | Cxxx-NCR-000031 | NCR | Civils - Laydown Area "D" Slab pour 5 - concrete surface defect |  | Contr | __ | PLU - Plumstead Stabling Facility |  | 2020-05-31 | 2020-03-25 13:56 | -67 | 2019-12-23 13:03 | Civil - Concrete Pavement | 6000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Concrete surface of slab 5 in lay-down slabs area "D" has some surface imperfections as a result of rain fall on top of concrete surface
| 05SY - Systemwide | Cxxx-NCR-000033 | NCR | Civils - LV duct to sliding gate not installed |  | Contr | __ | PLU - Plumstead Stabling Facility |  | 2020-04-30 | 2020-03-26 12:16 | -35 | 2020-01-14 17:05 | Civil - Civil Engineering General | 6000 |  | Supervision/Management | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | LV Duct from LVC 19 towards Sliding Gate was not installed prior to construction of ACO channel and Concrete laydown slab "Area C"
| 05SY - Systemwide | Cxxx-NCR-000035 | NCR | MEP - Non compliant cable and connections into the UPS |  | Contr | __ | PLU - Plumstead Stabling Facility |  | 2020-02-06 14:28 | 2020-03-04 15:17 | 27 | 2020-01-17 13:57 | Electrical - Electrical Engineering General | 3000 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The UPS installed in the utilities room within cleaners building is non-compliant to approved Crossrail standards. The key issues with UPS are as per below: 1. Terminations into connectors is not acceptable 2. The cable terminated is not secured properly as per photos attached. 3. The cable installed is twin and earth which is not acceptable.
| 05SY - Systemwide | Cxxx-NCR-000036 | NCR | MEP - Taps relocation on train access platforms |  | Contr | __ | PLU - Plumstead Stabling Facility |  | 2020-05-31 | 2020-03-03 13:20 | -89 | 2020-01-20 13:08 | Mechanical - Hot & Cold Water Supplies | 6000 |  | Design | Use As-Is | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | It has been identified that water taps part of CAT 5 water supply installation have been installed in a different location on Train Access Platform 5 to 8. This installation differs from design shown on drawings: 1) Cxxx-__-C-DDD-CR148_SD013_1-00101 platform 1 2) Cxxx-__-C-DDD-CR148_SD013_1-00102 platform 2 3) Cxxx-__-C-DDD-CR148_SD013_1-00103 platform 3 4) Cxxx-__-C-DDD-CR148_SD013_1-00104 platform 4 5) Cxxx-__-C-DDD-CR148_SD013_1-00105 platform 5 6) Cxxx-__-C-DDD-CR148_SD013_1-00106 platform 6 7) Cxxx-__-C-DDD-CR148_SD013_1-00107 platform 7 8) Cxxx-__-C-DDD-CR148_SD013_1-00108 platform 8 The new location of these taps matches with the location of the junction boxes under the train access platforms. Nevertheless, the contractors understand that this is not an issue since the junction boxes are IP65 rated, and a protection shade has also been installed. Final location of these taps is shown in the following attachments: 1) Cxxx-__-C-DDD-CR148_SD013_1-00101 platform 1 - Tap mark-up 2) Cxxx-__-C-DDD-CR148_SD013_1-00102 platform 2 - Tap mark-up 3) Cxxx-__-C-DDD-CR148_SD013_1-00103 platform 3 - Tap mark-up 4) Cxxx-__-C-DDD-CR148_SD013_1-00104 platform 4 - Tap mark-up 5) Cxxx-__-C-DDD-CR148_SD013_1-00105 platform 5 - Tap mark-up 6) Cxxx-__-C-DDD-CR148_SD013_1-00106 platform 6 - Tap mark-up 7) Cxxx-__-C-DDD-CR148_SD013_1-00107 platform 7 - Tap mark-up 8) Cxxx-__-C-DDD-CR148_SD013_1-00108 platform 8 - Tap mark-up
| 05SY - Systemwide | Cxxx-NCR-000038 | NCR | Cleaners Building - Base flashing clashing with Ventilation |  | Contr | __ | PLU - Plumstead Stabling Facility |  | 2020-07-01 11:42 | 2020-06-22 12:45 | -9 | 2020-03-24 11:46 | Architectural - General | 1000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | There is a clash between the underfloor ventilation grille covers around the Cleaners Building and the base flashing at the bottom of the Cladding. This has come about due a lack of integration between the Cxxx design and the manufacturer's detailed drawings. Looking at Elliot's and Cxxx design drawings, it seems like the flashing and cladding panel thickness was not taken into consideration to locate the ventilation grilles (please refer to the attached picture "CB - Pic 1"). This situation happens on all 4 sides of the cleaners building. From the point of view of __ and the modular building supplier, there is no concern for restricted ventilation since the design ventilation (151 976mm2) is much greater than the minimum area of ventilation required (69 000mm2) ( taken from manufacturing drawing Cxxx-__-A-DWG-CR526-50009). Worst case scenario, assuming that all vents are half covered, the remaining unobstructed area would be 76 027mm2 (still exceeding the minimum 69 000mm2 value). Furthermore, the flashing does not completely obstruct the opening and so air can flow. However, as a consequence, a number of vent grille covers have restricted access for removal which raises a maintenance issue. To combat this, __ is proposing to install the problematic grilles in 2 parts to facilitate removal of the grill for maintenance purpose.
| 05SY - Systemwide | Cxxx-NCR-000040 | NCR | Train Access Plaform Junction Box and Potable Water Tap Co-ordiantion |  | Contr | __ | PLU - Plumstead Stabling Facility |  | 2020-05-31 | 2020-02-26 11:10 | -95 | 2020-02-06 09:54 | Electrical - Electrical Engineering General | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | On the Train Access Platforms where the potable water taps have been installed directly above the junction boxes there is a risk of water ingress and increased degradation of the junction box over time due to the taps being left open or from drips.
| 05SY - Systemwide | Cxxx-NCR-000041 | NCR | Partial collapse of filter drain run between SWTR10 to SWTR11 (S16.000) |  | Contr | __ | PLU - Plumstead Stabling Facility |  | 2020-05-31 | 2020-03-17 16:27 | -75 | 2020-02-11 17:28 | Civil - Drainage | 6000 |  | Damaged | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following review of CCTV report Cxxx-__-N-RGN-CR526-50001 rev 1.0 a partial collapse (approx 2.5m section) of filter drain on run S16.000 between drainage chambers SWTR10 and SWTR11 can be seen.
| 05SY - Systemwide | Cxxx-NCR-000042 | NCR | Filter drain deformed (ovalised) at SWTR60 to SWTR61 run S23.005 |  | Contr | __ | PLU - Plumstead Stabling Facility |  | 2020-05-31 | 2020-03-18 10:43 | -74 | 2020-02-14 16:45 | Civil - Drainage | 6000 |  | System Defect | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following review of CCTV report Cxxx-__-N-RGN-CR526-50001 rev 1.0 deformation of 15% can be seen on the filter pipe of run S23.005 between SWTR60 and SWTR61 at 12.24m.
| 05SY - Systemwide | Cxxx-NCR-000043 | NCR | Cleaners Building - Elements of Installation commenced without being covered in a code 1 accepted ITP |  | Contr | __ | PLU - Plumstead Stabling Facility |  | 2020-04-30 | 2020-03-12 12:23 | -49 | 2020-02-21 11:27 | Architectural - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | The installation of the Cladding, Fascia, Gutter and Down Pipes on the Cleaners Building has commenced without the works being covered in a code 1 accepted ITP. ITP for Installation of Cleaners Building Cxxx-__-O4-ITP-CR526-50041 was submitted omitting these works.
| 05SY - Systemwide | Cxxx-NCR-000044 | NCR | Cxxx PLURA Separation Fence Post Foot installed without accepted MCR |  | Contr | __ | PLU - Plumstead Stabling Facility |  | 2020-04-30 | 2020-03-12 12:24 | -49 | 2020-02-24 18:26 | Materials - Approval | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | The PLURA Separation Fence Post Foot (Cxxx-__-O4-MCR-CR526-50074) has been installed without a code 1 accepted Material Compliance Record. Revision 1 and Revision 2 were returned Code 3. Revision 3 has been submitted for CRL review on 21/02/2020, addressing comments from revision 2 comment sheet Cxxx-__-O4-XCS-CR526-50118 .
| 05SY - Systemwide | Cxxx-NCR-000045 | NCR | Train Access Platform 6 - 2 No. Anchors cut too short |  | Contr | __ | PLU - Plumstead Stabling Facility |  | 2020-04-13 10:12 | 2020-03-05 13:53 | -39 | 2020-02-27 17:53 | Civil - Civil Engineering General | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Train Access Platform 6 - Two anchors have been cut too short and do not allow for two threads to protrude above the top of the nut when installed. This NCR is located on the south side of the 5th column underneath the platform of Train Access Platform 6. Drawing: Cxxx-__-C-DDD-CR148_SD013_1-00106
| 05SY - Systemwide | Cxxx-NCR-000046 | NCR | Civils - Remedial Works on Cladding due to CCTV installation (Camera 79) |  | Contr | __ | PLU - Plumstead Stabling Facility |  | 2020-04-30 08:51 | 2020-05-04 11:13 | 4 | 2020-03-10 12:10 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Due to incorrect installation of Cleaners building CCTV Camera 79 (reference drawing: Cxxx-__-A-DWG-CR526-50011), the brackets for CCTV installed have left 4 holes on the cladding as the Camera CCTV 79 has been relocated and installed in the location specified in the design.
| 05SY - Systemwide | Cxxx-NCR-000047 | NCR | orientation of anti-tamper fixings on SR3 Expanded Mesh fence parallel to PD2 and Cxxx area |  | Contr | __ | PLU - Plumstead Stabling Facility |  | 2020-05-22 11:12 | 2020-04-14 10:21 | -38 | 2020-03-16 10:38 | Civil - Civil Engineering General | 3000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Fencing sub-Contractor installed SR3 Expanded Mesh fence North of PD2. Inspection identified that anti-tamper fixings holding the panels between themselves (not the fixings to the posts, which are of different type fixings) were installed in incorrect orientation from north to south (rather than from south to north).
| 05SY - Systemwide | Cxxx-NCR-000048 | NCR | Cracked pipe on FW S1.000 between FW01 and FW02 |  | Contr | __ | PLU - Plumstead Stabling Facility |  | 2020-08-31 | 2020-10-12 16:05 | 42 | 2020-03-26 15:06 | Civil - Drainage | 3000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following FW drainage cleaning and CCTV inspection by sub-contractor (__ Group) Contractor (__jv) has become aware of damage to a section of 150mm clay pipe work from FW01 to FW02 on run S1.000 at approx. 9.6m. See attached extract from report. - As requested please also find evidence to show the CCTV file is mislabelled and FW01 to FW02 is installed as per design with vitrified clay not cast iron as the annotation shows. - Email evidence from sub contractor assuring pipe lining as a suitable solution for repair
| 05SY - Systemwide | Cxxx-NCR-000049 | NCR | Broken gully connection at G08 off run S1.004 in NE Corner |  | Contr | __ | PLU - Plumstead Stabling Facility |  | 2020-06-06 09:47 | 2020-09-14 16:31 | 100 | 2020-03-30 09:02 | Civil - Drainage | 3000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following SW drainage cleaning and CCTV inspection by sub-contractor (__ Group) Contractor (__jv) has become aware of damage to 150mm clay pipework junction connector from run S1.004 to gully pot G08. See attached extract from report.
| 05SY - Systemwide | Cxxx-NCR-000050 | NCR | Broken FW pipe from FW03 to FW04 on S1.002 in NE Corner |  | Contr | __ | PLU - Plumstead Stabling Facility |  | 2020-06-06 09:49 | 2020-07-25 08:34 | 49 | 2020-03-30 09:32 | Civil - Drainage | 6000 |  | Damaged | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following FW drainage cleaning and CCTV inspection by sub-contractor (__ Group) Contractor (__jv) has become aware of puncture to a section of 150mm clay pipe work from FW04 to FW03 on run S1.002 at approx. 4.91m. See attached extract from report.
| 05SY - Systemwide | Cxxx-NCR-000051 | NCR | Grade 3 or less defects identified by CCTV report for Track Drainage |  | Contr | __ | PLU - Plumstead Stabling Facility |  | 2020-05-06 17:25 | 2020-10-01 12:29 | 148 | 2020-04-01 08:56 | Civil - Drainage | 6000 |  | Damaged | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Grade 3 or less defects identified by drainage inspection sub-contractor (__ Group) as classified by SRM grading from the WRc. See attached summary of defects. Various locations of medium joint displacement (where the pipe is sealed but part of the band seal can be seen) and minor surface defects (minor damage causing minimal hydraulic loss) identified on the following runs: SWTR15 to 16 SWTR19 to 20 SWTR32 to 33 SWTR60 to 59 HS.3.06.CP to 3.07RE See CCTV report for CCTV footage: Cxxx-__-N-RGN-CR526-50001
| 05SY - Systemwide | Cxxx-NCR-000053 | NCR | MEP - Lighting Lux Levels Non-Compliance at Plumstead Sidings Train Loading Area |  | Contr | __ | PLU - Plumstead Stabling Facility |  | 2020-06-09 07:41 | 2020-09-14 15:20 | 97 | 2020-05-19 07:26 | Electrical - Lighting | 6000 |  | Design | Repair | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | __ conducted lux level lighting test across Plumstead Sidings. The findings from the site tests have indicated the train loading area as marked up on the attachment does not meet lighting requirements outline in Eav 50.7lx (Average Illuminance 50.7 Lux). (refer to table on LS24233_3 - Plumstead Crossrail Sidings A1 and Cxxx-__-E-XCL-CR526-50001 Rev 9.0 - CODE 1.
| 05SY - Systemwide | Cxxx-NCR-000054 | NCR | Cxxx Train Access Platforms - Removable GRP Panels not fit for purpose on TAP 5, 6, 7 & 8 |  | Contr | __ | PLU - Plumstead Stabling Facility |  | 2020-11-25 10:05 | 2020-10-01 08:28 | -55 | 2020-06-05 17:05 | Civil - Civil Engineering General | 6000 |  | Design | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The removable GRP panel installed on Train Access Platforms 5, 6, 7 and 8 are very difficult to remove and introduces a safety hazard for anyone who removes it Therefore these removable panels are considered not fit for purpose. The purpose of the removable panels is for cleaner access to the train passenger doors according to drawing Cxxx-OVE-C-DDL-CR148_SD013_1-37801 and should be possible to store safely when removed to prevent the item falling onto the tracks or posing a trip hazard on the TAP when removed (according to Cxxx-OVE-C-RGN-CR148-50031).
| 05SY - Systemwide | Cxxx-NCR-000055 | NCR | Landscaping - Area of Soft Landscaping concreted at the South East side of the Accommodation building |  | Contr | __ | PLU - Plumstead Stabling Facility |  | 2020-09-01 15:51 | 2020-10-15 08:41 | 44 | 2020-06-23 07:41 | Civil - Landscaping | 20000 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Design Problem - Not Defined | Completed |  | An area of Soft Landscaping which should have contained 20no. Vinca minor ‘ralph shugert’ has been concreted instead. At present, it creates an hazardous potential shortcut between walking on the footpath adjacent to the road and the Accommodation building Eastern entrance. The kerb and the steep slope present a trip and fall hazard.
| 05SY - Systemwide | Cxxx-NCR-000057 | NCR | Civil - Omission of Trotrof and Trotred anti-static units installation |  | Contr | __ | PLU - Plumstead Stabling Facility |  | 2020-12-31 | 2020-12-09 14:31 | -22 | 2020-07-29 14:56 | Civil - Utilities Engineering | 6000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The installation of anti-static units has been overseen by __ during the installation of Trotrof and Trotred units in Plumstead Sidings.
| 05SY - Systemwide | Cxxx-NCR-000058 | NCR | Civils - Crack in concrete underneath SR3 fence adjacent to Gate 10 |  | Contr | __ | PLU - Plumstead Stabling Facility |  | 2020-12-03 14:38 | 2020-10-29 09:20 | -35 | 2020-10-02 13:36 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A crack appeared on the surface of the concrete sill underneath the SR3 fence western side of the Sliding Gate (see attached photographs) between SOP 34 and 36 (refer to Cxxx-OVE-C-DDA-CR148_SD013_Z-37129 C03 for SOPs locations).
| 05SY - Systemwide | Cxxx-NCR-000059 | NCR | Civils - Failed air test SWTR50 to SWTR 39 |  | Contr | __ | PLU - Plumstead Stabling Facility |  | 2020-09-15 12:25 | 2020-09-16 16:11 | 1 | 2020-08-20 09:49 | Civil - Drainage | 6000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Carrier pipe run between SWTR50 to SWTR 39 has failed an air test. As instructed in Cxxx-NCR-00051 - Contractor raises this NCR in order to capture this failed air test and determine the appropriate remedial measures. See CCTV report for CCTV footage: Cxxx-__-N-RGN-CR526-50001 rev 3.0
| 05SY - Systemwide | Cxxx-NCR-000060 | NCR | Track labels have been installed without Design Alternative ID |  | Contr | __ | PLU - Plumstead Stabling Facility |  | 2020-12-31 | 2020-11-06 17:36 | -55 | 2020-09-11 06:08 | Information Management - Asset Information | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Cxxx Track labels have been installed without Design Alternative ID printed on the labels for various asset classes ( bearers, rail joints). Cxxx has followed the same approach as Cxxx central section where design IDs are also not printed on the physical labels. Design IDs, however, are available within asset data and when scanning the QR bar codes of these assets on site. Relabelling will affect minimum 2000 assets and this will have time and cost implications and it will further delay handover.
| 05SY - Systemwide | Cxxx-NCR-000061 | NCR | Civils - Failed water test on Cleaners Building |  | Contr | __ | PLU - Plumstead Stabling Facility |  | 2020-12-18 | 2021-01-07 11:06 | 20 | 2020-10-29 10:42 | Civil - Civil Engineering General | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On 15/10/20, __ carried out water penetration tests on the Cleaners Building. This is a requirement from the Cleaners Building Installation ITP (refer to section 4.8 of Cxxx-__-O4-ITP-CR526-50041). The attached report '68348s1.Report.pdf ' covers testing performed on Elevation A window, Elevation C door and roof. See conclusion from the attached report. At the time of testing: - Location 1 (Maintenance Door): failed both the hose and spray bar tests, water was seen to enter the building at several locations - Location 2 (Kitchen Window): failed the hose test, water was seen to enter the building at 2no. locations
| 05SY - Systemwide | Cxxx-NCR-000062 | NCR | Fencing - Incorrect types of gate installed at emergency exit gate and gate to headshunt locations |  | Contr | __ | PLU - Plumstead Stabling Facility |  | 2020-11-26 18:10 | 2020-11-20 12:08 | -6 | 2020-10-19 15:14 | Civil - Civil Engineering General | 6000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Supervision - Insufficient supervision | Completed |  | As raised during 14/10/20 Engineering meeting with Cxxx and CRL in presence, the pedestrian gate provided with lock shroud + padlock has been installed at the ‘emergency exit gate’ location West side of the Sliding Gate and the pedestrian gate without lock shroud + padlock has been installed at the ‘gate to headshunt’ location South West corner of the site. See attached pictures. It should have been the other way around.
| 05SY - Systemwide | Cxxx-NCR-000063 | NCR | CIV- Damage to ACO Channel and Drainage Connection- West of Cleaners Building |  | Contr | __ | PLU - Plumstead Stabling Facility |  | 2021-03-31 | 2021-03-12 17:51 | -19 | 2020-11-12 15:49 | Civil - Civil Engineering General | 6000 |  | Damaged | Repair | 3 (3-6k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | There is a section of ACO channel that has its lids cracked at the top West of the Cleaners Building (see attached photograph "Cracked ACO channel.jpeg" and image "Cracked ACO channel location.JPG"). When investigating further, it became apparent that the ACO structure has been damaged and needs to be replaced. In addition, the drainage connection from CD01 into main drainage run S2.002 has been damaged. From the initial CCTV investigation, the pipe needs to be replaced.
| 05SY - Systemwide | Cxxx-NCR-000064 | NCR | Civil - Section of clay pipe broken next to Sliding Gate |  | Contr | __ | PLU - Plumstead Stabling Facility |  | 2021-01-09 16:38 | 2020-12-14 13:39 | -26 | 2020-11-13 10:21 | Civil - Drainage | 3000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | As mentioned to Crossrail and Cxxx during 11/11/20 Engineering Meeting, __ found a section of clay pipe broken between CD04 and S8.000 which needs replacing (see attached "Broken clay pipe.JPG" and "Broken clay pipe location.JPG").
| 05SY - Systemwide | Cxxx-NCR-000065 | NCR | Plumstead Sidings SLPP (DB-M-EX-02) Door Clash with Train Access Platform Sign |  | Contr | __ | PLU - Plumstead Stabling Facility |  | 2020-02-29 | 2021-01-07 18:56 | 313 | 2020-11-20 11:01 | Electrical - General | 500 |  | Incomplete Works | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Please see attached photo showing a clash between SLPP (Distribution Board 033) and adjacent train access signage. The locations of the signage is preventing the SLPP access door from fully opening and latching correctly. This latching mechanism being required to facilitate maintenance.
| 05SY - Systemwide | Cxxx-NCR-000066 | NCR | Fire Hydrants- No Non-Return Device Installed |  | Contr | __ | PLU - Plumstead Stabling Facility |  | 2021-10-31 | 2021-09-23 14:28 | -38 | 2021-04-08 09:33 | Utilities Engineering - Water | 6000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The Contractor has failed to install anti backflow valves on the fire hydrants within Cxxx Site.
| 05SY - Systemwide | Cxxx-NCR-000067 | NCR | OHLE holding down bolt found broken |  | Contr | __ | PLU - Plumstead Stabling Facility |  | 2021-12-31 | 2022-03-22 09:06 | 81 | 2021-08-27 14:22 | Over Head Line Electrification - Supports | 6000 |  | Damaged | Repair | 3 (3-6k) | Complete | Personnel Error - Inattention to detail | Completed |  | OHLE structure Number XRS/22/023 holding down bolt found broken. The broken end of the holding down bolt is exhibiting signs of rust. It was reported by the engineering supervisor working within the area on the 16/8/21.
| 05SY - Systemwide | Cxxx-NCR-000068 | NCR | PLU headshunt West end - commencement of works without design being approved. |  | Contr | __ | PLU - Plumstead Stabling Facility |  | 2022-06-28 09:00 | 2022-06-13 09:03 | -15 | 2022-03-31 17:41 | Civil - Civil Engineering General | 6000 |  | Planning | Use As-Is | 3 (3-6k) | Complete | Procedure Problem - Lack of approval Code 1 procedures excessive | Completed |  | Contractor has submitted on EB for Client's acceptance design package for fence works in PLU headhunt West end on 15 Feb 2022. __ forms 2 and 3 were transmitted to __ and CRL representatives __ ) on 28 Feb 2022. As previously communicated at various meetings - Due to possession availability site works had to commence end of March. By this date design was not yet approved by Client on EB. Works commenced without approved design which is a procedural non-conformance.
| 01CV - Civils | Cxxx-NCR-000075 | NCR | Customs House Station, Victoria Dock Portal |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2010-10-29 | 2010-11-30 19:50 | 32 | 2010-10-25 | Surveying - Instrumentation and Monitoring | 500 |  | Design | Rework |  | Complete |  | Completed |  | Installation of automated track monitoring at Customs House Station, for Sewer re-alignment works
| 01CV - Civils | Cxxx-NCR-000105 | NCR | Stainless Steel Instrumentation Fixings |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2010-12-08 | 2011-01-11 12:19 | 34 | 2010-11-25 | Surveying - Instrumentation and Monitoring | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | The instrumentation fixings that are currently being installed are coated steel (painted), galvanised steel or zinc plated Steel, dependant on location and instrument type. These materials are more suitable for the proposed application and have been used for number of years by __ for instrumentation installation.
| 01CV - Civils | Cxxx-NCR-000165 | NCR | Change in Multiplexer Locations on the Jubilee Line, Bond Street |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2011-03-14 | 2011-04-21 10:50 | 38 | 2011-02-28 | Surveying - Instrumentation and Monitoring | 500 |  | Design | Rework |  | Complete |  | Completed |  | The locations are different to those initially agreed between __,CRL & LUL
| 01CV - Civils | Cxxx-NCR-000171 | NCR | Robotic Total Stations |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2011-03-25 | 2011-04-15 10:31 | 21 | 2011-03-11 | Surveying - Instrumentation and Monitoring | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | __ are currently using 1 arc second Robotic Total stations for monitoring installations.
| 01CV - Civils | Cxxx-NCR-000172 | NCR | Use of Black Steel Fixings (Angle Plate) for Installed RTS at Barbican |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2011-03-21 | 2011-04-15 11:01 | 25 | 2011-03-14 | Surveying - Instrumentation and Monitoring | 500 |  | Material | Reject |  | Complete |  | Completed |  | Black Steel (un-treated) angle plates were used for the installation of RTS1 installed at the crown of the Met line tunnel between Barbican and Farringdon.
| 01CV - Civils | Cxxx-NCR-000199 | NCR | Use of steel bung instead of perspex bung for __ levelling studs |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2011-05-03 | 2011-04-20 08:18 | -13 | 2011-04-19 | Surveying - Instrumentation and Monitoring | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | A steel bung has been used instead of a perspex bung. The steel bung is cheaper and more sustainable over the duration of the project. It provides better protection to the hole edge and is easily sourced. The steel bung has a curved edge to provide a better fit to the surrounding surface, therefore eliminating potential catch points and making it safer.
| 01CV - Civils | Cxxx-NCR-000203 | NCR | Bond Street Above Ground Works - ATS04 |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2011-05-10 | 2011-08-12 15:37 | 94 | 2011-04-26 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Reject |  | Complete |  | Completed |  | __ TM30 Total Station (ATS04 - Serial No: 361759) could not monitor any buildings due to reported error message; "8704 ERROR: Timeout while positioning of one or both axes".
| 01CV - Civils | Cxxx-NCR-000210 | NCR | Rusting on ATS Brackets |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2011-05-20 | 2012-01-05 15:43 | 230 | 2011-05-06 | Surveying - Instrumentation and Monitoring | 500 |  | Material | Repair |  | Complete |  | Completed |  | The threaded rods on the ATS brackets have begun to rust.
| 01CV - Civils | Cxxx-NCR-000237 | NCR | Loose Track Prisms |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2011-06-17 | 2011-07-08 16:12 | 21 | 2011-06-03 | Surveying - Instrumentation and Monitoring | 500 |  | Design | Rework |  | Complete |  | Completed |  | Current track prism design for use on Bullhead type rail can be dislodged relatively easily.
| 01CV - Civils | Cxxx-NCR-000240 | NCR | Additional __ levelling stud installed on 67-68 New Bond Street |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2011-06-24 | 2011-06-07 15:06 | -17 | 2011-06-06 | Surveying - Instrumentation and Monitoring | 500 |  | Design | Use As-Is |  | Complete |  | Completed |  | An additional __ levelling stud was installed on the front facade of 67-68 New Bond Street as per the attached photo and annotated photo-montage. __soil field operatives installed the additional __ levelling stud as the distance between the __ levelling studs shown on the photo-montage (Cxxx-OVE-C2-RGN-Cxxx-50005 Rev 1.0) exceeded that of a typical array.
| 01CV - Civils | Cxxx-NCR-000279 | NCR | Pudding Mill Lane City Mill River RTS 5 |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2011-07-22 | 2012-03-21 09:59 | 243 | 2011-06-22 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Repair |  | Complete |  | Completed |  | A fault has been reported with RTS 5 (Serial No. 361744) reading prism arrays installed at Pudding Mill Lane.
| 01CV - Civils | Cxxx-NCR-000287 | NCR | Plumstead Portal RTS 4 |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2011-07-14 | 2012-03-29 10:05 | 259 | 2011-06-30 | Surveying - Instrumentation and Monitoring | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | A fault has been reported with RTS 4 (Serial No. 361944) due to damaged lemo connector on instrument elimating ability for remote communications.
| 01CV - Civils | Cxxx-NCR-000304 | NCR | Bond St Jubilee Line Northbound EL sensors |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2011-08-01 | 2011-11-08 08:51 | 99 | 2011-07-18 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Repair |  | Complete |  | Completed |  | Electrolevel & BCS sensors in Northbound Jubilee Line south of Bond st not operational.
| 01CV - Civils | Cxxx-NCR-000322 | NCR | Bond Street Jubilee Line Automated System Failure |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2011-08-22 | 2011-11-08 08:55 | 78 | 2011-08-08 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Repair |  | Complete |  | Completed |  | The system went offline at approximately 23:00 on Saturday 30th July, __ attended site on the 2/8/11 to investigate, results indicated there was an internal fault in the Campbell CR800 Datalogger. An operative then attended site on 4/8/11 to replace the faulty hardware and return the system to operational. Unfortunately, as a result of the faulty CR800 no data was recorded between its failure on Saturday night and its return to operational in the early hours of the 5/8/11
| 01CV - Civils | Cxxx-NCR-000330 | NCR | RTSs shooting in excess of 50m at Moorgate Northern Line |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2011-09-02 | 2012-04-02 16:28 | 213 | 2011-08-19 | Surveying - Instrumentation and Monitoring | 500 |  | Design | Use As-Is |  | Complete |  | Completed |  | Following receipt of LWW-CRL RFI-Cxxx-00314 & LWW-CRL RFI-Cxxx-00234, it can be seen that there will be occasions where prisms are being sighted in excess of the specified 50m, to a maximum of 65m. From __soil’s perspective, this will result in an insignificant loss of accuracy, maintain a monitoring resolution within that dictated by the specification (that is distances to an accuracy of ±1mm + 1ppm and angles to ½ second of arc). This situation will arise at the southern-most original BCS locations (1&6) and also in the middle of both platforms. Regarding the BCS locations, there is only one location where the RTSs can be located, so the shooting distance is unavoidable. In the platform areas, the extended shooting distance is due to the relocation of RTSs to the northern headwalls of both platforms.
| 01CV - Civils | Cxxx-NCR-000332 | NCR | Damaged Equipment - Bond St Jubilee Line |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2011-09-05 | 2011-11-08 14:20 | 64 | 2011-08-22 | Surveying - Instrumentation and Monitoring | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | UCIMS reported that Electrolevel sensor 53 in the southbound tunnel (Cxxx-EL00253) began reading as 'open loop' at 03:00 on 15/08/2011. Whilst attending site on 18/08/2011, __soil operatives noticed that the cable had been damaged/severed and the core's exposed. It appears that this damage was the result of installation works associated with the Station Upgrade Project as new equipment had been installed in close vicinity of the cable.
| 01CV - Civils | Cxxx-NCR-000335 | NCR | RTS 5B, Barbican Station |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2011-09-07 | 2011-11-11 13:47 | 65 | 2011-08-24 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Repair |  | Complete |  | Completed |  | A fault has been reported by this RTS (361982)
| 01CV - Civils | Cxxx-NCR-000340 | NCR | Bond Street Station Jubilee Line BCS locations |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2011-09-09 | 2012-07-26 14:40 | 321 | 2011-08-26 | Surveying - Instrumentation and Monitoring | 500 |  | Planning | Reject |  | Complete |  | Completed |  | The installed locations of the 4 No. BCS do not reference to the TBM crossing points on the Jubilee Line South of Bond Street Station.
| 01CV - Civils | Cxxx-NCR-000345 | NCR | RTS 24, Moorgate Metropolitan Line |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2011-09-26 | 2011-11-14 20:31 | 49 | 2011-09-12 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Repair |  | Complete |  | Completed |  | A fault has been reported by this RTS (361760)
| 01CV - Civils | Cxxx-NCR-000347 | NCR | Moorgate Metrolpoliatan Line - RTS points files |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2011-09-26 | 2011-11-14 21:02 | 49 | 2011-09-12 | Surveying - Instrumentation and Monitoring | 500 |  | System Defect | Repair |  | Complete |  | Completed |  | Points file errors for the installed RTS between Moorgate and Liverpool St have resulted in the failure of the instruments to read all of the installed survey prisms. imtsoil are currently investigating and trying to correct the problem.
| 01CV - Civils | Cxxx-NCR-000348 | NCR | RTS 5 Plumstead Portal |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2011-09-27 | 2012-03-29 10:24 | 184 | 2011-09-13 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Repair |  | Complete |  | Completed |  | A fault has been reported by this RTS (362006).
| 01CV - Civils | Cxxx-NCR-000350 | NCR | City Mill River RTS 4 |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2011-09-27 | 2012-04-03 18:18 | 189 | 2011-09-13 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Repair |  | Complete |  | Completed |  | A fault was recently reported with this RTS (SN 361745). It was replaced with RTS SN 362209 on 08/09/2011.
| 01CV - Civils | Cxxx-NCR-000355 | NCR | Pudding Mill Lane River Lea RTS 9 |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2011-10-03 | 2012-04-03 18:19 | 183 | 2011-09-19 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Repair |  | Complete |  | Completed |  | A fault has been reported with this Total Station (361994) and it has been removed from site for further investigation. Another __ TM30 Total Station has taken its place (361753).
| 01CV - Civils | Cxxx-NCR-000356 | NCR | RTS 27, Moorgate Metropolitan Line |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2011-10-05 | 2011-11-22 10:53 | 48 | 2011-09-21 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Repair |  | Complete |  | Completed |  | A fault has been reported with this Total Station and it is to be repaired or removed from site for further investigation. If removed, another __ TM30 Total Station will replace it.
| 01CV - Civils | Cxxx-NCR-000357 | NCR | RTS 15, Moorgate Metrpolitan Line |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2011-10-05 | 2012-04-03 18:20 | 181 | 2011-09-21 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Repair |  | Complete |  | Completed |  | A fault has been reported with this Total Station and it is to be repaired or removed from site for further investigation. If removed, another __ TM30 Total Station will replace it.
| 01CV - Civils | Cxxx-NCR-000358 | NCR | RST 22, Moorgate Metropoliatan Line |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2011-10-05 | 2012-04-03 18:19 | 181 | 2011-09-21 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Repair |  | Complete |  | Completed |  | A fault has been reported with this Total Station and it is to be repaired or removed from site for further investigation. If removed, another __ TM30 Total Station will replace it.
| 01CV - Civils | Cxxx-NCR-000361 | NCR | Replacement of RTS5B at Barbican Station |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2011-10-06 | 2012-04-03 18:17 | 180 | 2011-09-22 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Repair |  | Complete |  | Completed |  | A fault has been reported with this Total Station (362203). It has been removed to be investigated. A replacement Total Station (SN 362192) was installed on 20/09/2011
| 01CV - Civils | Cxxx-NCR-000362 | NCR | RTS 25, Moorgate Metropolitan Line |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2011-09-29 | 2011-11-14 18:53 | 46 | 2011-09-22 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Repair |  | Complete |  | Completed |  | A fault has been reported with this Total Station preventing it from reading any prisms.
| 01CV - Civils | Cxxx-NCR-000363 | NCR | RTS 26, Moorgate Metropolitan Line |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2011-09-29 | 2012-04-03 18:18 | 187 | 2011-09-22 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Repair |  | Complete |  | Completed |  | A fault has been reported with this Total Station preventing it from reading any prisms.
| 01CV - Civils | Cxxx-NCR-000364 | NCR | RTS 14, Moorgate Metropolitan Line |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2011-09-29 | 2011-11-14 13:33 | 46 | 2011-09-22 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Repair |  | Complete |  | Completed |  | A fault has been reported with this Total Station preventing it from reading any prisms.
| 01CV - Civils | Cxxx-NCR-000365 | NCR | Bond Street Above Ground Works - ATS11 |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2011-10-06 | 2012-04-03 18:17 | 180 | 2011-09-22 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Repair |  | Complete |  | Completed |  | ATS11, __ TM30 Total Station (SN 361973) installed on the corner of 76 New Bond Street and Dering Street is reporting a fault.
| 01CV - Civils | Cxxx-NCR-000366 | NCR | Bond Street Above Ground Works - ATS09 |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2011-11-05 | 2012-04-03 18:17 | 150 | 2011-09-22 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Repair |  | Complete |  | Completed |  | ATS09, __ TM30 Total Station (SN 361218) installed on the rear of 104 New Bond Street is reporting a fault.
| 01CV - Civils | Cxxx-NCR-000368 | NCR | Replacement of Whitechapel H&C RTS 3 |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2011-09-29 | 2012-04-03 17:31 | 187 | 2011-09-22 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Repair |  | Complete |  | Completed |  | A fault has been reported with this Total Station (361753). It has been removed to be investigated and a replacement Total Station (SN:361730) was installed on 31/08/2011.
| 01CV - Civils | Cxxx-NCR-000369 | NCR | Replacement of Whitechapel H&C RTS 1 |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2011-09-29 | 2012-04-03 17:32 | 187 | 2011-09-22 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Repair |  | Complete |  | Completed |  | A fault has been reported with this Total Station (361752). It has been removed to be investigated and a replacement Total Station (SN:362183) was installed on 15/09/2011.
| 01CV - Civils | Cxxx-NCR-000377 | NCR | PMI012 - Two Barcode Scales not installed on 2-4 Brook Street |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2011-09-03 | 2012-01-20 10:10 | 139 | 2011-09-27 | Surveying - Instrumentation and Monitoring | 500 |  | Design | Rework |  | Complete |  | Completed |  | Two barcode scales (highlighted on the attached image) have not been installed due to repeated delays to accessing the appropriate locations.
| 01CV - Civils | Cxxx-NCR-000384 | NCR | Installation Report for Fisher Street Sub-Station |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2011-10-10 | 2012-03-26 10:57 | 168 | 2011-10-03 | Surveying - Instrumentation and Monitoring | 500 |  |  | Rework |  | Complete |  | Completed |  | Installation completed on the 23rd August and baseline monitoring started form the 24th August. No installation report submitted to date.
| 01CV - Civils | Cxxx-NCR-000386 | NCR | PMI012 - __ levelling stud not installed on 105-106 New Bond Street |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2011-10-14 | 2012-01-05 16:23 | 83 | 2011-10-04 | Surveying - Instrumentation and Monitoring | 500 |  | Design | Use As-Is |  | Complete |  | Completed |  | Installation of one __ levelling stud was not possible because the substrate consists of a thin stone block with a cavity behind. The property owner has not allowed for alternative instrumentation (such as barcode scales) to be installed.
| 01CV - Civils | Cxxx-NCR-000387 | NCR | PMI012 - Instrumentation not installed into wooden facade on 32 Brook Street |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2011-10-14 | 2011-12-02 11:58 | 49 | 2011-10-04 | Surveying - Instrumentation and Monitoring | 500 |  | Design | Use As-Is |  | Complete |  | Completed |  | Instrumentation highlighted on the attached image has not been installed because the wooden facade (added to the property after the designs were created) is not suitable to install instrumentation into.
| 01CV - Civils | Cxxx-NCR-000390 | NCR | Bond Street Above Ground Works - ATS02 |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2011-10-20 | 2012-04-03 17:32 | 166 | 2011-10-06 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Repair |  | Complete |  | Completed |  | ATS02, __ TM30 Total Station (SN 361734) installed on the front facade of 25-47 Cavendish Flats, Weighhouse Street, is producing __ error message 8704 "Timed out whilst trying to position in one or both axis". This error code is appearing more frequently as time progresses, causing cycles of data to be missed. This total station was removed from site for further investigation. Another __ TM30 Total Station (SN 361747) was installed to replace it.
| 01CV - Civils | Cxxx-NCR-000393 | NCR | Whitechapel platform 4 base prisms |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2011-10-15 | 2013-01-31 10:18 | 474 | 2011-10-07 | Surveying - Instrumentation and Monitoring | 500 |  | Design | Rework |  | Complete |  | Completed |  | The extension of platform 4 has been constructed using concrete columns and beams which support the platform slab. The spacing between these columns is greater than the 2 meter spacing needed to install the base prisms. the spaces between the columns are filled-in with concrete blocks but these are assumed to be non-structural (see attached photograph) 17 No. prisms have been installed where the columns align with the prism arrays on the tracks and retaining wall. The remaining prism will be installed when a solution is found Further details on dimensions and spacing of the columns will be provided at a later date.
| 01CV - Civils | Cxxx-NCR-000394 | NCR | Bond Street Above Ground Works - ATS03 |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2011-11-18 | 2012-04-03 17:32 | 137 | 2011-10-14 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Repair |  | Complete |  | Completed |  | ATS03, __ TM30 Total Station (SN 361980) installed on corner of 48-60 Hanover Flats, Gilbert Street is reporting a fault.
| 01CV - Civils | Cxxx-NCR-000395 | NCR | Bond Street Above Ground Works - ATS18 |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2011-11-15 | 2012-04-03 17:33 | 140 | 2011-10-14 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Repair |  | Complete |  | Completed |  | ATS18, __ TM30 Total Station (SN 361762) installed on side facade of 18 Haunch of Venison Yard is reporting a fault (Error 1454). This total station was removed from site for further investigation. Another __ TM30 Total Station (SN 362389) was installed to replace it.
| 01CV - Civils | Cxxx-NCR-000396 | NCR | Pudding Mill Lane RTS AT10002 |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2011-10-31 | 2012-04-03 17:26 | 155 | 2011-10-17 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Repair |  | Complete |  | Completed |  | A fault has been reported with this RTS (361251). To investigate this the instrument has been removed from site and replaced with another TM30 Total Station (362430).
| 01CV - Civils | Cxxx-NCR-000397 | NCR | Pudding Mill Lane AT10006 |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2011-10-31 | 2012-04-03 17:17 | 155 | 2011-10-17 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Repair |  | Complete |  | Completed |  | A fault has been reported by this instrument (361152). To investigate this the RTS has been replaced by another TM30 Total Station (SN 362345) on the night of 12/10/2011.
| 01CV - Civils | Cxxx-NCR-000398 | NCR | Barbican RTS4B |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2011-10-31 | 2012-04-03 17:19 | 155 | 2011-10-17 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Repair |  | Complete |  | Completed |  | A fault has been reported by this instrument (362000). To investigate this the instrument will need to removed and replaced with another TM30 Total Station.
| 01CV - Civils | Cxxx-NCR-000400 | NCR | Bond Street Above Ground Works - ATS07 |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2011-11-15 | 2012-07-06 09:41 | 234 | 2011-10-18 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Repair |  | Complete |  | Completed |  | ATS07, __ TM30 Total Station (SN 362012) installed on facade of 8 South Molton Lane is reporting a fault (Error code: 99960).
| 01CV - Civils | Cxxx-NCR-000410 | NCR | Pudding Mill Lane AT10001 |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2011-11-08 | 2012-04-03 17:18 | 147 | 2011-10-25 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Repair |  | Complete |  | Completed |  | The instrument (361772) reported a fault and as such has been removed from site for further investigation. A replacement TM30 Total Station (361752) has been installed and the Calibration Certificate can be found attached.
| 01CV - Civils | Cxxx-NCR-000412 | NCR | PMI030 - 1-7 Davies Mews (28-30 South Molton Lane) - PLP not installed |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2011-11-14 | 2012-01-18 09:58 | 65 | 2011-10-31 | Surveying - Instrumentation and Monitoring | 500 |  | Design | Use As-Is |  | Complete |  | Completed |  | The PLP stud described in LWW-CRL RFI-Cxxx-00334 has not been installed due to receiving PMI071.
| 01CV - Civils | Cxxx-NCR-000413 | NCR | PMI012 - 63 South Molton Street - PLPs installed in place of __ levelling studs |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2011-11-14 | 2012-02-24 09:51 | 102 | 2011-10-31 | Surveying - Instrumentation and Monitoring | 500 |  | Design | Use As-Is |  | Complete |  | Completed |  | Parts of the front facade of 63 South Molton Street are covered by wood. This material is not suitable to install __ levelling studs into. PLPs were installed into the ground approximately 100mm in front of the locations specified in Cxxx-OVE-C2-DDJ-CR001_Z-39248.
| 01CV - Civils | Cxxx-NCR-000414 | NCR | PMI012 - 64 South Molton Street - PLP installed in place of __ levelling stud |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2011-11-14 | 2012-02-02 12:20 | 80 | 2011-10-31 | Surveying - Instrumentation and Monitoring | 500 |  | Design | Use As-Is |  | Complete |  | Completed |  | Parts of the front facade of 64 South Molton Street are covered by wood. This material is not suitable to install __ levelling studs into. A PLP was installed into the ground approximately 100mm in front of the location specified in Cxxx-OVE-C2-DDJ-CR001_Z-39249, as displayed on the attached image.
| 01CV - Civils | Cxxx-NCR-000415 | NCR | PMI012 - 26 Brook Street - __ levelling stud not installed |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2011-11-14 | 2011-12-02 11:41 | 18 | 2011-10-31 | Surveying - Instrumentation and Monitoring | 500 |  | Design | Use As-Is |  | Complete |  | Completed |  | Parts of the instrumentation were installed according to the photo-montages approved by Imraan Mirza following LWW-CRL RFI-Cxxx-00147 and the photo-montages in LWW-CRL RFI-Cxxx-00286 because the official photo-montage had not been received. One __ levelling stud has not been installed. The installed instrumentation is displayed on the attached image.
| 01CV - Civils | Cxxx-NCR-000416 | NCR | PMI012 - 107 New Bond Street - PLPs installed in place of __ levelling studs |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2011-11-14 | 2011-12-02 12:22 | 18 | 2011-10-31 | Surveying - Instrumentation and Monitoring | 500 |  | Design | Use As-Is |  | Complete |  | Completed |  | Parts of the facade of 107 New Bond Street are covered by wood. This material is not suitable to install __ levelling studs into. PLPs were installed into the ground approximately 100mm in front of the locations specified in LWW-CRL RFI-Cxxx-00212. Please refer to the attached image.
| 01CV - Civils | Cxxx-NCR-000417 | NCR | PMI012 - 3-6 Haunch of Venison Yard - Prism not installed |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2011-11-14 | 2011-12-02 12:34 | 18 | 2011-10-31 | Surveying - Instrumentation and Monitoring | 500 |  | Design | Use As-Is |  | Complete |  | Completed |  | One prism has not been installed on 3-6 Haunch of Venison Yard (please refer to the attached image). Under PMI071, this prism will not be installed.
| 01CV - Civils | Cxxx-NCR-000418 | NCR | PMI012 - 10 Haunch of Venison Yard - Two prisms not installed |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2011-11-14 | 2011-12-02 10:47 | 18 | 2011-10-31 | Surveying - Instrumentation and Monitoring | 500 |  | Design | Use As-Is |  | Complete |  | Completed |  | Two prisms have not been installed on the facade of 10 Haunch of Venison Yard due to flags on this property obstructing line of sight to the ATS. Please refer to the attached image. There is no suitable location to install these prisms on this property. Under PMI071, these prisms will not be installed.
| 01CV - Civils | Cxxx-NCR-000419 | NCR | Replacement of H&C RTS 2 |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2011-11-15 | 2012-04-05 07:15 | 142 | 2011-11-01 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Repair |  | Complete |  | Completed |  | A fault has been reported with this Total Station (362014). It has been removed to be investigated and a replacement Total Station (SN: 362344) was installed on 24/10/2011.
| 01CV - Civils | Cxxx-NCR-000420 | NCR | Replacement of Whitechapel H&C RTS 3 |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2011-11-15 | 2012-04-03 17:08 | 140 | 2011-11-01 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Repair |  | Complete |  | Completed |  | A fault has been reported with this Total Station (361730). It has been removed to be investigated and a replacement Total Station (SN: 362203) was installed on 24/10/2011.
| 01CV - Civils | Cxxx-NCR-000424 | NCR | PMI012 - 56 South Molton Street - Two __ levelling studs not installed |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2011-11-18 | 2011-12-02 10:05 | 14 | 2011-11-04 | Surveying - Instrumentation and Monitoring | 500 |  | Design | Use As-Is |  | Complete |  | Completed |  | Two __ levelling studs in design Cxxx-OVE-C2-DDJ-CR001_Z-39515 have not been installed because the wooden facade of 56 South Molton Street is not suitable to install instrumentation into. Following PMI071, these __ levelling studs will not be installed.
| 01CV - Civils | Cxxx-NCR-000425 | NCR | Replacement of RTSs 5 & 6 at Plumstead Portal |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2011-11-09 | 2012-04-05 07:16 | 148 | 2011-11-07 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Repair |  | Complete |  | Completed |  | Both instruments are reporting error codes and need replacing on the next available shift.
| 01CV - Civils | Cxxx-NCR-000430 | NCR | RTS Failure - PML River Lea 2 (AT10002) |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2011-11-25 | 2012-04-05 07:13 | 132 | 2011-11-11 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Repair |  | Complete |  | Completed |  | A fault has been reported by this instrument and data is not currently being transmitted.
| 01CV - Civils | Cxxx-NCR-000431 | NCR | RTS Failure - PML River Lea 3 |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2011-11-25 | 2012-04-19 10:08 | 146 | 2011-11-11 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Repair |  | Complete |  | Completed |  | This instrument has reported a fault on 11/11/11 at 08:40 and is currently not transmitting data.
| 01CV - Civils | Cxxx-NCR-000432 | NCR | Replacement of RTSs 2 & 4 at Plumstead Portal |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2011-11-29 | 2012-04-27 07:56 | 150 | 2011-11-15 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Repair |  | Complete |  | Completed |  | Both instruments are reporting error codes and need replacing on the next available shift.
| 01CV - Civils | Cxxx-NCR-000434 | NCR | Pudding Mill Lane RL5 (AT10005) |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2011-11-30 | 2012-04-05 07:12 | 127 | 2011-11-16 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Repair |  | Complete |  | Completed |  | A fault has been reported by this instrument (15/11/11) and it is no longer functioning.
| 01CV - Civils | Cxxx-NCR-000436 | NCR | Pudding Mill Lane RL8 (AT10008) |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2011-11-30 | 2012-01-18 09:46 | 49 | 2011-11-16 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Repair |  | Complete |  | Completed |  | A fault has been reported by this instrument on 15/11/11 and it is no longer functioning
| 01CV - Civils | Cxxx-NCR-000443 | NCR | Power Failure - RTS 17,21 & 22 Moorgate Metropolitan Line |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2011-11-29 | 2012-04-03 17:19 | 126 | 2011-11-22 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Repair |  | Complete |  | Completed |  | All 3 instruments stopped working because of a apparent power failure on 17/11/11
| 01CV - Civils | Cxxx-NCR-000444 | NCR | PMI066 - 50 Eastbourne Terrace - One __ stud will not be installed |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2011-12-06 | 2012-04-25 10:05 | 141 | 2011-11-22 | Surveying - Instrumentation and Monitoring | 500 |  | Design | Rework |  | Complete |  | Completed |  | The __ stud highlighted on the attached montage cannot be installed in the intended location due to the structure attached to the base of the building preventing access. Installing the __ stud on the attached structure will not allow for measurements of movement of 50 Eastbourne Terrace.
| 01CV - Civils | Cxxx-NCR-000448 | NCR | Replacement of RTS 5 at Plumstead Portal |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2011-12-07 | 2012-04-24 07:22 | 139 | 2011-11-23 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Repair |  | Complete |  | Completed |  | Instrument has reported error code -99960, and needs to be removed and replaced on next available shift.
| 01CV - Civils | Cxxx-NCR-000457 | NCR | Replacement of Whitechapel LO RTS 3 |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2012-01-06 | 2012-04-03 17:24 | 88 | 2011-12-02 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Repair |  | Complete |  | Completed |  | A fault has been reported with this Total Station (361973). It has been removed to be investigated and a replacement Total Station (SN: 362772) was installed on 30/11/2011.
| 01CV - Civils | Cxxx-NCR-000458 | NCR | Replacement of Whitechapel LO RTS 11 |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2012-01-06 | 2012-04-05 07:11 | 90 | 2011-12-02 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Repair |  | Complete |  | Completed |  | A fault has been reported with this Total Station (362617). It has been removed to be investigated and a replacement Total Station (SN: 362668) was installed on 30/11/2011.
| 01CV - Civils | Cxxx-NCR-000460 | NCR | Replacement of Whitechapel LO RTS 7 |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2012-01-06 | 2012-04-03 17:24 | 88 | 2011-12-07 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Repair |  | Complete |  | Completed |  | A fault has been reported with this Total Station (361373). It has been removed to be investigated and a replacement Total Station (SN: 362787) was installed on 03/12/2011.
| 01CV - Civils | Cxxx-NCR-000461 | NCR | Replacement of Whitechapel H&C RTS 2 |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2012-01-06 | 2012-04-03 17:25 | 88 | 2011-12-07 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Repair |  | Complete |  | Completed |  | A fault has been reported with this Total Station (362344). It has been removed to be investigated and a replacement Total Station (SN: 362618) was installed on 06/12/2011.
| 01CV - Civils | Cxxx-NCR-000465 | NCR | Replacement of Barbican/Disused Thameslink RTS 6F |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2011-12-24 | 2012-04-24 08:18 | 122 | 2011-12-12 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Repair |  | Complete |  | Completed |  | This instrument has reported a -99960 fault and needs to be removed and replaced on next available shift.
| 01CV - Civils | Cxxx-NCR-000466 | NCR | Moorgate Northern Line , RTS5 Blindspots |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2011-12-20 | 2012-07-26 18:30 | 219 | 2011-12-13 | Surveying - Structural surveys | 500 |  | Design | Use As-Is |  | Complete |  | Completed |  | The position of RTS5 was redesigned to being positioned on the tunnel headwall rather than the tunnel roof(PMI61) , this was because asbestos was found in the tunnel lining. There is now a blindspot in sighting the platform nosing prisms, 3 prisms on the southbound platform cannot now be seen.
| 01CV - Civils | Cxxx-NCR-000468 | NCR | PMI034 - 4 No. PLPs to replace 4 No. __s on 140-142 Wardour Street |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2011-12-30 | 2012-04-27 09:13 | 119 | 2011-12-16 | Surveying - Instrumentation and Monitoring | 500 |  | Design | Rework |  | Complete |  | Completed |  | 4 No. __s on 140-142 Wardour Street cannot be surveyed, as railings on the building are obstructing the use of a staff. 4 No. PLPs have been installed to replace the __s, adjacent to the __ location and as close to the building as possible.
| 01CV - Civils | Cxxx-NCR-000475 | NCR | Replacement of RTS 3A (Cxxx-AT00004-CR088) in Barbican running tunnels |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2012-01-10 | 2012-04-03 17:25 | 84 | 2012-01-04 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Repair |  | Complete |  | Completed |  | This instrument has reported a -99960 fault and on inspection needs to be removed and replaced on next available shift.
| 01CV - Civils | Cxxx-NCR-000482 | NCR | ATS 0.5 Specification |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2012-01-12 | 2012-03-13 11:22 | 61 | 2012-01-09 | Civil - Geotechnical Engineering | 500 |  | Design | Use As-Is |  | Complete |  | Completed |  | 3D prism co-ordinates are stored in easting, northing and elevation to ±1mm Fro the specification text, prisms can not be more than 100m from the ATS (a __ TM30), the angular accuracy of the ATS when used in robotic mode is redundant in respect of either choosing a ½” or 1” arc, as the overriding component of the measurement system is its weakest part which is the EDM (distance) component at 1mm ±1ppm. The ±1ppm is irrelevant as at 100m ±1 part per million is 0.1mm and thus to stop the instrument being capable of measuring ±1mm the distance would have to be 1000m or more. Any measurement made by a TM30 under the range that the arc length of either a ½” or 1” will be at ±1mm within the max 100m range. 0.5” of arc @ 100m = 0.24mm, 1” of arc @ 100m = 0.48mm Over 100m, the angular component takes over the accuracy of the instrument with measurement unit becoming defined by angular spread, for the 0.5” instrument this is at 421.550m, for the 1” instrument this would be at 206.275m. Thus even if a reference prism were installed beyond the maximum 100m range, if it was within 206.275m it would still be a position defined within 1mm by the system.
| 01CV - Civils | Cxxx-NCR-000489 | NCR | Replacement of Royal Victoria RTS (VDP) |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2012-02-09 | 2012-04-03 17:08 | 54 | 2012-01-12 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Repair |  | Complete |  | Completed |  | A fault has been reported with this Total Station (361482). It has been removed to be investigated and a replacement Total Station (SN: 362926 ) was installed on 12/01/2012.
| 01CV - Civils | Cxxx-NCR-000492 | NCR | Disused Thameslink RTS 6G Failure/Replacement |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2012-01-31 | 2012-04-24 08:17 | 84 | 2012-01-17 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Repair |  | Complete |  | Completed |  | RTS 6G is not currently undertaking any montioring as a result fo the instrument being in -99960 error and being locked up.
| 01CV - Civils | Cxxx-NCR-000493 | NCR | Moorgate Met RTS14 & 15 -99960 error code |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2012-01-31 | 2012-04-05 07:02 | 65 | 2012-01-17 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Repair |  | Complete |  | Completed |  | Monitoring had ceased around these RTS location due to RTS breakdown
| 01CV - Civils | Cxxx-NCR-000495 | NCR | Replacement of Whitechapel LO RTS 11 |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2012-02-14 | 2012-04-05 07:04 | 51 | 2012-01-17 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Repair |  | Complete |  | Completed |  | A fault has been reported with this Total Station (362668). It has been removed to be investigated and a replacement Total Station (SN: 362939) was installed on 16/01/2012.
| 01CV - Civils | Cxxx-NCR-000496 | NCR | RTS4 Plumstead Portal |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2012-02-14 | 2012-04-19 12:37 | 65 | 2012-01-17 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Repair |  | Complete |  | Completed |  | RTS 4 was showing an error code of -99960 and monitoring had ceased.
| 01CV - Civils | Cxxx-NCR-000497 | NCR | Pudding Mill Lane RL9 (AT10009) |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2012-01-31 | 2012-04-19 10:37 | 79 | 2012-01-17 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Repair |  | Complete |  | Completed |  | A fault was reported with this instrument
| 01CV - Civils | Cxxx-NCR-000501 | NCR | RTS Replacement, AT10005 at Pudding Mill Lane (River Lea RTS 5) |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2012-02-06 | 2012-04-19 10:36 | 73 | 2012-01-23 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Repair |  | Complete |  | Completed |  | This instrument reported a fault and ceased to function correctly.
| 01CV - Civils | Cxxx-NCR-000504 | NCR | RTS 4 at Plumstead |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2012-02-25 | 2012-04-19 12:51 | 54 | 2012-01-25 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Repair |  | Complete |  | Completed |  | RTS4 is showing error -99960 and monitoring of track by this instrument has ceased.
| 01CV - Civils | Cxxx-NCR-000506 | NCR | Paddington D&C ATS03 -99960 error code |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2012-02-09 | 2012-04-24 08:16 | 75 | 2012-01-27 | Surveying - Instrumentation and Monitoring | 500 |  |  | Repair |  | Complete |  | Completed |  | This instrument has reported a -99960 fault and needs to be removed and replaced on next available shift.
| 01CV - Civils | Cxxx-NCR-000508 | NCR | PMI017-PLP studs not installed |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2012-02-07 | 2012-07-17 09:57 | 161 | 2012-01-31 | Surveying - Instrumentation and Monitoring | 500 |  | Design | Use As-Is |  | Complete |  | Completed |  | Five PLP studs on Eastbourne Terrace in the area on the attached plan were not installed due to the kerb being replaced at the time of installation.
| 01CV - Civils | Cxxx-NCR-000509 | NCR | Plumstead Portal Replacement of RTS3 |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2012-03-01 | 2012-04-19 10:18 | 49 | 2012-01-31 | Surveying - Instrumentation and Monitoring | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | The instrument concerned was bouncing in and out of -99960 error, causing distruption to monitoring.
| 01CV - Civils | Cxxx-NCR-000523 | NCR | Pudding Mill Lane RTS AT10007 (River lea 7) |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2012-02-21 | 2012-04-19 10:18 | 58 | 2012-02-07 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Repair |  | Complete |  | Completed |  | This instrument (361154) reported a fault and has subsequently been replaced by another __ TM30, SN # 361999 whilst this is investigated.
| 01CV - Civils | Cxxx-NCR-000525 | NCR | RTS 23 + 26 Moorgate Met |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2012-03-08 | 2012-04-05 07:17 | 28 | 2012-02-08 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Repair |  | Complete |  | Completed |  | Following a power outage RTS23 and RTS26 have developed a -99960 error
| 01CV - Civils | Cxxx-NCR-000526 | NCR | Moorgate Met Line - RTS14 |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2012-03-20 | 2012-04-19 12:33 | 30 | 2012-02-08 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Repair |  | Complete |  | Completed |  | RTS14 (serial number 362816) is currently displaying a -99960 error
| 01CV - Civils | Cxxx-NCR-000538 | NCR | Moorgate Northern Line rts 40002 |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2012-03-07 | 2012-04-19 10:13 | 43 | 2012-02-22 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Repair |  | Complete |  | Completed |  | The Instrument displayed a fault (-99960 error) and was replaced with serial number 362930 on 20/02/12.
| 01CV - Civils | Cxxx-NCR-000539 | NCR | Replacement of RTS 4C (Cxxx-AT00007-CR088) on Hayne Street bridge parapet wall. |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2012-03-03 | 2012-04-19 10:12 | 47 | 2012-02-24 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Repair |  | Complete |  | Completed |  | This instrument has reported a -99955 fault and on inspection needs to be removed and replaced on next available shift.
| 01CV - Civils | Cxxx-NCR-000540 | NCR | RTS3 at Plumstead Portal |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2012-03-12 | 2012-04-05 07:05 | 24 | 2012-02-27 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Repair |  | Complete |  | Completed |  | Instrument is displaying intermittent -99955 error causing disruption to monitoring
| 01CV - Civils | Cxxx-NCR-000541 | NCR | PMI066 - Prism sighting distances |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2012-03-12 | 2012-04-02 16:08 | 21 | 2012-02-28 | Surveying - Instrumentation and Monitoring | 500 |  | Design | Use As-Is |  | Complete |  | Completed |  | Due to line of sight and ATS location limitations in the Paddington Station area, ATS will be required to measure distances greater than 100m.
| 01CV - Civils | Cxxx-NCR-000542 | NCR | Moorgate Disused Spur - RTS 6A Line of sight distances |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2012-03-14 | 2012-07-25 17:48 | 133 | 2012-02-29 | Surveying - Instrumentation and Monitoring | 500 |  | Design | Use As-Is |  | Complete |  | Completed |  | RTS 6A 9underside of Lindsay Street bridge) is measuring structural monitoring prisms that are located 90m in horizontal distance from the instrument. This non-conforms to the above specification.
| 01CV - Civils | Cxxx-NCR-000544 | NCR | RTS 6A Disused Moorgate Spur - Prisms not sighted |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2012-03-14 | 2012-07-25 21:36 | 133 | 2012-02-29 | Surveying - Instrumentation and Monitoring | 500 |  | Design | Use As-Is |  | Complete |  | Completed |  | On the most eastern array of the northern tunnel (Underside of Lindsay Street bridge, disused tunnels) two prisms located in the first prism transect can not be observed from RTS 6A due to line of sight obstruction and the location of the sensor being too close to the RTS. Sensor Cxxx-RP300153-CR088 (tunnel crown) is unable to be monitored due to its location being within 2.5m of the RTS position. Sensor Cxxx-RP300155-CR088 (low level tunnel wall) is unable to be monitored as the line of sight is obstructed to the prism from the RTS.
| 01CV - Civils | Cxxx-NCR-000546 | NCR | High level prisms above LU IMR building on 'Array 1' Disused Mooregate Spur (Barbican - Farringdon) |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2012-03-14 | 2012-07-25 21:38 | 133 | 2012-02-29 | Surveying - Instrumentation and Monitoring | 500 |  | Design | Use As-Is |  | Complete |  | Completed |  | Due to access/egress restriction and the risk to operatives health and safety, these prisms have not been installed and therefore the horizontal beam is not being monitored.
| 01CV - Civils | Cxxx-NCR-000548 | NCR | RTS2 at Plumstead Portal |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2012-03-15 | 2012-04-12 16:40 | 28 | 2012-03-01 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Repair |  | Complete |  | Completed |  | Instrument is displaying -99960 error causing disruption to monitoring
| 01CV - Civils | Cxxx-NCR-000549 | NCR | Fisher Street LV__ 11 incorrect compression/tension ratio |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2012-03-15 | 2012-04-27 08:24 | 43 | 2012-03-01 | Surveying - Instrumentation and Monitoring | 500 |  | System Defect | Repair |  | Complete |  | Completed |  | It has now been confirmed that LV__ 11 is measuring tension/compression in reverse when compared to other installed instrument.
| 01CV - Civils | Cxxx-NCR-000552 | NCR | PMI11 - Prisms cannot be read by ATS |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2012-03-19 | 2012-07-26 12:50 | 129 | 2012-03-05 | Surveying - Instrumentation and Monitoring | 500 |  | Design | Rework |  | Complete |  | Completed |  | The following prisms cannot be read by the installed ATS due to the ATS cover obstructing the view; - 20116, 20118, 20119 - 20216, 20217, 20223, 20225, 20226 - 20311, 20313, 20314, 20316 - 20319.
| 01CV - Civils | Cxxx-NCR-000556 | NCR | ATS 05 Error Loop |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2012-03-23 | 2012-07-23 17:26 | 122 | 2012-03-09 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Use As-Is |  | Complete |  | Completed |  | PAD DC ATS 05 was stuck in an error loop after an incorrect compensator reading. This problem has been rectified and the RTS has been reading correctly.
| 01CV - Civils | Cxxx-NCR-000558 | NCR | ATS 01 Connection Failure |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2012-03-26 | 2012-07-23 17:52 | 119 | 2012-03-12 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Use As-Is |  | Complete |  | Completed |  | Cannot connect to ATS 01 via IP or Dial-up.
| 01CV - Civils | Cxxx-NCR-000559 | NCR | PMI069 - Line of sight to two PLP studs on 2 Eastbourne Terrace |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2012-03-23 | 2012-07-19 10:39 | 118 | 2012-03-12 | Surveying - Instrumentation and Monitoring | 500 |  | Design | Use As-Is |  | Complete |  | Completed |  | Two PLP studs have not been installed on 2 Eastbourne Terrace in the locations indicated on the attached image. Installing the PLPs at the base of the building would not allow line of sight from a levelling instrument. Line of sight would also be limited if barcode scales were installed at a higher level.
| 01CV - Civils | Cxxx-NCR-000563 | NCR | Cable Compliance |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2012-03-23 | 2012-06-06 13:17 | 75 | 2012-03-19 | Surveying - Instrumentation and Monitoring | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Communications cable 2403PTMFH, Power Cable LF-329 and Signal Cable LF-316. Have not meet compliance standards detailed in LU1-085
| 01CV - Civils | Cxxx-NCR-000565 | NCR | Pudding Mill Lane - Fault with AT10003 |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2012-04-02 | 2012-04-24 07:37 | 22 | 2012-03-19 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Repair |  | Complete |  | Completed |  | This instrument has intermittently been reporting a fault code indicating a mechanical error (99955).
| 01CV - Civils | Cxxx-NCR-000567 | NCR | Farringdon AT60002 Reported Fault |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2012-04-04 | 2012-04-24 07:36 | 20 | 2012-03-21 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Repair |  | Complete |  | Completed |  | This instrument has reported a fault and is currently not operating.
| 01CV - Civils | Cxxx-NCR-000577 | NCR | RTS23 Moorgate Met |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2012-05-04 | 2012-04-27 07:55 | -7 | 2012-04-04 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Repair |  | Complete |  | Completed |  | RTS23 ( serial number 361748) is displaying -99960 error and has ceased working.
| 01CV - Civils | Cxxx-NCR-000597 | NCR | Referencing Instruments to Points Outside the Zone of Influence |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2012-05-15 | 2012-07-27 15:21 | 73 | 2012-05-01 | Surveying - Instrumentation and Monitoring | 500 |  | System Defect | Rework |  | Complete |  | Completed |  | Automatic Total Stations positions monitoring the 3rd party assets are not related to stable datum reference targets, located outside the Zone of Influence of the works shown on the I&M drawings on various sites. In some areas the reference targets outside the Zone of Influence are physically installed, but the Total Stations do not relate their positions to the targets when the monitoring readings are taken and processed. This applies to the following sites: Liverpool Street Met Line Liverpool Street Moorgate Liverpool Street Moorgate Northern Line Whitechapel LO Whitechapel LU Farringdon Farringdon (Barbican) Paddington D&C
| 01CV - Civils | Cxxx-NCR-000598 | NCR | Replacement of Whitechapel H&C RTS 5 |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2012-06-06 | 2012-07-06 09:37 | 30 | 2012-05-02 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Rework |  | Complete |  | Completed |  | A fault has been reported with this Total Station (362608). It has been removed to be investigated and a replacement Total Station (SN: 362728) was installed on 30/04/2012.
| 01CV - Civils | Cxxx-NCR-000604 | NCR | Plumstead Portal RTS1 |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2012-06-14 | 2012-07-23 17:21 | 39 | 2012-05-14 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Rework |  | Complete |  | Completed |  | The instrument ( 361941) is displaying a -99960 eror and monitoring has ceased
| 01CV - Civils | Cxxx-NCR-000605 | NCR | RTS 4 Plumstead |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2012-06-14 | 2012-07-06 09:35 | 22 | 2012-05-14 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Rework |  | Complete |  | Completed |  | Instrument (362665) is displaying a -99957 error and monitoring has ceased
| 01CV - Civils | Cxxx-NCR-000611 | NCR | Replacement of DLR Limmo Shaft RTS 7 |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2012-06-19 | 2012-07-06 09:33 | 17 | 2012-05-22 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Rework |  | Complete |  | Completed |  | A fault has been reported with this Total Station (362629). It has been removed to be investigated and a replacement Total Station (SN: 363070) was installed on 09/05/2012.
| 01CV - Civils | Cxxx-NCR-000612 | NCR | Replacement of DLR Limmo Shaft RTS 7 |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2012-06-19 | 2012-07-06 09:20 | 17 | 2012-05-22 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Rework |  | Complete |  | Completed |  | A fault has been reported with this Total Station (363070). It has been removed to be investigated and a replacement Total Station (SN: 362215) was installed on 21/05/2012.
| 01CV - Civils | Cxxx-NCR-000613 | NCR | Replacement of Whitechapel H&C RTS 12 |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2012-06-19 | 2012-07-06 09:08 | 17 | 2012-05-22 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Rework |  | Complete |  | Completed |  | A fault has been reported with this Total Station (362010). It has been removed to be investigated and a replacement Total Station (SN: 361251) was installed on 08/05/2012.
| 01CV - Civils | Cxxx-NCR-000618 | NCR | Calibration of Total Stations |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2013-05-31 | 2013-05-31 14:39 | 0 | 2012-06-01 | Surveying - Instrumentation and Monitoring | 500 |  |  | Repair |  | Complete |  | Completed |  | Random review of calibration dates of Automatic Total Station installed at PML and PAD D&C show some instruments out of calibration date as follows: Pudding Mill Lane: 1- Cxxx-AT10010-CR094-SN 361754-Next Calibration Date 21/12/11 2- Cxxx-AT20001-CR094-SN 361774-Next Calibration Date 08/12/11 3- Cxxx-AT20002-CR094-SN 361487-Next Calibration Date 16/11/11 4- Cxxx-AT20003-CR094-SN 361775-Next Calibration Date 03/12/11 Paddington D&C: 1- RTS03- SN361977- Next Calibration Date 21/02/12 2- RTS04- SN362188- Next Calibration Date 10/05/12 3- RTS05- SN361759- Next Calibration Date 21/012/11 4- RTS06- SN362207- Next Calibration Date 09/05/12
| 01CV - Civils | Cxxx-NCR-000621 | NCR | UCIMS generated e-mails have non-standard e-mail header |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2012-06-15 | 2012-06-25 11:36 | 10 | 2012-06-14 | Systems - Software Engineering | 500 |  | System Defect | Rework |  | Complete |  | Completed |  | Currently headers of e-mails generated by UCIMS contain extra carriage returns between "MIME-Version:", "Content-type:" and "From:" fields. As carriage return is used as delimiter spam filters and e-mail clients that strictly follow RFC 2045 standard assume that after first extra carriage return body of e-mail follows thus causing spam filter to miss crucial header information and treat UCIMS e-mails as spam.
| 01CV - Civils | Cxxx-NCR-000622 | NCR | Calibration of Total Stations |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2013-05-31 | 2013-05-31 13:07 | 0 | 2012-06-15 | Surveying - Instrumentation and Monitoring | 500 |  |  | Repair |  | Complete |  | Completed |  | Automatic Total Station installed are out of calibration date as per the attached sheet.
| 01CV - Civils | Cxxx-NCR-000629 | NCR | Replacement of DLR Limmo Shaft RTS 12 |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2012-07-27 | 2012-07-17 10:50 | -10 | 2012-06-28 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Rework |  | Complete |  | Completed |  | A fault has been reported with this Total Station (361310). It has been removed to be investigated and a replacement Total Station (SN: 362808) was installed on 26/06/2012.
| 01CV - Civils | Cxxx-NCR-000646 | NCR | Replacement of VDP RTS 11 |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2012-08-06 | 2012-07-25 13:49 | -12 | 2012-07-09 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Rework |  | Complete |  | Completed |  | A 99960 fault has been reported with this Total Station (362822). It has been removed to be investigated and a replacement Total Station (SN: 363099) was installed on 05/07/2012.
| 01CV - Civils | Cxxx-NCR-000647 | NCR | PML River Lea - Fault with AT10008 |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2012-07-26 | 2012-07-25 13:05 | -1 | 2012-07-12 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Rework |  | Complete |  | Completed |  | RTS reported 99960 and 99963 error codes. The instrument was replaced on the night of 10/07/12 with another TM30, SN # 361136 (calibration certificate attached).
| 01CV - Civils | Cxxx-NCR-000649 | NCR | Whitechapel Above Ground Monitoring - Change in location of PLPs at Kempton Court. |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2012-07-30 | 2012-07-18 07:25 | -12 | 2012-07-16 | Geotechnical Engineering - Geotechnical Monitoring | 500 |  | Design | Use As-Is |  | Complete |  | Completed |  | PLPs 34107, 34108, 34109, 34110, 34111 and 34112 have been moved to the closest suitable location to the original. However this distance exceeds the suggested 1m.
| 01CV - Civils | Cxxx-NCR-000678 | NCR | RTS 23 at Moorgate |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2012-09-28 | 2012-12-21 16:09 | 84 | 2012-08-28 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Repair |  | Complete |  | Completed |  | Instrument (363065) is displaying a -99955 error and monitoring has ceased. It was removed for maintenance and a replacement instrument (362629) was installed upon 15/08/2012.
| 01CV - Civils | Cxxx-NCR-000695 | NCR | Instrument Replacement (AT10004) |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2012-09-26 | 2013-02-07 15:11 | 134 | 2012-09-12 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Repair |  | Complete |  | Completed |  | Instrument AT10004 (SN# 361743) reported a 99955 error code on 29/09/12 and ceased operation
| 01CV - Civils | Cxxx-NCR-000696 | NCR | Oxford Circus - Victoria Line - Multiplexor Failure |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2012-09-27 | 2013-02-13 09:39 | 139 | 2012-09-13 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Repair |  | Complete |  | Completed |  | Equipment failure.
| 01CV - Civils | Cxxx-NCR-000697 | NCR | Fault with Whitechapel H&C RTS 13 |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2012-10-05 | 2012-12-21 16:14 | 77 | 2012-09-14 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Repair |  | Complete |  | Completed |  | RTS reporting 99960 error code.
| 01CV - Civils | Cxxx-NCR-000702 | NCR | RTS Failure AT160009 |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2012-10-04 | 2012-12-21 16:16 | 78 | 2012-09-20 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Repair |  | Complete |  | Completed |  | RTS 9 has reported an error code on 17/09/2012
| 01CV - Civils | Cxxx-NCR-000706 | NCR | Restrictions to the manual monitoring of prisms at Paddington |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2012-10-19 | 2012-11-20 15:09 | 32 | 2012-10-02 | Surveying - Instrumentation and Monitoring | 500 |  | Design | Use As-Is |  | Complete |  | Completed |  | Further to LWW-CRL NCR-Cxxx-00530, under PMI118 __soil were required to manually monitor prisms that could not be read by the automated system. As the prisms were installed to be read by automated systems there were line of sight restrictions and potential differences in results due to prism facing errors. This resulted in a number of prisms not being able to be read. Please refer to UCIMS for prisms that could be manually monitored. Changing conditions on site and access restrictions also hindered the number of prism that could be measured.
| 01CV - Civils | Cxxx-NCR-000714 | NCR | Pre-Installation Surveys |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2013-05-31 | 2013-04-15 12:52 | -46 | 2012-10-04 | Geotechnical Engineering - Geotechnical Monitoring | 500 |  | Planning | Rework |  | Complete |  | Completed |  | This has not been completed for any of the areas under Cxxx remit. For PAD AG, __ have method statement for fixing methods meets the requirement stipulated in the specification. This does not meet this.
| 01CV - Civils | Cxxx-NCR-000719 | NCR | Farringdon 76350-76380 RTS Failure (AT00002) |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2012-02-10 | 2012-12-21 15:06 | 315 | 2012-10-05 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Repair |  | Complete |  | Completed |  | RTS1B (AT00002) has reported an error code since installation on 04/09/12
| 01CV - Civils | Cxxx-NCR-000720 | NCR | PMI069 - Delay to installation of prisms on 19-21 Spring Street and 199 Praed Street |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2012-10-12 | 2013-02-12 17:06 | 123 | 2012-10-05 | Surveying - Instrumentation and Monitoring | 500 |  | Design | Use As-Is |  | Complete |  | Completed |  | Installation of the four prisms detailed in LWW-CRL RFI-Cxxx-00648 (originally designed in Cxxx-OVE-C2-DDJ-CR001_Z-30399) has been delayed due to access restrictions (including developing a safe access method), design changes and the Olympic Embargo. The prisms cannot be installed until the relevant SA__ and OAN are approved which may result in installation not being completed prior to the arrival of the WB TBM inside the zone of influence for these buildings.
| 01CV - Civils | Cxxx-NCR-000728 | NCR | ITP Implementation - Outstanding IRFs |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2013-05-31 | 2013-05-09 08:40 | -22 | 2012-10-18 | Surveying - Instrumentation and Monitoring | 500 |  |  | Reject |  | Complete |  | Completed |  | i) Activities are not scheduled on the ITP; ii) IRFs are not regularly submitted as per requirements above.
| 01CV - Civils | Cxxx-NCR-000729 | NCR | Replacement of Whitechapel H&C RTS 12 |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2012-11-19 | 2012-12-21 15:05 | 32 | 2012-10-22 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Repair |  | Complete |  | Completed |  | A fault has been reported with this Total Station (361251). It has been removed to be investigated and a replacement Total Station (SN: 361749) was installed on 18/09/2012.
| 01CV - Civils | Cxxx-NCR-000730 | NCR | Replacement of Whitechapel H&C RTS 8 |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2012-11-19 | 2013-02-07 15:22 | 80 | 2012-10-22 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Repair |  | Complete |  | Completed |  | A fault has been reported with this Total Station (361767). It has been removed to be investigated and a replacement Total Station (SN: 361152) was installed on 17/10/2012.
| 01CV - Civils | Cxxx-NCR-000731 | NCR | RTS 14 at Moorgate |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2012-11-02 | 2012-12-21 15:03 | 49 | 2012-10-25 | Surveying - Instrumentation and Monitoring | 500 |  |  | Repair |  | Complete |  | Completed |  | Instrument (362816) is displaying a -99960 error and monitoring has ceased. It was removed for maintenance and a replacement instrument (363073) was installed upon 24/10/2012
| 01CV - Civils | Cxxx-NCR-000732 | NCR | RTS 27 at Moorgate |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2012-11-02 | 2012-12-21 15:00 | 49 | 2012-10-25 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Repair |  | Complete |  | Completed |  | Instrument (361118) is displaying a -99957 error and monitoring has ceased. It was removed for maintenance and a replacement instrument (362693) was installed upon 25/10/2012.
| 01CV - Civils | Cxxx-NCR-000735 | NCR | Replacement of Whitechapel LO RTS 11 |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2012-11-27 | 2013-02-07 15:27 | 72 | 2012-10-30 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Repair |  | Complete |  | Completed |  | A fault has been reported with this Total Station (362939). It has been removed to be investigated and a replacement Total Station (SN: 363065) was installed on 25/10/2012.
| 01CV - Civils | Cxxx-NCR-000743 | NCR | Late issue of Inspection Request Form |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2012-11-26 | 2012-12-20 15:17 | 24 | 2012-11-12 | Surveying - Instrumentation and Monitoring | 500 |  | Planning | Use As-Is |  | Complete |  | Completed |  | Failure to issue IRF in time for the inspection. An informal copy was issued via email but without sufficient information.
| 01CV - Civils | Cxxx-NCR-000759 | NCR | Whitechapel LO CW126 Manually Read Tell-tale Crackmeters |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2013-01-04 | 2013-02-14 11:26 | 41 | 2013-01-03 | Surveying - Instrumentation and Monitoring | 500 |  | System Defect | Repair |  | Complete |  | Completed |  | During installation, chemical adhesive has caused a specific part of the 2 No. crackmeters (Cxxx-CK300151 and Cxxx-CK300251) installed on the western abutment/girder interface of girders 1 and 2 to adhere to the iron girder. This specific part should have been free to move. The issue was observed and reported by Crossrail Cxxx to Crossrail Cxxx and __soil.
| 01CV - Civils | Cxxx-NCR-000764 | NCR | Health & Safety Surveillance |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2013-05-31 | 2013-05-09 10:04 | -22 | 2013-01-14 | Geotechnical Engineering - Geotechnical Monitoring | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | CAR 04 Q __requires __ to submit a schedule to CRL for acceptance detailing H&S surveillance visits. __ Quality Manager advised during QFM 6th Dec 2012 the schedule is incorrect in that more surveillances are planned than are intended to be carried out.
| 01CV - Civils | Cxxx-NCR-000765 | NCR | Holborn Station LU/12 Site Start Up IRF Sign-Off |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2013-05-31 | 2013-05-14 09:20 | -17 | 2013-01-14 | Surveying - Instrumentation and Monitoring | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | This procedure was not being followed for Holborn Piccadilly and Central Line sites and an IRF was not received for sign-off.
| 01CV - Civils | Cxxx-NCR-000776 | NCR | Replacement of RTS2 on the Northern Line at Moorgate |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2013-03-20 | 2013-04-10 10:44 | 21 | 2013-02-20 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Repair |  | Complete |  | Completed |  | A fault has been reported with this Total Station (362930). It has been removed to be investigated and a replacement Total Station (SN: 361759) was installed on 19/02/2013.
| 01CV - Civils | Cxxx-NCR-000777 | NCR | Replacement of RTS5 on the Northern Line at Moorgate |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2013-03-20 | 2013-04-10 10:52 | 21 | 2013-02-20 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Repair |  | Complete |  | Completed |  | A fault has been reported with this Total Station (SN: 362667). It has been removed to be investigated and a replacement Total Station (SN: 362203) was installed on 19/02/2013.
| 01CV - Civils | Cxxx-NCR-000778 | NCR | Replacement of RTS1a on the Northern Line at Moorgate |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2013-03-20 | 2013-04-10 10:18 | 21 | 2013-02-22 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Repair |  | Complete |  | Completed |  | A fault has been reported with this Total Station (SN: 361999). It has been removed from site to be investigated and a replacement Total Station (SN: 361487) was installed on 21/02/2013.
| 01CV - Civils | Cxxx-NCR-000780 | NCR | RTS Failure - Barbican AT00008 |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2013-03-11 | 2013-04-10 11:28 | 30 | 2013-02-25 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Repair |  | Complete |  | Completed |  | 99960 error reported since 09/11/12
| 01CV - Civils | Cxxx-NCR-000782 | NCR | Whitechapel LO communications outage |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2013-03-06 | 2013-04-16 14:04 | 41 | 2013-02-26 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Use As-Is |  | Complete |  | Completed |  | Communications outages have prevented data from being uploaded to UCIMS although the sensors are still running. An automated method of resetting the MD485 network has been installed which will attempt to reset the MD485 network without a communications link.
| 01CV - Civils | Cxxx-NCR-000785 | NCR | RTS Failure at Moorgate (GNER) |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2013-03-11 | 2013-04-11 09:52 | 31 | 2013-02-28 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Repair |  | Complete |  | Completed |  | Throughout the monitoring period RTS3 has become faulty, forcing replacement. RTS SN:101431 has been replaced by RTS SN:102081 during Engineering Hours of 18-11-2012.
| 01CV - Civils | Cxxx-NCR-000786 | NCR | RTS Failure at Moorgate (GNER) |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2013-03-11 | 2013-04-11 09:58 | 31 | 2013-02-28 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Repair |  | Complete |  | Completed |  | Throughout the monitoring period RTS0 has become faulty, forcing replacement. RTS SN: 101559 has been replaced by RTS SN:102145 during Engineering Hours of 04-02-2013
| 01CV - Civils | Cxxx-NCR-000788 | NCR | RTS Failure at Moorgate (GNER) |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2012-03-11 | 2013-04-11 10:00 | 396 | 2013-02-28 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Repair |  | Complete |  | Completed |  | Throughout the monitoring period RTS4. has become faulty, forcing replacement. RTS SN:101505 has been replaced by RTS SN:102149 during Engineering Hours of 04-02-2013.
| 01CV - Civils | Cxxx-NCR-000789 | NCR | RTS Failure at Moorgate (GNER) |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2013-03-11 | 2013-04-11 10:03 | 31 | 2013-02-28 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Repair |  | Complete |  | Completed |  | Throughout the monitoring period RTS3 has become faulty, forcing replacement. RTS SN:102081 has been replaced by RTS SN:102061 during Engineering Hours of 07-01-2013.
| 01CV - Civils | Cxxx-NCR-000790 | NCR | RTS Failure at Plumstead |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2013-03-11 | 2013-04-11 10:11 | 31 | 2013-02-28 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Repair |  | Complete |  | Completed |  | Throughout the monitoring period RTS7 has become faulty, forcing replacement. RTS SN:102141 has been replaced by RTS SN:102073 during Engineering Hours of 16/02/2013
| 01CV - Civils | Cxxx-NCR-000792 | NCR | RTS Failure at Plumstead |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2013-03-11 | 2013-04-11 10:13 | 31 | 2013-02-28 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Repair |  | Complete |  | Completed |  | Throughout the monitoring period RTS10 has become faulty, forcing replacement. RTS SN:101994 has been replaced by RTS SN:102273 during Engineering Hours of 26-02-2013.
| 01CV - Civils | Cxxx-NCR-000797 | NCR | Barbican Disused Thameslink RTS Failure |  | Contr | __ | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2013-07-20 | 2013-07-15 16:06 | -5 | 2013-03-12 | Surveying - Instrumentation and Monitoring | 1000 |  | Equipment Breakdown | Repair | 4 (0.5-3k) | Complete |  | Completed |  | 99960 error reported since 01/03/2013
| 01CV - Civils | Cxxx-NCR-000800 | NCR | Moorgate LU Station - Location of Wireless Tiltmeter - Trip hazard |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2013-03-15 | 2013-04-16 14:09 | 32 | 2013-03-11 | Surveying - Instrumentation and Monitoring | 500 |  | Design | Rework |  | Complete |  | Completed |  | One of the tiltmeters (highlighted on the attached I&M plan Cxxx-OVE-C2-DDA-CR001_Z-31143) has been installed on the floor instead of at height on the wall. While the sensor is installed in the corner (so that trip hazard is reduced), the current installation still poses an unacceptable level of risk to the public.
| 01CV - Civils | Cxxx-NCR-000813 | NCR | RTS Failure at Moorgate (GNER) |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2013-04-24 | 2013-05-02 13:50 | 8 | 2013-03-25 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Repair |  | Complete |  | Completed |  | RTS04 (SN:102149) on the GNER at Moorgate has failed and was removed from the site on 24-03-2013 for inspection. The instrument was replaced with a new RTS (SN: 101458).
| 01CV - Civils | Cxxx-NCR-000814 | NCR | RTS Failure at Plumstead |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2013-04-26 | 2013-05-02 14:20 | 6 | 2013-03-26 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Repair |  | Complete |  | Completed |  | RTS10 (SN: 102273) on the North __ Line at Plumstead has failed and was removed from site on 25-03-2013 for inspection. The instrument was replaced with a new RTS (SN: 101431).
| 01CV - Civils | Cxxx-NCR-000815 | NCR | RTS Failure at Limmo Shaft |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2013-05-31 | 2013-05-13 16:39 | -18 | 2013-03-28 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Repair |  | Complete |  | Completed |  | RTS07 (SN: 362215) on the DLR at Limmo Shaft has failed and was removed from site on 27-03-2013 for inspection. The instrument was replaced with a new RTS (SN:362930).
| 01CV - Civils | Cxxx-NCR-000818 | NCR | RTS Failure at Moorgate (NL) |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2013-05-31 | 2013-05-13 17:04 | -18 | 2013-04-05 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Repair |  | Complete |  | Completed |  | RTS1B (SN:362214) on the Northern Line at Moorgate has failed and was removed from site on 04-04-2013 for inspection. The instrument was replaced with a new RTS (SN:362762)
| 01CV - Civils | Cxxx-NCR-000819 | NCR | RTS Failure at Moorgate (Metropolitan Line) |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2013-05-31 | 2013-05-31 15:44 | 0 | 2013-04-10 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Repair |  | Complete |  | Completed |  | RTS1B (SN:362274) on the MetropolitanLine at Moorgate has failed and was removed from site on 09-04-2013 for inspection. The instrument was replaced with a new RTS (SN:361152). A certificate of conformance is attached for the new RTS.
| 01CV - Civils | Cxxx-NCR-000820 | NCR | RTS Failure at Moorgate (Metropolitan Line) |  | Contr | __ | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2013-07-20 | 2013-07-17 15:42 | -3 | 2013-04-12 | Surveying - Instrumentation and Monitoring | 1000 |  | Equipment Breakdown | Repair | 4 (0.5-3k) | Complete |  | Completed |  | RTS24 (SN: 361760) on the Metropolitan Line at Moorgate has failed and was removed from site on 21-03-2013 for inspection. The instrument was replaced with a new RTS (SN:361751)
| 01CV - Civils | Cxxx-NCR-000825 | NCR | RTS Failure at Canning Town (Limmo Shaft) |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2013-07-20 | 2013-06-25 13:38 | -25 | 2013-04-19 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Repair |  | Complete |  | Completed |  | RTS5 at Limmo Shaft has beecome faulty, forcing a replacement. RTS SN: 362664 was removed from site during engineering hours of 18-04-2013 for inspection, and replaced by a new RTS SN: 362000
| 01CV - Civils | Cxxx-NCR-000826 | NCR | RTS Failure at Whitechapel (Hammersmith & City Line) |  | Contr | __ | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2013-07-20 | 2013-07-15 16:24 | -5 | 2013-04-24 | Surveying - Instrumentation and Monitoring | 1000 |  | Equipment Breakdown | Repair | 4 (0.5-3k) | Complete |  | Completed |  | RTS11 at Whitechapel has become faulty, forcing a replacement. RTS 11 SN: 361447 developed a -99960 error on 20-04-2013 and was removed from site during engineering hours of 23-04-2013 for inspection. A new RTS (SN: 361741) has been installed as a replacement.
| 01CV - Civils | Cxxx-NCR-000837 | NCR | RTS Movement tracker |  | Contr |  | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2013-06-08 | 2013-06-07 14:45 | -1 | 2013-05-08 | Surveying - Instrumentation and Monitoring | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed |  | CRL are unable to track the location of RTS's at all times.
| 01CV - Civils | Cxxx-NCR-000838 | NCR | __ failure and preventive action implementation |  | Crossrail | PDP | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2013-06-07 | 2013-07-24 09:48 | 47 | 2013-05-08 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Repair | 4 (0.5-3k) | Complete |  | Completed |  | The __ RTS's have been identified as suffering excessive wear of the EDM shutter motor gearing resulting, partly from internal gearing component quality below the required design life and a command sequence which may keep the shutter motor operating for extended periods of time.
| 01CV - Civils | Cxxx-NCR-000841 | NCR | Monitoring Scheme not fully achievable to the south of Rounton Road at Eleanor Street District Line |  | Contr | __ | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2013-07-04 | 2013-08-09 15:14 | 36 | 2013-06-20 | Surveying - Instrumentation and Monitoring | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | The current monitoring scheme will not be achievable on the west side of the LU viaduct structure south of Rounton Road. There is an industrial unit here that blocks the bridge arches, and the parapet is not present on track to be monitored by track RTS, as per the attached image.
| 01CV - Civils | Cxxx-NCR-000031 | NCR | Inconsistency between Cxxx Design Assurance and materials supplied |  | Crossrail | PDP | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2014-10-13 | 2014-10-10 15:01 | -3 | 2014-08-18 11:56 | Surveying - Instrumentation and Monitoring | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The Cxxx Design Assurance document Cxxx-SOL-O-RGN-CRG03-50001 rev 1.0, states on page 1 under 'Assumptions' 'It is assumed that all of the metal box sections are steel as the worst case scenario' however the mounting plates and brackets supplied by __ are Aluminium. Either the design Assurance document must be revised to correct the assumptions made or the brackets must be changed. Please correct urgently within the close out date or before as this has the potential to delay and disrupt the installation programme at Barbican to Moorgate.
| 01CV - Civils | Cxxx-NCR-000032 | NCR | Deviation from approved LUL space allocation |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2014-10-22 | 2014-10-15 09:07 | -7 | 2014-10-08 16:56 | Surveying - Instrumentation and Monitoring | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | Whilst carrying out works on the Barbican – Moorgate installation, it was identified (prior to installation) that the approved Space Allocation did not include for all the equipment __ intended to install. The equipment in question was a number of 150 x 150 x 70mm junction boxes to house T-joints in a power cable. In addition, minor inaccuracies were found within dimensions stated for items within the approved Space Allocation.
| 01CV - Civils | Cxxx-NCR-000033 | NCR | Incorrect information contained within the approved Method Statement documentation |  | Contr | SOL | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2014-10-22 | 2014-10-10 16:32 | -12 | 2014-10-08 16:42 | Surveying - Instrumentation and Monitoring | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | Whilst intending to install a 240V monitoring system within Barbican to Moorgate running tunnel, an incorrect reference was made within the approved Method Statement ref: Cxxx-SOL-O1-GMS-CR088-50001 Rev 02. This method statement made reference to 48V.
| 01CV - Civils | Cxxx-NCR-000035 | NCR | COSHH Assessments |  | Crossrail | PDP | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2016-05-02 | 2016-07-04 12:23 | 63 | 2016-04-18 11:01 | Health & Safety General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The quality of the COSHH Assessments (as required) appended to the Method Statement/WPP is not acceptable. __ are self certifying with respect to quality, however a sample checked by CRL on the COSHH assessments has revealed several discrepancies. This has been raised formally through comment sheets against the document in eB, however despite many meetings/discussions/re-submissions the COSHH sheets still remain inaccurate and not representative of the manufacturers data sheet. These inaccuracies are not acceptable and prevent the approval of the method statement/WPP as a whole.
| 04UL - Utilities and Logistics | Cxxx-NCR-000004 | NCR | Testing Cxxx NCR |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2014-02-18 | 2014-02-04 09:19 | -14 | 2014-02-04 09:10 | Shafts - Shafts General | 0 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Testing Cxxx NCR
| 04UL - Utilities and Logistics | Cxxx-NCR-000004 | NCR | Testing C740 NCR |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Projectwide) |  | 2014-02-18 | 2014-02-04 09:56 | -14 | 2014-02-04 09:53 | Mechanical - Escalators | 0 |  | Equipment Breakdown | Repair | 4 (0.5-3k) | Complete | Design Problem - NCR excessive closure due to design issue | Completed |  | TEST
| 04UL - Utilities and Logistics | Cxxx-NCR-000001 | NCR | Provision of H&S Inspection Schedule |  | Contr |  | WAL - Wallasea Island (Projectwide) |  | 2011-09-20 | 2012-07-18 15:37 | 302 | 2011-09-16 | Construction Health & Safety - Construction Health & Safety General | 500 |  | Supervision/Management | Reject |  | Complete |  | Completed |  | The Contractor has been asked to provide a schedule of inspections relating to Health & Safety tours and random D & A testing. This has been asked for many times and was formally recorded in the minutes relating to document number Cxxx-XRL-R5-MRC-CRG03-50005 with an action on Cxxx to provide said by 2 September 2011. To date no such schedule has been received.
| 04UL - Utilities and Logistics | Cxxx-NCR-000002 | NCR | Process for completions certification at worksite groups |  | Contr |  | WAL - Wallasea Island (Projectwide) |  | 2011-09-26 | 2012-09-10 10:29 | 350 | 2011-09-20 | Construction Health & Safety - Construction Health & Safety General | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | Completions Certification documents need compiled by RJ and submitted one week after completion to GS and PFEs for review and acceptance. H & S files and Completions certificates are to be closed out for the Farringdon and Liverpool Street work sites initially.
| 01CV - Civils | Cxxx-NCR-000058 | NCR | Material Procurement Shedule & Reports |  | Contr |  | WAL - Wallasea Island (Projectwide) |  | 2012-01-13 | 2012-03-29 18:04 | 76 | 2011-11-28 | Consents - Planning and Heritage | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | A list of material suppliers has been submitted, however this does not comply with Crossrail procedures on material management, as it was not submitted prior to the procurement of any of the materials. Therefore no materials are currently accepted by the PM as acceptable for implememtation.
| 01CV - Civils | Cxxx-NCR-000069 | NCR | Inspection and Approvals |  | Contr |  | WAL - Wallasea Island (Projectwide) |  | 2012-06-04 | 2012-08-14 10:14 | 71 | 2012-05-21 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | The contractor has failed to provide requests for inspection, and quality sign off sheets in accordance with BM, CRL and relevent test and inspection plans in association with conveyor and electrical works.
| 01CV - Civils | Cxxx-NCR-000070 | NCR | Small Craft Pontoon Damage |  | Contr |  | WAL - Wallasea Island (Projectwide) |  | 2012-12-07 | 2013-05-02 10:00 | 146 | 2012-11-30 | Civil - Hydraulic Engineering | 500 |  | Damaged | Rework |  | Complete |  | Completed |  | The connection detail that connects the small craft pontoon to pontoon A has been damaged. The differential movement caused by waves between the small craft pontoon and the main pontoon has not been allowed for in the connection detail design. Urgent action is needed to remedy this problem. The same damage will inevitably occur on the other small craft pontoon too. Therefore the connection details on both small craft pontoons need redesign and installation. Also, the kee-klamp handrail to the small craft pontoons are starting to come apart.
| 01CV - Civils | Cxxx-NCR-000071 | NCR | Manoeuvering light on pontoon |  | Contr |  | WAL - Wallasea Island (Projectwide) |  | 2012-12-06 | 2013-01-09 12:18 | 34 | 2012-11-30 | Electrical - Lighting | 500 |  | Equipment Breakdown | Repair |  | Complete |  | Completed |  | The pontoon manoeuvring light at Wallasea continues to malfunction. The SIM card was reactivated and about three weeks ago ceased to function again with the same symptom - engaged. Please rectify this problem asap. We now have an official complaint from __, Crouch Harbour Authority (CHA).
| 01CV - Civils | Cxxx-NCR-000072 | NCR | Fire Hydrant Pump to pontoons |  | Contr |  | WAL - Wallasea Island (Projectwide) |  | 2013-06-28 | 2013-05-02 10:02 | -57 | 2012-12-05 | Mechanical - Pumps | 500 |  | System Defect | Repair |  | Complete |  | Completed |  | Faulty Pump.
| 01CV - Civils | Cxxx-NCR-000009 | NCR | Water supply pipework at __S |  | Contr |  | WAL - Wallasea Island (Projectwide) |  | 2012-04-27 | 2012-05-17 17:42 | 20 | 2012-05-15 | Utilities Engineering - Water | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | Engineer took off materials and completed the requisition. Purchasing arranged the order. Both parties missed the note on the quote regarding the pipe work. Pipe was purchased and laid 25 March. Error noticed when arranging pressure testing and chlorination.
| 01CV - Civils | Cxxx-NCR-000012 | NCR | Holding down bolts- Not cast in. Post fix |  | Contr |  | WAL - Wallasea Island (Projectwide) |  | 2012-05-22 | 2012-08-20 12:59 | 90 | 2012-05-23 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | On constructing the base an error was made and drawing incorrectly read. Cross reference was not made to __ drawings and 15 secondary bolts were not cast in
| 01CV - Civils | Cxxx-NCR-000013 | NCR | Base C bar mk 01 incorrectly detailed |  | Contr |  | WAL - Wallasea Island (Projectwide) |  | 2012-04-30 | 2012-08-30 15:07 | 122 | 2012-05-23 | Civil - Structural Engineering | 500 |  | Design | Use As-Is |  | Complete |  | Completed |  | Bar mark 01 incorrectly scheduled. The size had been copied from base B that was 500 thick overall while Base C is 400 thick overall
| 01CV - Civils | Cxxx-NCR-000035 | NCR | Temporary concrete pavement to soil tipping area |  | Contr |  | WAL - Wallasea Island (Projectwide) |  | 2012-08-20 | 2012-08-30 14:51 | 10 | 2012-08-06 | Civil - Concrete Pavement | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | On checking concrete test results it wa noted that a small number of results were marginaly lower than 35N/mm2.
| 01CV - Civils | Cxxx-NCR-000055 | NCR | Unsuitable material being shipped to Wallasea Island |  | Crossrail | XRL | WAL - Wallasea Island (Projectwide) |  | 2013-08-06 | 2013-07-30 17:39 | -7 | 2012-09-13 | Environmental - Waste & Material Management | 0 |  | Material | Rework | 4 (0.5-3k) | Complete |  | Completed
| 01CV - Civils | Cxxx-NCR-000056 | NCR | Sizers on Pontoon A and Pontoon B, performance. |  | Contr |  | WAL - Wallasea Island (Projectwide) |  | 2012-09-20 | 2012-10-18 13:38 | 28 | 2012-09-13 | Mechanical - Mechanical Engineering General | 500 |  | Design | Rework |  | Complete |  | Completed
| 01CV - Civils | Cxxx-NCR-000057 | NCR | Embankment Fill |  | Contr |  | WAL - Wallasea Island (Projectwide) |  | 2012-10-04 | 2012-10-04 08:51 | 0 | 2012-09-27 | Civil - Fill | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Prior to works commencing a series of xx trial holes have been completed to check that the material conforms to the specification requirements. An initial set of 8 holes was dug on the 20 July and a further set of 4 on the 30 August. The results indicate that the borrow materials do not conform to the specification requirements. Please advise your requirements with regard to this material and the embankment construction.
| 01CV - Civils | Cxxx-NCR-000061 | NCR | Environmental Risk Assessment |  | Contr |  | WAL - Wallasea Island (Projectwide) |  | 2012-09-26 | 2012-12-12 15:00 | 77 | 2012-09-19 | Environmental - Environmental General | 500 |  |  | Rework |  | Complete |  | Completed
| 01CV - Civils | Cxxx-NCR-000062 | NCR | Cxxx Constructed cable draw pit for MCC1 |  | Contr |  | WAL - Wallasea Island (Projectwide) |  | 2012-10-12 | 2012-11-19 11:15 | 38 | 2012-09-28 | Civil - Utilities Engineering | 500 |  | Design | Rework |  | Complete |  | Completed |  | We have noted on an observation card that the draw pit to MCC1 constructed by Cxxx has standing water within the draw pit. We consider this to be a safety issue. We are not conversant with Cxxx documentation but note that electrical pits are generally constructed with a drain sump or soakaway as an integral part of the base.
| 01CV - Civils | Cxxx-NCR-000063 | NCR | Cxxx Conveyor system |  | Contr |  | WAL - Wallasea Island (Projectwide) |  | 2012-10-12 | 2012-11-19 11:20 | 38 | 2012-09-28 | Civil - Civil Engineering General | 500 |  | System Defect | Rework |  | Complete |  | Completed |  | On wet commssioning the Cxxx system we have noted that a significant number of the belt rollers are falling out from CV1 and CV2. A total of 24 have been counted. This puts un even loads on the system and at the location of cv1 and 2 could injure someone when they fall out. From inspection it appears that the bracket that supports the roller is flexing allowing the roller to drop out.
| 01CV - Civils | Cxxx-NCR-000097 | NCR | CCTV Prrovision |  | Contr |  | WAL - Wallasea Island (Projectwide) |  | 2012-11-07 | 2012-11-30 15:13 | 23 | 2012-10-24 | Communications and Control Systems | 500 |  |  | Repair |  | Complete |  | Completed |  | Not installed
| 01CV - Civils | Cxxx-NCR-000098 | NCR | Electronic card and biometric access control |  | Contr |  | WAL - Wallasea Island (Projectwide) |  | 2012-11-07 | 2013-02-06 11:01 | 91 | 2012-10-24 | Communications and Control Systems | 500 |  |  | Repair |  | Complete |  | Completed |  | Not installed
| 01CV - Civils | Cxxx-NCR-000099 | NCR | Control of vehicles |  | Contr |  | WAL - Wallasea Island (Projectwide) |  | 2012-10-31 | 2012-11-30 15:12 | 30 | 2012-10-24 | Communications and Control Systems | 500 |  |  | Repair |  | Complete |  | Completed
| 01CV - Civils | Cxxx-NCR-000100 | NCR | Assignment Instructions to Manned Guarding Arrangements |  | Contr |  | WAL - Wallasea Island (Projectwide) |  | 2012-10-31 | 2012-11-30 15:10 | 30 | 2012-10-24 | Communications and Control Systems | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed
| 01CV - Civils | Cxxx-NCR-000101 | NCR | Security Manager |  | Contr |  | WAL - Wallasea Island (Projectwide) |  | 2012-10-31 | 2012-11-30 15:01 | 30 | 2012-10-24 | Human Factors - Human Factors General | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed
| 01CV - Civils | Cxxx-NCR-000102 | NCR | Main Entrance Welfare Compound Security |  | Contr |  | WAL - Wallasea Island (Projectwide) |  | 2012-11-07 | 2012-11-30 14:58 | 23 | 2012-10-24 | Communications and Control Systems | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed
| 01CV - Civils | Cxxx-NCR-000106 | NCR | Alcohol Testing |  | Contr |  | WAL - Wallasea Island (Projectwide) |  | 2012-11-19 | 2012-11-27 15:37 | 8 | 2012-11-21 | Construction Health & Safety - Construction Health & Safety General | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | Followinga Joint H&S Advisors review for KPI information a discrepancy in the figures for drugs testing against Alcohol testing was noticed. On investigation it was found that alcohol testing was not in line with the WI requirements due to Cxxx only having one alcohol testing machine available between __S and Wallasea
| 01CV - Civils | Cxxx-NCR-000112 | NCR | Pontoon maintenance |  | Crossrail | XRL | WAL - Wallasea Island (Projectwide) |  | 2013-07-15 | 2013-07-30 16:36 | 15 | 2012-11-30 | Civil - Civil Engineering General | 0 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete |  | Completed |  | Potential long term damage to the pontoon deck. Health and safety issues due to slips, trips and falls.
| 01CV - Civils | Cxxx-NCR-000128 | NCR | Waste Transfer Note |  | Contr |  | WAL - Wallasea Island (Projectwide) |  | 2013-01-30 | 2013-02-07 10:35 | 8 | 2013-01-23 | Environmental - Waste & Material Management | 500 |  | Material | Repair |  | Complete |  | Completed
| 01CV - Civils | Cxxx-NCR-000129 | NCR | Cxxx Northfleet material delivery |  | Crossrail | XRL | WAL - Wallasea Island (Projectwide) |  | 2013-07-29 | 2013-07-30 17:15 | 1 | 2013-01-24 | Civil - Civil Engineering General | 0 |  | System Defect | Rework | 4 (0.5-3k) | Complete |  | Completed
| 01CV - Civils | Cxxx-NCR-000132 | NCR | Pontoon fire hydrant pump adjacent to pontoon A |  | Contr |  | WAL - Wallasea Island (Projectwide) |  | 2013-07-15 | 2013-06-25 15:15 | -20 | 2013-02-01 | Fire - Suppression | 500 |  | System Defect | Repair |  | Complete |  | Completed |  | Faulty Pump.
| 01CV - Civils | Cxxx-NCR-000133 | NCR | Small craft pontoons - cleat connection to pile |  | Contr |  | WAL - Wallasea Island (Projectwide) |  | 2013-07-15 | 2013-06-25 15:20 | -20 | 2013-02-01 | Civil - Civil Engineering General | 500 |  | Design | Rework |  | Complete |  | Completed |  | The cleat connection on the small craft pontoons that connects it to the steel pile is loose allowing excessive movement at the cleat detail. The worry is that during the design life of the pontoon in bad weather they will fail and the connection of the small craft pontoons to the piles will seperate.
| 01CV - Civils | Cxxx-NCR-000138 | NCR | Damage sustained to Wallasea MHE during unloading operations |  | Contr |  | WAL - Wallasea Island (Projectwide) |  | 2013-07-15 | 2013-04-26 13:17 | -80 | 2013-02-08 | Civil - Civil Engineering General | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | During unloading the second delivery of material from Northfleet, (load N2) the MHE at Wallasea has sustained some damage, (pics attached): 1. The roof of CV7 and CV2 has been damaged due to large pieces of material falling back down the conveyor belt and striking CV7 and CV2 roof. Approx. 10 panels. 2. The scraper plates to the crusher/sizer hybrid have become excessively bent requiring replacement. 2 Number. 3. The plastic green clips to the guide rollers along the conveyor route are breaking, causing the guide rollers to move and on one occasion to fall off the frame mount. Approx 25 number, (green clips).
| 01CV - Civils | Cxxx-NCR-000146 | NCR | Embankment A construction |  | Contr |  | WAL - Wallasea Island (Projectwide) |  | 2013-03-29 | 2013-04-26 13:11 | 28 | 2013-03-15 | Civil - Fill | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Due to the issues arising from the use of site won scrape material it was accepted that the clay material exported from __S could be used to construct the embankment. Material had been used to construct a haul road and had compacted and performed well. Preconstruction tests indicated that the material complied with class 2B. Works have commenced and the first set of test results indicate that some of the material classifies as 2C material as only 63 % passes the 2mm seive rather than Table 6/2 requirement for 2A/2B requiring 80-100% passing the 2mm seive.
| 01CV - Civils | Cxxx-NCR-000148 | NCR | Small craft pontoon to Pontoon B |  | Contr |  | WAL - Wallasea Island (Projectwide) |  | 2013-03-28 | 2013-04-26 13:04 | 29 | 2013-03-22 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | On a site visit to the pontoon on the 22nd March, it was noticed that the small craft pontoon to pontoon B was missing. Crossrail had not been informed that it was to be removed.
| 01CV - Civils | Cxxx-NCR-000149 | NCR | Environmental Review of Method Statements |  | Contr |  | WAL - Wallasea Island (Projectwide) |  | 2013-04-01 | 2013-04-30 14:18 | 29 | 2013-03-25 | Environmental - Environmental General | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed |  | Environmental manager to review method statements
| 01CV - Civils | Cxxx-NCR-000151 | NCR | Vessel material collections from Cxxx Northfleet |  | Contr |  | WAL - Wallasea Island (Projectwide) |  | 2013-04-10 | 2013-04-29 16:23 | 19 | 2013-04-09 | Environmental - Waste & Material Management | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed |  | The Contractor has taken by ship Cxxx Northfleet excavated material to a different location to that advised and agreed with Crossrail and Cxxx without any notification / prior communication. Northfleet excavated material was agreed to be sent to the permitted waste transfer site at Ridham Dock (SITA) – however some material was sent to an adjacent facility at Ridham Dock (Brett Aggregates) rather than Ridhan Dock (SITA) leading to the incorrect destination being entered on Waste Transfer Notes. As a consequence of this Cxxx have stopped all ships being loaded until all the correct documentation is in place.
| 01CV - Civils | Cxxx-NCR-000154 | NCR | Use of hydraulic oil over watercourses |  | Contr |  | WAL - Wallasea Island (Projectwide) |  | 2013-05-24 | 2013-05-28 16:24 | 4 | 2013-05-10 | Environmental - Water resources | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed |  | Non biodegradable oil has been used in topping up the hydraulic powerpack used with the luffing conveyor at __S. Correct oil had been ordered however the incorrect oil was delivered. This was not noticed when the delivery was made. In topping up the system this oil was used.
| 01CV - Civils | Cxxx-NCR-000155 | NCR | Embankment A and B construction |  | Contr |  | WAL - Wallasea Island (Projectwide) |  | 2013-06-13 | 2013-06-20 08:22 | 7 | 2013-05-30 | Civil - Fill | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | See Material testing results attached; Below is a summary for each test that indicates a non conformance to the specification. S0102-2A with MCV of 16.3 HSV at ch 920-980 all pass. Use as is S0107-2A with MCV of 16.8 HSV at ch 1100 pases. Use as is. S0119-2A with MCV of 16.36 HSV at ch 1260 passes. Use as is. S0124-2A with MCV of 16.5 HSV at ch 1380 pases. Use as is. S0138-2A with MCV of 17 HSV at ch 600 layer 2 passes. Use as is. S0148-2A with MCV of 17 HSV at ch 1200 layer 2 passes. Use as is. S0172-2A with MCV of 14.5. HSV at ch 2250 passes. Use as is. S0185-2A with MCV of 16.2. Also PL given as 28 with mc of 17 implying it was to dry. HSV at ch 1800 layer 2 is good at 140. Accept and use as is. S0187-2A with MCV 13.8. HSV at embnkmnt B ch200 layer 2 acceptable. Use as is.
| 01CV - Civils | Cxxx-NCR-000161 | NCR | Embankment A construction - Materials |  | Contr |  | WAL - Wallasea Island (Projectwide) |  | 2013-07-02 | 2013-07-03 14:54 | 1 | 2013-06-18 | Civil - Fill | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | See material test results attached that have been loaded to eB. Below is a summary for each test that indicates a non conformance to the specification. S0-197 MCV of 18 however PL and mc appear acceptable, HSV at layer 1 ch 650 all pas at 140+ Use as is. S0-207 MCV of 17 Grades 2A and PL,mc and HSV AT 140 are all acceptable. Use as is. S0-211 MCV of 15.4, PL,mc and HSV at 138 acceptable. Use as is. S0-220 MCV of 18. PL.mc and HSV OF 140 all acceptable. Use as is. S0-226 MCV of 18. PL,mc and HSV of 140 all acceptable. Use as is. S0-230 MCV of 18 PL,mc and HSV OF 140 all acceptable. Use as is. S0-237 MCV of 18. PL excessive and have reverted to __ to check. No visible differences noted when placing and compacting. Use as is. S0-247 MCV of 18. pl,mc and HSV of 140 all acceptable. Use as is. S0-252 MCV of 28. PL,mc.HSV of 130 all acceptable. Use as is. SO-258 MCV of 17.9. PL,mc HSV of 140 all acceptable. Use as is.
| 01CV - Civils | Cxxx-NCR-000162 | NCR | Auto fire alarm to MCC1 room. |  | Crossrail | XRL | WAL - Wallasea Island (Projectwide) |  | 2013-07-29 | 2013-07-31 12:00 | 2 | 2013-07-02 | Fire - Fire Systems & General | 0 |  | Damaged | Repair | 4 (0.5-3k) | Complete |  | Completed |  | The Argus automatic fire system in MCC1 is not working. A report is attached to the effect that due to a surge of power, the control panel has blown and a new panel is required.
| 01CV - Civils | Cxxx-NCR-000166 | NCR | Fire hydrant pump adjacent to pontoon A broken down |  | Crossrail | XRL | WAL - Wallasea Island (Projectwide) |  | 2013-10-17 | 2013-10-21 16:32 | 4 | 2013-08-19 12:15 | Mechanical - Pumps | 500 |  | Equipment Breakdown | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The fire hydrant pump adjacent to pontoon A has broken down. PTR wasnt working at the time of the break down so the incident was instead logged as a Property Damage incident on the RIVO system, (number - 2462128, attached). The pump has been broken down since 12th July 2013 and has to date still not been repaired. There is now no working fire hydrant system on the pontoon as Cxxx never resolved the breakdown of the other fire hydrant which broke down in their defects period.
| 01CV - Civils | Cxxx-NCR-000167 | NCR | Embankment A and B construction |  | Contr | BNV | WAL - Wallasea Island (Projectwide) |  | 2013-09-02 | 2013-09-03 13:51 | 1 | 2013-08-19 17:44 | Civil - Fill | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Refer to material test summary sheet Rev 03 attached that has already been loaded to eB and sent to Crossrail and __. In checking soils test data we have noted some test results that do not conform fully to the material requirements of the specification. This is generally where the MCV is higher than the specification allowance. In reviewing MCV/MC relationship lines with PL we note that materials from both __S and Northfleet generally have high MCV's even though the PL and moisture appear to be inline with requirements. Further when compared to the site won scrape material at the same MC the MCV is considerably higher on the imported material being used in the embankment construction. See Rev 04 results S0423 to SO432 for site won material. Again this indicates where MC is the same as the PL that the MCV is > 12. Some of the reviewed reports are attached for ease of reference. S0264- 2A MCV of 15.4. The material was from __S. HSV results of 120. PL and MC look okay. Propose use as is. S0268 - 2A MCV of 16.5. The material was from __S. HSV result of 140. PL and MC look okay. Propose use as is S0269 - 2A MCV of 14.2. The material was from __S. HSV result of 140. PLand MC look okay. Propose use as is. S0273 - 2B. Please note the material should be classified as 2B and we have contacted __. MCV of 18. HSV result of 140. Propose use as is. S0281-2A. MCV of 18. The material was from __S. HSV result >140. PL and MC look okay. Propose use as is. S0285 -2A. MCV of 14. The material was from __S. HSV result >140. PL and MC look okay but slightly wetter than usual. Propose use as is. S0287 - 2a. MCV of 18. The material was from __S. HSV result >140. PL and MC look okay. Propose use as is. S0290-2A. MCV OF 14. The material was from __S. HSV result >140. PL and MC look okay. Propose use as is. S0295-2A. MCV of 17. The material was a __S Northfleet mix. HSV 90. PL and MC look okay. Propose use as is. S0299-2B. Please note that this material should be classified as 2B and we have contacted __ on this. The material was a __S Northfleet mix. HSV result>140. Material slightly drier than normal. Propose use as is. S0303-2A. MCV of 16. The material was a __S Northfleet mix. HSV >140. PL and MC look okay. Wet due to Northfleet influence. Propose us as is. S0309-2A. MCV 13.4. The material was a __S Northfleet mix. HSV>140. PL and MC look okay. Wet due t Northfleet influence. Propose us as is. S0314-2A. MCV 16. The material was a __S Northfleet mix. MCV >140. PL and MC look okay. Propose use as is. S0319-2A. MCV 13. Material __S Northfleet mix. HSV>66. Material wet due to Northfleet but MCV still high. Compacted okay. No movement in the embankment in next layers. Propose use as is. S0327-2A. MCV 16. Material __S. HSV >140.__S material. PL and MC look okay with MC 2% above PL. MCV still high. Propose use as is. S0330-2A.MCV 18. Material __S. HSV >140. PL and MC look okay but MCV still high. Propose us as is. S0340-2A. MCV 15. Material __S. HSV>140. PL and MC look okay but MCV still high. Propose use as is. S0345-2A. MCV14. Material ex __S. HSV 108. PL is lower than normal with the MC higher in comparison. MCV still high. No sign of movement in the embankment. __ have been asked to check the result. Propose use as is.
| 01CV - Civils | Cxxx-NCR-000168 | NCR | Embankment A and B construction Material testing. |  | Contr | BNV | WAL - Wallasea Island (Projectwide) |  | 2013-09-03 | 2013-09-03 14:07 | 0 | 2013-08-20 18:19 | Civil - Fill | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Refer to test summary sheet 04 attached that has already been uploaded to eB and forwarded to __. In checking data we have noted some results that do not fully conform to the requirements of the specification table 6/1 for material used in the embankment. This is generally that the MCV is higher than the specification allowance althoughthe MC is generally with in acceptable limits of the PL. As noted in NCR 167 the MCV of the imported material is generally higher than the specification or site won clays at the same moisture content. Additional MCV/MC and PL tests will be taken to assist in the valuation of the results. Refer to the additional reports attached to NCR167. S0354 AND S0355. These are __S samples No PL was taken so results need to be compared to results S0326 to S0345. Moisture content of 25 and 22 % would suggest a 2A. There should not be an issue with this material. S0357 - 2A as Northfleet material. MCV of 13. HSV of 51. MC 7% above PL so material would be soft. HSV okay so use as is. S0362-2A. MCV 16. Northfleet __S mix.MC 2% above PL. HSV 80. Use as is. S0364, S0365. __S material but no PL for direct comparison. Moisture in line with other results. HSV >140. Use as is. S0373- 2A. MCV 14. __S material. HSV >140. PL and MC appear okay. Use as is. S0377-2A. MCV18. __S material. HSV 130. MC 2% above PL seems normal. Use as is. S0381-2A. MCV 14. HSV >140. MC and PL appear normal with mc 1% below PL. As HSV acceptable use as is. S0384-2A. MCV 13. HSV >140. MC and PL within 1%. As HSV okay use as is. S0387-2A. MCV13. HSV 100. Northfleet __S mix with high MC indicating wet material. As HSV acceptable use as is. S0394-2A. MCV17. HSV >140. __S material. MC 3% below PL so seems okay. As HSV acceptable use as is. S0399-2a. MCV 17. HSV >140. __S material. MC 4% below PL seems okay. As HSV acceptable use as is. S0404-2A. MCV 17. HSV >140. __S material. MC 5% above PL but okay. As HSV acceptable use as is. S0410-2A. MCV 17. HSV >140. __S material MC 4% below PL okay. As HSV acceptable us as is.
| 01CV - Civils | Cxxx-NCR-000169 | NCR | Conveyor Tower C and D base extension - Concrete Testing |  | Contr | BNV | WAL - Wallasea Island (Projectwide) |  | 2013-09-04 | 2013-09-03 14:33 | -1 | 2013-08-21 10:41 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | 1) Specification clause 4.0 requires 1 cube crushed at 7 day and 2 at 28. The incorrect instruction was given to __. Cubes were crushed ; 1x7 day, 1 x14, 1x28. This error was noted when the certificates were issued so an instruction to crush the spare cube at 56 days was given. Results indicate concrete at 28 days exceeded the required strength of 40n/mm2. See test results attached. 2) The made cubes did not fully conform to the relevant clauses of BS EN 12390.
| 01CV - Civils | Cxxx-NCR-000170 | NCR | Embankment A Construction ch 1000 - 1100 |  | Contr | BNV | WAL - Wallasea Island (Projectwide) |  | 2013-09-24 | 2013-09-25 11:20 | 1 | 2013-08-27 15:55 | Civil - Fill | 500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Lack or improper material identification and traceability | Completed |  | The specification requires the use of class 2 material for the construction of the Embankments. As you are aware imported material, rather than site won material, has been used in construction. On the 20 August 2013 a mixed load of material arrived from __S that included some chalk in the matrix. Coming off the stacker this was not noticed and the material was incorrectly place in the embankment Layer 13 CH 1000 to Ch 1100 insted of going to cell 1 fill.
| 01CV - Civils | Cxxx-NCR-000171 | NCR | Wallasea - Embankment A construction |  | Contr | BNV | WAL - Wallasea Island (Projectwide) |  | 2013-09-18 | 2013-09-13 13:47 | -5 | 2013-09-04 13:23 | Civil - Fill | 0 |  | Material | Rework | 4 (0.5-3k) | Complete |  | Completed |  | For construction of the Embankment Table 6/1 requires the Undrained shear strength of the placed material to be a minimum value of 50kpa. On __ testing on the 4/9/13 we found failures at the following locations. Layer 8 ch 50-80, Layer 9 ch 300-100 Layer 10 ch 430-400 Results were generally in the 40kpa to 50kpa bracket. On inspection material is wet Nothfleet material delivered over the weekend and placed from Saturday and Monday.
| 01CV - Civils | Cxxx-NCR-000172 | NCR | Material Verification Testing |  | Crossrail | XRL | WAL - Wallasea Island (Projectwide) |  | 2013-10-10 | 2013-10-14 15:41 | 4 | 2013-09-24 10:00 | Environmental - Waste & Material Management | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | The Contractor has undertaken their verification testing to date in the ships before arrival at Wallasea, rather than where material has been placed at Wallasea as required in the Works Information (Volume 2C – Drawings & Specifications) (Cxxx-PDP-XWI-CRG003_ES001-50001) and as per the jointly produced Wallasea Island Excavated Material Waste Contingency Action Plan (Cxxx-XRL-R5-STP-CRT00_ES001-50001) agreed with the Environment Agency as a pre-operational condition of the Contractor’s environmental permit for Wallasea. Works Information (Volume 2C – Drawings & Specifications) (Cxxx-PDP-XWI-CRG003_ES001-50001) states in Section 3.4.2 Stage 3 Testing Procedure that ‘The Contractor shall take 3 random samples from an area of no more than 100,000 tonnes placed in the works. Samples will be distributed spatially within the test area to demonstrate any variability and the GPS coordinates of the samples recorded.’ Wallasea Island Excavated Material Waste Contingency Action Plan (Cxxx-XRL-R5-STP-CRT00_ES001-50001) states in Section 2 Waste Contingency Testing ‘Stage 3 Testing – After material has been placed: periodically, at a frequency of no less than every 100,000 tonnes accepted, 3 random samples will be taken and WAC tested to confirm the material is uncontaminated and is the same as that subjected to basic characterisation and meets the requirements of the Environmental Permit. Samples will be distributed spatially within the test area to demonstrate any variability and the GPS coordinated of the samples recorded. All soil samples will be prepared and analysed by a UKAS accredited laboratory using MCERTS performance standards where appropriate (see Figure 3).’ The Waste Contingency Action Plan includes a flow chart that was produced by the Contractor and is titled ‘Stage 3 Testing - After material has been place’ – it clearly shows that the verification testing should have been undertaken of placed material.
| 01CV - Civils | Cxxx-NCR-000173 | NCR | Fire hydrant pump adjacent to pontoon A broken down (Re-raise of NCR 166) |  | Crossrail | XRL | WAL - Wallasea Island (Projectwide) |  | 2014-01-15 | 2013-12-20 09:47 | -26 | 2013-11-15 17:25 | Mechanical - Pumps | 500 |  | Equipment Breakdown | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The fire hydrant pump adjacent to pontoon A has broken down. PTR wasnt working at the time of the break down so the incident was instead logged as a Property Damage incident on the RIVO system, (number - 2462128). The pump has been broken down since 12th July 2013 and has to date still not been repaired. NCR 166 raised to close this out but wasnt resolved. Therefore this NCR has been raised again.
| 01CV - Civils | Cxxx-NCR-000174 | NCR | Wallasea Island - Earthworks materials |  | Contr | BNV | WAL - Wallasea Island (Projectwide) |  | 2013-12-18 | 2013-12-17 08:24 | -1 | 2013-12-04 11:32 | Civil - Fill | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | Earth work materials for Embankment construction; Further to the submission of the Eartworks Testin summary sheet rev 5, already loaded to eB we have noted some results that do not fully conform to the requirements of the specification table 6/1 for materials used in the embankment. As previously noted in NCR 161, 167, 168 there are a number of samples where the MCV exceeds the specification requirements. The results are summarised on the attached spread sheet. The review indicates that moisture contents are generally in line with specification and the HSV results all exceed the specification requirements.
| 01CV - Civils | Cxxx-NCR-000175 | NCR | Wallasea Island - Cell 3 Fill areas |  | Contr | BNV | WAL - Wallasea Island (Projectwide) |  | 2013-12-27 | 2013-12-17 17:21 | -10 | 2013-12-13 12:22 | Civil - Fill | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Supervision - Other | Completed |  | On completing the as built survey of the islands formed as part of the Cell 3 landscaping activities we have found some areas where the completed level is not in accordance with the design model and accepted tolerances. The attached report indicates the areas in question, highlighted in yellow, and the level difference in red.
| 01CV - Civils | Cxxx-NCR-000176 | NCR | RMT TESTING PROCEDURE |  | Contr | BNV | WAL - Wallasea Island (Projectwide) |  | 2014-02-07 | 2014-02-11 16:42 | 4 | 2014-01-17 12:39 | Human Factors - Human Factors General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | The laboratory established at __S to carry out the RMT testing required failed to notify us when an exceedance was noted and failed to quarantine the load for further investigation as detailed in the submitted Excavated Material Plan. The issue was only discovered when the anomaly was noted in the test results loaded to eB where upon an investigation commenced.
| 01CV - Civils | Cxxx-NCR-000177 | NCR | Wallasea Island - Inlet structure Piling Platform |  | Contr | BNV | WAL - Wallasea Island (Projectwide) |  | 2014-05-01 | 2014-06-10 08:41 | 40 | 2014-04-17 13:47 | Civil - Fill | 2000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | 6F5 Crushed concrete not placed and compacted in accordance with the requirements of MSAP164 rev 6.
| 01CV - Civils | Cxxx-NCR-000178 | NCR | Wallasea Island - Stockpiling of Topsoil |  | Contr | BNV | WAL - Wallasea Island (Projectwide) |  | 2014-10-01 | 2014-09-25 09:37 | -6 | 2014-07-04 12:24 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | The topsoil stockpiled adjacent to Ditch 3 has become overgrown with vegetation ; __’s Technical Specification states: “The Specification shall be the Civil Engineering Specification for the Water Industry (CESWI), 6th Edition” : Clause 3.3.2: “topsoil shall be removed from the areas described in the contract and where required for re-use shall be stockpiled separately and kept free from weeds”.
| 01CV - Civils | Cxxx-NCR-000179 | NCR | Wallasea Island - Class 4 Material |  | Contr | BNV | WAL - Wallasea Island (Projectwide) |  | 2014-09-23 | 2014-10-15 10:48 | 22 | 2014-07-04 13:21 | Civil - Fill | 5000 |  | Incomplete Works | Repair | 3 (3-6k) | Complete | Material/Preservation Problems - Not Defined | Completed |  | As described by Cxxx-EWN-00442 & Observations 13885, 13946 & 14008, this NCR relates to the percentage of concrete in the Class 4 fill material deposited in Cell 1 Grid Reference K/17
| 01CV - Civils | Cxxx-NCR-000180 | NCR | Wallasea Island - RTE Outlet Structure (North) Excavation |  | Contr | BNV | WAL - Wallasea Island (Projectwide) |  | 2014-07-21 | 2014-07-28 17:04 | 7 | 2014-07-07 12:45 | Civil - Civil Engineering General | 3000 |  | Software | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | RTE Outlet Structure (North), the excavation to formation was over-dug in the north-east corner by 600mm due to a fault with the GPS equipment
| 01CV - Civils | Cxxx-NCR-000181 | NCR | TWB 048 Slope stability for the RTE outlet structures dig |  | Crossrail | XRL | WAL - Wallasea Island (Projectwide) |  | 2014-07-29 | 2014-07-29 09:24 | 0 | 2014-07-15 12:05 | Civil - Excavation | 0 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Design Check Certificate TWB 048 RTE Outlet Structure North and South Slope Stability makes some statements which are not being adhered to on site. For example: 1. The haul road to the N.Outlet structure is approx. 25m's away from the slope top, not 33m's as illustrated on page 29 in the design certificate. 2. There are no baulk timbers placed around excavation edges as marker barriers to either RTE structure dig as advised on page 6 of the design certificate. 3. The slope sides were originally specified as required to be at 1:1.5. Since excavation of the RTE N.Outlet, the design requirement has increased to a slope gradient of 1:2.5, (are the slopes excavated to this profile?). 4. A site 4x4 vehicle observed driving around the perimeter of the excavation to the Northern Outlet, (see attached pic) possibly inside the minimum 1m distance away from the slope top edge.
| 01CV - Civils | Cxxx-NCR-000182 | NCR | RTE Inlet Structure Reinforced Concrete Base Pour 1 |  | Contr | BAM | WAL - Wallasea Island (Projectwide) |  | 2015-03-31 | 2015-04-08 16:43 | 8 | 2014-07-25 13:31 | Civil - Civil Engineering General | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The poured concrete surface level is non compliant with the tolerance for concrete surfaces stated in Clause 4 of the Civil Engineering Specification for the Water Industry (6th Edition), as shown by the attached as-constructed survey The following points have also been raised following CRL inspection 1. Judging by the __ survey, there areas that are lower than design, by up to 8mm, presumption is these areas will have to be made good, expectation is the proposal is a repair procedure involving some sort of cementitious compound? 2. Discoloured area of the first pour. It may not be a cold joint, but there needs to be some sort of investigation to confirm one way or another. 3. Small amount of honeycombing
| 01CV - Civils | Cxxx-NCR-000183 | NCR | Geotextile exposed edge |  | Contr | BAM | WAL - Wallasea Island (Projectwide) |  | 2015-03-31 | 2015-01-20 10:38 | -70 | 2014-07-25 14:40 | Civil - Civil Engineering General | 1000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | Embanakment B has been removed for RTE southern outlet construction, the geotextile has been severed and not cut cleanly, leaving the correct lap length
| 01CV - Civils | Cxxx-NCR-000185 | NCR | Wallasea Island - Lime Treated Material |  | Contr | BNV | WAL - Wallasea Island (Projectwide) |  | 2014-09-30 | 2014-08-15 16:13 | -46 | 2014-07-29 13:36 | Civil - Fill | 500 |  | Incomplete Works | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Lime Treated Material has been placed in a trial area at Wallasea Island, this material is non compliant with the specification due to the Lime
| 01CV - Civils | Cxxx-NCR-000186 | NCR | Wallasea Island - RTE South Outlet Structure Damaged Geotextile |  | Contr | BNV | WAL - Wallasea Island (Projectwide) |  | 2014-09-23 | 2014-09-25 15:55 | 2 | 2014-08-18 09:21 | Civil - Civil Engineering General | 1000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | RTE South Outlet Structure ; areas of geotextile damaged during piling works,
| 01CV - Civils | Cxxx-NCR-000187 | NCR | Wallasea Island - RTE Inlet Structure Pour 2 |  | Contr | BNV | WAL - Wallasea Island (Projectwide) |  | 2015-03-31 | 2015-04-08 16:49 | 8 | 2014-08-22 13:00 | Civil - Civil Engineering General | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | RTE Inlet Structure : Base Pour No. 2 There is a small area of unsatisfactory surface finish, immediately adjacent to the south wingwall, created by "topping up" a low area of finished concrete during the concrete pour
| 01CV - Civils | Cxxx-NCR-000188 | NCR | Wallasea Island : RTE Inlet Structure Base Pour No. 3 |  | Contr | BNV | WAL - Wallasea Island (Projectwide) |  | 2014-10-31 | 2014-10-31 13:06 | 0 | 2014-08-22 13:08 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | RTE Inlet Structure Base Pour No. 3, post pour inspection has shown a small area of honeycombing to the east elevation of the base
| 01CV - Civils | Cxxx-NCR-000189 | NCR | Wallasea Island : RTE Inlet Structure Reinforced Concrete Base Pour 3 |  | Contr | BNV | WAL - Wallasea Island (Projectwide) |  | 2015-10-06 | 2015-10-09 08:47 | 3 | 2014-09-09 15:07 | Civil - Civil Engineering General | 7500 |  | Material | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | RTE Inlet Structure Reinforced Concrete Base Pour No. 3 We have received early notification of low 28 day cube strengths from site sampling & testing, undertaken by __, of the concrete from RTE Inlet Structure base pour No. 3
| 01CV - Civils | Cxxx-NCR-000190 | NCR | Wallasea Island - RTE Inlet Structure PreCast Concrete Units Minor Defects |  | Contr | BNV | WAL - Wallasea Island (Projectwide) |  | 2014-10-31 | 2014-10-31 13:07 | 0 | 2014-09-10 10:02 | Civil - Civil Engineering General | 4750 |  | Damaged | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | RTE Inlet Structure Minor Defects have been observed during inspections of the Pre-Cast Concrete Units supplied by ABM Precast Solutions, the defects are categorised as follows : 1. Damaged concrete to the corners of the units, as shown by the attached photographs, damage caused during transportation 2. Omitted 25mm x 25mm chamfer to the exposed arrisses of the parapet upstand wall, first 3No. Units delivered to site
| 01CV - Civils | Cxxx-NCR-000191 | NCR | Wallasea Island : RTE Outlet Structure (North) East Headwall Base |  | Contr | BNV | WAL - Wallasea Island (Projectwide) |  | 2014-10-31 | 2014-10-08 15:31 | -23 | 2014-09-17 12:21 | Civil - Civil Engineering General | 1200 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Drawing 60148989/3519/233 (Cxxx-FAB-C-DWG-CRT00_ES001-50033) Revision 04 Note 6 states "All walls to have a minimum 150mm high kicker"; the east headwall base was cast with a 100mm kicker
| 01CV - Civils | Cxxx-NCR-000192 | NCR | Wallasea Island : RTE Inlet Structure Stop Log Fabricated Steelwork |  | Contr | BNV | WAL - Wallasea Island (Projectwide) |  | 2015-07-03 | 2015-08-18 11:44 | 46 | 2014-09-19 14:23 | Civil - Civil Engineering General | 5000 |  | Documentation and Records | Use As-Is | 3 (3-6k) | Complete | Procedure Problem - Lack of procedure | Completed |  | Drawing 60148989/3601/228 (Cxxx-FAB-C-DWG-CRT00_ES001-50026) Revision 06 The fabricated steelwork for the stop log posts has been delivered to site without the requisite CE Certification, being ; 1. Factory Production Control (FPC) Certificate 2. Welding Certificate 3. Declaration of Performance
| 01CV - Civils | Cxxx-NCR-000193 | NCR | RMT Testing: reporting test failures |  | Contr | BAM | WAL - Wallasea Island (Projectwide) |  | 2015-01-31 | 2015-02-12 08:14 | 12 | 2014-10-03 13:17 | Civil - Civil Engineering General | 1000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | RMT testing that is carried out at Docklands Transfer Station has had exceedances that have not been sent for subsequent off site independent testing in accordance with The Excavated Materials Plan Cxxx-BAM-C-STP-CRT00-50003
| 01CV - Civils | Cxxx-NCR-000194 | NCR | Wallasea Island : RTE Outlet Structure (North) Headwall RC Details |  | Contr | BNV | WAL - Wallasea Island (Projectwide) |  | 2014-11-30 | 2014-10-31 14:20 | -30 | 2014-10-08 12:51 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Drawing 60148989/3519/233 (Cxxx-FAB-C-DWG-CRT00_ES001-50033) Revision 05 RTE Outlet Structure (North) East Headwall ; BM 13 has been incorrectly fixed in pairs, with a U top & bottom
| 01CV - Civils | Cxxx-NCR-000195 | NCR | Wallasea Island : RTE Structures Code 1 Documents |  | Contr | BNV | WAL - Wallasea Island (Projectwide) |  | 2014-10-31 | 2014-11-12 16:33 | 12 | 2014-10-08 14:15 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Lack of approval Code 1 procedures excessive | Completed |  | Observation 16015 (Unsatisfactory) Works have commenced to some activities in-advance of the applicable documents; method statements, inspection & test plans and material compliance records, being at Code 1 status
| 01CV - Civils | Cxxx-NCR-000196 | NCR | Wallasea Island : RTE Outlet Structure (North) East Headwall |  | Contr | BNV | WAL - Wallasea Island (Projectwide) |  | 2015-03-31 | 2014-12-08 10:27 | -113 | 2014-10-30 11:34 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | RTE Inlet Structure (North) East Headwall Pour, post pour inspection has shown two small areas of honeycombing
| 01CV - Civils | Cxxx-NCR-000197 | NCR | Wallasea Island : RTE Outlet Structures Application of Bitumen Emulsion |  | Contr | BNV | WAL - Wallasea Island (Projectwide) |  | 2014-12-19 | 2015-01-08 16:10 | 20 | 2014-11-07 13:34 | Civil - Civil Engineering General | 1500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | RTE Outlet Structures North & South Bitumen Emulsion applied to the concrete surface in weather conditions outside the parameters specified by the product manufacturer causing the bond between the bitumen emulsion & the concrete to fail
| 01CV - Civils | Cxxx-NCR-000198 | NCR | Wallasea Island : RTE Outlet Structure (South) Installation of Weholite Pipes |  | Contr | BNV | WAL - Wallasea Island (Projectwide) |  | 2015-12-19 | 2014-12-23 08:38 | -361 | 2014-11-13 16:06 | Civil - Civil Engineering General | 1500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | RTE Outlet Structure (South) Installation of Weholite Pipes The 2No. most northerly weholite pipes were not backfilled in accordance with the method statement causing displacement of the pipes, and the joint to open-up greater than the allowable tolerances
| 01CV - Civils | Cxxx-NCR-000199 | NCR | Wallasea Island : RTE Outlet Structure Post Cradles for Handrailing |  | Contr | BNV | WAL - Wallasea Island (Projectwide) |  | 2015-01-31 | 2015-01-15 16:33 | -16 | 2014-11-19 09:30 | Civil - Civil Engineering General | 950 |  | Incomplete Works | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | RTE Outlet Structure (North) East Headwall 2-Post Cradles for Hand-railing 2No. 2-Post cradle anchors, as MCR 054, have been inadvertently omitted from the east elevation headwall, as shown by the attached sketch
| 01CV - Civils | Cxxx-NCR-000200 | NCR | Wallasea Island : RTE Outlet Structure (North) : Access Steps Type C |  | Contr | BNV | WAL - Wallasea Island (Projectwide) |  | 2015-12-19 | 2014-12-03 12:27 | -381 | 2014-11-19 12:04 | Civil - Civil Engineering General | 150 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | RTE Outlet Structure (North) Access Steps Type C (West) Placement of the concrete into the formwork for the Type C Access Steps was not carried out in manner that was corresponding with the concrete consistence class, causing the wet concrete to spill over the formwork
| 01CV - Civils | Cxxx-NCR-000201 | NCR | Wallasea Island : RTE Outlet Structure (North) West Headwall |  | Contr | BNV | WAL - Wallasea Island (Projectwide) |  | 2014-12-19 | 2014-12-18 17:11 | -1 | 2014-11-19 16:06 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | RTE Inlet Structure (North) West Headwall Pour, post pour inspection has shown small areas of honeycombing, see attached photograph
| 01CV - Civils | Cxxx-NCR-000202 | NCR | Wallasea Island : Embankment B Undrained Shear Strength Testing |  | Contr | BNV | WAL - Wallasea Island (Projectwide) |  | 2015-01-09 | 2015-01-12 13:13 | 3 | 2014-12-03 10:15 | Civil - Fill | 500 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Supervision - Other | Completed |  | Embankment B Undrained Shear Strength Testing __ Engineer & Technician not carrying out shear vane testing in full compliance with the Specification, 1No. test taken at each location, specification requires an average of four over a 1m2 area to be considered as one representative test, see attached observation report (ID 17116)
| 01CV - Civils | Cxxx-NCR-000203 | NCR | Wallasea Island : RTE Outlet Structure (South) / Embankment B |  | Contr | BNV | WAL - Wallasea Island (Projectwide) |  | 2015-02-06 | 2015-02-23 11:39 | 17 | 2014-12-18 11:16 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | With reference to unsatisfactory observation 00056 (attached for ease of reference) un-compacted material has been placed with the footprint of Embankment B adjacent to the RTE Outlet Structure (South)
| 01CV - Civils | Cxxx-NCR-000204 | NCR | Wallasea Island : RTE Outlet Structures Handrails Cast In Post Cradle Anchors |  | Contr | BNV | WAL - Wallasea Island (Projectwide) |  | 2015-06-30 | 2015-05-27 10:35 | -34 | 2015-01-16 | Civil - Civil Engineering General | 1200 |  | Design | Repair | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | Drawings 60148989-3519-230 & 231 (Cxxx-FAB-C-DWG-CRT00_ES001-50013 & 50014) The post cradle anchors cast into the corners of the RTE Outlet Structure (North) West Headwall and (South) East & West Headwalls are not required, as confirmed by the submission of the handrail drawings (RFI 000384, copy attached)
| 01CV - Civils | Cxxx-NCR-000205 | NCR | Wallasea Island : RTE Outlet Structure (South) Weholite Pipes Failed Air Test |  | Contr | BNV | WAL - Wallasea Island (Projectwide) |  | 2015-03-31 | 2015-01-30 14:30 | -60 | 2015-01-19 16:49 | Civil - Civil Engineering General | 1500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Civil Engineering Specification for the Water Industry Sixth Edition Clause 7.6 RTE Outlet Structure (South) Weholite Pipes, the air test to Row 4 & Row 5 Pipes Failed (CRL-OBS-00293)
| 01CV - Civils | Cxxx-NCR-000206 | NCR | Wallasea Island : RTE Outlet Structure (North) Dycel 125 Revetment |  | Contr | BNV | WAL - Wallasea Island (Projectwide) |  | 2015-03-06 | 2015-03-05 09:29 | -1 | 2015-01-29 08:39 | Civil - Civil Engineering General | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | Drawing 60148989/3519/231 (Cxxx-FAB-C-DWG-CRT00_ES001-50014) RTE Outlet Structure (North) Scour Protection : Type B Geotextile has been placed beneath the Dycel 125 Revetment blocks, Wallasea Island Earthworks Volume 2C Technical Specification (Cxxx-FAB-C-RSP-CRT00_ES001-50002) Appendix 6/5 states ; Type A Geotextile to be used as separator layer
| 01CV - Civils | Cxxx-NCR-000208 | NCR | Wallasea Island : RTE Outlet Structure (North) Dycel 125 Revetment |  | Contr | BNV | WAL - Wallasea Island (Projectwide) |  | 2015-02-12 | 2015-02-09 13:30 | -3 | 2015-01-29 15:06 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Drawing 60148989/3519/231 (Cxxx-FAB-C-DWG-CRT00_ES001-50014) RTE Outlet Structure (North) Scour Protection Cxxx-RFI-000350 and Inspection & Test Plan (ITP) 050 states 10/20mm Granite washed material (MCR 065) will be used to infill the Dycel 125 Revetment blocks, A Limestone material has been used to infill the revetment blocks
| 01CV - Civils | Cxxx-NCR-000209 | NCR | Wallasea Island : RTE Outlet Structures (Gabion Baskets) |  | Contr | BNV | WAL - Wallasea Island (Projectwide) |  | 2015-03-11 | 2015-03-10 13:56 | -1 | 2015-02-04 14:20 | Civil - Civil Engineering General | 1200 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Drawing 60148989/3519/230 (Cxxx-FAB-C-DWG-CRT00_ES001-50013) & Cxxx-RFI 000365 A number of workmanship issues related to the construction of the gabion baskets have been observed 1. North & South Structures : Insufficient stone placed in the baskets 2. South Structure : Stone has not been correctly laid to the visible face (1No. Basket) 3. North Structure : Gap between the gabion basket and the reinforced concrete wall 4. North & South Structures : No compaction to the material placed in the "triangle" between the gabion basket and the reinforced concrete wall
| 01CV - Civils | Cxxx-NCR-000210 | NCR | Wallasea Island : Planning Condition 14 Movement of Soils |  | Contr | BNV | WAL - Wallasea Island (Projectwide) |  | 2015-06-30 | 2015-07-14 10:18 | 14 | 2015-03-20 06:53 | Civil - Landscaping | 1000 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Planning Condition 14 Movement of Soils Topsoil was moved on the 18 March 2015, Planning Condition 14 sates no movement of topsoil shall take place during the months November to March (inclusive) unless otherwise approved in writing by the Waste Planning Authority
| 01CV - Civils | Cxxx-NCR-000211 | NCR | Wallasea Island : RTE Inlet Structure Application of Bitumen Emulsion |  | Contr | BNV | WAL - Wallasea Island (Projectwide) |  | 2015-04-30 | 2015-04-14 16:01 | -16 | 2015-03-31 12:03 | Civil - Civil Engineering General | 2100 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Drawing 60148989/3601/223 (Cxxx-FAB-C-DWG-CRT00_ES001-50021) With reference to Note 5 on the above referenced drawing, on inspection (CRL-OBS-01481) areas of the bitumen emulsion applied to the base concrete surface have not cured adequately.
| 01CV - Civils | Cxxx-NCR-000212 | NCR | Wallasea Island : Embankment A Chainage 1150 Appendix 6/8 Topsoiling |  | Contr | BNV | WAL - Wallasea Island (Projectwide) |  | 2015-06-12 | 2015-06-18 12:43 | 6 | 2015-05-15 07:10 | Civil - Landscaping | 1000 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Previous Construction - Not Defined | Completed |  | Wallasea Island Earthworks Volume 2 Part C: Technical Specification Appendix 6/8 Topsoiling As identified by CRL Observation CRL-OBS-02365 crushed concrete fragments greater than 50mm in diameter are visible on the surface at the location of the now removed temporary access ramp Embankment A Chainage 1150
| 01CV - Civils | Cxxx-NCR-000217 | NCR | Wallasea Island : Sea Wall Breaching Tidal Salting's Excavation |  | Contr | BNV | WAL - Wallasea Island (Projectwide) |  | 2015-07-11 | 2015-07-14 10:22 | 3 | 2015-07-03 12:42 | Civil - Civil Engineering General | 1000 |  | Material | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | Following completion of the excavation of the tidal salting's at Breach 1, there was a local slippage of the seaward face of the seawall over the footprint of the deeper channel section
| 04UL - Utilities and Logistics | Cxxx-NCR-000033 | NCR | Commencement of Works Without Approved ITPs |  | Contr |  | ATA - Aldersbrook Tunnelling Academy (Technical (Design)) |  | 2010-12-10 | 2011-02-22 11:07 | 74 | 2010-12-07 | Construction Health & Safety - Construction Health & Safety General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Commencement of site activities without having accepted Inspection and Test Plans in place.
| 04UL - Utilities and Logistics | Cxxx-NCR-000034 | NCR | Inspection Requests Forms |  | Contr |  | ATA - Aldersbrook Tunnelling Academy (Technical (Design)) |  | 2010-12-10 | 2011-02-22 10:58 | 74 | 2010-12-07 | Construction Health & Safety - Construction Health & Safety General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Failure to notify the Supervisor when site activities (whether Hold or Witness points) are ready for inspection and to ensure that defined hold points are released by the Supervisor as defined on the relevant Inspection and Test Plan
| 04UL - Utilities and Logistics | Cxxx-NCR-000035 | NCR | Concrete Mix Grade |  | Contr |  | ATA - Aldersbrook Tunnelling Academy (Technical (Design)) |  | 2010-12-01 | 2011-02-23 16:00 | 84 | 2010-12-07 | Civil - Structural Engineering | 500 |  | Material | Reject |  | Complete |  | Completed |  | use of blinding concrete mix design of C15/C20 (shown on delivery ticket) as opposed to C25/C30 stated in specification
| 04UL - Utilities and Logistics | Cxxx-NCR-000070 | NCR | Road works commenced without approved ITP in place |  | Contr |  | ATA - Aldersbrook Tunnelling Academy (Technical (Design)) |  | 2011-05-17 | 2011-07-05 13:16 | 49 | 2011-05-13 | Civil - Roadworks Formation | 500 |  | Planning | Use As-Is |  | Complete |  | Completed |  | Commencement of site Activities (General Asphalt/Bitumen surfacing) without having accepted Inspection and test plan.
| 04UL - Utilities and Logistics | Cxxx-NCR-000071 | NCR | __ NCR - concrete cubes |  | Contr |  | ATA - Aldersbrook Tunnelling Academy (Technical (Design)) |  | 2011-05-13 | 2011-07-05 13:15 | 53 | 2011-05-16 | Structural Engineering - Concrete Member | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Concrete cylinder samples for crushing strength testing were taken instead of the requisite cubes given that the site testing lab were not present during the concrete operation.
| 01CV - Civils | Cxxx-NCR-000007 | NCR | __ Ex-works Inspection and QC Audit (Paint Shop and Logistics Building) |  | Crossrail | XRL |  |  | 2014-03-31 | 2014-03-28 16:58 | -3 | 2014-02-25 11:22 | Structural Engineering - Structural Engineering - General | 0 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | A CRL witnessed inspection took place on the 20/02/14 at __ with __ Quality representatives - Ex-Works Inspection/QC Audit Paint Shop and Logistics Building structural steelwork. The CRL consultant inspectors Paint Inspections Limited (PIL) have reported a documentation non-conformance for the fabrication and coatings process of the ready to ship structural steelwork. Inadequate evidence of the fabrication, preparation and coatings process has been brought to the attention of CRL. See attached Report ‘Site visit at __ for the Ilford Yard Stabling project covering steelwork and painting’ KW/CR/582/2 rev 02 [Cxxx-PIL-C-RGN-CRG03-50002]
| 01CV - Civils | Cxxx-NCR-000008 | NCR | Document Title: Cxxx - Stage 1E - Logistics Building Fit Out Details (__) Cxxx-VLK-A-DWG-CR112_SD007-50005 Rev 1.0 |  | Crossrail | XRL |  |  | 2014-03-17 | 2014-03-11 14:24 | -6 | 2014-03-03 16:52 | Architectural - General | 0 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Drawing numbers 21310, 21311, 21312, 21313, 21424, 21430, 21431 & 21435 contained in Cxxx - Stage 1E - Logistics Building Fit Out Details (__) Cxxx-VLK-A-DWG-CR112_SD007-50005 Rev 1.0 are not compliant to the Cxxx Ilford Yard Stabling Project CAD Management Plan Cxxx-VLK-N2-STP-CR112_SD007-50013 Rev 2.0 sections: • Section 5.5 __ Design • 5.5.1 Drawings/Documents to be submitted in Projectwise/eB • Appendix A - Architectural Series and sections: The designs require to be incorporated in the master and building models so that other design packages can be coordinated: • 5.3 __ • 5.3.3 __-__ Interface • 5.6 (__) Design
| 01CV - Civils | Cxxx-NCR-000010 | NCR | Foundation to Paintshop GL C |  | Contr | VLK |  |  | 2014-03-25 | 2014-03-11 16:19 | -14 | 2014-03-11 11:01 | Civil - Civil Engineering General | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Foundations to the Paintshop have been set out incorrectly, to low and the wrong orientation of the bolts
| 01CV - Civils | Cxxx-NCR-000011 | NCR | Cladding colour on Gable ends |  | Contr | VLK |  |  | 2015-02-27 | 2015-02-27 16:43 | 0 | 2014-06-06 15:17 | Architectural - Finishes | 10000 |  | Design | Repair | 2 (6-60k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Cladding panels installed as per approved drawings to the gable ends This isnt correct to planning drawings and a 1m panel at the base is required
| 01CV - Civils | Cxxx-NCR-000012 | NCR | Cladding - Vertical Capping Strip RAL Colour - Paint Shop & Logistics Building |  | Crossrail | XRL |  |  | 2014-05-15 | 2014-06-09 10:12 | 25 | 2014-05-01 16:33 | Architectural - Walls | 0 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Black Vertical Capping Strip has been observed as being fitted to both the White RAL 9010 and the Black is RAL 9005 Paint Shop Cladding Panels. CRL requested clarification of the use of Black Capping Strip on White Cladding Panels from __ on Site. __ advised the use of the Black Capping strip was accepted by CRL in the FDS. The FDS was reviewed and the advised drawing could not be located in the FDS - Logistics and Paint Shop Building Submission 1 Stage 1D Cxxx-VLK-A-STP-CR112_SD007-50001 rev 6.0 and Cxxx __ Roofing and Cladding Drawings Cxxx-VLK-A-DWG-CR112_SD007-50001 Rev 2.0.
| 01CV - Civils | Cxxx-NCR-000013 | NCR | Top hat colour on Paintshop |  | Contr | VLK |  |  | 2014-05-16 | 2014-06-06 15:27 | 21 | 2014-05-02 08:48 | Architectural - Walls | 0 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Colour of top hat doesnt match the adjacent wall cladding panel
| 01CV - Civils | Cxxx-NCR-000014 | NCR | Cxxx - Pile IL/31D Orientation |  | Contr | VLK |  |  | 2014-09-09 | 2014-09-12 12:46 | 3 | 2014-05-28 15:49 | Over Head Line Electrification - Catenary Masts | 1500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Plessey Road - Pile IL/31D Orientation is incorrect by 90 degrees due to __ design.
| 01CV - Civils | Cxxx-NCR-000015 | NCR | material compliance |  | Crossrail | XRL |  |  | 2014-09-15 | 2014-09-15 09:45 | 0 | 2014-06-16 08:57 | Materials - Approval | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | During a CRL led surveillance at the __ site office, it was found that on reviewing the material compliance records that the external bricks that are in use on both the Logistic and Paint sheds have been omitted from MCR Cxxx-VLK-A-LRC-CR112_SD007-50010 Rev 1.0. Titled bricks, blocks, mortar, lintels and ties. Submitted 26/03/2014. decal code 2 reviewed 22/04/2014
| 01CV - Civils | Cxxx-NCR-000016 | NCR | Records |  | Crossrail | XRL |  |  | 2014-06-30 | 2014-06-20 14:35 | -10 | 2014-06-16 09:08 | Architectural - Brickworks/Blockworks | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | During a CRL led surveillance at the __ site office, A review of the brick work check sheets found that only 6 no. check sheets had been raised for the paint shed external brickwork all dated 15/05/2014. 2 no. check sheets had been raised for the logistic shed dated 30/05/2014 and 06/06/2014. The ITP states that the frequency of checks carried out is to be daily. The brickwork started week commencing 13/04/2014 and at the time of the surveillance the external brickwork for both the Logistic and Paint sheds are approximately 70% complete.
| 01CV - Civils | Cxxx-NCR-000017 | NCR | Slump Testing |  | Crossrail | XRL |  |  | 2014-07-04 | 2014-09-16 13:08 | 74 | 2014-06-20 11:25 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | During a planned CRL led surveillance there was a review of the sampling of fresh concrete for the traverser pit pour taking place in the Paint Shed, the Contractors engineer confirmed that only one in three loads of concrete are slumped tested by the UKAS approved concrete technician.
| 01CV - Civils | Cxxx-NCR-000018 | NCR | ITP |  | Crossrail | XRL |  |  | 2014-07-04 | 2014-08-13 09:46 | 40 | 2014-06-20 11:44 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Lack of approval Code 1 procedures excessive | Completed |  | On reviewing the ITPs for in progress concrete works in Paint Shed and Logistic Shed, found that the Paint Shed concrete slab ITP Cxxx-VLK-N2-ITP-CR112_SD007-50017 Rev 2.0 had specification and control document references missing. The Logistic Shed concreting ITP Cxxx-VLK-N2-ITP-CR112_SD007-50017 rev 2.0 issued for review 17/06/2014 was not approved.
| 01CV - Civils | Cxxx-NCR-000019 | NCR | Materials compliance records |  | Crossrail | XRL |  |  | 2014-07-04 | 2014-09-19 10:29 | 77 | 2014-06-20 11:51 | Materials - Approval | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | During a review of the MCRs relevant for the concrete activity’s in progress at the time of the surveillance, the Contractor confirmed that the concrete mix for the traverser pit in the Paint shed had been changed from M6 to M5 with approval from the designer RSP, on further investigation it was found that M5 mix MCR Cxxx-VLK-C-LRC-CR112_SD007-50006 Rev 2.0 had been approved but not revised to cover the area concerned. The 32/40 concrete mix that was in use for the mezzanine floor slab in the Logistic shed, MCR Cxxx-VLK-C-LRC-CR112_SD007-50023 Rev 1.0 was not approved. The review also found that there were no approved MCRs for reinforcement, concrete spacing blocks, tying wire, release oil and concrete curing agent. The MCR for steel mesh that was used for the Logistic shed mezzanine floor number Cxxx-VLK-C-LRC-CR112_SD007-50004 Rev 1.0 is code 3 not accepted revise and resubmit, work may not proceed
| 01CV - Civils | Cxxx-NCR-000021 | NCR | Materials Compliance |  | Crossrail | XRL |  |  | 2014-07-17 | 2014-09-12 16:58 | 57 | 2014-07-03 14:04 | Systems - Drainage/Pumping Systems | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Management Problem - Other management problem | Completed |  | during a planned CRL led surveillance it was found that the symphonic drainage MCR Cxxx-VLK-C-LRC-CR112_SD007-50007 rev 1.0 had not been approved and the syphonic drainage has been installed in the Paint Shed.
| 01CV - Civils | Cxxx-NCR-000022 | NCR | Drawings |  | Crossrail | XRL |  |  | 2014-07-31 | 2014-07-18 14:02 | -13 | 2014-07-03 14:13 | Architectural - Roofing & Exterior Treatment | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | During a planned CRL led surveillance a review of the drawings in use for the roof and cladding for both the Paint and Logistic Buildings, found that the latest issued on eB Cxxx-VLK-A-DWG-CR112_SD007-50001 rev 3, code 3.
| 01CV - Civils | Cxxx-NCR-000023 | NCR | paint repairs |  | Crossrail | XRL |  |  | 2014-11-30 | 2014-10-24 10:36 | -37 | 2014-07-03 15:28 | Structural Engineering - Steel Member | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other management problem | Completed |  | During a planned CRL surveillance an inspection of the paint repairs was carried out from ground level in the Paint and Logistic buildings, it appeared that little or no preparation work had been carried out prior to painting on any of the repairs that were visible from ground level. It was also confirmed by the Contractor that there was no procedure in place for the structural steel paint repairs.
| 01CV - Civils | Cxxx-NCR-000024 | NCR | records |  | Crossrail | XRL |  |  | 2014-07-17 | 2014-10-06 16:14 | 81 | 2014-07-03 15:37 | Structural Engineering - Bolted Connections | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | During a planned CRL surveillance of the structural steel erection on the paint and logistic buildings the Contractor confirmed that the final tightening of bolts in both the Paint and Logistic Buildings was witnessed but was unable to produce records to confirm this.
| 01CV - Civils | Cxxx-NCR-000025 | NCR | Equipment and Calibration |  | Crossrail | XRL |  |  | 2014-10-31 | 2014-10-13 08:20 | -18 | 2014-07-03 15:48 | Structural Engineering - Bolted Connections | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Insufficient surveillance of subcontractors | Completed |  | During the planned CRL surveillance on the paint and logistic building structural steel work,On request the Contractor was unable to supply information for the torque wrench i.e. type/size and calibration certification, that their sub-contractor used for the final tightening of the bolts in both the Paint and Logistic Buildings.
| 01CV - Civils | Cxxx-NCR-000026 | NCR | Material compliance |  | Crossrail | XRL |  |  | 2014-09-23 | 2014-09-18 10:50 | -5 | 2014-07-03 15:52 | Structural Engineering - Steel Member | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | During the planned CRL surveillance on the paint and logistic building structural steel work A review of the MCR for Structural Steel, Bolts, Steel fittings and paint, MCR Cxxx-VLK-A-LRC-CR112_SD007-50002 rev 2.0 code 1. Found that no technical information or evidence of compliance had been submitted.
| 01CV - Civils | Cxxx-NCR-000027 | NCR | training for staff making cubes |  | Contr | VLK |  |  | 2014-07-31 | 2014-09-16 12:17 | 47 | 2014-07-10 10:29 | Civil - Civil Engineering General | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | Staff required to have correct training for making concrete cubes
| 01CV - Civils | Cxxx-NCR-000028 | NCR | Storage of materials |  | Contr | VLK |  |  | 2014-07-24 | 2014-07-25 16:14 | 1 | 2014-07-10 10:32 | Civil - Base Course | 700 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Material not stored as manufactures recomendations (grout)
| 01CV - Civils | Cxxx-NCR-000029 | NCR | Material compliance |  | Contr | VLK |  |  | 2014-07-24 | 2014-09-02 11:39 | 40 | 2014-07-10 10:43 | Materials - Approval | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | This item was raised by __ as material was being used on site without review by the CRL team The material is used as per the spec which is approved by the __ design team __ can confirm some things have slipped through but we have had meetings to discuss a better system of uploading these to CRL this has now been put into place so materials should be reviewed by CRL with no further issues
| 01CV - Civils | Cxxx-NCR-000030 | NCR | Drawings used on site out of date |  | Contr | VLK |  |  | 2014-07-31 | 2014-08-13 10:56 | 13 | 2014-07-10 10:47 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Training Deficiency - Other | Completed |  | While carrying out site survey it was found that drawings being used on site not the latest issue on EB or __ WS
| 01CV - Civils | Cxxx-NCR-000032 | NCR | Material compliant for stone capping layer |  | Contr | VLK |  |  | 2014-07-24 | 2014-09-16 13:37 | 54 | 2014-07-10 10:53 | Civil - Civil Engineering General | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | Materials coming to site not approved by design team
| 01CV - Civils | Cxxx-NCR-000034 | NCR | chemical analysis higher than first issue from GRS |  | Contr | VLK |  |  | 2014-07-24 | 2014-08-13 11:02 | 20 | 2014-07-10 11:05 | Materials - Approval | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | Chemical analysis higher than previous tests
| 01CV - Civils | Cxxx-NCR-000035 | NCR | latest drawings not being uploaded onto WS 006 |  | Contr | VLK |  |  | 2014-09-29 | 2014-09-18 10:58 | -11 | 2014-07-10 11:08 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | Drawings not being uploaded on to __ WS system
| 01CV - Civils | Cxxx-NCR-000036 | NCR | working outside section 61 011 |  | Contr | VLK |  |  | 2014-07-24 | 2014-07-25 10:41 | 1 | 2014-07-10 11:13 | Environmental - Environmental General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | Working outside section 61 various task on site
| 01CV - Civils | Cxxx-NCR-000037 | NCR | Paintshop concrete bases |  | Contr | VLK |  |  | 2014-09-30 | 2014-09-22 14:23 | -8 | 2014-07-10 11:15 | Civil - Civil Engineering General | 7500 |  | Workmanship | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | Paintshop concrete bases (C/6, C/8, C/9) were casted 50 mm too low.
| 01CV - Civils | Cxxx-NCR-000038 | NCR | IBJ not installed correctly 13 |  | Contr | VLK |  |  | 2015-08-20 | 2015-08-23 17:57 | 3 | 2014-07-10 11:19 | Track - Track General | 6000 |  | Workmanship | Use As-Is | 3 (3-6k) | Complete | Management Problem - Other management problem | Completed |  | IBJ not installed in the corrct location during the christmas works
| 01CV - Civils | Cxxx-NCR-000039 | NCR | Concrete blinding to high 014 |  | Contr | VLK |  |  | 2014-09-29 | 2014-09-19 10:58 | -10 | 2014-07-10 11:22 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Blinding to the foundation for the logistics building poured to high The information that was on __ drawings needed confiormation from trial holes which were done but due to the drawing review process the site team didnt get the information until late as they didnt know things had changed
| 01CV - Civils | Cxxx-NCR-000040 | NCR | steel angle not fitted correctly 015 |  | Contr | VLK |  |  | 2014-07-24 | 2014-08-13 12:18 | 20 | 2014-07-10 11:25 | Structural Engineering - Structural Engineering - General | 500 |  | Incomplete Works | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Steel angle not fitted correctly to the paintshop to allow __ start there works which was highlighted when inspected by __ prior to __ starting work in that area
| 01CV - Civils | Cxxx-NCR-000041 | NCR | supplier not supplying pipes as per order (closed)17 |  | Contr | VLK |  |  | 2014-07-24 | 2014-08-13 12:19 | 20 | 2014-07-10 11:38 | Materials - Approval | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Other | Completed |  | Materials purchased as per spec. The material requested was printed on the __ request form that was sent to the suppliers
| 01CV - Civils | Cxxx-NCR-000042 | NCR | Column encasment not as per __ detail 018 (closed) |  | Contr | VLK |  |  | 2014-09-29 | 2014-10-20 11:57 | 21 | 2014-07-10 11:40 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | paintshop column encasment not as per __ detaill for the steel brace and column surround the detail shows a 70mm cover in concrete from the steel to the edge of the concrete but in some areas this was a lot shorter
| 01CV - Civils | Cxxx-NCR-000043 | NCR | discharge pipe not installed as per drawing 21 (closed) |  | Contr | VLK |  |  | 2014-09-29 | 2014-10-09 11:04 | 10 | 2014-07-10 11:45 | Civil - Hydraulic Engineering | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | Pipe installed lower than drawing human error
| 01CV - Civils | Cxxx-NCR-000044 | NCR | flat brace bolts missing 22 (closed) |  | Contr | VLK |  |  | 2014-10-24 | 2014-10-24 10:06 | 0 | 2014-07-10 11:49 | Structural Engineering - Structural Engineering - General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Flat brace to the steels in the logisics build have middle bolts missing
| 01CV - Civils | Cxxx-NCR-000045 | NCR | Manhole installed without rocker pipes |  | Contr | VLK |  |  | 2014-11-30 | 2014-11-28 18:49 | -2 | 2014-07-10 11:52 | Civil - Drainage | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | drainage run installed without rocker pipes to the west end of site next to the Paintshop Building
| 01CV - Civils | Cxxx-NCR-000046 | NCR | unpainted steels to parapet of the logistics and paintshop closed (24) |  | Contr | VLK |  |  | 2014-09-23 | 2014-09-22 14:10 | -1 | 2014-07-10 11:55 | Civil - Structural Engineering | 500 |  | Material | Repair | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | steels not touched up on the parapet after inatlled on site
| 01CV - Civils | Cxxx-NCR-000047 | NCR | warning tape not installed above drainage to the paintshop (Closed) 25 |  | Contr | VLK |  |  | 2014-07-24 | 2014-08-13 15:13 | 20 | 2014-07-10 12:08 | Civil - Civil Engineering General | 1500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | foul water Pipe was buried without the warning tape in place
| 01CV - Civils | Cxxx-NCR-000048 | NCR | Brickwork has mortar snots on the face 26 |  | Contr | VLK |  |  | 2014-07-24 | 2014-08-13 15:46 | 20 | 2014-07-10 12:11 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | mortar snots on the face work of the brickwork to the peremeter of the Paintshop and L&S building this is highlighted as a snag but raised on NCR as this is the requirement of CRL
| 01CV - Civils | Cxxx-NCR-000049 | NCR | draiange installed outside of spec |  | Contr | VLK |  |  | 2014-09-29 | 2014-10-20 12:00 | 21 | 2014-07-10 12:13 | Civil - Sewage/Water services | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | Draiange pipe installed outside of the spec
| 01CV - Civils | Cxxx-NCR-000050 | NCR | OLE pile orientation is incorrect (Closed)28 |  | Contr | VLK |  |  | 2014-09-16 | 2014-09-15 09:42 | -1 | 2014-07-10 12:16 | Over Head Line Electrification - Catenary Masts | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | OLE pile orientation was incorrect on __ drawings
| 01CV - Civils | Cxxx-NCR-000051 | NCR | concrete came to site but failed slump test |  | Contr | VLK |  |  | 2014-08-20 | 2014-09-12 16:22 | 23 | 2014-07-10 12:18 | Civil - Civil Engineering General | 500 |  | Material | Reject | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Concrete came to site by for the floor slab but when the slump test carried out it was out of spec and returned
| 01CV - Civils | Cxxx-NCR-000052 | NCR | not working in line with the ITP 32 |  | Contr | VLK |  |  | 2014-07-24 | 2014-08-13 12:12 | 20 | 2014-07-10 12:22 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | ITP inspection frequency not being followed
| 01CV - Civils | Cxxx-NCR-000053 | NCR | missing steel to GL7c (closed) 33 |  | Contr | VLK |  |  | 2014-07-24 | 2014-08-13 15:20 | 20 | 2014-07-10 12:25 | Archaeology - General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Interfacing problems | Completed |  | Missing steel to allow __ fix the cladding There was a steel angle missing which is requiered on the steel to allow __ fix the panels to
| 01CV - Civils | Cxxx-NCR-000054 | NCR | cladding damage internally from concrete splashes |  | Contr | VLK |  |  | 2014-07-24 | 2014-09-12 16:35 | 50 | 2014-07-10 12:34 | Archaeology - General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | concrete spashes on the internal face of the claddding to the logistics building
| 01CV - Civils | Cxxx-NCR-000055 | NCR | ITP |  | Crossrail | XRL |  |  | 2014-07-25 | 2014-09-19 16:57 | 56 | 2014-07-11 10:27 | Architectural - Roofing & Exterior Treatment | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | During a planned CRL led surveillance a review of ITPs for activity’s that were in progress during the surveillance found; Roofing, Cladding and drainage ITP number Cxxx-VLK-N2-ITP-CR112_SD007-50009 rev 6.0 was code 3 (not accepted, revise and resubmit, work may not proceed)
| 01CV - Civils | Cxxx-NCR-000056 | NCR | ITP |  | Crossrail | XRL |  |  | 2014-07-25 | 2014-09-19 16:59 | 56 | 2014-07-11 10:39 | Surveying - Instrumentation and Monitoring | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | During a CRL led planned surveillance a review of ITPs found that the ITP for Monitoring instruments and record surveys number Cxxx-VLK-N2-ITP-CR112_SD007-50009 rev 1.0 code 2 (not accepted, revise and resubmit, work may proceed subject to incorporation of changes indicated) reviewed 05/12/2013. The corrective action has not been carried out in a timely manner.
| 01CV - Civils | Cxxx-NCR-000057 | NCR | No Drainage ITP |  | Crossrail | XRL |  |  | 2014-07-28 | 2014-09-19 17:00 | 53 | 2014-07-14 12:20 | Civil - Drainage | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | It was found during a review of ITPs, that although the drainage work within the Logistic and Paint buildings was in progress there was no ITP in place to cover this activity.
| 01CV - Civils | Cxxx-NCR-000059 | NCR | Cladding |  | Crossrail | XRL |  |  | 2014-09-26 | 2014-09-18 10:52 | -8 | 2014-07-17 14:22 | Architectural - Walls | 1800 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Between Gridlines 14 and 15 on the south elevation of the new Paintshop, the incorrect cladding panel configuration has been installed
| 01CV - Civils | Cxxx-NCR-000060 | NCR | Testing of fresh concrete |  | Crossrail | XRL |  |  | 2014-08-11 | 2014-08-13 15:51 | 2 | 2014-07-28 13:17 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | During a CRL planned surveillance, The Contractor confirmed that the operative that has been assigned to carry out the testing of fresh concrete had received training for this activity by UKAS approved company __ Infrastructure Division (UKAS accreditation number 0927). At the time of the surveillance there were no records available to substantiate this.
| 01CV - Civils | Cxxx-NCR-000061 | NCR | Training records |  | Crossrail | XRL |  |  | 2014-08-18 | 2014-08-13 15:47 | -5 | 2014-08-04 11:20 | Structural Engineering - Testing | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | During a planned surveillance on insitu concrete the Contractor confirmed that the operative that has been assigned to carry out the testing of fresh concrete had received training for this activity by UKAS approved company __ Infrastructure Division (UKAS accreditation number 0927). At the time of the surveillance there were no records available to substantiate this.
| 01CV - Civils | Cxxx-NCR-000062 | NCR | structural Steel |  | Crossrail | XRL |  |  | 2014-10-31 | 2014-10-24 15:26 | -7 | 2014-08-08 09:29 | Structural Engineering - Bolted Connections | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | The Contractor was unable to confirm whether the bolted connections had been correctly tightened in both the Paint and Logistic Buildings as there is no controlling specification for the torque value in the __ specification Cxxx-VLK-N2-RSP-CR112_SD007-50005 Rev 3.0 clause 605 which states;” Final fix: Tighten nut to specified torque. Torque: As required by design” On reviewing the Hambleton Structural Steel drawings that were available numbers Cxxx-VLK-S-DDA-CR112_SD007_2-5210, Cxxx-VLK-S-DDA-CR112_SD007_2-5211, Cxxx-VLK-S-DDD-CR112_SD007_Z-52203, Cxxx-VLK-S-DDC-CR112_SD007_Z-52200, 52201 for the Paint Building shows no reference for the tightening of bolted connections
| 01CV - Civils | Cxxx-NCR-000063 | NCR | Materials |  | Crossrail | XRL |  |  | 2015-11-06 | 2015-11-09 18:52 | 3 | 2014-08-08 09:36 | Materials - Approval | 2000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | It was found that the Contractor has made considerable progress with the installation of the spray booths within the Paint shop building. The steel frame work for the sides and roof on both spray booths has been erected; the access ladders and the steel walkways have also been installed. The installation that has been carried to date has no material compliance acceptance by CRL. The MCR for all __ materials MCR number Cxxx-VLK-C-LRC-CR112_SD007-50010 rev 1.0 decal code 3 dated 25th July 2014.
| 01CV - Civils | Cxxx-NCR-000066 | NCR | Concrete pour |  | Contr | VLK |  |  | 2014-10-24 | 2014-10-24 10:10 | 0 | 2014-08-18 11:45 | Structural Engineering - Structural Engineering - General | 7500 |  | Incomplete Works | Repair | 2 (6-60k) | Complete | External Phenomenon - Other | Completed |  | Logisitc Building Internal Floor Slab GL B-D/16-20 + 3.1m - Interruption in the concrete pour sequence resulting in Cold-joint to Internal floor slab.
| 01CV - Civils | Cxxx-NCR-000067 | NCR | NCR - Testing of fresh concrete |  | Contr | VLK |  |  | 2014-09-05 | 2014-09-18 10:47 | 13 | 2014-08-22 09:14 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Inspector not properly qualified | Completed |  | During the pre-pour and cube sampling/testing inspection, we've noticed that the technican assigned to carry out the sampling and slump testing activity had limited experienced and wasn't following the right method as is shown in BS EN 12350-2:2009. The techincian has been stopped and __, __'s __ trained engineer has been assigned to carry out the testing. __'s engineer will do the sampling and slump testing untill Subcontractor will provide their own. During a post surveillance check on __ UKAS accreditation that is employed by the subcontratcor for testing and sampling fresh concrete, it appearss that they are only accredtited for sampling and not for testing (slumping).
| 01CV - Civils | Cxxx-NCR-000068 | NCR | New Permanent Wheel Lathe Crossing - MCR's & ITP's |  | Crossrail | XRL |  |  | 2014-09-04 | 2014-09-08 15:07 | 4 | 2014-08-21 10:31 | Civil - Track | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Works to the new permanent wheel lathe crossing (detailed within design document Cxxx-VLK-Y-RGN-CR112_SD007-50003 and drawing Cxxx-VLK-R4-DDA-CR112_SD007_1-16110) have been substantially completed over the past number of weeks. These works have been undertaken without Material Compliance Records for any of the materials used except for the concrete (which itself is a Code 2 document requiring resubmission). Missing MCR’s include but are not limited to slab reinforcement, blinding, rails, baseplates, fixings, holding down bolts, grout and the buffer stop. There is also no relevant up to date ITP covering these works – the related ITP’s for Groundworks and P-Way do not reference any of the design and documentation associated with the Wheel Lathe Crossing Works
| 01CV - Civils | Cxxx-NCR-000070 | NCR | Logistics Building Slab - Crack |  | Contr | VLK |  |  | 2015-12-22 | 2015-12-12 01:17 | -10 | 2014-08-22 09:24 | Structural Engineering - Structural Engineering - General | 160000 |  | Material | Repair | 1 (>60k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Logistics Building Ground Floor Slab Logistics Building Slab (Please see attached photos and Drawing) – 1 – Cracking on the surface of the slab 2 – Locations of slab delamination 3 - Marks observed on top of the finished slab
| 01CV - Civils | Cxxx-NCR-000071 | NCR | Concrete testing and Sampling |  | Crossrail | XRL |  |  | 2014-09-05 | 2014-09-19 17:02 | 14 | 2014-08-22 10:52 | Materials - Approval | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Inspector not properly qualified | Completed |  | Whilst witnessing the first delivery of concrete for the Logistic Building floor slab, it was noted that the concrete technician that was carrying out the slump test, appeared to have limited experience in carrying the activity i.e. he had to be told by the Contractors engineer that he was not carrying out the slumping correctly; concrete placed in the cone in 3 layers with each layer compacted maximum 25 tamps as shown in BS EN 12350-2:2009;” Fill the mould in three layers, each approximately one-third of the height of the mould when compacted. Compact each layer with 25 strokes of the tamping rod”. A post surveillance check of the concrete technician’s employer __ (UKAS 2478) found that they only UKAS accredited for carrying out compressive strength test of concrete cubes including curing and density tests and not accredited for the testing (slumping) of fresh concrete that was carried out during the surveillance.
| 01CV - Civils | Cxxx-NCR-000072 | NCR | Materials Compliance |  | Crossrail | XRL |  |  | 2014-09-09 | 2014-10-06 13:40 | 27 | 2014-08-22 10:56 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | During a post surveillance check on accepted MCRs for materials used in the construction of the Logistic Building concrete floor slab, it was found that there was no accepted MCR on eB for the armoured formed free movement Joint 10mm wide x 40mm deep double CSS (stainless steel) strip joint.
| 01CV - Civils | Cxxx-NCR-000073 | NCR | Evidence of rusting to steels and fixings in Logistics and Stores building |  | Crossrail | XRL |  |  | 2014-10-30 | 2014-10-24 13:23 | -6 | 2014-09-24 11:34 | Structural Engineering - Structural Engineering - General | 500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | During a site inspection it was noted that there was evidence of rusting to the cladding fixings and also the structural steel frame in the Logistics and Stores building. The columns inspected were 17D and 18D however other areas showed similar signs and a comprehensive survey is required.
| 01CV - Civils | Cxxx-NCR-000074 | NCR | Control of printed drawings |  | Contr | VLK |  |  | 2014-09-20 | 2014-09-12 13:51 | -8 | 2014-09-06 11:19 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | A number of drawings located in the site office next to the printer have not been stamped ar referenced 'uncontrolled'.
| 01CV - Civils | Cxxx-NCR-000075 | NCR | Subcontractor Electronic document system (workspace) |  | Contr | VLK |  |  | 2014-09-20 | 2014-09-12 15:13 | -8 | 2014-09-06 12:02 | Communications and Control Systems | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Lack of procedure | Completed |  | A number of key records are missing off the contractor electronic document system (workspace) and in particular construction records.
| 01CV - Civils | Cxxx-NCR-000076 | NCR | MCR’s for Dry Shake Topping & Curing Agent - Logistics Building Slab |  | Crossrail | XRL |  |  | 2014-10-31 | 2014-10-30 16:21 | -1 | 2014-09-09 15:45 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | During a post surveillance check on accepted MCRs for materials used in the construction of the Logistics Building concrete floor slab, it was found that there were no MCR’s submitted for the dry shake topping (Qualidur HP or similar approved) and the curing agent (Aquacure PUA or similar approved) that have been applied to the slab.
| 01CV - Civils | Cxxx-NCR-000077 | NCR | Paint Shop Construction proceeding beyond the scope of the RIR and IFC design |  | Crossrail | XRL |  |  | 2015-07-31 | 2015-07-31 17:49 | 0 | 2014-09-09 17:31 | Mechanical - Mechanical Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | The Paint Shop Construction proceeding beyond the scope of the RIR and IFC design ‘Cxxx – Stage 1E (Architectural) Mini Gate Drawings for __ Enclosures & Associated Rooms & Stores Cxxx-VLK-A-DWG-CR112_SD007-50009 rev 1.0’ as issued on RIR Cxxx-VLK-N2-LRG-CR112_SD007-50004 Rev 8.0 on 15/07/14. The Mini Gate 3 Pass Certificate limits the Scope of Work to booth contraction only and No M&E installation. Two examples of Non-Conformance are: 1. Wiring of the Prep __ Lights 2. Installation of the Gas Pipe at High Level
| 01CV - Civils | Cxxx-NCR-000078 | NCR | Records |  | Crossrail | XRL |  |  | 2014-11-10 | 2014-11-11 08:45 | 1 | 2014-09-23 08:30 | Civil - Fill | 500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Management Problem - Other management problem | Completed |  | During a planned Crossrail led surveillance on earthworks, a review of the check sheets found WIS-98 dated 20th-21st August 2014, it was found that sections on the check sheets the information could not be read i.e. sections; check for number of passes for roller and check compaction in layers, both sections were not legible, in addition to this there was no record for the number of layers and level although the Contractor has a check sheet for this WIS-87.
| 01CV - Civils | Cxxx-NCR-000079 | NCR | Materials Compliance |  | Crossrail | XRL |  |  | 2015-01-31 | 2015-01-09 11:44 | -22 | 2014-09-23 08:39 | Civil - Fill | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | During a planned Crossrail led of earthworks A review of the material compliance records found that the as dug site material that had been used as back fill in the area adjacent to the recently constructed shot blast reclaim pit, had no accepted MCR.
| 01CV - Civils | Cxxx-NCR-000080 | NCR | Testing of materials |  | Crossrail | XRL |  |  | 2014-11-24 | 2014-11-13 17:19 | -11 | 2014-09-23 08:47 | Civil - Fill | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | At the time of the CRL led surveillance of earthworks, the Contractor was unable to provide test results to verify the classification of the as dug site material that had been used as back fill in the area adjacent to the recently constructed shot blast reclaim pit. A post surveillance request was made on the 27th August 2014 for the testing evidence to be supplied, but as of the 17th of September it has not been received.
| 01CV - Civils | Cxxx-NCR-000081 | NCR | Incorrect installation of isolation joints |  | Crossrail | XRL |  |  | 2015-08-31 | 2015-08-30 10:20 | -1 | 2014-09-26 15:23 | Civil - Civil Engineering General | 10000 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | It would appear that the isolation joints around the 26 structural steel bracings that are incorporated into the floor slab have either been formed incorrectly or have not been formed at all. 24 of the 26 bracings have a non conforming IJ.
| 01CV - Civils | Cxxx-NCR-000082 | NCR | ITP |  | Crossrail | XRL |  |  | 2014-11-19 | 2014-11-26 08:33 | 7 | 2014-09-29 10:42 | Civil - Civil Engineering General | 100 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | During a CRL led surveillance a review of the ITP for Ground works Cxxx-VLK-N2-ITP-CR112_SD007-50002 Rev 3.0 found that the only reference to the installation of the Attenuation Tank was the check sheet number WIS-105 titled Install Attention Tank Crates.
| 01CV - Civils | Cxxx-NCR-000083 | NCR | Concrete slab Restrain Joints not as per drawing |  | Contr | VLK |  |  | 2014-10-31 | 2014-11-04 16:35 | 4 | 2014-10-02 12:56 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | After an inspection of the concrete slab GL 11-16 in the Paintshop building, found that the depth of the Restrain Joints varies from 25mm to 50 mm and not as per drawing (1/3 of slab thickness of the slab i.e. 66 mm). The measurement of 25 mm has been found around the columns where the space is limitted for a saw cutting machine to achieve the required depth.
| 01CV - Civils | Cxxx-NCR-000084 | NCR | Manhole (SWMH8) installed 250 mm too low |  | Contr | VLK |  |  | 2014-11-15 | 2014-10-22 17:35 | -24 | 2014-10-08 14:11 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Manhole cover (Biscuit) to Manhole (SWMH 8) installed in the car park near corker’s path found to be 250 mm lower than the level specified in the drawing. Please see location in the drawing attacehed.
| 01CV - Civils | Cxxx-NCR-000085 | NCR | Syphonic System installation |  | Contr | VLK |  |  | 2014-11-30 | 2014-11-14 09:24 | -16 | 2014-10-08 16:36 | Systems - Drainage/Pumping Systems | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | It is unclear what revision drawing was used for the Syphonic System installation in the Paintshop Building. CRL has a visibility of Revision E as the latest and the drawing has gone up to revision K with some changes without being uploaded into eB system.
| 01CV - Civils | Cxxx-NCR-000086 | NCR | Working without an accepted ITP |  | Crossrail | XRL |  |  | 2014-11-21 | 2014-11-01 21:54 | -20 | 2014-10-09 10:56 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | During a CRL planned a review of the records for the Workshop A acoustic wall installation, it was found that the work had commenced without an accepted ITP Cxxx-VLK-N2-ITP-CR112_SD007-50020 Rev 1.0 decal 3.
| 01CV - Civils | Cxxx-NCR-000087 | NCR | No Records for pull out testing |  | Crossrail | XRL |  |  | 2014-10-31 | 2014-10-24 15:40 | -7 | 2014-10-09 14:05 | Structural Engineering - Bolted Connections | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | During the review of the structural steel records the Contractor was unable to provide evidence of pull out tests carried out on the holding down bolts for both the Paint and Logistic Buildings.
| 01CV - Civils | Cxxx-NCR-000088 | NCR | Handover process not followed within works carried out in Workshop A |  | Contr | VLK |  |  | 2014-11-14 | 2014-11-07 11:58 | -7 | 2014-10-11 10:04 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Insufficient information made available to the worker. | Completed |  | __ commencing work on the sheeting to installed to steelwork / purlins to Acoustic wall. The purlins and associated bracketry had not been checked as complete and __ were allowed to start the sheeting element of works with no formal handover.
| 01CV - Civils | Cxxx-NCR-000089 | NCR | Logistic Buiding crane beam/rails |  | Contr | VLK |  |  | 2015-04-30 | 2015-05-01 17:04 | 1 | 2014-10-15 14:48 | Structural Engineering - Structural Engineering - General | 3000 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Through Design calculations, __ have highlighted that under full load conditions, the crane beam grids B/23, 22, 20, 18, 16, 14, 12 & D/23, 21, 19, 17, 15, 13, 12, has the potential to distort at the connecting junctions.
| 01CV - Civils | Cxxx-NCR-000090 | NCR | Over sprayed cladding panels |  | Contr | VLK |  |  | 2015-01-31 | 2015-01-29 18:26 | -2 | 2014-10-16 14:54 | Architectural - Finishes | 1000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Following the painting of Cladding panels (3no in high from bottom) to west elevation of Paintshop building (GL A-D) has been identified that the panels above have been over sprayed. The initial spraying has been carried out as part of a previous remedial work which wasn’t satisfactory.
| 01CV - Civils | Cxxx-NCR-000094 | NCR | Non compliant concrete in the permenant works |  | Crossrail | XRL |  |  | 2015-03-02 | 2015-03-08 20:38 | 6 | 2014-10-22 12:44 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | During the CRL planned surveillance of the Logistic building concrete slab pour, the second delivery of C32/40 S4 concrete was witnessed, the first slump test recorded 80mm which was below the target for S4; 160mm-210mm with a -20mm+30mm deviation. The Contractor’s engineer instructed the delivery driver to add 30 litres of water to the mix, a second slump recorded 120mm, the Contractors engineer instructed a further 30 litres to be added and a third slump recorded 110mm, The Contractors engineer instructed the placement of the out of specification S4 concrete into the permanent works even though it was outside of the S4 slump class requirement.. The adding of water to gain the accepted S4 slump target also occurred with the third delivery of concrete.
| 01CV - Civils | Cxxx-NCR-000095 | NCR | Concrete used did not match the approved MCR |  | Crossrail | XRL |  |  | 2014-12-31 | 2014-12-18 19:29 | -13 | 2014-10-22 12:50 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | The Contractor used concrete mix C32/40 S4 The approved C32/40 mix MCR Cxxx-VLK-C-LRC-CR112_SD007-50023 Rev 2.0 decal 1 indicates a consistency slump of S2-S3.
| 01CV - Civils | Cxxx-NCR-000096 | NCR | The contractor added water to concrete mix without an approved procedure in place |  | Crossrail | XRL |  |  | 2015-03-02 | 2015-03-08 20:39 | 6 | 2014-10-22 12:58 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | During a CRL planned surveillance of the Logistic building concrete slab pour, the Contractor added in excess of 30 litres water to two delivered loads of concrete that were placed in the permanent works. The Contractor was asked to provide their documented water addition procedure however it was stated that no document existed.
| 01CV - Civils | Cxxx-NCR-000097 | NCR | Materials used before acceptance |  | Contr | VLK |  |  | 2015-01-20 | 2015-01-21 09:31 | 1 | 2014-10-27 12:44 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | As the construction of the car park is in progress some materials have been used but not submitted for acceptance. They are as follows: -Manhole chambers -Kerbs -Petrol interceptor
| 01CV - Civils | Cxxx-NCR-000098 | NCR | Utilities works |  | Contr | VLK |  |  | 2015-01-25 | 2015-01-23 18:29 | -2 | 2014-10-28 17:48 | Utilities Engineering - Utilities General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | Utilities works commenced in the car park near corkers path without having an ITP in place.
| 01CV - Civils | Cxxx-NCR-000099 | NCR | Installation of gas pipe |  | Contr | VLK |  |  | 2015-01-25 | 2015-01-30 17:43 | 5 | 2014-10-28 18:05 | Utilities Engineering - Utilities General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | Gas pipe has been installed in the car park near corkers path without a MCR in place.
| 01CV - Civils | Cxxx-NCR-000100 | NCR | Paint Shop & Logistics Stores - Utility Pipes |  | Crossrail | XRL |  |  | 2015-01-25 | 2015-01-21 09:47 | -4 | 2014-11-05 15:25 | Utilities Engineering - Utilities General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | The Current RIR Rev 11, referenced in this NCR does not contain the design and Specifications of the actual Utility pipes being installed on site at the time of this NCR being raised. Document Cxxx-VLK-C-XST-CR112_SD007-50006 Rev 2.0 Below Ground Drainage & Utilities - Stage 1C has a section: This document also includes the containment design for new below ground utilities which serve the site. These utilities include; gas, water, electric, communications, external lighting, depot protection and LV supplies. It should be noted that utilities containment is considered to comprise; ducting, troughing, and chambers only. The size and specification of supplies (including cable sizes etc) is not contained within this document - Cxxx-VLK-C-XST-CR112_SD007-50006. The design being used for permanent works shall be accepted by CRL as per the Works Information
| 01CV - Civils | Cxxx-NCR-000102 | NCR | Paint Shop – Shot Blast Plant delivered to site Without an Accepted Design |  | Crossrail | XRL |  |  | 2015-08-31 | 2015-08-12 10:27 | -19 | 2014-11-05 16:00 | Mechanical - Piping | 20000 |  | Design | Use As-Is | 2 (6-60k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | It has been observed the Paint Shop Shot Blast Plant has been delivered to site Without an Accepted Design. The Plant is currently stored in the logistics Building.
| 01CV - Civils | Cxxx-NCR-000103 | NCR | Failure of pre pour inspection for car park slab |  | Crossrail | XRL |  |  | 2015-01-21 | 2015-01-21 10:15 | 0 | 2014-11-19 15:44 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | CRL were formally invited to inspect the car park slab in line with works information procedure volume 2a section 20.8.The works inspected did not achieve the minium requirement stated in the specification for the car park slab resulting in a failed inspection.
| 01CV - Civils | Cxxx-NCR-000104 | NCR | Extarnal concrete slab |  | Contr | VLK |  |  | 2014-12-23 | 2014-11-25 13:07 | -28 | 2014-11-07 11:02 | Civil - Civil Engineering General | 5000 |  | Workmanship | Rework | 3 (3-6k) | Complete | Personnel Error - Other human error | Completed |  | A part of bay no 12 of the external slab has been poured 120mm to high.
| 01CV - Civils | Cxxx-NCR-000105 | NCR | External slab materials |  | Contr | VLK |  |  | 2015-01-09 | 2015-01-08 16:17 | -1 | 2014-11-07 12:38 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Work commenced on the external slabs without acceptance for the following materials:- •Insolation joint •Dowell bars •Mesh •De-bonding agent
| 01CV - Civils | Cxxx-NCR-000106 | NCR | Shot Blasting equipment |  | Contr | VLK |  |  | 2016-02-12 | 2016-02-08 13:48 | -4 | 2014-11-11 15:52 | Mechanical - Mechanical Engineering General | 20000 |  | Manufacturing Defect | Repair | 2 (6-60k) | Complete | Management Problem - Not Defined | Completed |  | After an inspection to the Shot blasting equipment that has been delivered to site and stored in the east end of logistic building the following quality issues have been found:- •Inconsistent / Incomplete runs of welding of generally poor quality – See photos 1, 3 & 4 within the attachment •Inconsistant/ incomplete gaskets – See photo 2 within the attahchment At the time there was no evidence of quality checks prior to being delivered to site.
| 01CV - Civils | Cxxx-NCR-000107 | NCR | ITP not fit for purpose |  | Crossrail | XRL |  |  | 2014-12-10 | 2014-12-12 13:43 | 2 | 2014-11-13 08:12 | Civil - Concrete Pavement | 200 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | The C32/40 S3 Air Entrained concrete mix MCR Cxxx-VLK-C-LRC-CR112_SD007-50051 rev 1, requires testing to establish the percentage of air created by the addition of Air-entraining admixture to the mix, this activity including the acceptance criteria for the test have not been itemised in the ITP Cxxx-VLK-N2-ITP-CR112_SD007-50002 Rev 3.0. As there was no acceptance criteria detailed in the documented ITP, the __ technician did not know what limits he was working to and non compliant concrete could have been placed into the works
| 01CV - Civils | Cxxx-NCR-000108 | NCR | Records |  | Crossrail | XRL |  |  | 2014-11-12 | 2014-12-01 13:41 | 19 | 2014-11-13 08:16 | Civil - Concrete Pavement | 50 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | __ (UKAS accreditation number xxxx), carried out air testing of the C32/40 S3 Air Entrained concrete mix used for bay 3 of the car park on the 05/11/2014, no records of these test were recorded by the Contractor. __ supplied the results on request on the 07/11/2014.
| 01CV - Civils | Cxxx-NCR-000110 | NCR | Dowel bars to Bay 12 external slab |  | Contr | VLK |  |  | 2015-05-29 | 2015-05-29 16:29 | 0 | 2015-04-16 14:00 | Civil - Civil Engineering General | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Dowel bars to the west edge of the external slab bay 12 have been installed incorrectly (not as per drawing), bars have been found not to a correct depth and not level/perpendicular into the slab.
| 01CV - Civils | Cxxx-NCR-000111 | NCR | Contractor working to decal code 3 Environmental Management Plan |  | Crossrail | XRL |  |  | 2015-01-15 | 2015-01-16 14:48 | 1 | 2014-11-28 09:42 | Environmental - Environmental General | 0 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | A post surveillance check on the eB numbers supplied found the Environmental Management Plan document number Cxxx-VLK-T1-STP-CR112_SD007-50003 rev 3 decal 3. eB document status current.
| 01CV - Civils | Cxxx-NCR-000112 | NCR | Off-site Fabrication ITP |  | Contr | VLK |  |  | 2016-01-20 | 2016-01-25 23:18 | 5 | 2014-12-01 20:02 | Mechanical - Mechanical Engineering General | 10000 |  | Documentation and Records | Use As-Is | 2 (6-60k) | Complete | Procedure Problem - Not Defined | Completed |  | Street Crane subcontractor starting fabrication of the crane for Logistic Building without an accepted off-site fabrication ITP being in place.
| 01CV - Civils | Cxxx-NCR-000113 | NCR | Embedded Track Installation |  | Contr | VLK |  |  | 2015-02-02 | 2015-01-20 13:37 | -13 | 2014-12-03 21:40 | Track - Track General | 0 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Personnel Error - Not Defined | Completed |  | Embedded Track Installation commenced in the Paintshop without an Accepted ITP.
| 01CV - Civils | Cxxx-NCR-000115 | NCR | Pump Station Works |  | Contr | VLK |  |  | 2015-02-13 | 2015-02-13 17:18 | 0 | 2014-12-13 10:34 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Pump station works commenced without an accepted ITP.
| 01CV - Civils | Cxxx-NCR-000116 | NCR | Capping beam installation |  | Contr | VLK |  |  | 2015-06-30 | 2015-06-12 14:14 | -18 | 2014-12-18 13:02 | Civil - Civil Engineering General | 10000 |  | Documentation and Records | Rework | 2 (6-60k) | Complete | Procedure Problem - Other | Completed |  | Capping beam installation to sheet piles along Corkers Path commenced without an accepted ITP.
| 01CV - Civils | Cxxx-NCR-000117 | NCR | Not adhering to ITP hold point |  | Crossrail | XRL |  |  | 2015-01-20 | 2015-01-23 18:16 | 3 | 2014-12-30 16:36 | Structural Engineering - Concrete Member | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | The check sheets created for the ongoing logistics slab remedials clearly states a pre pour inspection is required for every individual delamination repair with CRL invited using the IRF system. The delamination remedial that was ready for pouring on 17/12/14 was poured without CRL present at the pre pour inspection and an IRF was only issued for this post pour.This is a contravention of the works information 20.8.
| 01CV - Civils | Cxxx-NCR-000118 | NCR | Not adhering to design change process on UTX works |  | Crossrail | XRL |  |  | 2015-03-02 | 2015-02-02 12:49 | -28 | 2015-01-05 12:14 | Civil - Civil Engineering General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | Chambers 1 on both UTX 1 and 2 were to be pre cast concrete chambers as stated in the form 2/3 for these works and the design.Both chambers were changed to HDPE without following the FCD procedure.
| 01CV - Civils | Cxxx-NCR-000119 | NCR | Removal of bolts from cross braces |  | Crossrail | XRL |  |  | 2015-03-31 | 2015-04-03 09:59 | 3 | 2015-01-05 12:38 | Civil - Civil Engineering General | 500 |  | Incomplete Works | Reject | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | NCR 44 was closed on 24/10/14 on the proviso that the central bolts to the steel work braces in both the logistics building and the paint shop were removed. Punchworks PWK-00002 was also raised with a date of 25/12/14 as the agreed date for these to be removed by and assurances were made by __ this would be the case however this date was also missed.
| 01CV - Civils | Cxxx-NCR-000120 | NCR | Track monitoring |  | Contr | VLK |  |  | 2015-02-27 | 2015-02-27 17:00 | 0 | 2015-01-06 18:13 | Track - Track General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | Following the installation of the UTX to West of workshop A stage 1C, the track has been reinstated but the monitoring regime hasn’t been followed as is specified in ITP 043 section 2.16: Track Monitoring parameters ‘daily check of cant, twist and level throughout works and for 7 days after the point the settlement becomes negligible’.
| 01CV - Civils | Cxxx-NCR-000121 | NCR | Omitted purlin |  | Contr | VLK |  |  | 2015-03-30 | 2015-04-02 16:10 | 3 | 2015-01-06 19:02 | Civil - Civil Engineering General | 1500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | A purlin that supports the roof cladding joints around the access hatch to Logistic Building GL 1-2 has been omitted from the drawing number Cxxx-VLK-S-DDA-CR112_SD007_Z-51050 and during the installation process. The __ External Envelope Specifications Cxxx-VLK-N2-RSP-CR112_SD007-50006 in section 410 (fixing panels and sheets generally) states that panels and sheet ends are to be supported with fxings. This outstanding work has been raised as Punchworks (Cxxx-PWK-0001) and overdue from 25.12.2014.
| 01CV - Civils | Cxxx-NCR-000122 | NCR | Arcing of OLE on Plessey Road/Road 22 |  | Crossrail | PDP |  |  | 2015-01-28 | 2015-01-28 15:54 | 0 | 2015-01-14 20:52 | Electrical - OHLE | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Supervision - Insufficient supervision | Completed |  | During the evening of Wednesday the 3rd of December, the AGA (Abellio Greater Anglia) Yard Controller, __, observed arcing between the pantograph of a train unit traversing Road 22 and an OLE structure in the yard. He advised the SDM (Service Delivery Manager), __, who in turn alerted Romford ECO (Electrical Control Operator). The on call __ Maintenance Team was mobilised and attended site on the early morning of 4th of December. The team advised that Road 22 should be Blocked To Electric Traction (BTET) and observed that the structure was new and the issue may be attributed to the Crossrail works recently undertaken. The initial visit identified that the registration tube on structure IL29D was orientated ‘nose down’ that may be affecting height on the installed OLE. Standard practice was for registration components to be level. It was also discussed that the works on the previous weekend, to alter the Small Part Steel (SPS) on the next structure down, IL31D, may have affected the design values of the OLE.
| 01CV - Civils | Cxxx-NCR-000123 | NCR | Non conformance to temp works design |  | Crossrail | XRL |  |  | 2015-02-12 | 2015-02-13 17:22 | 1 | 2015-01-22 14:47 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The temporary works design using sheet piles for ground retention for Chamber 1 UTX 1 was not adhered to.Sheet piles should have been interlocking however they were installed hit and miss which mirrored the installation method in the adjoining trench.The hit and miss method was approved for the trench retention but should not have been repeated in the chamber.
| 01CV - Civils | Cxxx-NCR-000124 | NCR | Internal flashing to cladding pannel |  | Contr | VLK |  |  | 2015-06-30 | 2015-05-29 16:27 | -32 | 2015-01-24 15:20 | Architectural - General | 2000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate resources | Completed |  | The installation of the Insulation to internal flashing (skirting) in various areas of Logistic and Paintshop buildings hasn't been carried out as per drawing (Cxxx-VLK-A-DWG-CR112_SD007-50001 Rev 7.0).
| 01CV - Civils | Cxxx-NCR-000125 | NCR | Foul water pipework between FWIC4-FWIC5 |  | Contr | VLK |  |  | 2015-02-25 | 2015-02-27 17:40 | 2 | 2015-01-31 11:30 | Civil - Drainage | 2000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Following a __ work inspection has been identified that the subcontractor installed Foul water pipework connecting FWIC4-FWIC5 to an incorrect gradient. Section of drainage has been reworked and brought within the specified drawing details on the following day. Re-works have been inspected by __ engineers and works inspection sheets filled in accordingly.
| 01CV - Civils | Cxxx-NCR-000126 | NCR | Substation works |  | Contr | VLK |  |  | 2015-04-30 | 2015-04-02 16:38 | -28 | 2015-01-31 13:16 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Error by manufacturer in shipping or marking | Completed |  | First lorry of concrete delivered to site part of the substation slab construction/pour has been slump tested and defined a slump of 200 mm which is within S4 mix (160-210, -20, +30) where on the concrete ticket the S3 mix was specified with a slump of 100-150mm, -20, +30. The concrete has been used following designers confirmation that S4 mix is okay to use. The following 2 concrete deliveries met the S3 mix slump required.
| 01CV - Civils | Cxxx-NCR-000127 | NCR | DPM membrane to substation ground slab |  | Contr | VLK |  |  | 2015-07-15 | 2015-07-03 14:42 | -12 | 2015-02-04 12:08 | Civil - Civil Engineering General | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following a planned surveillance to the substation slab foundation during the pre-pour inspection has been identified that in various areas where the slab meets the temporary sheet piles, the DPM polyethylene didn’t had enough overlap or not at all. Following a post pour inspection has been found that on the edge of the south-west corner of the slab concrete has infiltrated through DPM joint.
| 01CV - Civils | Cxxx-NCR-000128 | NCR | Substation fondation slab |  | Contr | VLK |  |  | 2015-04-25 | 2015-04-02 16:49 | -23 | 2015-02-04 13:41 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | During a planned surveillance to the construction of the foundation slab to substation the following materials have been used without CRLs acceptance:- •Reinforcement (A393 Mesh) •Chairs, spacers and tying wire •DPM (1200g Polythene) membrane
| 01CV - Civils | Cxxx-NCR-000129 | NCR | Grout Infilling to embedded track |  | Contr | VLK |  |  | 2015-03-31 | 2015-04-02 17:33 | 2 | 2015-02-04 14:45 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | During a planned inspection to embedded track voids in Paint-shop building has been found that underside of track hasn’t been cleaned prior to grout infill.
| 01CV - Civils | Cxxx-NCR-000130 | NCR | Brickwork perimeter to paintshop |  | Contr | VLK |  |  | 2015-04-26 | 2015-04-02 17:35 | -24 | 2015-02-04 15:03 | Architectural - Brickworks/Blockworks | 2000 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | During a planned inspection to brickwork perimeter to South elevation of the Paintshop Building GL B (13-16) the followings have been found:- •Inconsistent movement joint •Missing movement joint •Loose bricks on top 2 course
| 01CV - Civils | Cxxx-NCR-000131 | NCR | __s walkways equipment |  | Contr | VLK |  |  | 2015-10-15 | 2015-10-01 14:35 | -14 | 2015-02-04 15:29 | Materials - General | 15000 |  | Manufacturing Defect | Repair | 2 (6-60k) | Complete | Verification Problems - Other | Completed |  | During a visual inspection over the walkways/platforms of the paint booths (to be installed) the following have been found:- •Poor/inconsistent welding or not at all on some parts of steel members •Damage to an adjacent welded steel plate •Unaligned steel flanges
| 01CV - Civils | Cxxx-NCR-000132 | NCR | External car park slabs Bays number 17, 18, and the southern half of 14 |  | Contr | VLK |  |  | 2016-01-28 | 2016-01-25 23:21 | -3 | 2015-05-15 13:30 | Civil - Civil Engineering General | 20000 |  | Workmanship | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Worker not trained for the work being performed | Completed |  | Following a pre-pour quality inspection to the car park slabs, inconsistent flatness and discontinued brush finish have been identified.
| 01CV - Civils | Cxxx-NCR-000133 | NCR | Inlet pipe to interceptor tank |  | Contr | VLK |  |  | 2015-07-31 | 2015-06-09 22:24 | -52 | 2015-02-07 12:30 | Civil - Civil Engineering General | 10000 |  | Supervision/Management | Rework | 2 (6-60k) | Complete | Supervision - Insufficient supervision | Completed |  | Further to the installation of the interceptor tank a section of the inlet pipe (3M longx300mm diameter) has been intentionally left out to be installed at a further date along with the parallel drainage runs either side of the petrol interceptor tank. This has been missed prior to casting the external slabs above.
| 01CV - Civils | Cxxx-NCR-000134 | NCR | Paintshop drainage |  | Contr | VLK |  |  | 2015-07-31 | 2015-06-09 22:26 | -52 | 2015-02-09 10:33 | Civil - Drainage | 10000 |  | Damaged | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A crack is observed in the pipe bend to the drain running across the Shot-blasting track slab G/L 11 B-C.
| 01CV - Civils | Cxxx-NCR-000135 | NCR | Fusamatic Pipework Inspection |  | Crossrail | XRL |  |  | 2015-04-17 | 2015-04-17 17:25 | 0 | 2015-02-16 12:57 | Civil - Utilities Engineering | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | Requested to attend witness point inspection by __ for fire hydrant pipework on the south elevation of the Logistic and Stores building. During the initial paperwork review it was noticed that the (straight through) couplers had not been covered by an MCR.
| 01CV - Civils | Cxxx-NCR-000136 | NCR | Drainage and duct works |  | Contr | VLK |  |  | 2015-04-30 | 2015-05-01 16:54 | 1 | 2015-02-24 07:34 | Civil - Civil Engineering General | 1000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Not Defined | Completed |  | A substantial amount of Pipework has been installed and backfilled within site footprint recently (since November) without being tested. Works haven’t been carried out as per __ spec ( Below Ground Drainage Specification Clause 3.3.13 Pipe Testing) or as per ITP 04e – Groundworks, Drainage and Ducts Works section 4.4 Jointing states “Joints to be fully connected (flexible and watertight). Each run to pass air and water test before acceptance” therefore possible non-compliant works have gone past the hold point identified in the aforementioned ITP. At present time there no assurance of works being compliant with Works Information volume 2A.
| 01CV - Civils | Cxxx-NCR-000137 | NCR | Embedded track grouting |  | Contr | VLK |  |  | 2015-04-30 | 2015-05-01 17:38 | 1 | 2015-02-26 11:28 | Civil - Civil Engineering General | 5000 |  | Supervision/Management | Repair | 3 (3-6k) | Complete | Design Problem - Not Defined | Completed |  | Following the self-levelling grout pour to embedded track slots in the Paint-shop booths a small step (10mm max) is identified in various locations where the grout bonds into concrete track slab. Although all activities were carried out as per drawings/specifications, the concrete FFL achieved the specified tolerances so the track installation,, the grout has been levelled to the lowest level edge and the overall quality finish is not to a satisfied standard therefore a remedial action/plan is to be proposed.
| 01CV - Civils | Cxxx-NCR-000138 | NCR | No test results for witness point |  | Crossrail | XRL |  |  | 2015-04-03 | 2015-04-02 17:44 | -1 | 2015-02-26 16:40 | Utilities Engineering - Utilities General | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Not Defined | Completed |  | Witness point inspection for the gas and potable water pipes to allow for back fill. __ did not present the electrofusion test results of the couplers. This does not give assurance on the integrity of the joints. If the results come back negative then the ground will need to be removed to allow re-jointing.
| 01CV - Civils | Cxxx-NCR-000139 | NCR | MCR for joint tape and inconsistency in installation |  | Crossrail | XRL |  |  | 2015-04-03 | 2015-04-02 18:01 | -1 | 2015-02-26 16:46 | Utilities Engineering - Water | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | No MCR for Potable water joint tape. The site installation is using metal barrier tape and PVC/Denso tape cover. The cover tape is also inconsistent through the installation.
| 01CV - Civils | Cxxx-NCR-000140 | NCR | Cladding panels to West elevation of Paintshop |  | Contr | VLK |  |  | 2015-09-30 | 2015-09-18 09:01 | -12 | 2015-02-27 12:50 | Architectural - General | 30000 |  | Incorrect Installation | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Other | Completed |  | Following the closing action for Cxxx-NCR-000011, nine cladding panels to west have elevation of Paintshop Building have been replaced but not installed as per drawing. Although Is work in progress the following issues are identified:- • Washers to fixings installed back to front • Some panels do not align • 2no. damaged panels • Oversized penetration cut in the panel around the Syphonic drainage outlet. Considering that the action for Cxxx-NCR-000011 has been completed this can now be closed but this NCR 140 will continue to highlight the issue.
| 01CV - Civils | Cxxx-NCR-000141 | NCR | Temporary works Between UTX 1 Ch 1 and Draw pit chamber O01 |  | Contr | VLK |  |  | 2015-06-30 | 2015-05-29 16:42 | -32 | 2015-03-10 17:38 | Civil - Excavation | 4000 |  | Supervision/Management | Rework | 3 (3-6k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | The temporary works design to excavation between UTX1 CH1 and included Draw pit chamber O01 hasn’t been followed as part of excavation for utilities pipe installation. The intumescent trench sheets have been installed as per drawing/design but draw pit chamber excavation had no temporary support when inspected.
| 01CV - Civils | Cxxx-NCR-000142 | NCR | Ducting penetration to Chamber 1 UTX 1 |  | Contr | VLK |  |  | 2015-07-15 | 2015-06-18 10:35 | -27 | 2015-03-11 13:20 | Civil - Civil Engineering General | 3000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | As part of the installation of Chamber 1 UTX 1 carried out by Stobart rail, approximately 600mm long duct stubs heading towards draw pit O01 have been installed and backfilled with mass concrete. When the temporary works have been removed in order to allow duct connection to the aforementioned, the following have been found:- • The ducts were compressed when the concrete was poured • Concrete entered the ducts due to insufficient protection • There are voids found between the ducts which should have been filled with concrete During the breaking out process to rectify the issue, the ducting chamber formed of Stakkaboxes has been damaged.
| 01CV - Civils | Cxxx-NCR-000143 | NCR | Intumescent paint to Logistic Building structural steel |  | Contr | VLK |  |  | 2015-07-18 | 2015-07-14 11:45 | -4 | 2015-03-11 14:26 | Architectural - General | 20000 |  | Workmanship | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In various ‘hard to reach’ areas of the steel frame of the Logistic Building has been found that the intumescent painting is not meeting the required/agreed DFT average.
| 01CV - Civils | Cxxx-NCR-000144 | NCR | DPM membrane to north-east elevation of the sub-station |  | Contr | VLK |  |  | 2015-07-09 | 2015-06-09 12:26 | -30 | 2015-03-11 15:05 | Civil - Civil Engineering General | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following the cutting of temporary sheet piles around the north-east of substation, the DPM membrane that separates the concrete from sheet piles has been damaged/melted not giving sufficient overlap detail.
| 01CV - Civils | Cxxx-NCR-000145 | NCR | Intumescent Paint to Paintshop |  | Contr | VLK |  |  | 2015-07-01 | 2015-05-29 16:59 | -33 | 2015-03-16 10:33 | Architectural - General | 10000 |  | Workmanship | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | Thickness of intumescent paint to the inside face of a steel member (channel above the doorway) of Paintshop East elevation GL 1 A-B has been identified to be lower than the Specification requirement.
| 01CV - Civils | Cxxx-NCR-000146 | NCR | Concrete foundations construction records |  | Contr | VLK |  |  | 2015-05-30 | 2015-05-29 16:47 | -1 | 2015-03-17 07:59 | Civil - Civil Engineering General | 1000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | After reviewing the ITP records for the foundations of the Paintshop and Logistic Buildings, it was noted that some pre-pour construction records were missing. ITP 004 Ground works (eB number: Cxxx-VLK-N2-ITP-CR112_SD007-50002) covered the mentioned works and includes the __ check sheet WIS-33 and WIS-72. WIS-72 has been used for pad and strip foundations but it doesn't define the different checks to be done for a pre-pour inspection (blinding, reinforcement, formwork, etc.)
| 01CV - Civils | Cxxx-NCR-000147 | NCR | Blockwork materials |  | Contr | VLK |  |  | 2015-06-30 | 2015-06-30 08:38 | 0 | 2015-03-23 13:11 | Architectural - General | 1000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | Following a planned surveillance blockwork to Logistic building has been identified that some materials have been used without going through the MCR acceptance process. They are as follows:- • 20mm Expandfoam board by __ • Windposts • Siderise Lamatherm TW-CS-DF60 – Firestop
| 01CV - Civils | Cxxx-NCR-000148 | NCR | Installation of windows |  | Crossrail | XRL |  |  | 2015-05-29 | 2015-05-29 18:09 | 0 | 2015-03-25 13:36 | Architectural - Glazing | 5000 |  | Supervision/Management | Rework | 3 (3-6k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | It was identified on 18/03/15 the window openings being formed to the south elevation of the logistics building were not being formed to the __ design on drawing 21426.The drawing being followed was a code 3 drawing previously submitted by the window fitting company.Further investigation revealed 1 of the comments for the code3 drawings was to incorporate the __ design from drawing 21426.Assurances were given by __ the __ design would be followed however a site inspection on 24/03/15 revealed the work was continuing to the code 3 drawing.
| 01CV - Civils | Cxxx-NCR-000149 | NCR | Logistic Building - Application of Firetherm Intumastic |  | Contr | VLK |  |  | 2015-08-30 | 2015-07-31 17:23 | -30 | 2015-03-28 10:16 | Architectural - General | 2000 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Firetherm Intumastic has been found to be poorly applied to the horizontal beam between grids 17-21 as part of the fire strategy. The Hold Point identified in ITP 041 – Intumescent Works @code1 was not adhered as the area was about to be concealed by blockwork and no records were available at the time.
| 01CV - Civils | Cxxx-NCR-000150 | NCR | Records |  | Crossrail | XRL |  |  | 2015-05-18 | 2015-05-22 16:13 | 4 | 2015-04-02 08:13 | Architectural - Roofing & Exterior Treatment | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Other management problem | Completed |  | The check sheet records for the roof installation were reviewed, and the following was found; the Contractor has adopted the Sub-Contractors check sheets as stated on the ITP items 2.4, 2.5, 2.7 and 2.9. The three check sheets referenced grid lines 19-16, 16-13 and 13-10 for the installation of roof sheets and roof lights. On review all had been checked and signed off as per the ITP by the Sub-Contractor carrying out the installation, however there was no intervention by the Contractor as per the ITP on any of the check sheets despite 50 linear meters of roof sheets and roof lights having been installed on the East side of Work Shop A.
| 01CV - Civils | Cxxx-NCR-000151 | NCR | Inspection Request Form |  | Crossrail | XRL |  |  | 2015-05-18 | 2015-05-22 16:21 | 4 | 2015-04-02 08:18 | Architectural - Roofing & Exterior Treatment | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | The Contractors management for Workshop A are not issuing Inspection Request Forms (IRF) to CRL in line with the rest of the site works. The ITP-Cxxx-VLK-N2-ITP-CR112_SD007-50044 rev 1.0 decal code 2 has hold points for all CRL interventions, as such with out the issuing of Inspection Request Forms to CRL, ITP hold point interventions are being missed.
| 01CV - Civils | Cxxx-NCR-000152 | NCR | Records |  | Crossrail | XRL |  |  | 2015-05-18 | 2015-05-22 16:24 | 4 | 2015-04-02 08:20 | Architectural - Roofing & Exterior Treatment | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | The Contractor quotes check sheet WS1a for ITP items 2.1 Removal of existing roof materials and Removal of gable end cladding, although the stripping of roof sheets is on going there were no copies of check sheet WS1a on file despite 75 linear meters of roof on the east side of work shop A being removed.
| 01CV - Civils | Cxxx-NCR-000153 | NCR | Materials |  | Crossrail | XRL |  |  | 2015-05-18 | 2015-05-22 16:24 | 4 | 2015-04-02 08:23 | Architectural - Roofing & Exterior Treatment | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | During a post surveillance review of materials that are in use during the installation of the Workshop Roof the following was found; SFS Seamseal BR sealant MCR Cxxx-VLK-C-LRC-CR112_SD007-50072 rev 1.0 decal code 3 (reviewed 19/03/2015)
| 01CV - Civils | Cxxx-NCR-000154 | NCR | Instalation of level crossing Rosehill panels |  | Contr | VLK |  |  | 2017-05-31 | 2017-02-23 16:42 | -97 | 2015-04-10 17:08 | Track - Track General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Not Defined | Completed |  | During the installation of Rosehill panels at the west level crossing location, the hold point of the ITP 045, activity 14 has been missed. Activity 14 Installation of panels states that “panels to ‘L’ edge beam gap <5mm and panels sit flush to top of edge beams”. The L edge beams haven’t been installed as part of the initial design due to existing concrete slabs obstruction, the changes to design were made by __ CRE and agreed with NWR but not communicated to CRL and IRFs were not raised for any of the CRL witness points stipulated in the ITP.
| 01CV - Civils | Cxxx-NCR-000155 | NCR | Dowel bars to the north edge of the external slab bay 2 |  | Contr | VLK |  |  | 2015-07-31 | 2015-06-09 22:29 | -52 | 2015-04-16 13:52 | Civil - Civil Engineering General | 4000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Dowel bars to the north edge of the external slab bay 2 haven't been installed as part of the slab construction.
| 01CV - Civils | Cxxx-NCR-000156 | NCR | Pre-pour inspection to external slab bay 17 |  | Contr | VLK |  |  | 2015-07-31 | 2015-06-02 11:21 | -59 | 2015-04-16 15:13 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following a pre-pour inspection to external car park slabs, some issues have been found in bay number 17:- • Mesh in some areas had as little as 20mm cover • Flex cell installed to kerb was of poor quality and would not have given the slab a clean edge post pour • Insufficient ties to mesh • H12 bar missing beneath impending saw cut
| 01CV - Civils | Cxxx-NCR-000157 | NCR | Inspection and Test Plan (ITP) |  | Crossrail | XRL |  |  | 2015-05-18 | 2015-05-22 16:07 | 4 | 2015-04-20 14:18 | Architectural - Brickworks/Blockworks | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | On reviewing the ITP ITP-Cxxx-VLK-N2-ITP-CR112_SD007-50049 rev 2.0 decal code 2 (reviewed 27/02/2015), it was found that the Contractor had omitted the sample test panel and benchmark panel for blockwork as a pre-construction requirement as stated in the Works Information Volume 2A Cxxx-XRL-N2-SPB-CR112_SD007_Z-50001 revision 2.0 clause 20.8:
| 01CV - Civils | Cxxx-NCR-000158 | NCR | failed inspection |  | Crossrail | XRL |  |  | 2015-06-30 | 2015-06-18 10:42 | -12 | 2015-04-27 12:44 | Fire - Fire Systems & General | 20000 |  | Supervision/Management | Rework | 2 (6-60k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Invited to inspect the steel columns and beams within the kitchen area of the paint shop.20 linear metres of steels in varying locations were checked and 3 failings were recorded.The beam from grids C to D on grid line 3 recorded consistant low readings the lowest of which was 608 microns when the required loading was 1200 microns.The columns on grids 3C and 4C also registered low readings of which 427 microns was the lowest,with the required loading being 638 microns.
| 01CV - Civils | Cxxx-NCR-000159 | NCR | Underfloor heating to Logistic Building office area |  | Contr | VLK |  |  | 2016-02-27 | 2016-02-29 09:30 | 2 | 2015-04-29 17:34 | Mechanical - Mechanical Engineering General | 1000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Following an inspection to the installation of the underfloor heating in the Logistic Building the following have been found:- • Irregularities within the drawing being used on site (Cxxx-VLK-M-DDA-CR112_SD007_Z-77016 CO1) • Insufficient information within the drawing being used on site (Cxxx-VLK-M-DDA-CR112_SD007_Z-77016 CO1) • Information in underfloor heating zone Key does not correspond to drawing • Information contained in Subcontractor’s () underfloor heating drawing hasn’t been incorporated in the aforementioned AFC drawing.
| 01CV - Civils | Cxxx-NCR-000160 | NCR | Instalation of level crossing and barrier |  | Contr | VLK |  |  | 2015-10-19 | 2015-10-18 19:43 | -1 | 2015-04-30 10:15 | Track - Track General | 500 |  | Design | Reject | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | The installation of Rosehill panels at the west level crossing hasn’t been carried out as per design as the L edge beams have been omitted. The was made by __ CRE and agreed with NWR but not communicated to CRL and IRFs were not raised for any of the CRL witness points stipulated in the ITP. As part of the same level crossing, a temporary barrier adjacent to an open line has been installed without a design.
| 01CV - Civils | Cxxx-NCR-000161 | NCR | Embedded track instalation |  | Contr | VLK |  |  | 2015-07-29 | 2015-06-29 14:21 | -30 | 2015-05-01 09:00 | Track - Track General | 1500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | Following a review of the ITP 007- Pway (Cxxx-VLK-N2-ITP-CR112_SD007-50008) and the documentation related to embedded track installation has been found that under section 24.1 of the same ITP bolt pull out testing is required but there were no records available on check sheets (trackwork form QF 465) although the works have been inspected and check sheets have been signed by all parties (subcontractor, __, CRL).
| 01CV - Civils | Cxxx-NCR-000162 | NCR | External car park slab |  | Contr | VLK |  |  | 2015-07-31 | 2015-06-17 21:32 | -44 | 2015-05-02 15:40 | Civil - Civil Engineering General | 1000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | Following a surveillance to external car park bay 15 has been identified that 600mm long Dowel bars were used for the Contraction (Transverse) joint instead of 500mm, as detailed on the Highways details drawing. At the time there were no records of TQs or FCD avaialble.
| 01CV - Civils | Cxxx-NCR-000163 | NCR | External car park bay 15 |  | Contr | VLK |  |  | 2015-07-23 | 2015-06-10 16:50 | -43 | 2015-05-02 15:47 | Civil - Civil Engineering General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Following a planned surveillance to external car park slab bay 15 has been found that Anti cracking reinforcement (bars) was of 3 no.16mm bars instead of 2no. 20mm as detailed on the Highways details drawing (Cxxx-VLK-D-DDL-CR112_SD007_2-15151 ). At the time, there wasn't a TQ nor an FCD to confirm changes/acceptance.
| 01CV - Civils | Cxxx-NCR-000164 | NCR | Workshop A Sheet pilling |  | Contr | VLK |  |  | 2015-07-31 | 2015-06-02 11:25 | -59 | 2015-05-02 15:51 | Civil - Civil Engineering General | 1000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | Sheet piling activities in Workshop A have commenced without an approved ITP in place.
| 01CV - Civils | Cxxx-NCR-000165 | NCR | Re-Roofing works to Workshop A |  | Contr | VLK |  |  | 2015-10-30 | 2015-10-15 09:04 | -15 | 2015-05-02 15:55 | Architectural - General | 4000 |  | Documentation and Records | Use As-Is | 3 (3-6k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | Re-roofing activities at WSA roads 3 to 5 building have commenced with Code 3 MCRs. Also, there have been materials used for which no MCRs have been submitted. Code 3 MCRs refer to the following materials: Seamseal BR, Insulation infill, Metal Fabrications and Fire Rated Foam. Materials for which no MCRs have been submitted are: Butyl Tape Sealants and Magnetic Spacers
| 01CV - Civils | Cxxx-NCR-000166 | NCR | Silencing equipment |  | Contr | VLK |  |  | 2015-11-28 | 2015-11-27 16:18 | -1 | 2015-05-07 11:00 | Systems - Systems Engineering General | 1000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | The off-site fabrication of the silencing equipment commenced without an accepted ITP
| 01CV - Civils | Cxxx-NCR-000167 | NCR | Silencing equipment materials |  | Contr | VLK |  |  | 2015-12-11 | 2015-12-07 13:59 | -4 | 2015-05-07 11:05 | Architectural - General | 1000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | The off-site fabrication of the silencing equipment commenced without an accepted MCR. Materials used haven’t been submitted to CRL for acceptance.
| 01CV - Civils | Cxxx-NCR-000168 | NCR | Paintshop Traverser |  | Contr | VLK |  |  | 2015-07-22 | 2015-07-15 09:13 | -7 | 2015-05-07 11:19 | Track - Track General | 15000 |  | Documentation and Records | Use As-Is | 2 (6-60k) | Complete | Verification Problems - Other | Completed |  | Has been identified that the off-site fabrication of the traverser equipment commenced without an accepted ITP. Rev 1. of ITP 026 - Paintshop Traverser (Cxxx-VLK-N2-ITP-CR112_SD007-50019) has been submitted in July 2014 but after a couple of revisions is still @code 3.
| 01CV - Civils | Cxxx-NCR-000169 | NCR | Shotblast enclosure steelwork |  | Contr | VLK |  |  | 2015-10-30 | 2015-10-22 10:48 | -8 | 2015-05-07 12:41 | Architectural - General | 1000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | The installation of the shotblast enclosure steelwork adjacent to paintshop has commence without an accepeted MCR. The MCR for structural steel (Paintshop and Logistic Building) is on eB @code 1 (Cxxx-VLK-A-LRC-CR112_SD007-50002 - Material Compliance Record - Structural Steel) but not including the aforementioned element of work.
| 01CV - Civils | Cxxx-NCR-000170 | NCR | Utility works |  | Contr | VLK |  |  | 2015-10-30 | 2015-11-01 21:04 | 2 | 2015-05-07 14:23 | Utilities Engineering - Utilities General | 500 |  | Documentation and Records | Reject | 4 (0.5-3k) | Complete | Verification Problems - Not Defined | Completed |  | During the week 6 possession, utility works have been carried out dictated by the following ITPs :- ITP - Underground Utilities - Potable Water (Cxxx-VLK-N2-ITP-CR112_SD007-50041) ITP 074 - Fire Hydrant (Cxxx-VLK-E1-ITP-CR112_SD007-50002). Throughout the works, it has been identified that the ITPs requirements haven’t been followed and some evidence couldn’t be provided when the subcontractor (CUS/Megson) was asked:- • Production of calibration cert for fusion welding machine • __ completion of contractor Construction Checklists • Submission of Electrofusion test results
| 01CV - Civils | Cxxx-NCR-000171 | NCR | Logistic Building internal anti slippery coating |  | Contr | VLK |  |  | 2016-03-07 | 2016-03-14 10:18 | 7 | 2016-01-28 09:08 | Civil - Civil Engineering General | 2000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | It has been identified that the edges of the anti slippery coating in Logistic building appears to be de-bonding and inconsistent in straightness.
| 01CV - Civils | Cxxx-NCR-000172 | NCR | Surface damages and imperfections to external car park bays 13, 15, 20 21A |  | Contr | VLK |  |  | 2016-03-24 | 2016-03-22 08:54 | -2 | 2015-05-26 15:27 | Civil - Civil Engineering General | 15000 |  | Workmanship | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Other | Completed |  | Following a post pour inspection to the external car park slabs (bay 13, 15, 20 21A), surface damages and imperfections have been identified along with poorly formed edges.
| 01CV - Civils | Cxxx-NCR-000173 | NCR | External car park slab bay 15 |  | Contr | VLK |  |  | 2016-01-26 | 2016-01-26 14:01 | 0 | 2015-05-26 16:58 | Civil - Civil Engineering General | 10000 |  | Workmanship | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Other | Completed |  | Following a post pour inspection to Bay 15 it has been identified that the northern side surface finish has imperfections ( inconsistent flatness / brush finish ) and the concrete repairs carried out to the south east corner of bay 15 are not satisfactory.
| 01CV - Civils | Cxxx-NCR-000174 | NCR | Use of resin without MCR |  | Crossrail | XRL |  |  | 2015-07-23 | 2015-07-15 10:18 | -8 | 2015-05-27 10:26 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | The resin used by __ to install the dowels for the remedial works to the car park slab in bays 13 and 14 was not the resin specified in the MCR.The resin used can be seen in the picture enclosed which was an unapproved product.
| 01CV - Civils | Cxxx-NCR-000175 | NCR | Installation of secondary steel to Workshop A |  | Contr | VLK |  |  | 2015-07-31 | 2015-07-31 17:18 | 0 | 2015-05-28 16:04 | Structural Engineering - Steel Member | 1500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | The installation of Secondary steel to Workshop A building has commenced without an accepted MCR
| 01CV - Civils | Cxxx-NCR-000176 | NCR | Specification |  | Crossrail | XRL |  |  | 2015-07-17 | 2015-07-15 09:54 | -2 | 2015-05-29 09:22 | Architectural - Roofing & Exterior Treatment | 1500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A review of Work Shop A phase 1 roof installation was carried out and the following was found: the Contractor has failed to paint the tops of the existing roof trusses, after removing the existing Galbestos roof sheeting and prior to the installation of new roof sheeting as per the specification,
| 01CV - Civils | Cxxx-NCR-000177 | NCR | Design |  | Crossrail | XRL |  |  | 2015-07-17 | 2015-06-29 09:47 | -18 | 2015-05-29 09:30 | Architectural - Roofing & Exterior Treatment | 1000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | The made-to-measure gutter lining has not been fitted due to the sequencing of the removal of the existing Galbestos roof sheeting which was removed in 20 linear meter sections, with the new roof installed as this progressed. The gutter liner will be fitted along with additional flashings and sealant once the new roof has been completed, this design change has not been documented by way of a Field Change Document (FCD) and issued for acceptance. The design of the smoke vent upstand details 20(1:5) and 21(1:5), drawing number 1798/18 which is part of drawing pack Cxxx-VLK-E-DWG-CR112_SD007-50001 rev 3.0, has been changed to a purpose made upstand frame, the design change has also not been documented by way of a Field Change Document (FCD) and issued for acceptance.
| 01CV - Civils | Cxxx-NCR-000178 | NCR | Drawings |  | Crossrail | XRL |  |  | 2015-06-26 | 2015-06-23 18:14 | -3 | 2015-05-29 13:04 | Architectural - Roofing & Exterior Treatment | 1000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | On reviewing the Work Shop A roof installation drawings that were in use on site, the following was found: drawings 1798-01 to 1798-18 marked C01 issued for construction. The drawings were issued as a pack under eB number Cxxx-VLK-E-DWG-CR112_SD007-50001 rev 4.0 the decal sheet had not been signed off, and as such was not approved. Work Shop A roof installation drawings Cxxx-VLK-E-DWG-CR112_SD007-50001 rev 3.0 decal code 1 dated 17/12/2014 are the latest issued on eB but the individual drawings have not been issued for construction.
| 01CV - Civils | Cxxx-NCR-000179 | NCR | Off-site fabrication ITP |  | Contr | VLK |  |  | 2017-03-30 | 2017-02-01 14:35 | -57 | 2015-06-01 17:40 | Architectural - General | 3000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Cat-ladders and walkways for the paintshop high level access above the paint booths have been fabricated in March 2014 without an off-site fabrication ITP. These are part of __’s (sub-contractor) scope of works. These items have been installed on site as per drawings and are part of the access above the paint booths.
| 01CV - Civils | Cxxx-NCR-000180 | NCR | Primer to structural steel |  | Contr | VLK |  |  | 2015-07-31 | 2015-07-15 10:38 | -16 | 2015-06-01 16:23 | Structural Engineering - Steel Member | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Shot blasting enclosure structural steel has been delivered to site and installed with a number of areas presenting corrosion and imperfections to the primer. Additional, as part of the installation process, the washers to the holding down bolts have been missed.
| 01CV - Civils | Cxxx-NCR-000181 | NCR | Substation finishes works |  | Contr | VLK |  |  | 2015-08-31 | 2015-08-30 10:28 | -1 | 2015-06-02 17:17 | Architectural - Finishes | 3000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The intervention point of the ITP 086 – 'Installation of the substation activity 9.10 Floor paint' has been missed prior to the floor paint being applied. The slab has been painted without being snagged nor sealed with 2 coats of concrete sealer as per the specification.
| 01CV - Civils | Cxxx-NCR-000182 | NCR | Substation works |  | Contr | VLK |  |  | 2015-08-15 | 2015-08-13 12:53 | -2 | 2015-06-04 15:43 | Architectural - Finishes | 5000 |  | Supervision/Management | Rework | 3 (3-6k) | Complete | Subcontractor Problems - Interfacing problems | Completed |  | Substation interior brickwork and concrete soffit have been painted without being inspected nor MCR in place for the paint.
| 01CV - Civils | Cxxx-NCR-000183 | NCR | Door reveals to paintshop building |  | Contr | VLK |  |  | 2015-08-14 | 2015-08-12 10:52 | -2 | 2015-06-09 15:03 | Architectural - Finishes | 6000 |  | Workmanship | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | Following an inspection on the door reveals to paintshop building shotblasting area has been identified that the skimming is flaking away possibly due to accelerated drying of the plaster. The flaked areas were filled in, however is not a suitable remedial method.
| 01CV - Civils | Cxxx-NCR-000184 | NCR | Application of paint to paintshop building internal drylining |  | Contr | VLK |  |  | 2015-07-31 | 2015-07-15 10:14 | -16 | 2015-06-09 18:03 | Architectural - Finishes | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Painting has been carried out to shotblasting drylining walls before the plaster was fully dry. ITP 027 – Dry lining section 4E states that plaster should be fully dry before any paint is applied.
| 01CV - Civils | Cxxx-NCR-000185 | NCR | M&E Inspection Request Forms |  | Contr | VLK |  |  | 2015-07-31 | 2015-07-31 17:29 | 0 | 2015-06-10 08:19 | Mechanical - Mechanical Engineering General | 1000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | M&E installation works are progressing but IRFs aren’t issued to CRL for inspection
| 01CV - Civils | Cxxx-NCR-000186 | NCR | Temporary works |  | Contr | VLK |  |  | 2015-07-31 | 2015-07-15 10:15 | -16 | 2015-06-10 14:31 | Civil - Civil Engineering General | 1000 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate resources | Completed |  | Temporary works to UTX 1 Chamber 1 has been found to be unsafe and inaccessible for utility works to be carried out. The temporary works requirements haven’t been followed as there was no access and egress nor leaning edge protection
| 01CV - Civils | Cxxx-NCR-000187 | NCR | Groundworks adjacent to Denis road |  | Contr | VLK |  |  | 2015-08-20 | 2015-08-12 10:53 | -8 | 2015-06-12 16:16 | Civil - Civil Engineering General | 5000 |  | Supervision/Management | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | During the installation of kerbs adjacent to Denis Road the track ballast along the track side has been contaminated with GEN3 concrete used for Kerbs bedding.
| 01CV - Civils | Cxxx-NCR-000188 | NCR | 1.3.1.1.a Paintshop foundation |  | Contr | VLK |  |  | 2015-07-15 | 2015-06-11 17:36 | -34 | 2015-06-10 17:30 | Civil - Civil Engineering General | 2000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Setting out details for foundation pad on GL13 A were incorrectly set out. As a result the excavation measurements changed to 3.2x3.2M against requirement of 2.3x2.3M resulting in a larger concrete base.
| 01CV - Civils | Cxxx-NCR-000189 | NCR | No design of External Concrete slab adjacent to wheel lathe |  | Contr | VLK |  |  | 2016-03-17 | 2016-03-14 14:52 | -3 | 2015-06-12 16:32 | Civil - Civil Engineering General | 1500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | Concrete slab adjacent to wheel lathe building to north side of Logistic building has been constructed without a design nor a sketch. The infill is part of the old existing slab replacement.
| 01CV - Civils | Cxxx-NCR-000190 | NCR | Concrete slab adjacent to wheel lathe building |  | Contr | VLK |  |  | 2016-03-24 | 2016-03-22 08:55 | -2 | 2015-06-12 16:40 | Civil - Civil Engineering General | 8000 |  | Workmanship | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Other | Completed |  | Following a post pour inspection to the concrete slab adjacent to wheel lathe building to north side of Logistic building the following have been found:- •Inconsistent / variation of finish levels •Poor edge finish along the movement joints
| 01CV - Civils | Cxxx-NCR-000191 | NCR | Dry lining to shotblasting area |  | Contr | VLK |  |  | 2015-07-31 | 2015-07-31 17:30 | 0 | 2015-06-12 16:55 | Architectural - Partitions | 4000 |  | Supervision/Management | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the construction of the dry lining walls to the shot blasting area of the paintshop, the plasterboard hasn’t been fixed 20mm of the floor as per the specification.
| 01CV - Civils | Cxxx-NCR-000192 | NCR | Utility works to UTX1 Chamber 1 |  | Contr | VLK |  |  | 2015-07-31 | 2015-07-31 17:36 | 0 | 2015-06-12 17:03 | Utilities Engineering - Utilities General | 1000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Not Defined | Completed |  | IRFs haven’t been issued for Utility works to UTX1 Chamber 1 that have been completed and backfilled. The subcontractor has completed the check sheets and __ has inspected the works and found to be to a satisfactory standard.
| 01CV - Civils | Cxxx-NCR-000193 | NCR | Inspection of ramp access pre pour |  | Crossrail | XRL |  |  | 2015-08-31 | 2015-08-12 16:37 | -19 | 2015-06-16 21:44 | Civil - Civil Engineering General | 2000 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | Invited to pre pour inspection of ramp to the south of the logistics.The design had been changed from mass fill 6n with a 200mm slab to mass concrete with a TQ however no FCD had been submitted for design acceptance from CRL.The designer had even highlighted acceptance was needed by CRL for work to commence.
| 01CV - Civils | Cxxx-NCR-000194 | NCR | pre pour inspection of ramp |  | Crossrail | XRL |  |  | 2015-07-31 | 2015-07-15 10:22 | -16 | 2015-06-16 21:59 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | Invited to inspect the ramp pre pour to the south of the logistics building.A number of snags were picked up which should have been picked up by __/__. 95mm cover on the 393 mesh was evident in areas next to the building.As little as 20mm cover was apparent to a number of areas throughout the pour were edges of mesh had not been trimmed.Dowels were still present from the existing logistics slab pours.Drawing 21500 shows this detail of the internal slab meeting the external slab with no dowels so these needed removing.Flexcell was used to create separation between the logistics building and the ramp and had been nailed to the building to the recently handed over brickwork.Flexcell shouldn`t have been used as it was identified for previous failings in quality and strip foundations hadn`t been covered in hydrocell/flexcell meaning they would have been incorporated in the ramp and making the rest of the separation detail pointless.
| 01CV - Civils | Cxxx-NCR-000195 | NCR | External concrete slab to south of Logistic Building |  | Contr | VLK |  |  | 2015-10-30 | 2015-11-01 21:08 | 2 | 2015-06-17 14:17 | Civil - Concrete Pavement | 20000 |  | Workmanship | Rework | 2 (6-60k) | Complete | Subcontractor Problems - Interfacing problems | Completed |  | During the concrete pour to bay no.6 and no. 8 to south of Logistic Building, the concrete has gone off and couldn’t be finished properly or not at all. Bay no.6 has been removed within the same shift but bay no.8 adjacent to the OLE gantry will be removed and reinstated at a further date.
| 01CV - Civils | Cxxx-NCR-000196 | NCR | Plessey Road/Road 22 faults |  | Contr | VLK |  |  | 2015-10-16 | 2015-10-15 09:05 | -1 | 2015-06-20 15:53 | Over Head Line Electrification - Over Head Line Electrification General | 6000 |  | Damaged | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | Following the rectification to IL29D detailed in Cxxx-NCR-000122, a further fault has been reported on the weekend of week 9 and __ were called to rectify the issue.
| 01CV - Civils | Cxxx-NCR-000197 | NCR | Grout to floor |  | Crossrail | XRL |  |  | 2015-08-28 | 2015-08-12 16:39 | -16 | 2015-06-26 14:23 | Civil - Civil Engineering General | 1000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | Invited to inspect the grouting to the recess that was left after removal of the bulk paint store.An FCD was raised as there was no design for these works.The approved FCD stated Cemtop would be used however on arrival at the inspection __ had changed this to Ardek without confirmation from their designer or approval from CRL.
| 01CV - Civils | Cxxx-NCR-000198 | NCR | Bulk paint store infill |  | Contr | VLK |  |  | 2015-08-31 | 2015-08-31 19:58 | 0 | 2015-07-01 16:40 | Architectural - General | 8000 |  | Workmanship | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following a post pour inspection to the bulk paint store infill in paintshop building has been identified that the finish on the industrial topping material used, has imperfections such as visible air bubbles (voids).
| 01CV - Civils | Cxxx-NCR-000199 | NCR | Manhole under concrete bay 15 |  | Contr | VLK |  |  | 2015-11-17 | 2015-11-09 18:53 | -8 | 2015-07-07 15:58 | Civil - Civil Engineering General | 10000 |  | Supervision/Management | Repair | 2 (6-60k) | Complete | Subcontractor Problems - Interfacing problems | Completed |  | During the weekend possession concrete pour to bay 15 has been identified that the formation of a manhole opening / box out has been missed during the formation of the slab. The manhole has been temporary covered with steel road plate but missed out when the separation membrane has been installed. The engineers have identified it during the pour and during the circumstances was too late to rectify at the time.
| 01CV - Civils | Cxxx-NCR-000200 | NCR | Damage to concrete edges (corners) of bay 15, 12 |  | Contr | VLK |  |  | 2016-01-11 | 2016-01-18 15:53 | 7 | 2015-07-07 16:33 | Civil - Civil Engineering General | 5000 |  | Damaged | Repair | 3 (3-6k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Following the formwork removal of the concrete bays 12,15 damages occurred to the NE corner of bay 15 and SE corner of bay 12.
| 01CV - Civils | Cxxx-NCR-000201 | NCR | Mezzanine concrete floor slab |  | Contr | VLK |  |  | 2015-11-30 | 2015-11-16 14:55 | -14 | 2015-07-16 07:31 | Civil - Civil Engineering General | 25000 |  | Workmanship | Repair | 2 (6-60k) | Complete | Material/Preservation Problems - Not Defined | Completed |  | Following a site walk out to mezzanine level of the logistic building has been identified that delamination of the concrete slab surface occurs in few isolated areas.
| 01CV - Civils | Cxxx-NCR-000202 | NCR | External concrete slabs to South of Logistic Building |  | Contr | VLK |  |  | 2015-11-30 | 2015-11-23 09:29 | -7 | 2015-07-16 10:39 | Civil - Concrete Pavement | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | External Phenomenon - Weather or ambient condition | Completed |  | Following a post pour inspection of bay 2 to south of Logistic Building concrete slabs has been identified that the surface of the slab is delaminating.
| 01CV - Civils | Cxxx-NCR-000203 | NCR | Utility works throughout the project |  | Contr | VLK |  |  | 2015-08-20 | 2015-08-23 17:44 | 3 | 2015-07-17 07:36 | Utilities Engineering - Utilities General | 1000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | A review of fusion weld print outs received to date suggest that there is no demonstration of acceptable installation practices regarding fusion welding of PE pipeworks prior to excavations being backfilled. There is insufficient data regarding clamp usage heating and cooling times. CRL have also not witnessed any of the welding or pressure testing to assure compliant installation methods.
| 01CV - Civils | Cxxx-NCR-000204 | NCR | Syphonic drainage test to high level Paintshop building |  | Contr | VLK |  |  | 2015-08-31 | 2015-08-12 16:49 | -19 | 2015-07-17 09:48 | Architectural - Roofing & Exterior Treatment | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | Following an un-planned inspection to the siphonic roof drainage to paintshop high level has been identified that the fitter/tester wasn’t aware of the accurate testing criteria or pass/fail parameters. The test resulted in a fail as no information has been given to CRL before the formal inspection and the water in the gauge dropped significantly in a 3min period.
| 01CV - Civils | Cxxx-NCR-000205 | NCR | Damage to 4 core 240mm SWA cable |  | Contr | VLK |  |  | 2015-10-30 | 2015-10-09 10:51 | -21 | 2015-07-21 12:47 | Electrical - General | 10000 |  | Damaged | Rework | 2 (6-60k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | During the cable pull activity from outside the carpark through the pits into the Logistics building, the last section of approximately 10M of the 4 core 240mm SWA cable was found to be damaged.
| 01CV - Civils | Cxxx-NCR-000206 | NCR | Bamage to blockwall to office area of Logistic Building |  | Contr | VLK |  |  | 2015-08-20 | 2015-08-20 18:21 | 0 | 2015-07-21 14:47 | Architectural - Finishes | 20000 |  | Damaged | Rework | 2 (6-60k) | Complete | External Phenomenon - Other | Completed |  | Damage has occurred to a block wall panel to the office area GL 12 DE of the Logistic Building after a MEWP has driven into it. The damages occurred to the internal finishes of the mess room to the plasterboard and ceiling grids.
| 01CV - Civils | Cxxx-NCR-000207 | NCR | Traverser paint remedial works |  | Contr | VLK |  |  | 2015-08-20 | 2015-08-23 17:37 | 3 | 2015-07-23 11:13 | Mechanical - Mechanical Engineering General | 1000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | Following an inspection to paint remedial works to traverser the following have been found:- • Check sheets not completed progressively • DFT tests not carried out as per ITP and as mentioned in the paint remedial procedure
| 01CV - Civils | Cxxx-NCR-000208 | NCR | Delamination works materials |  | Contr | VLK |  |  | 2015-08-20 | 2015-08-20 18:22 | 0 | 2015-07-28 12:23 | Architectural - General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | During the delamination works to Logistic building has been identified that the aggregate used with the primer hasn’t gone through the MCR process therefore not accepted by CRL.
| 01CV - Civils | Cxxx-NCR-000209 | NCR | __ compressors |  | Contr | VLK |  |  | 2015-08-20 | 2015-08-20 18:23 | 0 | 2015-07-24 10:21 | Electrical - General | 1000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | __’s Compressors have been delivered to site and installed into the Paintshop compressor room without an MCR.
| 01CV - Civils | Cxxx-NCR-000210 | NCR | Roof leak to Logistic Building |  | Contr | VLK |  |  | 2015-10-30 | 2015-10-15 09:07 | -15 | 2015-08-04 08:15 | Architectural - Flooring | 3000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A leak has been identified in the Logistic Building roof between GL 1-2 A/B.
| 01CV - Civils | Cxxx-NCR-000211 | NCR | Crack in screeding to wealfare area |  | Contr | VLK |  |  | 2015-10-30 | 2015-10-18 19:44 | -12 | 2015-08-03 15:53 | Architectural - Flooring | 3000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Cracks in screeding have been identified to welfare area of the Logistic Building through the width of the corridor approximately between GL 6-7 and in front of lobby entrance door.
| 01CV - Civils | Cxxx-NCR-000212 | NCR | Concrete level to Logistic Building entrences |  | Contr | VLK |  |  | 2017-05-31 | 2017-03-31 16:51 | -61 | 2015-08-04 08:32 | Civil - Civil Engineering General | 10000 |  | Workmanship | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Other | Completed |  | Following a post pour inspection to Logistic Building external slabs, incorrect falls in the concrete have been identified to the south main entrance (top of stairs to lobby door) and the pedestrian access on the east end.
| 01CV - Civils | Cxxx-NCR-000213 | NCR | Damaged Armoured joints to Logistic Building slab |  | Contr | VLK |  |  | 2015-11-30 | 2015-11-30 14:26 | 0 | 2015-08-04 08:41 | Architectural - General | 20000 |  | Damaged | Repair | 2 (6-60k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | During the remedial works to Logistic Building floor slab, the ride on planer has passed over the armoured joint resulting in a damage to already installed product. Additional, following a post pour inspection, variation in finished level heights between the armoured joints and screeding have been identified.
| 01CV - Civils | Cxxx-NCR-000214 | NCR | OLE foundations to WSA |  | Contr | VLK |  |  | 2015-11-21 | 2015-11-19 10:13 | -2 | 2015-08-04 09:00 | Civil - Civil Engineering General | 10000 |  | Documentation and Records | Repair | 2 (6-60k) | Complete | Supervision - Supervisor does not have sufficient experience | Completed |  | Following an inspection to the OLE foundation on GL 1 at WSA a cable and duct were identified. The solution implemented on site was to cantilever approx. a150mm of blinding with mesh over the ducts and place the OLE bases over the top. The solution has not been endorsed by the designer.
| 01CV - Civils | Cxxx-NCR-000215 | NCR | Damage to floor screed due to roof leak |  | Contr | VLK |  |  | 2015-11-20 | 2015-11-23 08:52 | 3 | 2015-08-04 17:02 | Architectural - General | 6000 |  | Damaged | Repair | 3 (3-6k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | Damaged to floor screed (isolated spot approx. 100-150mm diameter) has occurred due to a leak in the Logistic Building high level roof GL1/2 A-B.
| 01CV - Civils | Cxxx-NCR-000216 | NCR | Denis Road line and levels |  | Contr | VLK |  |  | 2016-03-07 | 2016-03-18 12:25 | 11 | 2015-08-05 08:51 | Track - Track General | 15000 |  | Design | Use As-Is | 2 (6-60k) | Complete | Design Problem - Other | Completed |  | A variation in levels has been identified while making the connection on Denis Road from the SNC into the paintshop. A full investigation has commenced and more details will be provided once collated.
| 01CV - Civils | Cxxx-NCR-000217 | NCR | Welfare area screed |  | Contr | VLK |  |  | 2015-08-31 | 2015-08-30 13:40 | -1 | 2015-08-07 15:23 | Architectural - General | 2000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following the compressive test on the screed samples the results do not comply with the requirements of the ITP and the specification (i.e. >25N/mm2 after 28 days).
| 01CV - Civils | Cxxx-NCR-000218 | NCR | WSA Precast pit units concrete mix design |  | Contr | VLK |  |  | 2015-09-30 | 2015-09-30 22:30 | 0 | 2015-08-07 17:09 | Civil - Civil Engineering General | 1000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | Following a surveillance performed at __ premises (pre-cast pits manufacturer), it was identified that concrete mix design has been changed between __ and __ without __ been informed.
| 01CV - Civils | Cxxx-NCR-000219 | NCR | WSA Inconsistent concrete flow test performed during casting of __ PC units |  | Contr | VLK |  |  | 2015-10-31 | 2015-11-01 21:55 | 1 | 2015-08-07 17:40 | Civil - Civil Engineering General | 1000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During a surveillance performed at __ premises (pre-cast manufacturer of pit units) it was identified that the number of concrete flow tests performed was not in line with the ITP requirements.
| 01CV - Civils | Cxxx-NCR-000220 | NCR | WSA Inconsistent concrete cube sampling during casting of __ pre-cast pit units. |  | Contr | VLK |  |  | 2016-02-12 | 2016-03-14 15:12 | 31 | 2015-08-07 17:48 | Civil - Civil Engineering General | 4000 |  | Supervision/Management | Use As-Is | 3 (3-6k) | Complete | Verification Problems - Other | Completed |  | During a surveillance performed at __ premises (pre-cast concrete manufacturer) it was identified that the number of concrete cube sampling was not in line with the ITP requirements.
| 01CV - Civils | Cxxx-NCR-000221 | NCR | WSA Use of non ISO 9001 (UKAS) accredited supplier |  | Contr | VLK |  |  | 2015-09-30 | 2015-10-01 09:13 | 1 | 2015-08-07 18:06 | Civil - Civil Engineering General | 3000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | During an off-site subcontractor audit/review performed at __ premises (pre-cast concrete manufacturer) it was identified that __ precast, the UK branch of __ Holland, is not accredited to UKAS ISO 9001:2008.
| 01CV - Civils | Cxxx-NCR-000222 | NCR | Grout pads to traverser pit rail |  | Contr | VLK |  |  | 2016-01-22 | 2016-01-29 17:34 | 7 | 2015-08-07 18:05 | Track - Track General | 6000 |  | Damaged | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | Cracks have been identified to the grouted pads underneath the travereser rail to Paintshop building.
| 01CV - Civils | Cxxx-NCR-000223 | NCR | Bulk paint store design |  | Contr | VLK |  |  | 2015-12-10 | 2015-12-12 01:51 | 2 | 2015-08-07 18:20 | Architectural - General | 10000 |  | Documentation and Records | Rework | 2 (6-60k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | Bulk paint store has been relocated to the logistic building from the paintshop as agreed with the stakeholders and CRL but the installation has commenced without a design being accepted by CRL.
| 01CV - Civils | Cxxx-NCR-000224 | NCR | WSA Fabrication of OLE gantries (Hambleton) without approved MCRs |  | Contr | VLK |  |  | 2015-09-30 | 2015-10-01 08:48 | 1 | 2015-08-07 18:12 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | The fabrication of OLE gantries (Hambleton) for WSA has commenced without approved MCRs.
| 01CV - Civils | Cxxx-NCR-000225 | NCR | Floor vinyl |  | Contr | VLK |  |  | 2015-09-30 | 2015-10-01 08:51 | 1 | 2015-08-08 13:16 | Architectural - Flooring | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | It has been noticed that sub-contractor doing the vinyl flooring works has brought and used materials on site without going through MCR process.
| 01CV - Civils | Cxxx-NCR-000226 | NCR | UKAS Accreditation |  | Crossrail | XRL |  |  | 2015-10-30 | 2015-10-26 14:17 | -4 | 2015-08-10 13:09 | Architectural - Flooring | 1000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Not Defined | Completed |  | A post review of __ Limited UKAS accreditation numberxxxx was carried out; it was found that no information existed on the UKAS website regarding the company and its accreditation. UKAS were consulted on this matter and they stated by email that __ Ltd resigned their UKAS accreditation in September 2014 and part of the resignation process is that they should cease to claim accreditation and remove all trace of the UKAS accreditation symbols from reports and marketing materials. UKAS also stated that the report in question has been issued after the date of resignation, and in light of the potential to confuse and mislead the market place, UKAS has logged this matter as feedback into its database under the reference 345322, and have written to __ Ltd to request they remove all references to UKAS from their documentation including the accreditation symbol. UKAS have also asked that they identify all reports issued with the UKAS symbol and accreditation number contained within it, which have been issued post resignation, be withdrawn and reissued to their customers. Evidence of this correction has been requested on or before 4th September 2015. On request the Contractor was not able to supply evidence that the Works Information Volume 2A – Part 20.8 had been complied with
| 01CV - Civils | Cxxx-NCR-000227 | NCR | No Evidence of flow Test Training |  | Crossrail | XRL |  |  | 2015-10-31 | 2015-11-01 21:57 | 1 | 2015-08-10 13:17 | Architectural - Flooring | 1500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not trained for the work being performed | Completed |  | The Contractor was asked to supply the appropriate training records for the flow testing of pump screed. On request the Contractor was not able to supply evidence as per the Works Information Volume 2A – Part 20.8
| 01CV - Civils | Cxxx-NCR-000228 | NCR | UKAS Accreditation |  | Crossrail | XRL |  |  | 2016-01-15 | 2016-01-26 09:42 | 11 | 2015-08-10 13:24 | Architectural - Flooring | 3500 |  | Documentation and Records | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Worker not qualified | Completed |  | A post review of the testing laboratories schedule of accreditation was carried out , and it was found that __ Company Ltd (UKAS xxxx), are not accredited to carry compressive and flexural strength testing to BS EN 13892-2 which is a test requirement as shown on the Fastfloor IT technical data sheet. The Contractor was requested to supply evidence of acceptance to an alternative testing proposal by the CRL Project Manager, as described in the Works Information Volume 2A – Part 20.8 which they were unable to provide
| 01CV - Civils | Cxxx-NCR-000229 | NCR | Materials |  | Crossrail | XRL |  |  | 2015-09-21 | 2015-09-17 21:46 | -4 | 2015-08-10 13:30 | Architectural - Flooring | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Error by manufacturer in shipping or marking | Completed |  | The materials for the Logistic Building floor slab screed were not referenced in the latest revision of the Material Proposal Schedule (MPS) Cxxx-VLK-N2-LRC-CR112_SD007-50004 Rev 4.0 (09/07/2015)
| 01CV - Civils | Cxxx-NCR-000230 | NCR | Essex&Suffolk inspection |  | Contr | VLK |  |  | 2015-11-20 | 2015-11-18 16:59 | -2 | 2015-08-12 11:16 | Utilities Engineering - Water | 15000 |  | Incorrect Installation | Rework | 2 (6-60k) | Complete | External Phenomenon - Other | Completed |  | Following an inspection to the water services, Essex&Suffolk Water has identified Regulation contraventions/issues that require rectification to ensure that the water supply remains wholesome and waste does not occur. Details of these issues and the remedial work required to resolve them are provided in the report appended.
| 01CV - Civils | Cxxx-NCR-000231 | NCR | Condensers on Mezzanine level |  | Contr | VLK |  |  | 2016-03-18 | 2016-03-22 09:08 | 4 | 2015-08-12 11:41 | Mechanical - Mechanical Engineering General | 2000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Radiators on new condensers to Mezzanine level found to be damaged and will require repair/replacement prior to completion of works.
| 01CV - Civils | Cxxx-NCR-000232 | NCR | WSA Injection Resin verification records |  | Contr | VLK |  |  | 2015-10-30 | 2015-10-08 09:49 | -22 | 2015-08-12 13:40 | Civil - Civil Engineering General | 2000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Not Defined | Completed |  | The check sheets used on site as part of the Uretek - ground improvement works (resin injection), are differenet in content than the check sheet template as provided with the ITP. Also the __e 2.5 in the ITP; "Exctraction of Injection Tubes and Filling the Holes", is not inlcuded in either check sheet.
| 01CV - Civils | Cxxx-NCR-000233 | NCR | Concrete bays to east of Logistic Building |  | Contr | VLK |  |  | 2016-03-07 | 2016-03-14 11:57 | 7 | 2015-08-12 15:23 | Civil - Civil Engineering General | 1500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | During the concrete pour within the possession works has been identified that the concrete used hasn't been tested for air content.
| 01CV - Civils | Cxxx-NCR-000234 | NCR | Screed Joints to welfare area of Logistic Building |  | Contr | VLK |  |  | 2015-11-17 | 2015-10-15 09:08 | -33 | 2015-08-12 15:29 | Architectural - General | 2000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the vinyl flooring it has been identified that the screed joints along the gridlines and doorways have been covered with latex.
| 01CV - Civils | Cxxx-NCR-000235 | NCR | Damage to DBs and MDUs |  | Contr | VLK |  |  | 2015-10-30 | 2015-11-01 22:03 | 2 | 2015-08-12 15:50 | Electrical - General | 1000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Not Defined | Completed |  | Damages occurred to the Distribution Boards and Mechanical Distribution Units in the Paintshop building.
| 01CV - Civils | Cxxx-NCR-000236 | NCR | WSA Drainage pipe not installed trough rail slab ar road 5 |  | Contr | VLK |  |  | 2015-11-30 | 2015-11-19 10:13 | -11 | 2015-08-12 17:00 | Civil - Drainage | 10000 |  | Supervision/Management | Repair | 2 (6-60k) | Complete | Supervision - Insufficient supervision | Completed |  | While casting the rail sub slab at road 5, a drainage pipe was ommited.
| 01CV - Civils | Cxxx-NCR-000237 | NCR | Vehicle restrain barrier |  | Contr | VLK |  |  | 2016-03-17 | 2016-03-25 14:27 | 8 | 2015-08-14 13:46 | Civil - Civil Engineering General | 2000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | During a informal inspection to the installation of ther vehicle restrain barrier it has been identified that the chemfix has been used to infill the underside of the foot plate instead of grout as the initial specification. The chem fix used wasn't accepted via MCR process.
| 01CV - Civils | Cxxx-NCR-000238 | NCR | M&E inspection to paintshop - LV MDB |  | Contr | VLK |  |  | 2015-11-30 | 2015-10-22 11:08 | -39 | 2015-08-16 10:08 | Electrical - General | 5000 |  | Supervision/Management | Rework | 3 (3-6k) | Complete | Supervision - Not Defined | Completed |  | Following an inspection to the LV MDB in the Paint Shop the following have been found:- • Material of door gaskets to be checked that they are neoprene, as per the spec. • Traverser door gasket not secure • Doors are not lockable as per the spec • No windows provided for thermal imaging, as per the spec and requested to be added at the FAT • Heavy duty cable trays to support cables are not installed, as per the spec and cables in the chambers are very untidy • No circuit schedule or diagrams • DB earth bar is mounted externally and all earths have to exit the panel via a gland. Earth bar should be mounted internally. • Blemishes on door panels (minor) • Screw protector on main incomer chamber missing • Spring washers missing on main incoming terminals • Labels for cables are handwritten, do not have a from and to on them and are not distinguished between PB1 (1+2) • Cables to be re-crimped and heat shrink added in External lighting MCCB • Mech Control Panel label is not consistent with field device, one will need to be re-labelled • __ frame is fixed to top of panel, the panel don't seem to be designed for this amount of load • MCCP panel gland to be re-done, SWA protruding from rear • Stuffing glands for earth cables are not tight.
| 01CV - Civils | Cxxx-NCR-000239 | NCR | Fixing issue for the main earth bar in the Paint Shop |  | Contr | VLK |  |  | 2015-10-30 | 2015-10-26 14:29 | -4 | 2015-08-16 10:16 | Electrical - General | 5000 |  | Workmanship | Rework | 3 (3-6k) | Complete | Design Problem - Not Defined | Completed |  | Following an inspection to the Paintshop it has been identified that the earth bar has been fixed directly to cladding with self tappers and is in a position it will be used for standing on, additional supporting frame required.
| 01CV - Civils | Cxxx-NCR-000240 | NCR | Primary containment to Paintshop between GL 7/C and GL10/C |  | Contr | VLK |  |  | 2015-11-30 | 2015-10-15 09:10 | -46 | 2015-08-16 10:24 | Electrical - General | 5000 |  | Supervision/Management | Rework | 3 (3-6k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Following a survey to Paint Shop primary containment between GL7/C and GL10/C the following have been found:- • Tray directly above MDB holding earth cables is buckled due to cables being too tight • Trunking directly above MDB has no end cap • Significant amount of hold down brackets missing on ladder rack and brackets are distorted due to stress from cables. Brackets need to be extended • Various brackets are loose • __ brackets on vertical run to PB1 and Security Panel are not level. • Tray for comms cabinet is not consistent and has not used manufactured bends • Trunking and tray at GL7/C is not adequately supported for offsets at 3x locations (GL7 x2 & GL9/10 x1) • Threaded rod cap missing • Double unstrut at GL10 has sustained damage and will need to be replaced. • End caps missing in various locations.
| 01CV - Civils | Cxxx-NCR-000241 | NCR | Duct work above booths in Paintshop |  | Contr | VLK |  |  | 2015-11-30 | 2015-11-23 16:02 | -7 | 2015-08-16 11:06 | Mechanical - Mechanical Engineering General | 2000 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Following repetitive inspections to duct work above booths installed by __, the following have been found:- • Loose bolts to connections or not at all • Bolts being too short • Clamps to connections being loose or falling down at movement • Some bolts being over tight and bent • Water leaking through roof penetration of duct work • Dents in various locations
| 01CV - Civils | Cxxx-NCR-000242 | NCR | Trunking to booths, shot blasting area of the Paintshop |  | Contr | VLK |  |  | 2015-10-30 | 2015-10-08 09:55 | -22 | 2015-08-17 07:54 | Electrical - General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Following an informal inspection through the Paintshop ( booths, shot blasting area) has been identified that sub-contractor __ has installed LeGrand 'Salamande' trunking instead of Unitrunk Trunking which has been accepted by CRL @code 2 ( Cxxx-VLK-A-LRC-CR112_SD007-50048 ). This is also applicable for the cable tray which should be __ ( Heavy duty Galvanized Cable tray - @code 2 ) but they have installed LeGrand 'Swift'.
| 01CV - Civils | Cxxx-NCR-000244 | NCR | Vehicle restraint barreir and bollards |  | Contr | VLK |  |  | 2015-10-16 | 2015-10-09 10:54 | -7 | 2015-08-19 15:09 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | The installation of the Vehicle restrain barriers and bollards commenced without MCRs accepted by CRL. The MCRs were submitted 2 days before the installation.
| 01CV - Civils | Cxxx-NCR-000245 | NCR | Above ground drainage installation |  | Contr | VLK |  |  | 2015-10-16 | 2015-10-05 12:03 | -11 | 2015-08-19 15:44 | Mechanical - Mechanical Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | The installation of drainage above ground to paintshop has commenced governed by ITP 113 @code 3.
| 01CV - Civils | Cxxx-NCR-000246 | NCR | Shortfall in documentation for shear stud welding to mezzanine deck |  | Contr | VLK |  |  | 2015-11-28 | 2015-11-27 16:22 | -1 | 2015-08-19 16:01 | Structural Engineering - Welding | 2000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | Following a review of the available documentation for the composite mezzanine deck shear stud welding it has been identified that there is a shortfall in documentation required by CRL. A TQ has been raised to __ and confirmed acceptable as per the attached response to TQ.
| 01CV - Civils | Cxxx-NCR-000247 | NCR | Pre pour inspection to south of the paintshop concrete pour |  | Contr | VLK |  |  | 2015-10-09 | 2015-10-08 10:01 | -1 | 2015-08-20 15:22 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | Following a formal inspection to the concrete pre-pour to south of the paintshop the following have been identified:- • Inadequate separation between impending pour and the existing structure. Brickwork and strip foundations were exposed in numerous locations. • Loose sub base next to buildings. • Incorrect level ( 15mm too low) of the separation between impending pour and the top of the Rosehil angle.
| 01CV - Civils | Cxxx-NCR-000248 | NCR | Earthing and Bonding Strategy |  | Contr | VLK |  |  | 2015-10-30 | 2015-11-01 22:07 | 2 | 2015-08-20 16:14 | Over Head Line Electrification - Earthing & Bonding | 10000 |  | Design | Rework | 2 (6-60k) | Complete | Design Problem - Inadequate or defective design | Completed |  | 2No AFC E&B documents available for Stage 1 works are incorrect and in conflict: C11187-4.18-TICS-BONDING PLAN Ext 828-VLK-R2-DDD-R12-SD007-1-48010 C11187-4.10-Cxxx-VLK-E-STP-CR112_SD007-50002 – Earthing and bonding strategy The former document does not take into consideration how to dissipate the OLE fault back to traction return if the OLE comes into contact with the Paintshop The latter document details substation is bonded to the to a spider plate Neither document details the extent of bonding required to commission stage 1 works detailed in A02ILF-TC-2_AQE5-RED (TICS 3-6 Bonding Plan)
| 01CV - Civils | Cxxx-NCR-000249 | NCR | __'s compressors |  | Contr | VLK |  |  | 2015-11-30 | 2015-11-16 13:37 | -14 | 2015-08-21 12:23 | Mechanical - Mechanical Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Not Defined | Completed |  | __’s Compressors have been delivered to site and installed into the Paintshop compressor room without an MCR. This NCR is raised as a result of Cxxx-NCR-000209 being closed out incorrectly as a code 3 comment for the MCR was raised after closure of the NCR
| 01CV - Civils | Cxxx-NCR-000250 | NCR | Substation back wall |  | Contr | VLK |  |  | 2015-10-30 | 2015-10-15 09:15 | -15 | 2015-08-24 15:41 | Architectural - Masonary | 1500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following a snagging inspection to the substation it has been identified that a section of the external switch room brickwall doesn't look plumb.
| 01CV - Civils | Cxxx-NCR-000251 | NCR | Paintshop intruder alarm |  | Contr | VLK |  |  | 2015-11-30 | 2015-12-07 14:35 | 7 | 2015-08-24 16:36 | Systems - Other | 10000 |  | Workmanship | Rework | 2 (6-60k) | Complete | Supervision - Not Defined | Completed |  | Paint Shop intruder alarm door contacts in the Paint and Prep booth escape doors are not installed to specification and standards. Drops from high level are completed in an unsupported flexible conduit to the door contact and when it is taken from the door frame it has been left in it drops and covers the door.
| 01CV - Civils | Cxxx-NCR-000252 | NCR | Electrical instalation in the Shot Blast enclosure |  | Contr | VLK |  |  | 2016-02-15 | 2016-02-18 09:49 | 3 | 2015-08-28 11:45 | Electrical - General | 10000 |  | Workmanship | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Following an inspection to Shot Blasting enclosure the following have been identified:- • Switches and fire alarm break glasses are at different heights • Fire alarm beacons are fitted to fire stop materials • Conduits are loose and not earthed • Inadequate supports to containment • Cantilever brackets are installed to cladding • Trunking lid on bends are not to specification • Tray in areas have not maintained the required spacing containment runs will hinder maintenance on shot blast equipment
| 01CV - Civils | Cxxx-NCR-000253 | NCR | Gas fired heating installation |  | Contr | VLK |  |  | 2016-02-11 | 2016-02-23 15:04 | 12 | 2015-08-31 09:41 | Systems - Other | 10000 |  | Workmanship | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Other | Completed |  | The feed cable for the exhaust extract system at high level in the paint shop is routed through the lighting containment contrary to the specification. This will need to be rerouted.
| 01CV - Civils | Cxxx-NCR-000254 | NCR | Shunt Spur OLE |  | Contr | VLK |  |  | 2015-10-30 | 2015-11-09 19:03 | 10 | 2015-09-01 08:36 | Over Head Line Electrification - Over Head Line Electrification General | 1500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | At location 07/49 on shunt spur road, the height of the wire is 5171mm showing non-conformity in a survey carried out by Podtrack on 12/07/15.This location 07/49 is the flying tail location and the height is not held, only the stagger.
| 01CV - Civils | Cxxx-NCR-000255 | NCR | LV Switchboard |  | Contr | VLK |  |  | 2015-11-12 | 2015-10-09 11:01 | -34 | 2015-09-09 15:33 | Electrical - LV Equipment | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Not Defined | Completed |  | Main LV Switchboard is not installed to a general arrangement drawing and a co-ordinated site drawing was not offered for verification of placement. SAT test results have not been forthcoming from __
| 01CV - Civils | Cxxx-NCR-000256 | NCR | Worshop A - Fabrication of Lifting Jacks (Mechan) has commenced without an approved ITP and MCR |  | Contr | VLK |  |  | 2015-10-31 | 2015-11-01 22:10 | 1 | 2015-09-14 13:25 | Mechanical - Mechanical Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | Workshop A - The off site fabrication of Listing Jacks has commenced without an approved ITP and MCR.
| 01CV - Civils | Cxxx-NCR-000257 | NCR | BMS installation to Paintshop and L&S Building |  | Contr | VLK |  |  | 2015-11-17 | 2015-10-09 11:23 | -39 | 2015-09-14 15:52 | Systems - Other | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Not Defined | Completed |  | The installation of BMS to Logistic Building has commenced without an accepted (minimum code2 ) ITP. The current status of ITP 088 Logistic and Stores Building Management System ITP is accepted code 3.
| 01CV - Civils | Cxxx-NCR-000258 | NCR | Construction drawings |  | Crossrail | XRL |  |  | 2015-10-31 | 2015-10-15 09:27 | -16 | 2015-09-14 16:28 | Mechanical - Mechanical Engineering General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | The following sample drawings for space heating have been provided by the Contractor during the surveillance Cxxx-VKL-M-DDA-CR112_SD007_Z-78017, Cxxx-VLK-M-DDB-CR112_SD007_Z-03012, 828-VLK-M-DDB-CR112_SD007_Z-03013. These drawings have been used for the installation of the gas fired tube heaters although they were in revision P0x and not Issued For Construction (IFC). The Project Field Engineer (PFE) informed that this is a result of PMI176 and that the Gate approval process had not been finalised yet. During the surveillance the IFC design and drawings for the Paintshop were not released. The provided P0x drawings are not to sufficient detail. Setting out information are missing and causing a potential risk in respect of installation, services coordination and abortive work on site. To ensure that the IFC drawings are issued immediately and the potential risk is minimised Cxxx-NCR-000258 has been raised on the grounds that the contractor is still proceeding with the installation based on the P0x drawings beyond the date of 16 March 2015 which was the cut off date agreed by the Project Manager in PMI171.
| 01CV - Civils | Cxxx-NCR-000259 | NCR | Construction Programme for Paint Shop |  | Crossrail | XRL |  |  | 2015-10-31 | 2015-10-15 09:20 | -16 | 2015-09-14 16:48 | Mechanical - Mechanical Engineering General | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Stage 1 Commissioning Programme Draft 21 07 2015_ Full document, which is part of the ‘Testing and Commissioning Plan’ (doc. ref. no. Cxxx-VLK-O8-STP-CR112_SD007-50001) for the Paint Shop has been reviewed. It shows a number of activities scheduled post the current hand-over date (28 August 2015 - as advised at the meeting). For instance, activity reference number 655-COM-3780 ‘Paintshop Building Full Commissioning’ ends on 16 September 2015. Similarly, activity number 655-COM-4060 ‘Fire Alarm Integration Testing’ is scheduled until 1 October 2015. Also, phase 2 gas installation strength, tightness and purging testing activities are planned for completion on 11 September 2015 (activity number 655-COM-1450 to 1470).
| 01CV - Civils | Cxxx-NCR-000260 | NCR | Glazed screen to mess room |  | Contr | VLK |  |  | 2016-01-04 | 2016-01-04 15:31 | 0 | 2015-09-15 15:20 | Architectural - Finishes | 5000 |  | Design | Repair | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | It has been identified that the glazed screen to mess room of office area in the Logistic Building hasn't been installed as per details within drawing NK 017437-21424 part of Logistic Building fit out details (Cxxx-VLK-A-DWG-CR112_SD007-50005 Rev 4.0 @code 1). The glazed screen is installed approximately 30 mm from the external blockwork face.
| 01CV - Civils | Cxxx-NCR-000261 | NCR | Failure of Gen 3 concrete on kerb backing south of logistics |  | Contr | VLK |  |  | 2015-12-21 | 2015-12-14 16:14 | -7 | 2015-09-22 09:51 | Civil - Kerbs | 5000 |  | Workmanship | Rework | 3 (3-6k) | Complete | Management Problem - Inadequate supervision | Completed |  | Concrete backing on the kerb line south of logistics building ( near to goods in road ) G/L 1-4 has not set. Concrete crumbles off and need replacement.
| 01CV - Civils | Cxxx-NCR-000262 | NCR | ceiling to shot blast area |  | Crossrail | XRL |  |  | 2015-11-21 | 2015-10-22 11:05 | -30 | 2015-09-22 09:47 | Architectural - Ceilings & Soffits | 2000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Supervision - Other | Completed |  | Contractor was instructed to ensure all the plasterboard ceiling panels should be free from tears.This was also stated in ITP 183 section 3.2.
| 01CV - Civils | Cxxx-NCR-000265 | NCR | Manhole covers |  | Crossrail | XRL |  |  | 2015-12-07 | 2015-11-30 09:56 | -7 | 2015-09-23 18:08 | Civil - Utilities Engineering | 1000 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | It has been identified on site that manhole lids have been used that do not have accompanying MCR`s.1 mcr has been submitted for Hart manhole covers however Centurion and Peter Savage covers have also been used on site.
| 01CV - Civils | Cxxx-NCR-000266 | NCR | Water penetration into ducts and man holes. |  | Crossrail | XRL |  |  | 2015-12-12 | 2015-12-20 22:20 | 8 | 2015-09-23 18:18 | Civil - Utilities Engineering | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | It was noted during a surveilance to the cable duct inspection chambers the water levels were considerably high and increasing.This will mean water will be in the cable ducts in the not so near future.These ducts according to the __ should be water tight and free from water.The sump that was removed early stages of the product needs to be reintroduce or a similar scheme.
| 01CV - Civils | Cxxx-NCR-000267 | NCR | 2.2.2.4.a Incorrect installtion of cat ladder on grid 16A |  | Contr | VLK |  |  | 2016-01-25 | 2016-01-31 22:19 | 6 | 2015-09-30 12:03 | Archaeology - General | 1000 |  | Supervision/Management | Reject | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | During a joint site inspection by __ & CRL, it is noticed that the cat ladder on grid 16 A/B was NOT installed as per drawing.
| 01CV - Civils | Cxxx-NCR-000268 | NCR | Paint Shop - Shot Blast bay - electrical sockets installed are not meeting IP 65 requirements |  | Contr | VLK |  |  | 2016-04-30 | 2016-05-03 09:34 | 3 | 2015-09-30 14:17 | Electrical - Power Distribution | 5000 |  | Supervision/Management | Rework | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | it is observed that the electrical sockets installed in paint shop shot blast bay are not meeting IP 65 requirements
| 01CV - Civils | Cxxx-NCR-000269 | NCR | 1.3.2.2.a - Multiple dmages to Paintshop Cladding |  | Contr | VLK |  |  | 2016-04-30 | 2016-04-27 07:35 | -3 | 2015-09-30 15:10 | Architectural - Roofing & Exterior Treatment | 40000 |  | Damaged | Repair | 2 (6-60k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | During joint site inspections with __, CRL and BT, it is observed that the external cladding was damaged at several locations. a separate snag list is being prepared.
| 01CV - Civils | Cxxx-NCR-000270 | NCR | 2.2.2.2.a - Multiple damages to logisticks builing cladding works |  | Contr | VLK |  |  | 2016-04-30 | 2016-04-27 08:05 | -3 | 2015-09-30 15:14 | Architectural - Roofing & Exterior Treatment | 20000 |  | Damaged | Repair | 2 (6-60k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | During joint site inspections with __, CRL and BT, it was observed that the cladding works are damaged at several locations. A separate snag list is being prepared
| 01CV - Civils | Cxxx-NCR-000271 | NCR | Rain water Harvesting System |  | Contr | VLK |  |  | 2015-11-30 | 2015-12-07 14:47 | 7 | 2015-10-05 19:08 | Systems - Other | 1000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | It ha been identified that the pipework installed for the Rain Harvesting Water System is outside the specification, copper instead of Mapress stainless steel or equal approved.
| 01CV - Civils | Cxxx-NCR-000272 | NCR | 2.5.1.1.a SITE WIDE GAS DISTRIBUTION |  | Contr | VLK |  |  | 2015-10-30 | 2015-11-01 22:14 | 2 | 2015-10-07 11:14 | Utilities Engineering - Gas | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Not Defined | Completed |  | Assurance documentation missing as required by ITP 12 No Missing CUS check-sheets 10 No Electrofusion Reports 18 No Photographs
| 01CV - Civils | Cxxx-NCR-000273 | NCR | Manhole Cover for SC1 and SC2 |  | Contr | VLK |  |  | 2015-11-05 | 2015-11-09 19:05 | 4 | 2015-10-08 11:06 | Civil - Drainage | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | D400 to BS EN 124, 600x600 clear opening, 100mm manhole covers are used in place of D400 to BS EN 124, 600x600 clear opening, 150mm throughout the project
| 01CV - Civils | Cxxx-NCR-000274 | NCR | Ventilated Manhole Cover |  | Contr | VLK |  |  | 2016-02-25 | 2016-03-03 15:49 | 7 | 2015-10-08 11:57 | Civil - Drainage | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Three number manhole covers, Inter-Ax BD141/ 1 by Pam (or similar approved). load Class D400 to BS EN 124, 600x600 clear opening, 100mm deep Covers are used in place of Inter-Ax BD161/ 1 by Pam (or similar approved). load Class D400 to BS EN 124, 600x600 clear opening, 150mm deep (Ventilated Covers). Note, this NCR relates to use of non ventilated covers only. The change in depth is covered under Cxxx-NCR-000273.
| 01CV - Civils | Cxxx-NCR-000275 | NCR | Cat ladders |  | Contr | VLK |  |  | 2017-02-25 | 2017-02-24 10:34 | -1 | 2015-10-09 14:20 | Architectural - General | 5000 |  | Design | Repair | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | I has been identified that the Cat Ladder on GL16 AB of Logistic Building hasn't been installed as per design / drawing. The landing braces / brackets to structural steel are different from design information and the cat ladder is braced on structures cross bracings limiting the movement allowance.
| 01CV - Civils | Cxxx-NCR-000276 | NCR | cable bond chamber covers |  | Contr | VLK |  |  | 2015-11-13 | 2015-11-13 17:48 | 0 | 2015-10-11 18:19 | Civil - Civil Engineering General | 1500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | The installation of the cable bond chamber covers has commenced without the acceptance of materials via MCR process and as per drawing where peter Savage 1800 series bespoke covers are mentioned.
| 01CV - Civils | Cxxx-NCR-000277 | NCR | Workshop A - DPS Beacon lights location clashes with the secondary steel |  | Contr | VLK |  |  | 2016-06-30 | 2016-06-27 07:59 | -3 | 2015-10-13 16:05 | Electrical - LV Equipment | 2000 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | Workshop A - DPS Beacon lights location clashes with the secondary steel beams.
| 01CV - Civils | Cxxx-NCR-000278 | NCR | Workshop A - Diesel extract ends left open |  | Contr | VLK |  |  | 2016-03-31 | 2016-03-18 12:16 | -13 | 2015-10-13 16:06 | Mechanical - Heating Ventilation & Air Conditioning | 10000 |  | Supervision/Management | Use As-Is | 2 (6-60k) | Complete | Management Problem - Other management problem | Completed |  | Workshop A - High level diesel extract ductwork ends left open prior to completion of works.
| 01CV - Civils | Cxxx-NCR-000279 | NCR | Workshop A - High bay lights position clash with the new OLE gantry beams. |  | Contr | VLK |  |  | 2016-06-30 | 2016-06-07 10:55 | -23 | 2015-10-13 16:07 | Electrical - Lighting | 4000 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | Workshop A - High bay lights position clash with the position of the new OLE gantries. Total of 9 lights: Grid line 2, walkway 3, i no. light, Grid line 5, walkway 3, i no. light, Grid lines 7-8, all 4 no. lights, Grid lines 11-12, walkways 3 and 4, 2no. lights, Grid lines 15-14, walkways 3, 1 no. lights.
| 01CV - Civils | Cxxx-NCR-000280 | NCR | 2.6.1.1.a Statuary Water & Meter & Distribution to Buildings |  | Contr | VLK |  |  | 2015-10-30 | 2015-10-26 14:51 | -4 | 2015-10-15 12:43 | Utilities Engineering - Water | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | Assurance Documentation missing as required by ITP 1 No Missing CUS check-sheet of 63 reqd. 19 No Missing Electrofusion Reports of 63 reqd. 7 No Photographs of 63 reqd.
| 01CV - Civils | Cxxx-NCR-000281 | NCR | 2.6.1.2.a Site Wide Fire Hydrants - Stage 1 |  | Contr | VLK |  |  | 2015-10-29 | 2015-10-26 14:53 | -3 | 2015-10-15 13:43 | Utilities Engineering - Water | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | Assurance Documentation missing as required by ITP 16 No missing CUS check sheets from 132 reqd. 20 No electrofusion reports from 131 reqd. 15 No photographs from 131 Reqd.
| 01CV - Civils | Cxxx-NCR-000282 | NCR | Containment to GL 12 DC |  | Contr | VLK |  |  | 2016-02-20 | 2016-03-07 19:39 | 16 | 2015-10-19 13:20 | Electrical - Electrical Engineering General | 7000 |  | Incorrect Installation | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Other | Completed |  | It has been identified that a section of containment installed on GL 12 DC (above admin room) has been supported on to structural cross braces.
| 01CV - Civils | Cxxx-NCR-000283 | NCR | Bulk paint store instalation to Logistic Building |  | Contr | VLK |  |  | 2016-01-04 | 2016-01-04 07:14 | 0 | 2015-10-19 11:20 | Electrical - Electrical Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | Following the review of the ITP 176 - Bulk Paint Store Enclosure it has been identified that the installation has commenced on a code 3 ITP. The building work elements were reviewed and accepted by CRL but the comments related to M&E activities weren't fully addressed at the time, Rev. 2 of the aforementioned ITP has been resubmitted to CRL on 15.10.2015 with all comments addressed.
| 01CV - Civils | Cxxx-NCR-000284 | NCR | Powder coating to hand rail and Armco barrier |  | Contr | VLK |  |  | 2016-03-21 | 2016-03-22 09:14 | 1 | 2015-10-19 13:33 | Architectural - General | 5000 |  | Manufacturing Defect | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | In various locations has been identified that the powder coating to handrail and Armco barrier system has a number of imperfections and the paint is flacking.
| 01CV - Civils | Cxxx-NCR-000285 | NCR | Walkway hand rail and protection barrier |  | Contr | VLK |  |  | 2016-02-20 | 2016-02-19 10:16 | -1 | 2015-10-21 13:20 | Architectural - General | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | Following a site inspection it has been identified that the protection barrier along the welfare area GL Bb/C 12 /1 hasn't been installed as per drawing detail ( Cxxx-VLK-A-DWG-CR112_SD007-50033 ). The protection barrier foot plates supposed to be installed the other way round on the other side of the walkway.
| 01CV - Civils | Cxxx-NCR-000286 | NCR | Model 700/80, Centrifugal Gas Booster |  | Contr | VLK |  |  | 2015-11-11 | 2015-10-26 15:17 | -16 | 2015-10-21 16:08 | Utilities Engineering - Gas | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | The Centrifugal Gas Booster has been installed on a code 3 MCR.
| 01CV - Civils | Cxxx-NCR-000287 | NCR | Logistic and Stores Gas Meter |  | Contr | VLK |  |  | 2015-11-04 | 2015-11-06 18:05 | 2 | 2015-10-21 16:12 | Utilities Engineering - Gas | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | The gas meter has been installed into Logistic building on a code 3 MCR
| 01CV - Civils | Cxxx-NCR-000288 | NCR | Workshop A - Rail installation |  | Contr | VLK |  |  | 2015-12-31 | 2015-12-07 14:49 | -24 | 2015-11-24 17:41 | Track - Rails and Sleepers | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | The fixing of the base plate bolts has commenced without inspecting the holes for cleanliness.
| 01CV - Civils | Cxxx-NCR-000289 | NCR | Workshop A - Rail Installation |  | Contr | VLK |  |  | 2015-11-30 | 2015-11-09 19:06 | -21 | 2015-10-22 17:32 | Track - Rails and Sleepers | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Not Defined | Completed |  | Worshop A, Road 3; Fixing of the base plate bolts has commenced without holes been inspected for cleanliness.
| 01CV - Civils | Cxxx-NCR-000290 | NCR | Metal works fabrication drawings |  | Contr | VLK |  |  | 2016-01-30 | 2016-01-31 22:22 | 1 | 2015-10-25 12:16 | Architectural - General | 2000 |  | Documentation and Records | Reject | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | It has been identified that metal works fabrication drawings haven't been submitted to CRL.
| 01CV - Civils | Cxxx-NCR-000291 | NCR | Cladding repairs |  | Contr | VLK |  |  | 2015-11-30 | 2015-12-13 13:39 | 13 | 2015-10-27 08:42 | Architectural - General | 2000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | As part of the cladding repairs activity it has been identified that no MCRs have been submitted nor check sheets being completed progressively.
| 01CV - Civils | Cxxx-NCR-000292 | NCR | Debonded delamination repairs |  | Contr | VLK |  |  | 2016-01-20 | 2016-01-31 22:25 | 11 | 2015-10-29 18:10 | Civil - Civil Engineering General | 7000 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Other | Completed |  | Further to remedial works to Logistic Building floor slab captured in Cxxx-NCR-000070 it has been identified that some patch repairs carried out prior to screed toppings are de-bonding.
| 01CV - Civils | Cxxx-NCR-000293 | NCR | WSA-Omitted sump at Western Apron |  | Contr | VLK |  |  | 2016-01-31 | 2016-01-31 22:27 | 0 | 2015-11-03 13:28 | Structural Engineering - Reinforcement | 3000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Reinforcement detail on drawing 23320 states to locally offset H16 bars around 150 dia outlet hole. Sump detail shown on drawing 15502 specified sump to be 200x200 formed to a depth 500mm below bottom of slab.
| 01CV - Civils | Cxxx-NCR-000295 | NCR | Welfare area sealing to pedestrian doors - Smoke enclosure |  | Contr | VLK |  |  | 2015-12-24 | 2015-12-08 15:30 | -16 | 2015-11-04 17:23 | Architectural - Doors | 2000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Gap between flashing and door leaf should be sealed and should not exceed 3mm
| 01CV - Civils | Cxxx-NCR-000296 | NCR | Missing Armoured edge |  | Contr | VLK |  |  | 2016-02-21 | 2016-03-02 19:50 | 10 | 2015-11-05 10:44 | Structural Engineering - Joints | 8000 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Other | Completed |  | The armoured edge on the south side of the table lift slab pit, currently cast 100mm below the design level within the concrete pour. Also there is a slight step in the north side armoured joint resulting a trip hazard.
| 01CV - Civils | Cxxx-NCR-000298 | NCR | Water puddle on concrete |  | Contr | VLK |  |  | 2016-04-08 | 2016-03-29 13:05 | -10 | 2015-11-05 14:05 | Civil - Concrete Pavement | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | A puddle has been noted on the concrete slab north of the substation size of puddle approx. 500 x 500 depth of puddle 4mm
| 01CV - Civils | Cxxx-NCR-000299 | NCR | Installtion of drain and shot balst covers without an MCR |  | Contr | VLK |  |  | 2016-01-15 | 2016-01-29 12:21 | 14 | 2015-11-05 14:21 | Civil - Drainage | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Drains and shot blast covers installed with an MCR
| 01CV - Civils | Cxxx-NCR-000300 | NCR | Lack of off site ITP for __ works-OLE Structure fabrication |  | Contr | VLK |  |  | 2016-04-29 | 2016-04-17 20:15 | -12 | 2015-11-06 09:35 | Structural Engineering - Steel Member | 1000 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Verification Problems - Not Defined | Completed |  | It is noticed that OLE structural fabrication contractor for __ works (LU__) didn't submit any off site fabrication ITP of steel structure for cross rail acceptance.
| 01CV - Civils | Cxxx-NCR-000301 | NCR | Workshop A - Pumping chamber installed without no approved MCR |  | Contr | VLK |  |  | 2016-02-10 | 2016-02-19 10:25 | 9 | 2015-11-07 12:52 | Systems - Drainage/Pumping Systems | 1000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | Pumping chamber installed without no approved MCR in place
| 01CV - Civils | Cxxx-NCR-000302 | NCR | East of Logistic car park concrete slab |  | Contr | VLK |  |  | 2016-01-08 | 2016-01-31 22:31 | 23 | 2015-11-13 09:01 | Civil - Concrete Pavement | 30000 |  | Workmanship | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Other | Completed |  | East of Logistic car park concrete slab bays 32,35 & 38 finished level & texture are not meeting requirements
| 01CV - Civils | Cxxx-NCR-000303 | NCR | Not sufficient clearance to the underside of the base plate for Grouting along grid line E |  | Contr | VLK |  |  | 2016-01-31 | 2016-01-28 19:52 | -3 | 2015-11-16 09:10 | Structural Engineering - Grouting | 5000 |  | Workmanship | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | Not sufficient clearance to the underside of the base plate for Grouting along grid line E
| 01CV - Civils | Cxxx-NCR-000304 | NCR | Cast in items missed or incorrect material. |  | Contr | VLK |  |  | 2016-04-14 | 2016-04-16 20:22 | 2 | 2015-11-16 14:12 | Structural Engineering - Pre-cast | 1500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | Incorrect material pipe cast within the units for drainage purpose .Also there is no collar left in the precast unit to extend the pipe from precast unit to the manhole.
| 01CV - Civils | Cxxx-NCR-000305 | NCR | Concrete Surface Damages, Cast in items out of aligments, Uneven finishes and Defects to Pre-cast units |  | Contr | VLK |  |  | 2016-04-22 | 2016-03-18 13:11 | -35 | 2015-11-24 14:35 | Structural Engineering - Pre-cast | 5000 |  | Manufacturing Defect | Repair | 3 (3-6k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Damages to finish surface,Cast in items out of alignments, Uneven finishes and defects to precast units. Please refer to PC units Quality inspection Schedule for road 3, 4 & 5
| 01CV - Civils | Cxxx-NCR-000306 | NCR | The __ Kwikastrip Starter bars are missing on some units. |  | Contr | VLK |  |  | 2016-05-31 | 2016-06-07 11:19 | 7 | 2015-11-16 16:50 | Structural Engineering - Pre-cast | 5000 |  | Incomplete Works | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | The __ Kwikastrip Starter bars are missing on units P/1, E/1 & K along the south side and the top of the precast units.
| 01CV - Civils | Cxxx-NCR-000307 | NCR | 2.2.3.2h - Air conditioning installation to L&S Building |  | Contr | VLK |  |  | 2016-02-15 | 2016-03-22 09:15 | 36 | 2015-11-19 09:42 | Systems - Systems Engineering General | 2000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Refrigerant lagging installed on the logistics mezz deck has been ‘sausaged’ by using plastic and metal cable ties instead of proprietary clamps which do not impact the thermal properties of lagging by reducing the cross section.
| 01CV - Civils | Cxxx-NCR-000308 | NCR | 2.2.3.2.h - Smoke Damper cables to L&S Building |  | Contr | VLK |  |  | 2016-03-31 | 2016-03-22 09:20 | -9 | 2015-11-19 11:33 | Electrical - General | 2000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | No mechanical protection has been provided to smoke damper cabling at ground level on the walking route immediately at the top of the spiral stair case on the mezz deck. The position of the electrical equipment is exposed to damage particularly from any access equipment
| 01CV - Civils | Cxxx-NCR-000309 | NCR | 2.2.3.1.d - __ pipework instalation to east of L&S Building |  | Contr | VLK |  |  | 2016-02-10 | 2016-02-08 15:10 | -2 | 2015-11-19 11:54 | Systems - Systems Engineering General | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | The vesda pipework at the east end of the logistics building looks kinked and might have been installed incorrectly.
| 01CV - Civils | Cxxx-NCR-000310 | NCR | L&S Building Switchboard |  | Contr | VLK |  |  | 2016-03-31 | 2016-04-04 08:21 | 4 | 2015-11-19 12:07 | Electrical - Electrical Engineering General | 10000 |  | Workmanship | Rework | 2 (6-60k) | Complete | Design Problem - Other | Completed |  | Initial observations of the Logistics switchboard has given rise to the following concerns: 1. There are no cable boots/shrouds on the incomer busbar 2. The transparent guard over the incoming supplies cannot be installed due to the route of the incoming cable 3. The lug of one phase is touching the bolt for a second phase 4. The busbar looks to be under tension due to the installation of incomer which has not been formed 5. The lugs appear to have 10mm fixing bolts and a 12mm eye 6. The busbar appears to have been drilled for a second fixing (this may be dismissed when the correct bolts are used) 7. The fixing bolts appear to be standard steel fixing bolts opposed to proprietary parts 8. Earth sheathing for demarcation of a black conductor is not continuous
| 01CV - Civils | Cxxx-NCR-000311 | NCR | __ security cabin design |  | Contr | VLK |  |  | 2016-01-17 | 2016-01-28 19:53 | 11 | 2015-11-19 12:54 | Electrical - Electrical Engineering General | 3000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Inadequate design for __ to understand the extent of work therefore grant access There are insufficient dimensions and/or containment routes on the design to allow __ to grant access for the installation
| 01CV - Civils | Cxxx-NCR-000312 | NCR | Containment above switchboard to L&S Building |  | Contr | VLK |  |  | 2016-04-08 | 2016-03-22 09:32 | -17 | 2015-11-19 15:00 | Electrical - Electrical Engineering General | 5000 |  | Workmanship | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | Initial observations of the containment above the Logistics switchboard has given rise to the following concerns: 1. There are no restraints/fingers to take the weight of the 10m of cable hanging from high level 2. There doesn’t appear to be 45% spare capacity 3. There appears to be mixed voltages
| 01CV - Civils | Cxxx-NCR-000313 | NCR | Paint Shop - damage to steel around PS01 |  | Contr | VLK |  |  | 2016-02-25 | 2016-02-19 10:29 | -6 | 2015-11-19 15:38 | Architectural - General | 5000 |  | Damaged | Repair | 3 (3-6k) | Complete | Material/Preservation Problems - Improper storage of material | Completed |  | Minor damage to steel members. Rust to edges.
| 01CV - Civils | Cxxx-NCR-000314 | NCR | Lighting contactor to L&S Building |  | Contr | VLK |  |  | 2016-02-15 | 2016-02-19 10:27 | 4 | 2015-11-19 15:49 | Electrical - General | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | Initial observations of the lighting contactor in the Logistics has given rise to the following concerns: A distribution board extension box has been utilised as a lighting contactor panel which is not as its intended use. The manufacturers intended use does not require a top plate hence the labour has manufactured a top plate and filler section out of paxoline.
| 01CV - Civils | Cxxx-NCR-000315 | NCR | 2.2.3.1.d - Fire alarm equipment to mezz deck |  | Contr | VLK |  |  | 2016-02-15 | 2016-02-08 15:11 | -7 | 2015-11-19 16:00 | Systems - Fire Detection systems and Mains | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | The fire alarm equipment at the western end of the logistics mezz deck has been installed behind a hand rail at a non workable height. The installation method deems any future maintenance requirements needs to be by podium (which need to be carried up a spiral staircase) and hanging over the handrail. We do not believe this is compliant with CDM, BS7671 (900mm clear).
| 01CV - Civils | Cxxx-NCR-000316 | NCR | Rain water harvesting System |  | Contr | VLK |  |  | 2015-12-18 | 2015-11-30 15:12 | -18 | 2015-11-23 09:57 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | The installation of the rainwater harvesting system has commenced on a code 3 ITP. The ITP 103 rev. 2.0 (Cxxx-VLK-N2-ITP-CR112_SD007-50156 - ITP 103 - Logistics and Stores Rain Water Harvesting System) has been resubmitted for acceptance 28.10.15 awaiting comments.
| 01CV - Civils | Cxxx-NCR-000317 | NCR | WSA - Site records not available in WSA site offices |  | Contr | VLK |  |  | 2016-04-16 | 2016-03-25 14:42 | -22 | 2015-11-23 14:44 | Electrical - General | 2000 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Verification Problems - Not Defined | Completed |  | During CRL inspection it was identified that site records for M&E works were not available in WSA site offices.
| 01CV - Civils | Cxxx-NCR-000318 | NCR | WSA compressed air installation - no specification in Mechanical Spec. |  | Contr | VLK |  |  | 2016-04-29 | 2016-03-29 12:01 | -31 | 2015-11-24 12:47 | Mechanical - Piping | 1000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Installation of compressed air Teseo system has commenced without an approved specification.
| 01CV - Civils | Cxxx-NCR-000320 | NCR | WSA - 3 comp PIT trunking not covered in MCR |  | Contr | VLK |  |  | 2016-06-30 | 2016-05-23 09:51 | -38 | 2015-11-23 15:21 | Electrical - Cable Management | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | 3 Compartment trunking used in low level pit containment was not in the MCR.
| 01CV - Civils | Cxxx-NCR-000321 | NCR | Oversized PC units |  | Contr | VLK |  |  | 2016-06-15 | 2016-06-10 17:03 | -5 | 2015-11-24 15:21 | Structural Engineering - Pre-cast | 5000 |  | Manufacturing Defect | Repair | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | Oversized PC units - Duck Under units
| 01CV - Civils | Cxxx-NCR-000322 | NCR | fixing of CMS and DB equipmenton the South Wall of WSA |  | Contr | VLK |  |  | 2017-05-31 | 2017-05-05 16:55 | -26 | 2015-11-25 10:53 | Electrical - LV Equipment | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Programmed activities for installation of containment and distribution equipment on the South wall of WSA seems delayed due to the unknown method of fixing and lack of standard installation detail incorporated in the design. have had access for surveys to validate any assumptions made by the designer and verify fixing method yet we now face delay to programme for A. the lack of design, B. lack of advantage taken to access and validate the design
| 01CV - Civils | Cxxx-NCR-000323 | NCR | WSA - Water Supply SE Corner WSA |  | Contr | VLK |  |  | 2016-06-30 | 2016-07-01 16:56 | 1 | 2015-11-25 11:01 | Mechanical - Hot & Cold Water Supplies | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | water distribution design for WSA has been based on a water supply available in the South East corner of WSA. The water supply is dead therefore need to confirm what flow rates and pressure the design is based on and how pipe work for WSA was sized by the designer. This design shortfall by may have implication on the utilities design and will incur time and money implications from __ for the additional below ground pipework, shortfall in the Grip 5 submission and subsequent design change
| 01CV - Civils | Cxxx-NCR-000324 | NCR | WSA -The current design of the compressor house size south of workshop a incurs a clash between train and GRP housing |  | Contr | VLK |  |  | 2016-05-31 | 2016-05-12 17:19 | -19 | 2015-11-25 11:07 | Mechanical - Mechanical Engineering General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The current design of the compressor house size south of workshop a incurs a clash between train and GRP housing
| 01CV - Civils | Cxxx-NCR-000326 | NCR | Pockets for bolts in the PC units are out of Plump |  | Contr | VLK |  |  | 2015-12-11 | 2015-12-12 02:08 | 1 | 2015-11-25 14:33 | Structural Engineering - Pre-cast | 3000 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Majority of the pockets in PC units for the bolts are out of Plump
| 01CV - Civils | Cxxx-NCR-000327 | NCR | PV cables, LV Distribution and Comms/control cabling |  | Contr | VLK |  |  | 2016-02-29 | 2016-03-14 15:47 | 14 | 2015-11-26 14:36 | Electrical - Electrical Engineering General | 5000 |  | Workmanship | Rework | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | It has been identified that multiple wiring systems have been installed on the same containment route in the Logistics and Stores building, namely the PV cables, LV Distribution and Comms/control cabling. Subsequent to this the cables do not appear to follow “bunching” that would consider grouping factors. This does not constitute considered measures against electromagnetic influences and contravenes several regulations over a number of standards.
| 01CV - Civils | Cxxx-NCR-000328 | NCR | Cube Tank left outside with no working heating filament or thermometer |  | Contr | VLK |  |  | 2016-01-10 | 2016-01-31 22:52 | 21 | 2015-11-30 15:43 | Structural Engineering - Testing | 2000 |  | Equipment Breakdown | Rework | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | Cube tank was left outside and with the temperatures dropping recently the water temperatures have dropped below allowable levels for the cubes. A working thermometer was not present within the tank either.
| 01CV - Civils | Cxxx-NCR-000329 | NCR | Landing Spiral stairs to mezz deck |  | Contr | VLK |  |  | 2016-02-29 | 2016-03-02 19:52 | 2 | 2015-12-01 07:30 | Architectural - General | 5000 |  | Design | Repair | 3 (3-6k) | Complete | Design Problem - Not Defined | Completed |  | The landing to the spiral stairs has not been installed as per design 21310 which shows the lading sitting on the block work.Currently the landing is sitting on a 40x75 angle that is fixed with resin into the top course of blocks.
| 01CV - Civils | Cxxx-NCR-000330 | NCR | Spiral Staircase handrail |  | Contr | VLK |  |  | 2016-02-20 | 2016-02-19 10:36 | -1 | 2015-12-01 07:35 | Architectural - General | 1000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | Mesh infill panels to the spiral staircase leading to the Mezz deck in the logistics building haven't been installed as shown in drawing no Cxxx-VLK-A-DWG-CR112_SD007-50019 - NK017437_21310.
| 01CV - Civils | Cxxx-NCR-000331 | NCR | Semmco platforms being fabricated prior to an ITP being in place |  | Contr | VLK |  |  | 2016-03-31 | 2016-02-19 11:45 | -41 | 2015-12-02 15:52 | Civil - Structural Engineering | 1000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Lack of procedure | Completed |  | Semmco platforms being placed between Road 3-5 have had fabrication started prior to an ITP being in place for the works
| 01CV - Civils | Cxxx-NCR-000332 | NCR | Air entrained Test |  | Contr | VLK |  |  | 2016-02-26 | 2016-03-02 19:55 | 5 | 2015-12-07 16:54 | Civil - Concrete Pavement | 3000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | air entrained test was not carried out because __ technician did not turned up.
| 01CV - Civils | Cxxx-NCR-000333 | NCR | Paintshop booths - Metal work finish |  | Contr | VLK |  |  | 2017-01-31 | 2017-02-01 15:20 | 1 | 2015-12-07 18:49 | Architectural - General | 8000 |  | Workmanship | Rework | 2 (6-60k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | It has been identified that the metal work finish of the Paint shop booths occurred installation damages such as dents and scratches.
| 01CV - Civils | Cxxx-NCR-000334 | NCR | Insufficient ITP for SBE acoustic insulation |  | Contr | VLK |  |  | 2016-01-04 | 2016-01-04 14:45 | 0 | 2015-12-08 15:41 | Architectural - Ceilings & Soffits | 1000 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Information not detailed | Completed |  | Works in the Shotblast enclosure was carried out under ITP 217. This had no reference to the ceiling.
| 01CV - Civils | Cxxx-NCR-000336 | NCR | Formation of door opening |  | Crossrail | XRL |  |  | 2016-01-18 | 2016-01-15 13:26 | -3 | 2015-12-09 17:33 | Architectural - Doors | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Supervision - Not Defined | Completed |  | The double door opening between grids 11 and 10 to the north side of the paint shop has been formed too small in height.__ have attempted to overcome this by way of grinding the slab.However in doing so they have ground 15mm out of a finished slab with out following the design change process.
| 01CV - Civils | Cxxx-NCR-000337 | NCR | failure to adhere to the works infoprmation when submitting IRN's |  | Crossrail | XRL |  |  | 2016-01-21 | 2016-01-31 22:58 | 10 | 2015-12-12 15:11 | Electrical - General | 1000 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | Recent IRN's submitted have failed to adhere to works information 2A sections 5.1 , 5.2 , 5.6.2 , 5.8, 20.8
| 01CV - Civils | Cxxx-NCR-000338 | NCR | WSA clash between Gas pipe and OLE support frame between GL18-19 along GL E |  | Contr | VLK |  |  | 2016-07-30 | 2016-07-28 16:46 | -2 | 2015-12-18 09:39 | Utilities Engineering - Gas | 5000 |  | Design | Repair | 3 (3-6k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | have installed the gas pipe shown in the attached photo along the south wall between GL 18-19 in WSA in Dec 2014. __ site team have installed all the OLE bases from GL1-18 as per HSL drawings, but when they came to lay out the bases between GL18-19 they realised the OLE support frame steels will clash with ’s gas pipe. For clarity, please view the photographic survey of the gas pipe and the Hambleton support frame sketch (attached). View E is looking up from the base of the wall. It is not an option to move the gas pipe closer to the wall as sufficient clearance will not be obtained. This lack of co-ordination by will have implications on the utilities design and will incur time and money implications from __ for the relocation of the gas pipe, shortfall in the Grip 5 submission and subsequent design change.
| 01CV - Civils | Cxxx-NCR-000341 | NCR | Lighting trunking in logistic and paint shop buildings |  | Contr | VLK |  |  | 2016-02-20 | 2016-03-14 15:53 | 23 | 2015-12-31 09:33 | Electrical - Lighting | 5000 |  | Supervision/Management | Rework | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | Lighting trunking does not conform to BS7671 section 521.10.1 in logistic and paint shop buildings
| 01CV - Civils | Cxxx-NCR-000342 | NCR | Workshop A - Emergency lighting circuit |  | Contr | VLK |  |  | 2016-06-30 | 2016-07-01 16:57 | 1 | 2015-12-30 14:27 | Electrical - General | 1500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | appear to be using FP200 for all emergency lighting circuits in the pits in WSA yet, having provided only a single 20mm conduit entry. If the intent is to strip the outer sheath inside the multi compartment trunking to enable installation this will not be accepted on the grounds of bad workmanship and not achieving fire integrity throughout length. (we suggest fire rated singles - Huber suhner or Saffire)
| 01CV - Civils | Cxxx-NCR-000343 | NCR | Logistic and Stores - Secondray containment |  | Contr | VLK |  |  | 2016-02-01 | 2016-02-06 13:01 | 5 | 2015-12-30 14:49 | Electrical - Cable Management | 10000 |  | Workmanship | Rework | 2 (6-60k) | Complete | Verification Problems - Other | Completed |  | have offered items for inspection on stage 1 works on 29/12/15 including a. secondary containment for lighting b. secondary containment for power c. secondary containment for clock. __ have identified 24 snags on initial inspection on the small power secondary containment alone. __ do not consider the installation is fit for inspection.
| 01CV - Civils | Cxxx-NCR-000344 | NCR | Inadequate spacing on trunking for SWA |  | Contr | VLK |  |  | 2016-03-14 | 2016-03-14 16:59 | 0 | 2015-12-31 10:34 | Electrical - General | 4000 |  | Supervision/Management | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | Following an inspection to Depot Protection System it has been identified that the space on trunking for Steel Wired Armoured cable glands might not be adequate to allow maintainability on Road Control Panel.
| 01CV - Civils | Cxxx-NCR-000345 | NCR | Containment to Workshop A GL E |  | Contr | VLK |  |  | 2016-04-15 | 2016-03-29 10:13 | -17 | 2015-12-31 10:48 | Electrical - Electrical Engineering General | 5000 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | The containment installed along Gridline E of Workshop A will clash with, and therefore, prevent the movement of mobile access platforms. The containment has not been installed in accordance with the AFC (rev. C01) drawing Cxxx-VLK-E-DDA-CR112_SD007_Z-76012. When comparing the P01 and C01 revisions of the drawing. The P01 drawing doesn’t show the “150x50mm 3 compartment trunking @2400AFFL”. Instead, the drawing shows “100mm cable tray @6870 AFFL”. The amendment to the containment doesn’t appear to have been highlighted or noted in the revision description, and therefore, is unlikely to have been reviewed appropriately prior to Acceptance. In summary, the design has not been produced in accordance with the Design Management Plan: • The Design Review and Acceptance process has not been followed (evidenced by discrepancies between the P01 and C01 drawing revisions). • Design has not been coordinated with those of the Lead Designer (__). • The Design Change Management Control process has not been followed (evidenced by the absence of FCD).
| 01CV - Civils | Cxxx-NCR-000346 | NCR | Bulk paint store relocation - Incomplete /Un-Coordinated Design |  | Contr | VLK |  |  | 2016-02-26 | 2016-03-02 19:57 | 5 | 2015-12-31 11:33 | Systems - Other | 500 |  | Design | Reject | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | were instructed via Contractors Instruction (CI-079) to relocate the Bulk Paint Store (BPS). The instruction included the requirement to: “revisit the coordinated design for Logistics Building and include fire alarm, PA, door access, ducting and fire damper, lighting and power modifications to suit the new bulk store. are to include in their quotation: 1. Liaison with __, __ and __ 2. Design changes and subsequent installation changes to works 3. Provision of ducting external to the bulk store 4. Provision of fire damper to __ ductwork 5. Additional commissioning arising from __ interface” It has become evident that these instructed works have not been completed resulting in non-Conformance for the fire alarm installation.
| 01CV - Civils | Cxxx-NCR-000347 | NCR | Instalation of power sockets, phone and data to Logistics & Stores Building ‘Goods Inward Area’ |  | Contr | VLK |  |  | 2016-02-27 | 2016-02-23 16:21 | -4 | 2016-01-02 14:44 | Electrical - Electrical Engineering General | 3000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | The design/installation to the Logistics & Stores Building ‘Goods Inward Area’ is not fit for purpose, as it does not consider the requirements of the end-user. The locations of the power sockets, phone and data points are such that they will result in numerous trailing cables, which will present a potential trip hazard. Consequently, the design/installation exhibits an unacceptable health and safety risk, which is in discord with CDM Regulations. The result of these non-compliances is a shortfall in the Grip 5 submission, and shall require a subsequent design change.
| 01CV - Civils | Cxxx-NCR-000348 | NCR | Segregation of BMS and LV cables for the ambi radiant panels to Paintshop |  | Contr | VLK |  |  | 2016-03-24 | 2016-03-29 11:56 | 5 | 2016-01-02 15:06 | Electrical - Electrical Engineering General | 2500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The BMS and LV cables for the ambi radiant panels run in the same containment, the cables should be segregated in different containments
| 01CV - Civils | Cxxx-NCR-000349 | NCR | s brackets installation to substation |  | Contr | VLK |  |  | 2016-02-29 | 2016-03-02 17:00 | 2 | 2016-01-02 15:22 | Electrical - Electrical Engineering General | 1500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Not Defined | Completed |  | The bracket installed by ’s has been fixed using nut and bolt through into the busbar chamber, with vibration the nut could potentially work free and fall onto live busbar’s
| 01CV - Civils | Cxxx-NCR-000350 | NCR | Non-maintainable services above the radiant panels to paintshop |  | Contr | VLK |  |  | 2016-02-26 | 2016-03-15 23:04 | 18 | 2016-01-02 15:28 | Mechanical - Mechanical Engineering General | 10000 |  | Design | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Other | Completed |  | The radiant panels in the shot blast bay are installed in a way that makes most of the services above them non-maintainable.
| 01CV - Civils | Cxxx-NCR-000351 | NCR | __ cable tray instalation to L&S Building |  | Contr | VLK |  |  | 2016-04-15 | 2016-04-16 20:32 | 1 | 2016-01-02 15:35 | Electrical - Electrical Engineering General | 2000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The design/installation of light duty __ cable tray to the Logistics & Stores Building is not fit for purpose. It would be expected heavy duty tray to be used in this type of environment.
| 01CV - Civils | Cxxx-NCR-000353 | NCR | High level Fire alarm instalation to WSA road 3/4/5 |  | Contr | VLK |  |  | 2016-02-29 | 2016-03-18 12:34 | 18 | 2016-01-03 10:18 | Electrical - Electrical Engineering General | 2000 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | Following a review of the Fire Alarm ITP (Cxxx-VLK-N2-ITP-CR112_SD007-50093 - ITP 124 Workshop A Fire Alarm) it has been identified that progressive check sheets weren't available.
| 01CV - Civils | Cxxx-NCR-000354 | NCR | High level Gas Pipe installation to WSA |  | Contr | VLK |  |  | 2016-02-29 | 2016-03-18 12:31 | 18 | 2016-01-03 10:41 | Utilities Engineering - Gas | 2000 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Verification Problems - Not Defined | Completed |  | Following a review of the Gas Pipe installation to WSA high level it has been identified that progressive check sheets weren't available.
| 01CV - Civils | Cxxx-NCR-000355 | NCR | Use of unapproved materials |  | Crossrail | XRL |  |  | 2016-02-13 | 2016-02-23 16:26 | 10 | 2016-01-04 10:41 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | During an inspection on 18/12/15 is was noted that a considerable number of repairs were being carried out to the precast concrete in particular to the east of WSA with Tiestop which is an unapproved product. A repair procedure has not yet been agreed for these repairs nor has a bench mark been agreed.
| 01CV - Civils | Cxxx-NCR-000356 | NCR | Not working in accordance with ITP |  | Crossrail | XRL |  |  | 2016-02-19 | 2016-04-16 20:53 | 57 | 2016-01-04 10:59 | Civil - Civil Engineering General | 1000 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | During an inspection of the mass concrete in fill wall along grid E to WSA it was identified ITP 157 does not cover the installation of mass fill concrete only reinforced concrete.After scrutinising ITP 157 it was deemed not fit for purpose for the mass concrete pour and had been used as a go to document to get the work done.
| 01CV - Civils | Cxxx-NCR-000357 | NCR | No MCR OR FCD in place for the grid E mass concrete mix design |  | Crossrail | XRL |  |  | 2016-02-19 | 2016-02-06 13:17 | -13 | 2016-01-04 11:40 | Civil - Civil Engineering General | 1000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | During an inspection on Sat 12th December to the mass concrete on grid E WSA it was noted there was no MCR for the concrete mix design nor was the requested FCD raised for these works.The drawing for these works has limited information and only identifies this wall as a concrete infill and has no other information.
| 01CV - Civils | Cxxx-NCR-000358 | NCR | Failed inspection of WSA pre pour turntable |  | Crossrail | XRL |  |  | 2016-02-12 | 2016-02-19 11:38 | 7 | 2016-01-04 11:56 | Civil - Civil Engineering General | 1000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Verification Problems - Inspector not properly qualified | Completed |  | During a pre pour inspection of the turntable slab on GL 17-18 in WSA it was noted the top mat of the reinforcement had considerable concrete on it which needed cleaning. It was also noted the rocker pipe was not installed inside the turntable to the soak away pipe. To date no photo`s have been produced these remedials were carried out.
| 01CV - Civils | Cxxx-NCR-000359 | NCR | Hand rail to north of Logistics Building |  | Contr | VLK |  |  | 2016-02-29 | 2016-03-02 19:58 | 2 | 2016-01-05 12:39 | Civil - Civil Engineering General | 1500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Hand rail rusting and deep gouges are also evident to this handrail and some appear to be deeper than the 140 micron galvanising thus exposing the steel beneath.
| 01CV - Civils | Cxxx-NCR-000360 | NCR | Damage to track concrete rebate |  | Contr | VLK |  |  | 2017-05-31 | 2017-04-12 14:02 | -49 | 2016-01-05 14:00 | Structural Engineering - Concrete Member | 2000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | Section of the track rebate damaged and there are places the track rebate concrete nib has cracked significantly beside the east end of service trench.
| 01CV - Civils | Cxxx-NCR-000361 | NCR | WSA The terminals in the commando socket are too small to accept the cables for the 400V and 110V sockets |  | Contr | VLK |  |  | 2017-07-31 | 2017-08-04 13:12 | 4 | 2017-06-30 09:02 | Electrical - LV Equipment | 5000 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | WSA The terminals in the commando socket are too small to accept the cables for the 400V and 110V sockets
| 01CV - Civils | Cxxx-NCR-000362 | NCR | WSA Emergency Lighting wired in FP 200 cable , which will not fit in the installed 20mm conduit where the fittings are looped in and out. |  | Contr | VLK |  |  | 2016-04-04 | 2016-03-29 10:14 | -6 | 2016-01-07 16:17 | Electrical - Lighting | 500 |  | Design | Reject | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | n/a
| 01CV - Civils | Cxxx-NCR-000364 | NCR | wsa -No detailed design of Transition Box from trunking to tray at the end of each pit in WSA Rows 3,4 and 5. |  | Contr | VLK |  |  | 2017-08-31 | 2017-08-04 15:06 | -27 | 2017-07-10 14:38 | Electrical - LV Equipment | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | WSA -No detailed design of Transition Box from trunking to tray at the end of each pit in WSA Rows 3,4 and 5.
| 01CV - Civils | Cxxx-NCR-000368 | NCR | wsa 400v sockets-20 mm conduit does not have the adequate capacity to accept the wiring where sockets are looped |  | Contr | VLK |  |  | 2017-12-29 | 2017-07-31 08:59 | -151 | 2017-07-10 14:11 | Electrical - LV Equipment | 0 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | 400v sockets-20 mm conduit does not have the adequate capacity to accept the wiring where sockets are looped
| 01CV - Civils | Cxxx-NCR-000370 | NCR | Remedial works to repair the pour finish around the manholes. |  | Contr | VLK |  |  | 2016-03-07 | 2016-04-10 11:50 | 34 | 2016-01-07 18:23 | Structural Engineering - Grouting | 5000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Procedure Problem - Not Defined | Completed |  | Remedial works carried out to pour finish manhole edges without approved material and methodology.
| 01CV - Civils | Cxxx-NCR-000371 | NCR | Quality of IRN and red line drawings for secondary containamnt |  | Crossrail | XRL |  |  | 2016-03-31 | 2016-03-22 09:35 | -9 | 2016-01-21 08:40 | Electrical - Cable Management | 1500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | To ensure the IRN for secondary containment installation is the correct format and the IRN’s quality, including the red-line drawings, will be improved an NCR eB ref. no. Cxxx-NCR-000371 has been raised on the grounds of non-compliance with WIv2B part 13.3.6 Redlines, As Built and Operational Records. For details refer to surveillance report ref. no. Cxxx-XRL-O4-RGN-CR001-50022
| 01CV - Civils | Cxxx-NCR-000372 | NCR | Quality of IRN and red line drawings for BMS containamnt |  | Crossrail | XRL |  |  | 2016-03-31 | 2016-03-22 09:36 | -9 | 2016-01-21 08:44 | Electrical - Cable Management | 1000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | To ensure the IRN for BMS containment installation is in the correct format and the IRN’s quality, including the red-line drawings, will be improved an NCR eB ref. no. Cxxx-NCR-000372 has been raised on the grounds of non-compliance with WIv2B part 13.3.6 Redlines, As Built and Operational Records. For details refer to surveillance report Cxxx-XRL-O4-RGN-CR001-50022
| 01CV - Civils | Cxxx-NCR-000373 | NCR | Fire protection in Welfare Area - Design change |  | Contr | VLK |  |  | 2016-03-15 | 2016-03-25 14:38 | 10 | 2016-01-25 14:54 | Fire - Fire Systems & General | 1500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Fire protection between compartments within Welfare area was changed once RED Line drawings had been submitted.
| 01CV - Civils | Cxxx-NCR-000374 | NCR | Guy wire fixings to paintshop roof |  | Contr | VLK |  |  | 2017-03-31 | 2017-03-27 15:16 | -4 | 2016-02-02 16:57 | Architectural - General | 500 |  | Material | Reject | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Following a inspection to Paintshop roof it has been identified that some fixings (nuts, bolts, D shackle) to guy wire are rusted.
| 01CV - Civils | Cxxx-NCR-000377 | NCR | Damaged purlin - high level Logistics |  | Contr | VLK |  |  | 2016-05-31 | 2016-05-16 12:46 | -15 | 2016-02-12 09:41 | Structural Engineering - Steel Member | 5000 |  | Damaged | Repair | 3 (3-6k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Damaged high level purlin between grid 2 and 3 in the logistics building
| 01CV - Civils | Cxxx-NCR-000378 | NCR | 2.2.3.1.c - Small Power - Installation of trunking without correct reducers |  | Contr | VLK |  |  | 2016-02-29 | 2016-03-22 09:37 | 22 | 2016-02-13 12:39 | Electrical - Power Distribution | 3000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Trunking at east goods entrance (high level) Logistics Building - Flat 90 - 50 x 50 trunking bend connected to 100 x 50 bend without correct reducer. Circuits are tested and found to be safe.
| 01CV - Civils | Cxxx-NCR-000379 | NCR | WSA - Damaged Holophane light fittings |  | Contr | VLK |  |  | 2016-04-03 | 2016-03-18 13:24 | -16 | 2016-02-17 17:47 | Electrical - Lighting | 2000 |  | Supervision/Management | Reject | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | WSA - Roads 3, 4 and 5 - Holophane light fittings - During client's site visit it was identified that a number of damaged Holphane Liighting Fitings that were not part of the permanent works, are stored and prepared to be disposed.
| 01CV - Civils | Cxxx-NCR-000380 | NCR | failed inspection of compressor slab |  | Crossrail | XRL |  |  | 2016-04-22 | 2016-04-21 16:04 | -1 | 2016-02-19 16:26 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Reject | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Invited to a pre pour inspection of the compressor slab to the south of WSA at 9am on the 18/02/16.The slab was not complete however 2 items that had been completed were identified as non compliant by CRL namely insufficient membrane to the sw corner of the pour and the 3 saw cuts being incorrectly formed. Crl were invited back an hour later and the issues raised still hadn`t been closed out.An attempt had been made to rectify formation of the saw cut however the dowel bar had been tied tightly to the mesh either side of the saw cut formation.This would eliminate the movement required had it been poured.
| 01CV - Civils | Cxxx-NCR-000381 | NCR | Emergency lighting method of passing through contaiment - WorkShop A - 3,4 & 5 |  | Contr | VLK |  |  | 2016-07-20 | 2016-07-08 09:13 | -12 | 2016-02-23 17:14 | Electrical - Lighting | 4000 |  | Design | Use As-Is | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | To comply with the relevant British standards the following instruction was issued relating to the 3 comp pit trunking, Top Compartment- Emergency Lighting Middle Compartment- Fire Alarm Bottom Compartment – 230v, 110v, 400V, Depot Protection As cables are having to move compartments, no details available for the following while the works are being executed on site. 1) What is the plan for the 100s of holes left in the Trunking , when the back boxes get extended, 2) What is the plan on Row 5 ( 90 degree bends to fittings) for the general lighting circuits to pass through the segregation to the bottom compartment.
| 01CV - Civils | Cxxx-NCR-000382 | NCR | BMS system in the Logistics and Stores building |  | Contr | VLK |  |  | 2016-03-31 | 2016-03-18 13:27 | -13 | 2016-02-25 06:04 | Electrical - Electrical Engineering General | 5000 |  | Workmanship | Rework | 3 (3-6k) | Complete | Supervision - Other | Completed |  | Following an inspection at the MCC panel the following have been found: •Header trunking has not been cleaned of metal swarf and now cables have been installed. •Cable slot in the header trunking has not been painted with zinc rich paint. •Earth cables have come loose from several crimps, this is due to the earth cable being the incorrect size for the crimps. •Glands on header trunking are not accessible for removal and replacement (should a fault occur) would require an extensive strip down of unaffected circuits for maintenance. •Glands have steel wire protruding from the rear of the glands •FP200 cables (soft skin) have been kinked at the glands. •Spare cable cores have not been sealed and the bare conductor is “floating” in the header trunking. •Data cable cores have incorrect crimp sizes and are not crimped correctly.
| 01CV - Civils | Cxxx-NCR-000383 | NCR | Damaged to PC units plinths |  | Contr | VLK |  |  | 2016-05-31 | 2016-06-03 17:24 | 3 | 2016-03-01 08:57 | Structural Engineering - Pre-cast | 5000 |  | Damaged | Repair | 3 (3-6k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Damaged to Precast units plinths on road 3, Unit no - A35/9, B/2, A35/18, A35/20 & B/3.
| 01CV - Civils | Cxxx-NCR-000384 | NCR | Cabling route for Rain water harvesting control and supply cables |  | Contr | VLK |  |  | 2016-05-02 | 2016-05-03 09:33 | 1 | 2016-03-04 10:52 | Civil - Civil Engineering General | 10000 |  | Design | Repair | 2 (6-60k) | Complete | Design Problem - Other | Completed |  | There is currently no direct cabling route for the Logistics Rain Water harvesting tank supply or control cabling.
| 01CV - Civils | Cxxx-NCR-000385 | NCR | No MCR`s for WSA welding remedials |  | Crossrail | XRL |  |  | 2016-05-27 | 2016-05-31 10:10 | 4 | 2016-03-10 15:32 | Structural Engineering - Welding | 1500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Improper resource allocation | Completed |  | Remedials were carried out on corroded columns in gridline 1 in workshop A with no MCR`s in place as defined in ITP 282.
| 01CV - Civils | Cxxx-NCR-000386 | NCR | Use of incorrect concrete mix for external WSA slabs |  | Crossrail | XRL |  |  | 2016-08-31 | 2016-09-29 11:56 | 29 | 2016-03-15 14:47 | Civil - Concrete Pavement | 1500 |  | Design | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | The __ specification for the WSA concrete pavement states an S2 IIIB-V or III-A concrete mix design is to be used. __ have used an S3 CEM1 mix design instead.
| 01CV - Civils | Cxxx-NCR-000387 | NCR | Resin paint in concrete joints WSA |  | Crossrail | XRL |  |  | 2016-06-30 | 2016-06-07 11:25 | -23 | 2016-03-18 08:32 | Civil - Civil Engineering General | 3000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Roads 3,4 and 5 slabs have had the isolation joints painted over with the recently applied resin paint.The Kijstra precast concrete blocks have also had the connection joints painted over.
| 01CV - Civils | Cxxx-NCR-000388 | NCR | 2.4.1.1.a car park around SC1 and SC2 (Stage 1) - missing documentation for kerb laying |  | Contr | VLK |  |  | 2016-04-29 | 2016-04-16 20:58 | -13 | 2016-03-18 14:56 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | Missing delivery tickets of concrete for kerb laying. Kerbs were laid 2014 and early 2015 Concrete delivery tickets and respective check sheets (QMF-22) are missing at 8 locations. Structural concrete records and respective QMFs are available for rest of car park.
| 01CV - Civils | Cxxx-NCR-000389 | NCR | Hydraulic Platforms |  | Contr | VLK |  |  | 2016-07-16 | 2016-07-18 08:45 | 2 | 2016-03-29 13:36 | Mechanical - Mechanical Engineering General | 40000 |  | Testing and Commissioning | Repair | 2 (6-60k) | Complete | Material/Preservation Problems - Other | Completed |  | Hydraulic Platforms - failure to maintain equal pressure. uneven lifting
| 01CV - Civils | Cxxx-NCR-000390 | NCR | BMS Installation to WSA |  | Contr | VLK |  |  | 2016-04-28 | 2016-04-04 10:18 | -24 | 2016-03-29 17:02 | Electrical - Electrical Engineering General | 500 |  | Documentation and Records | Reject | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Following a review of the documentation has been identified that the BMS installation to WSA has commenced on a code 3 ITP.
| 01CV - Civils | Cxxx-NCR-000391 | NCR | WSA BMS works undertaken under unapproved ITP |  | Contr | VLK |  |  | 2016-06-10 | 2016-06-19 14:34 | 9 | 2016-03-31 12:53 | Systems - Other | 2000 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | WSA - Building Management Systems installation is undertaken under Code 3 ITP.
| 01CV - Civils | Cxxx-NCR-000392 | NCR | WSA Unapproved drawing used as part of BMS works |  | Contr | VLK |  |  | 2016-05-13 | 2016-04-27 07:48 | -16 | 2016-03-31 13:26 | Systems - Other | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | WSA During a routine surveillance it was identified that an unapproved drawing was used for the BMS works. Cxxx-VLK-M-DDA-CR112_SD007_Z-93011 Compressed Air Layout.
| 01CV - Civils | Cxxx-NCR-000393 | NCR | WSA Compressed Air Specification Code 3 |  | Contr | VLK |  |  | 2016-05-13 | 2016-05-12 23:27 | -1 | 2016-03-31 17:45 | Mechanical - Piping | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | WSA Installation of Compressed Air works undertaken without an approved specification.
| 01CV - Civils | Cxxx-NCR-000394 | NCR | WSA Compressed air instalaltion ITP Code 3 |  | Contr | VLK |  |  | 2016-04-29 | 2016-04-27 07:57 | -2 | 2016-03-31 17:50 | Mechanical - Piping | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | WSA Installation of Compressed Air works have been undertaken without an approved ITP.
| 01CV - Civils | Cxxx-NCR-000395 | NCR | WSA Compressed Air MCR at Code 3 |  | Contr | VLK |  |  | 2016-04-29 | 2016-05-12 23:21 | 13 | 2016-03-31 17:54 | Mechanical - Piping | 1500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | WSA Compressed Air works undertaken without an approved MCR.
| 01CV - Civils | Cxxx-NCR-000397 | NCR | SC1/SC2 concrete bays - compressive strength / cube failure |  | Contr | VLK |  |  | 2016-06-17 | 2016-05-16 11:44 | -32 | 2016-04-06 13:27 | Civil - Concrete Pavement | 2000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | Location: Bay 23 and steps 2,3,and 5 Subject: Compressive strength of concrete not reaching specified strength after 28 days
| 01CV - Civils | Cxxx-NCR-000399 | NCR | Stage 3-6 UTX works |  | Contr | VLK |  |  | 2016-08-24 | 2016-08-25 13:54 | 1 | 2016-04-14 14:18 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | It has been identified that shingle and back fill for the UTX work haven't been submitted through the MCR process for acceptance.
| 01CV - Civils | Cxxx-NCR-000400 | NCR | Stage 3-7 - External Troughing |  | Contr | VLK |  |  | 2017-03-30 | 2017-02-22 20:53 | -36 | 2016-04-14 14:28 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Reject | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | It has been identified that Troughing installed to stage 3-7 works is non-compliant and MCR returned back code 3.
| 01CV - Civils | Cxxx-NCR-000401 | NCR | Non-compliant chambers to stage 3-7 works |  | Contr | VLK |  |  | 2017-07-30 | 2017-05-18 17:44 | -73 | 2016-04-14 14:35 | Civil - Civil Engineering General | 0 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Not Defined | Completed |  | Non-compliant chambers installed to stage 3-7 works. They should have been Naylor with preformed holes for services.
| 01CV - Civils | Cxxx-NCR-000402 | NCR | Fire Alarm to paintshop |  | Contr | VLK |  |  | 2016-05-31 | 2016-06-07 13:08 | 7 | 2016-04-15 10:04 | Fire - Fire Systems & General | 2500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Following a fire strategy compliance review the following have been identified: -There is an inconsistency between the location of fireman’s microphone as shown on Fire Alarm Layout drawing Rev C01 and the actual installed microphone in the Paintshop. The specification (extract below) states that the microphone needs to be placed on the exterior of the building, while it is currently installed inside. Section 8.5 of C161-MMD-O9-STP-CR112_SD007-50001 Rev. 2.0 - C161 Fire Design Strategy “Fireman’s microphone will be provided adjacent to the main fire panel”. This requires the emergency microphone to be adjacent to a panel. - Fire control equipment located on south wall – non compliant with BS5839 section 23.1. This will require a repeater panel to be installed in the security hut if the security hut is manned 24 hours, the link to the panel gives the precise address and zone of the fire, and the cable connection is made in enhanced fire resistant cable (120minutes).
| 01CV - Civils | Cxxx-NCR-000403 | NCR | Desks to admin room of L&S Building |  | Contr | VLK |  |  | 2016-05-26 | 2016-05-13 12:57 | -13 | 2016-04-15 10:13 | Architectural - Finishes | 3000 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | The desks currently installed in the Admin office in the Logistics building do not match those shown attached drawing Cxxx-VLK-A-DDA-CR112_SD007_Z-21110 (Rev X04).
| 01CV - Civils | Cxxx-NCR-000404 | NCR | External Lighting to South of Paintshop |  | Contr | VLK |  |  | 2016-06-30 | 2016-06-28 16:23 | -2 | 2016-04-15 10:19 | Electrical - Electrical Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | No access is provided for maintenance purposes to exterior lights on the South wall of the Paintshop building. Exterior lights include one wall mounted light and signage lighting. Please see drawing - Signage Lighting Layout Cxxx-VLK-E-DDA-CR112_SD007_Z-72003 (Rev X01)
| 01CV - Civils | Cxxx-NCR-000405 | NCR | Personnel doors to Prep / Spray booths |  | Contr | VLK |  |  | 2016-05-31 | 2016-05-31 11:11 | 0 | 2016-04-15 10:33 | Architectural - Doors | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | It has been identified that the personnel doors to booths aren't compliant with C161-MMD-R-RSP-CR112_SD007-50002 - Bombardier Transportation Paint Shop Technical Specification as they suppose to include facilities to be locked and be provided with a means of internal emergency egress.
| 01CV - Civils | Cxxx-NCR-000406 | NCR | WSA Semmco Train Roof Access Platforms - Corrosion Appearance |  | Contr | VLK |  |  | 2016-08-31 | 2016-07-12 07:58 | -50 | 2016-04-19 14:34 | Structural Engineering - Surface Treatment | 4000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Material/Preservation Problems - Improper handling of material | Completed |  | WSA Semmco mobile Train Roof Access Platform - Corrosion appearance to the counter balance weights plates and the stainless steel brackets. Also the FAT has not been performed as part of these works. Counter balance weights plates are made of mild steel and have been painted in multiple coats of __ paint as a corrosion prevention measure. The corrosion spots on the stainless steel plates appear to be as a result of cross contamination in the process of laser cutting where shavings of a non stainless steel have contaminated the stainless steel brackets.
| 01CV - Civils | Cxxx-NCR-000407 | NCR | __ - Delaminated Panel South of Logistics |  | Contr | VLK |  |  | 2018-01-31 | 2018-02-02 14:59 | 2 | 2016-04-26 16:36 | Architectural - Walls | 8000 |  | Manufacturing Defect | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Other | Completed |  | 1no cladding panel south of Logistics Building is delaminated
| 01CV - Civils | Cxxx-NCR-000408 | NCR | Fibre optic cable installed between L&S and Paint Shop |  | Contr | VLK |  |  | 2016-07-15 | 2016-07-22 16:17 | 7 | 2016-04-28 12:41 | Communications and Control Systems - Fibre Optic Network | 3000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | A multi-mode fibre optic cable has been installed between L&S and Paint Shop buildings contrary to GRIP 5 design which states 12 core single mode fibre optic cable.
| 01CV - Civils | Cxxx-NCR-000409 | NCR | WSA Rd 3-5 Internal mansafe systems - Lack of approved MCR |  | Contr | VLK |  |  | 2016-05-31 | 2016-05-13 13:10 | -18 | 2016-05-02 13:44 | Materials - Approval | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | WSA Rd.3-5: Following Client's Inspection on the installation of the Internal Mansafe System it was identified that no approved MCR was in place.
| 01CV - Civils | Cxxx-NCR-000410 | NCR | WSA - Offices - Lack of progressive QA records |  | Contr | VLK |  |  | 2016-06-18 | 2016-06-07 14:08 | -11 | 2016-05-03 14:59 | Architectural - Roofing & Exterior Treatment | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | WSA - Offices - During a regular surveillance it was identified that no progressive QA records were available for the re-roofing activities to the WSA Offices.
| 01CV - Civils | Cxxx-NCR-000411 | NCR | White rust to Armco barrier |  | Crossrail | XRL |  |  | 2016-06-30 | 2016-06-27 08:23 | -3 | 2016-05-04 14:27 | Civil - Civil Engineering General | 5000 |  | Damaged | Rework | 3 (3-6k) | Complete | Material/Preservation Problems - Improper storage of material | Completed |  | Armco barrier has been installed to the western apron with excessive white rust due to poor storage pre installation. The appearance is now aesthetically poor and there are no guarantees the zinc coating has not been damaged.
| 01CV - Civils | Cxxx-NCR-000412 | NCR | WSA - Rd.3-5 - Internal Man Safe system installed without an upproved FCD |  | Contr | VLK |  |  | 2016-10-14 | 2016-09-29 11:58 | -15 | 2016-05-05 07:51 | Systems - Other | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | During the installation of the internal man safe system in WSA it was identified that there was a clash between the positions of the wire brackets of the man safe system and the installed high bay lights. Decision was made to alter the position of the wire brackets to avoid this clash.
| 01CV - Civils | Cxxx-NCR-000413 | NCR | WSA - Rd.3-5 - Clash between the Man Safe system and the High Bay Lights |  | Contr | VLK |  |  | 2016-07-31 | 2016-07-05 15:42 | -26 | 2016-05-05 08:10 | Systems - Other | 5000 |  | Design | Repair | 3 (3-6k) | Complete | Design Problem - Not Defined | Completed |  | WSA - Rd.3-5 - Man safe system - When performing a test run with the inertia reel, it was identified that there is a clash between 2no. High Bay lights at GL10 and GL18 (south of Rd.3) and the inertia reel.
| 01CV - Civils | Cxxx-NCR-000414 | NCR | WSA - Rd.3-5 - Man safe systems - Not adhering to a Hold Point in the ITP |  | Contr | VLK |  |  | 2016-08-31 | 2016-06-28 16:32 | -64 | 2016-05-05 08:22 | Systems - Other | 2500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | The wire swage pull test undertaken as per the requirements of ITP 277 "Installation of Internal Man Safe system" point 3.8 was not witnessed by __, even though this requirement has been identified as a Hold Point in the ITP.
| 01CV - Civils | Cxxx-NCR-000415 | NCR | WSA - Rd.3-5 - Louvre Infill Mastic - Material Installed not as per the approved MCR |  | Contr | VLK |  |  | 2016-06-30 | 2016-06-10 17:19 | -20 | 2016-05-05 08:40 | Archaeology - General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | WSA - Rd.3-5 - The material used as a mastic infill around the Louver is different then the one described in the approved MCR: Cxxx-VLK-C-LRC-CR112_SD007-50242 "Everbuild 825 Mastic".
| 01CV - Civils | Cxxx-NCR-000416 | NCR | Installation of pedestrian doors to WSA |  | Contr | VLK |  |  | 2016-07-17 | 2016-06-27 10:56 | -20 | 2016-05-05 12:56 | Architectural - Doors | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Verification Problems - Inspection points not adequate | Completed |  | Following a inspection to pedestrian doors at WSA it has been identified that there is no ITP in place for the works although is a replacement of the existing doors.
| 01CV - Civils | Cxxx-NCR-000417 | NCR | Installation of pedestrian doors to WSA |  | Contr | VLK |  |  | 2016-07-17 | 2016-06-27 11:05 | -20 | 2016-05-05 13:14 | Architectural - Doors | 1500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Following an inspection to pedestrian doors at WSA it has been identified that the materials wasn't covered by MCR(s) although they form part of existing doors replacement.
| 01CV - Civils | Cxxx-NCR-000418 | NCR | External mansafe/walksafe system to WSA road 3-5 |  | Contr | VLK |  |  | 2016-08-23 | 2016-08-03 17:42 | -20 | 2016-05-06 06:48 | Systems - Other | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | Following a review of the external mansafe/walksafe systems to WSA road 3-5 has been identified that there are no check sheets available to review although the installation is complete.
| 01CV - Civils | Cxxx-NCR-000419 | NCR | Brick work installation to WSA road 3-5 |  | Contr | VLK |  |  | 2016-08-10 | 2016-08-03 17:45 | -7 | 2016-05-06 15:41 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | It has been identified that the brickwork alteration works have commenced without an accepted MCR although reclaimed bricks are used.
| 01CV - Civils | Cxxx-NCR-000420 | NCR | WSA road 3 and 4 installation of pumping chamber frame and lid |  | Contr | VLK |  |  | 2016-07-29 | 2016-07-18 09:05 | -11 | 2016-05-07 07:02 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | Following an inspection to WSA road 3 and 4 it has been identified that the pumping chamber frame and lid ( NIF ) has been installed without an MCR in place.
| 01CV - Civils | Cxxx-NCR-000421 | NCR | WSA road 3-5 isolation joints around the pumping chamber frame |  | Contr | VLK |  |  | 2016-07-14 | 2016-06-27 12:21 | -17 | 2016-05-07 07:11 | Civil - Civil Engineering General | 2500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Following an inspection to WSA roads 3-5 it has been identified that the isolation joints around pumping chamber have not been cut on site as per drawings 23530 and 23520.
| 01CV - Civils | Cxxx-NCR-000422 | NCR | WSA roads 3-5 grout around pumping chamber frame |  | Contr | VLK |  |  | 2016-07-15 | 2016-06-10 17:21 | -35 | 2016-05-07 07:18 | Civil - Civil Engineering General | 2500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The Parex grout that has been used around the pumping chamber frame is not suitable due to the excessive shrinkage that is evident. This product although approved for use in WSA on the precast KIljstra units has not been approved to be used around the pump chamber. Parex has a minimum usage of 50mm so is not suitable for this application as it reduces to 20mm in places around the chamber. The recommended product identified on the designs for manholes is Weber and not used.
| 01CV - Civils | Cxxx-NCR-000423 | NCR | WSA roads 3-5 brickwork instalation |  | Contr | VLK |  |  | 2016-08-10 | 2016-08-03 17:47 | -7 | 2016-05-07 07:27 | Architectural - Brickworks/Blockworks | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | Following a surveillance on the brick work alterations pack the following have been found- • Check sheet for brickwork carried out on gridline E are not signed by __. • Check sheets for brickwork around door openings on gridline 1 are not signed by subcontractor • Check sheets for brickwork around doorways on gridline 10 are not signed by subcontractor • There is no MCR for the reclaimed bricks. This issue is captured on Cxxx-NCR-000419. • No records of cubes results. • No delivery tickets for any materials are in the pack.
| 01CV - Civils | Cxxx-NCR-000424 | NCR | Cladding to WSA road 3-5 |  | Contr | VLK |  |  | 2017-05-31 | 2017-05-05 16:37 | -26 | 2016-05-17 14:35 | Architectural - General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Following a review of the cladding installation to WSA road 3-5 has been identified that the changes to design aren't captured and confirmed by designers. Angle has been omitted behind the drips at the base of the cladding and the details around the door. Additionally the profile on the vertical flashings is not to design.
| 01CV - Civils | Cxxx-NCR-000425 | NCR | Instalation of lighting contactors to WSA road 3-5 |  | Contr | VLK |  |  | 2017-10-30 | 2017-09-08 14:42 | -52 | 2016-05-18 14:41 | Electrical - Electrical Engineering General | 6000 |  | Design | Use As-Is | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | It has been identified that the lighting contactors in WSA road 3-5 have been installed at a height. Isolation my be required to access this if required.
| 01CV - Civils | Cxxx-NCR-000426 | NCR | Ilford Concrete Car Park Slabs - Bay 10 Compressive Strength Result below required |  | Contr | VLK |  |  | 2016-06-30 | 2016-06-19 16:33 | -11 | 2016-05-18 14:50 | Civil - Concrete Pavement | 2500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | The Concrete cube result for Bay 10 are below the requirement. The Characteristic Strength is specified as 40N/mm2. The highest result achieved via the __ crushing test was 39.2N/mm2
| 01CV - Civils | Cxxx-NCR-000427 | NCR | Cables to Diesel Extract System to WSA road 3-5 |  | Contr | VLK |  |  | 2016-07-22 | 2016-06-29 07:46 | -23 | 2016-05-18 14:50 | Electrical - Electrical Engineering General | 5000 |  | Supervision/Management | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | During a walk out with both __ and it was noted that SY cables have been used for the power cabling to Diesel Extract System to WSA road 3-5. This is not compliant to BS 7671 and the cables will need to be changed to adhere to the regulations.
| 01CV - Civils | Cxxx-NCR-000428 | NCR | WSA - ITP 193 Resin Floor Paint - Lack of progressive checksheets |  | Contr | VLK |  |  | 2016-06-30 | 2016-06-27 15:23 | -3 | 2016-05-23 17:29 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Not Defined | Completed |  | WSA - Resin Floor Paint - During a regular surveillance on ITP 193, it was identified that no progressive check sheets were maintained.
| 01CV - Civils | Cxxx-NCR-000429 | NCR | WSA - Design Clashes - Lack of Design Coordination |  | Contr | VLK |  |  | 2017-04-11 | 2017-03-02 08:30 | -40 | 2016-05-23 17:52 | Civil - Civil Engineering General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | WSA - Design Clashes - Lack of Design Coordination - In a number of cases it was identified that there was a clash between two different designs such as clash between the High bay lights and the Secondary steel, clash between the DPS lights and the secondary steel, clash between the Gas pipe and OLE gantries, clash between the High Bay lights and the Mansafe system.
| 01CV - Civils | Cxxx-NCR-000430 | NCR | Workshop A Pit Lighting |  | Crossrail | XRL |  |  | 2017-12-22 | 2018-01-26 16:17 | 35 | 2016-05-24 12:26 | Electrical - Lighting | 10000 |  | Incorrect Installation | Use As-Is | 2 (6-60k) | Complete | Design Problem - Other | Completed |  | WSA pit lit lighting installation is not as per the agreed MMD design ref C161-MMD-E-RSP-CR112_WS129-50005 rev 1.0, Page 16 of 22, 9.1 Lighting which states that “The pit lighting will utilise wall mounted stainless steel with toughened glass fluorescent fittings rated IP 65 complete with non maintained emergency battery packs where required. Final Workshop A Building Electrical Services Reference Design arrangement of luminaires shall be coordinated with all other services and detailed” This deviation to a lesser quality fitting has also given rise to a further departure from the specification in which a maintained lighting system has been introduced with a UPS system. This will require additional maintenance and training that has not been agreed by the Project Manager or the stakeholder and it should be noted the additional cost of extra segregation throughout the installation for the purposes of segregation that was never an original requirement.
| 01CV - Civils | Cxxx-NCR-000431 | NCR | PAVA Test Results |  | Crossrail | XRL |  |  | 2016-07-31 | 2016-06-27 15:30 | -34 | 2016-05-24 12:44 | Systems - Fire Detection systems and Mains | 5000 |  | System Defect | Use As-Is | 3 (3-6k) | Complete | Verification Problems - Other | Completed |  | Safety critical PAVA (Public Address and Voice Alarm System) has test results for the STI (Speech Transmission Index) testing that are unintelligible and poor and the independent test company (TG Baker) also noted “The results that are returning after processing are proving to be poor and we suspect this is due to the high reverberation within the buildings.”
| 01CV - Civils | Cxxx-NCR-000432 | NCR | Workshop A ( road 3-5 ) isolators and thermostats for heaters along G/L – C |  | Contr | VLK |  |  | 2016-11-30 | 2017-01-03 12:21 | 34 | 2016-05-25 13:53 | Electrical - Electrical Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Due to site conditions (acoustic wall presence) in workshop A, isolators and thermostats for heaters along G/L – C are installed at truss level close to the new heaters
| 01CV - Civils | Cxxx-NCR-000433 | NCR | Installation of coroded Semmco platforms |  | Crossrail | XRL |  |  | 2016-07-10 | 2016-07-12 07:47 | 2 | 2016-05-31 08:10 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Reject | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The Semmco mobile platforms have been installed in WSA even though the MCR is code 3 and the existing NCR for the corrosion to the mild steel stiffeners has not been closed out.The platforms when previously delivered to site were removed when corrosion was identified however they have now been installed with no remedial works being carried out. The suggestion the remedials can be addressed in situ is unacceptable as all sides of the stiffener will not be accessible.
| 01CV - Civils | Cxxx-NCR-000434 | NCR | Non conformance to sections 13.1 and 13.2 of WI for drainage pack 3.1.1.5d. |  | Crossrail | XRL |  |  | 2016-07-18 | 2016-06-30 08:42 | -18 | 2016-05-31 09:14 | Civil - Drainage | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | Further to the surveillance of the WSA drainage pack 3.1.1.5d it was identified numerous check sheets were unsigned for progressive sign of works and completed air tests. Some check sheets have incorrect references to products or reference products that have been omitted.This contravenes sections 13.1 and 13.2 of the works information.
| 01CV - Civils | Cxxx-NCR-000435 | NCR | __ __ Platforms safety interlocks and operational constraints |  | Crossrail | XRL |  |  | 2017-04-30 | 2017-03-29 14:16 | -32 | 2016-05-31 09:07 | Mechanical - Lifts | 0 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | __'s specification requires the following: "4* 3.4 Safety Interlocks: (PSS-0153, PSS-0159, PSS-0165) We propose to fit a mechanical gate at either end of the platform, at the door end of the booth, these gates would close off between the carriage and the side wall, to prevent people from walking into the booth and below the platform, when it is raised. These gates are fitted with interlocks which if ‘broken’ will prevent any gantry movement." The current system shuts down the platform which is on that side of the booth rather than both of the platforms. Therefore, any gantry movement is not prevented and the specification is not complied with. Furthermore, during commissioning, __ have advised that there is a constraint on the operation of the booths in that upward motion can not follow downward motion unless the platforms are brought back to ground level. Failure to adhere to this constraint may result in the platforms jamming out of alignment. __ did not advise of this operational constraint in any of the design/specification documentation. In addition, there is no system to prevent or warn the operator not to carry out these movements. Therefore, it could be argued that the safety risk associated with platform failure has not been reduced to ALARP using the principles of prevention.
| 01CV - Civils | Cxxx-NCR-000436 | NCR | Missing MCR`s from drainage surveillance 3.1.1.5d |  | Crossrail | XRL |  |  | 2016-07-23 | 2016-07-18 09:27 | -5 | 2016-05-31 09:45 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Reject | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | During a recent surveillance to the WSA drainage pack it was noted a number of MCR`s were missing from the pack. Correspondence was sent to __ asking for confirmation if the missing MCR`s from the pack had been submitted. Due to __`s reluctance to respond to the we can only assume they are not. The following MCR`S require confirmation they have been accepted or require submitting. 1) FND 2 and C32/40 with 20mm aggregate used for chamber encasement,bedding and bases. 2) Roding eye covers and frame. 3) 100mm and 150mm pipe fittings and bends. 4) Manhole rings and biscuits. 5) 50mm compressible filler. 6) Manhole ring sealing gaskets. 7) Trench dividers/water stops.
| 01CV - Civils | Cxxx-NCR-000437 | NCR | Installation of UPS to WSA |  | Contr | VLK |  |  | 2017-11-30 | 2017-09-28 15:15 | -63 | 2016-06-28 14:55 | Electrical - Electrical Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The service life of the batteries as confirmed by the manufacturer is 20 years based on temperature of batteries being mentioned at 20-25 degree C. Currently there are no means of maintaining this temperature in the enclosure. Also, it is observed that the UPS enclosure does not have a suitable IP rating for WSA.
| 01CV - Civils | Cxxx-NCR-000438 | NCR | WSA - Rd.3-5 - OLE Installation - Lack of __ QA records |  | Contr | VLK |  |  | 2016-09-30 | 2016-10-07 16:20 | 7 | 2016-06-30 08:36 | Over Head Line Electrification - Over Head Line Electrification General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Not Defined | Completed |  | WSA - Rd.3-5 - OLE Installation - During regular __ Surveillance it was identified that no progressive QA records were in place.
| 01CV - Civils | Cxxx-NCR-000439 | NCR | WSA Rd.3-5 - OLE Installation - OLE installed not included in the approved site wide OLE MCR. |  | Contr | VLK |  |  | 2016-11-05 | 2016-10-11 14:33 | -25 | 2016-06-30 08:46 | Over Head Line Electrification - Over Head Line Electrification General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | WSA Rd.3-5 - OLE Installation - During regular __ surveillance it was identified that the OLE installed in WSA Rd.3-5 has not been included in the site wide approved OLE MCR: "Material Compliance Record": Cxxx-VLK-R6-XDS-CR112_SD007-50001
| 01CV - Civils | Cxxx-NCR-000440 | NCR | Paintshop - incorrect amperage circuit breaker installed to spray booth. |  | Contr | VLK |  |  | 2017-04-30 | 2017-03-15 09:11 | -46 | 2016-07-05 06:36 | Electrical - Electrical Engineering General | 1000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | Paintshop - it appears that incorrect amperage (4A) circuit breaker was installed to the spray booth resulting in over-heating and tripping.
| 01CV - Civils | Cxxx-NCR-000441 | NCR | WSA West Area DB Trunking |  | Crossrail | XRL |  |  | 2017-05-21 | 2017-05-12 17:06 | -9 | 2016-07-06 12:47 | Electrical - Power Distribution | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | Trunking header above DB's is non complaint due to poor segregation for emergency lighting cables (maintained system as per BS5266) and not enough spare capacity for power cables as per specification and BS 7671.
| 01CV - Civils | Cxxx-NCR-000442 | NCR | WSA West End UPS |  | Crossrail | XRL |  |  | 2017-07-30 | 2017-08-24 15:23 | 25 | 2016-07-06 14:27 | Electrical - Power Distribution | 0 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Trunking for UPS is not as per specification (screwed fixed lid) and turnbuckle has been installed on the bends. This has since been modified with screws but demonstrates mixing of material (not allowed) and we still have the non-compliant containment. Trunking should also be raised in this environment as per BS7671
| 01CV - Civils | Cxxx-NCR-000443 | NCR | WSA South West Containment Fixings |  | Crossrail | XRL |  |  | 2018-01-26 | 2018-02-09 14:38 | 14 | 2016-07-07 15:18 | Electrical - Cable Management | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Supervision - Other | Completed |  | __ fixings to render have damaged the finished works and excessive.
| 01CV - Civils | Cxxx-NCR-000444 | NCR | 3.1.1.10.b - WSA - Wall and Floor Paint |  | Contr | VLK |  |  | 2016-09-30 | 2016-10-07 16:22 | 7 | 2016-07-11 15:26 | Civil - Civil Engineering General | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Management Problem - Other | Completed |  | Setting out dimension detailed in the drawing Cxxx-VLK-A-DDL-CR112_SD007_Z-23120 Rev C01 has not been followed.
| 01CV - Civils | Cxxx-NCR-000446 | NCR | 3.1.1.7.b - Main Door Frames - Grout cubes |  | Contr | VLK |  |  | 2016-08-21 | 2016-08-19 13:28 | -2 | 2016-07-12 10:14 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | During the process of grouting, steel columns for main door frames no grout cubes have been collected for testing compressive strength as required by ITP.
| 01CV - Civils | Cxxx-NCR-000447 | NCR | 3.1.1.5.c - RC Works - Soft spot |  | Contr | VLK |  |  | 2017-03-30 | 2017-03-23 16:38 | -7 | 2016-07-12 16:49 | Civil - Civil Engineering General | 3000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Not Defined | Completed |  | As part of repairing the soft spot in Workshop A all the soft spoil has been removed and replaced with concrete. The change has made the repair works location hard and potentially could make the loads not distributed uniformly. __ to clarify through their designer that the works carried out to avoid soft spot are acceptable.
| 01CV - Civils | Cxxx-NCR-000448 | NCR | Duck under steps |  | Contr | VLK |  |  | 2017-09-30 | 2017-06-13 08:15 | -109 | 2016-07-12 18:54 | Structural Engineering - Pre-cast | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Changes made to the concrete step installation details from drawing Cxxx-VLK-S-DDL-CR112_SD007_1-23580, due to the detail given in the listed drawing will result in uneven stepping and trip hazard.
| 01CV - Civils | Cxxx-NCR-000449 | NCR | Noise assessments |  | Contr | VLK |  |  | 2017-01-31 | 2017-01-05 08:55 | -26 | 2016-07-28 11:21 | Environmental - Noise and Vibration | 500 |  | Planning | Reject | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Noise assessments not carried out as per Works Information volume 2A; section 21.8.3.3
| 01CV - Civils | Cxxx-NCR-000450 | NCR | Failure to provide Design Risk Log |  | Contr | VLK |  |  | 2017-03-30 | 2017-02-24 10:46 | -34 | 2016-07-28 11:26 | Civil - Civil Engineering General | 0 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Design Risk Log was not produced and updated periodically.
| 01CV - Civils | Cxxx-NCR-000451 | NCR | DPS in Paintshop - onsite modifications after FAT testing |  | Contr | VLK |  |  | 2017-09-30 | 2017-05-19 08:06 | -134 | 2016-08-01 07:03 | Electrical - General | 6000 |  | Software | Repair | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | The following faults were observed on Paint shop DPS in the last few days 1. July 1, 2016-DPS derailer failed to operate on enabling of road protection 2. July 28, 2016-DPS system main PLC hung and would not accept any commands despite operator being logged in. 3. July 29, 2016-DPS system main PLC hung again and standby PLC could not run DPS program
| 01CV - Civils | Cxxx-NCR-000452 | NCR | Logistics and Stores Building consumable store room |  | Contr | VLK |  |  | 2017-01-31 | 2017-01-03 15:16 | -28 | 2016-08-01 07:48 | Architectural - General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The Logistics and Stores Building Technical Specification C161-MMD-R-RSP-CR112_SD007-50003 requirement number LSB-0114 A consumable store room shall be provided with the following as a minimum: o Storage cupboards; and o Shelving. Furniture in this room has not been provided.
| 01CV - Civils | Cxxx-NCR-000453 | NCR | Antigraffti paint along South side of paint shop between grid line 3 and 4 - visual imperfection |  | Contr | VLK |  |  | 2017-09-30 | 2017-06-28 14:53 | -94 | 2016-08-08 15:09 | Civil - Civil Engineering General | 3000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | After completion of anti - graffiti painting works around paint shop; visual imperfection was observed on one panel (second panel from bottom) along south side of paint shop and between grid line 3 and 4.
| 01CV - Civils | Cxxx-NCR-000454 | NCR | Stage 3-6 Design Drawings |  | Contr | VLK |  |  | 2017-03-30 | 2017-02-01 15:59 | -57 | 2016-08-09 10:49 | Civil - Civil Engineering General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Verbal communication problem | Completed |  | In order to meet the Stages 3 to 6 construction programme, the design technical assurance of the pway, OLE and drainage drawings has been obtained through the CRL by exception process (CRL1-XRL-O7-GPD-CR001-50023). Refer to the following completed technical assurance by exception risk assessment forms for details of the drawings and scope: Cxxx-XRL-Y-__-CR112_SD007-50001 Cxxx-XRL-Y-__-CR112_SD007-50002 Cxxx-XRL-Y-__-CR112_SD007-50003 Cxxx-XRL-Y-__-CR112_SD007-50004
| 01CV - Civils | Cxxx-NCR-000455 | NCR | The monorail hoist running beams in WSA are sitting approximately 30mm lower than design |  | Contr | VLK |  |  | 2017-05-31 | 2017-05-05 16:28 | -26 | 2016-08-26 07:40 | Structural Engineering - Structural Engineering - General | 6000 |  | Design | Use As-Is | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | The monorail hoist running beams are sitting approximately 30mm lower than design. Through investigation it appeared that this is due to the steelwork and not the foundations to the steelwork.
| 01CV - Civils | Cxxx-NCR-000457 | NCR | The Contractor does not comply with Works information Vol 2A,with regards to Contract master Deliverables List (CMDL). |  | Contr | VLK |  |  | 2018-03-08 | 2018-06-29 09:51 | 113 | 2016-08-26 07:41 | Consents - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | The Contractor did not comply with Works information Vol 2A, Section 13.3.1 and its own Assurance Plan Cl 12.2 (Cxxx-VLK-O4-GPD-CR112_SD007-50002 Rev 5.0), with regards to Contract master Deliverables List (CMDL).
| 01CV - Civils | Cxxx-NCR-000458 | NCR | Site Wide Fire Strategy document need to be updated and must include all building on site, assembly points and all site walkways. |  | Contr | VLK |  |  | 2017-05-31 | 2017-04-05 10:44 | -56 | 2016-08-26 07:42 | Health & Safety General | 0 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Not Defined | Completed |  | Site Wide Fire Strategy document, while previously having been developed for the four main building on site needs to be expanded to include all building on site, assembly points and all site walkways.
| 01CV - Civils | Cxxx-NCR-000459 | NCR | Site Operation & Emergency Plan should be produced to identify the people, processes and precautions prior to areas of the site becoming operational and being handed over. |  | Contr | VLK |  |  | 2017-05-31 | 2017-03-23 11:44 | -69 | 2016-08-26 07:43 | Health & Safety General | 0 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Not Defined | Completed |  | Workscope Specification - C161-MMD-R-RSW-CR112_SD007-50002 Rev 1.3 4.14.23 Prior to areas of the site becoming operational and being handed over to the Depot Operator, a Site Operation and Emergency Plan shall be produced by the Contractor to identify the people, processes and precautions that are required to be managed within the new or modified buildings and this may include the update of existing site documents as necessary.
| 01CV - Civils | Cxxx-NCR-000460 | NCR | For Fire Risk Assessments, the Contractor shall provide a “responsible person” to undertake Fire Risk Assessments for any new or modified premises that comprise the Works |  | Contr | VLK |  |  | 2017-05-31 | 2017-05-09 15:08 | -22 | 2016-08-26 07:44 | Health & Safety General | 0 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Workscope Specification - C161-MMD-R-RSW-CR112_SD007-50002 Rev 1.3 4.14.22 The Contractor shall provide a “responsible person” to undertake Fire Risk Assessments for any new or modified premises that comprise the Works including but not limited to the Logistics and Stores Building, the new Paint Shop building, the Operations and Welfare building and Workshop A.
| 01CV - Civils | Cxxx-NCR-000461 | NCR | Depot Walkways, including designated safe walking routes, shall be laid out around the Site to provide safe access for operational and maintenance staff and configured to allow equipment and machinery movements. |  | Contr | VLK |  |  | 2017-09-29 | 2019-01-25 09:04 | 483 | 2016-08-30 13:40 | Environmental - Transport and Traffic Management | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | The roadways, crossings and authorised walking routes depot wide are key to identifying routes for items 2.1, 2.2, 2.3. The requirements are defined within: Workscope Specification - C161-MMD-R-RSW-CR112_SD007-50002 Rev 1.3 4.11.15 Walkways, including designated safe walking routes, shall be laid out around the Site to provide safe access for operational and maintenance staff and configured to allow equipment and machinery (including stores and refuse) to be taken to and from the point of use. When this NCR was raised GA did not believe the design does not showed these as a site wide solution.
| 01CV - Civils | Cxxx-NCR-000462 | NCR | RAMs deliverables have not been submitted. |  | Contr | VLK |  |  | 2017-09-30 | 2017-06-12 10:51 | -110 | 2016-08-26 07:45 | Health & Safety General | 0 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The RAMs deliverables required by part 30 of Works Information Volume 2A have not been submitted.
| 01CV - Civils | Cxxx-NCR-000463 | NCR | Non CRE’s are approving changes to the works and that FCD’s are required to be raised as per the project change control process |  | Contr | VLK |  |  | 2017-04-30 | 2017-04-04 08:44 | -26 | 2016-08-25 15:24 | Architectural - Interior Design & Art | 0 |  | Design | Repair | 4 (0.5-3k) | Complete | Verification Problems - Inspector not properly qualified | Completed |  | Non CRE’s are approving changes to the works and that FCD’s are required to be raised as per the project change control process
| 01CV - Civils | Cxxx-NCR-000464 | NCR | A Section 61 Dispensation was submitted to the local authority without employer's Project Manager acceptance |  | Crossrail | XRL |  |  | 2016-11-30 | 2017-01-03 12:44 | 34 | 2016-08-26 15:29 | Environmental - Noise and Vibration | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Contractor has submitted a Section 61 Consent Dispensation to the Local Authority without employer Project Manager acceptance. This relates to the dispensation signed by the local authority on 21st August 2016.
| 01CV - Civils | Cxxx-NCR-000465 | NCR | Section 61 consent |  | Crossrail | XRL |  |  | 2016-10-31 | 2016-11-11 22:57 | 11 | 2016-08-26 15:26 | Environmental - Noise and Vibration | 500 |  | Documentation and Records | Reject | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Dispensation from S61 consent was sought with the local authority for Stage 3 works on 9/8/16 without prior approval of Crossrail PM.
| 01CV - Civils | Cxxx-NCR-000466 | NCR | Section 61 application |  | Crossrail | XRL |  |  | 2016-10-22 | 2016-11-11 23:05 | 20 | 2016-08-26 15:37 | Environmental - Noise and Vibration | 500 |  | Documentation and Records | Reject | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | The contractor has applied for Section 61 consent for the main blockade works August - December 2016 without formal agreement from the Project Manager. While a review of the consent application was undertaken and a version of the consent application (Draft Control of Construction Noise & Vibration Plan) agreed, the final version that was submitted to Redbridge borough council had material alterations to it that concerned the works the consent was being sought for.
| 01CV - Civils | Cxxx-NCR-000467 | NCR | EMC deliverables-EMC matrix not received for any stage of work to date. |  | Contr | VLK |  |  | 2017-09-29 | 2020-02-18 16:37 | 872 | 2016-08-30 13:52 | Electrical - Electro Magnetic Compatibility | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | EMC matrix not received for any stage of work to date. __ have not completed this element of work. The outstanding issues are detailed in the Executive summaries of the following documents: • Cxxx-VLK-N3-RGN-CR112_SD007-50001-EMC_Stage1_Risk_Analysis&Design_Review • Cxxx-VLK-Y-RGN-CR112_SD007-50013-EMC_Stage2_Risk_Analysis&Design_Review • Cxxx-VLK-N2-STP-CR112_SD007-50031-EMC_Stage3-6_Risk_Analysis&Design_Review The deliverables identified within the Cxxx - GRIP 5 EMC Management Plan Cxxx-VLK-E-STP-CR112_SD007-50001 section 6 have not been provided
| 01CV - Civils | Cxxx-NCR-000468 | NCR | Traverser running slow and stop half way. Unit had to be reset to allow move to continue. |  | Contr | VLK |  |  | 2017-01-31 | 2017-01-03 15:17 | -28 | 2016-09-02 08:06 | Mechanical - Mechanical Engineering General | 40000 |  | Equipment Breakdown | Rework | 2 (6-60k) | Complete | External Phenomenon - Not Defined | Completed |  | Traverser was running slow and stop half way. Unit had to be reset to allow move to continue. Log faults indicated on video. Traverser platform is rubbing /catching on rail Dennis road spray booth end. Concern is that if this worsens it may collide causing further damage. Traverser pin did not engage to complete move in back road. This required us to reverse move towards Denis road. Pin engaged second time allowing train to be shunted.
| 01CV - Civils | Cxxx-NCR-000469 | NCR | CAD Model acceptance criteria by Crossrail. |  | Contr | VLK |  |  | 2017-09-30 | 2017-05-26 10:47 | -127 | 2016-09-06 14:34 | Systems - Software Engineering | 0 |  | Software | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | CRL has reviewed the last Interference report off __’s CAD model for Stage 3-6 and commented that the Bentley Microstation (BM) extension used by __ is incorrect – Bentley Structural & Mechanical should have been used. Historically, since 2014, __ have submitted 6+ Interference Reports for acceptance to CRL in BM and have received a Code 1 acceptance of the Report on each occasion with the type of extension file not raised as an issue.
| 01CV - Civils | Cxxx-NCR-000471 | NCR | Loading of the telehandler |  | Contr | VLK |  |  | 2017-09-29 | 2017-07-05 10:14 | -86 | 2016-09-06 16:17 | Civil - Civil Engineering General | 0 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | As part of the re-sequencing of the works, a telehandler has been provided by the project to allow Bombardier Transportation to carry out bogie movements using the Western Apron. There is no evidence that the design has been checked for the loading of the telehandler on the relevant hard standing areas (logistics, western apron and crossing).
| 01CV - Civils | Cxxx-NCR-000472 | NCR | LSB-0010 - Movement of 45ft road vehicle |  | Contr | VLK |  |  | 2016-12-11 | 2017-01-03 12:52 | 23 | 2016-09-06 16:22 | Civil - Civil Engineering General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | LSB-0010 requires the design of the logistics and stores building to allow for the approach of movements of a 45ft road vehicle. To date, there is no vehicle tracking study available on eB.
| 01CV - Civils | Cxxx-NCR-000473 | NCR | LSB-0012 - Bollards to protect Logistics Building |  | Contr | VLK |  |  | 2017-09-29 | 2018-01-26 09:57 | 119 | 2016-09-06 16:28 | Civil - Civil Engineering General | 2000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | LSB-0012 requires bollards to protect the logistics building roller shutter door structures from a vehicle strike. The bollards in their current position do not fulfil this function.
| 01CV - Civils | Cxxx-NCR-000474 | NCR | LSB-0014 - Provision of vision panels on fire exit doors |  | Contr | VLK |  |  | 2017-07-30 | 2017-07-31 07:59 | 1 | 2016-09-06 16:35 | Civil - Civil Engineering General | 0 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | LSB-0014 requires for the provision of vision panels on personnel fire exit doors. The current design has a mixture of doors with and without vision panels and there is no clear acceptance of their omission.
| 01CV - Civils | Cxxx-NCR-000475 | NCR | LSB-0020 - Gas and water design capacity requirements |  | Contr | VLK |  |  | 2018-03-15 | 2018-03-19 15:56 | 4 | 2016-09-06 16:41 | Civil - Civil Engineering General | 0 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | LSB-0020 requires the gas & water utility supply capacity requirements to be determined through design development. There are no calculations to support this. Calculations are a deliverable as set out in Works Information Volume 2A Appendix 7C.
| 01CV - Civils | Cxxx-NCR-000476 | NCR | LSB-0024 - building lighting to include high efficiency fluorescent lights with individual sensor control via a programmable output |  | Contr | VLK |  |  | 2017-05-26 | 2017-03-06 13:21 | -81 | 2016-09-06 16:46 | Electrical - Electrical Engineering General | 0 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | LSB-0024 requires the logistics and stores building lighting to include high efficiency fluorescent lights with individual sensor control via a programmable output. The requirement for an individual control via a programmable output has not been met.
| 01CV - Civils | Cxxx-NCR-000477 | NCR | LSB-0026 - building ventilation to include mechanical ventilation to provide air movement in line with current standards |  | Contr | VLK |  |  | 2017-05-26 | 2017-04-05 10:48 | -51 | 2016-09-06 16:51 | Mechanical - Mechanical Engineering General | 0 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | LSB-0026 requires the logistics and stores building ventilation to include mechanical ventilation to provide air movement in line with current standards. There is insufficient evidence to demonstrate that this requirement has been met for the main stores area.
| 01CV - Civils | Cxxx-NCR-000478 | NCR | Fire alarm design and related issues |  | Contr | VLK |  |  | 2017-09-30 | 2017-05-18 18:04 | -135 | 2016-09-06 16:55 | Electrical - Electrical Engineering General | 0 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The following inconsistencies have been found with the fire alarm records: o Design check certificate does not reflect the current design o There is no details of the fire alarm network to the gate house and red care call system o There is no evidence of compliance to BS 5839-8 for the PAVA system o The design certificate for all parts of the system needs to be included o The compliance of the overall system including all parts of the system (e.g. __, PAVA) needs to be demonstrated by a competent person
| 01CV - Civils | Cxxx-NCR-000479 | NCR | LSB-0035 - fire system to be provided with a unique address which is linked to room identification |  | Contr | VLK |  |  | 2016-12-11 | 2017-01-03 13:14 | 23 | 2016-09-06 17:00 | Electrical - Electrical Engineering General | 500 |  | Design | Reject | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | LSB-0035 requires the fire system to be provided with a unique address which is linked to room identification - this has not been met.
| 01CV - Civils | Cxxx-NCR-000480 | NCR | LSB-0035 requires the fire detection system to be wirelessly linked to the adjacent paint shop and wheel lathe buildings and be integrated to the overall Bombardier Transportation site fire detection |  | Contr | VLK |  |  | 2017-10-13 | 2018-02-21 16:09 | 131 | 2016-09-06 17:07 | Electrical - Electrical Engineering General | 0 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | LSB-0035 requires the fire detection system to be wirelessly linked to the adjacent paint shop and wheel lathe buildings and be integrated to the overall Bombardier Transportation site fire detection. This requirement has not been met.
| 01CV - Civils | Cxxx-NCR-000481 | NCR | LSB-0042 - Logistics and stores building between gridlines 1 to 16 was extended by 3.255m instead of 2m on the north elevation. |  | Contr | VLK |  |  | 2017-02-20 | 2017-02-22 21:47 | 2 | 2016-09-06 17:16 | Civil - Civil Engineering General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | LSB-0042 - Logistics and stores building between gridlines 1 to 16 was extended by 3.255m instead of 2m on the north elevation.
| 01CV - Civils | Cxxx-NCR-000482 | NCR | LSB-0045 requires the energy performance of the logistics and stores building to achieve an A rating |  | Contr | VLK |  |  | 2016-12-11 | 2016-10-17 08:37 | -55 | 2016-09-06 17:20 | Electrical - Electrical Engineering General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | LSB-0045 requires the energy performance of the logistics and stores building to achieve an A rating. To date, this certificate has not been provided.
| 01CV - Civils | Cxxx-NCR-000483 | NCR | Design calculation for structural steelworks for the logistics and stores and paintshop buildings have not been submitted for acceptance |  | Contr | VLK |  |  | 2016-12-11 | 2016-10-17 08:38 | -55 | 2016-09-06 17:26 | Structural Engineering - Structural Engineering - General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Design calculation for structural steelworks for the logistics and stores and Paintshop buildings have not been submitted for acceptance.
| 01CV - Civils | Cxxx-NCR-000484 | NCR | LSB-0210 requires the logistics and stores building gantry crane to have a 30 year design life subject to routine maintenance. |  | Contr | VLK |  |  | 2016-12-11 | 2017-02-01 16:49 | 52 | 2016-09-06 17:30 | Civil - Civil Engineering General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Not Defined | Completed |  | LSB-0210 requires the logistics and stores building gantry crane to have a 30 year design life subject to routine maintenance. Confirmation of this design life has not been received to date.
| 01CV - Civils | Cxxx-NCR-000485 | NCR | LSB-0228 requires the bulk paint store to be accessible by a forklift or hand pallet entry to deliver paint |  | Contr | VLK |  |  | 2016-12-11 | 2017-01-03 13:20 | 23 | 2016-09-06 17:33 | Civil - Civil Engineering General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | LSB-0228 requires the bulk paint store to be accessible by a forklift or hand pallet entry to deliver paint. There is no evidence to demonstrate that the ramp can take for lift loading.
| 01CV - Civils | Cxxx-NCR-000486 | NCR | New Panel Ghosting |  | Contr | VLK |  |  | 2017-01-31 | 2017-01-11 15:39 | -20 | 2016-09-09 08:17 | Electrical - Lighting | 1000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | It has been identified that the LED bulbs of the new panel in the YCO pick up any stray current causing a ghosting effect.
| 01CV - Civils | Cxxx-NCR-000488 | NCR | The chambers have been installed incorrectly due to incorrect schedule. |  | Contr | VLK |  |  | 2018-04-05 | 2018-06-27 08:55 | 83 | 2016-09-13 07:59 | Civil - Drainage | 6000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Supervision - Other | Completed |  | The chambers have been installed incorrectly due to incorrect schedule as it doesn't comply with the specification requirement for chambers within 1.4m of the running rail to be GRP. There are a number of chambers that have been installed within the track zone of influence in pre-cast concrete.
| 01CV - Civils | Cxxx-NCR-000489 | NCR | Works carried out without undertaking prior surveys causing risk. |  | Contr | VLK |  |  | 2017-10-31 | 2017-08-14 10:15 | -78 | 2016-09-13 08:10 | Surveying - Surveying General | 0 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The GRIP 5 drainage design shows the existing drainage tying into the new drainage installed during the stage 3 to 6 works at catch pit 1003. This connection was not made as the existing drain could not be located. Instead of investigating where the existing drainage goes, the works proceeded at risk. An investigation into the existing has now been undertaken and as a result re-work is required to connect the drainage at an alternative location.
| 01CV - Civils | Cxxx-NCR-000490 | NCR | Defective multimedia coverters in demarcation cabinet |  | Contr | VLK |  |  | 2016-12-21 | 2016-10-17 08:40 | -65 | 2016-09-16 13:35 | Electrical - Electrical Engineering General | 500 |  | Equipment Breakdown | Reject | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | The fibre system is not working between demarcation cabinet and paint shop and logistic building (inclusive). It is suspected that the multimedia converters are at fault
| 01CV - Civils | Cxxx-NCR-000491 | NCR | Cladding documentation |  | Contr | VLK |  |  | 2016-12-21 | 2017-01-11 15:45 | 21 | 2016-09-16 13:41 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Reject | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Cladding documentation was not submitted to CRL
| 01CV - Civils | Cxxx-NCR-000492 | NCR | Missing Fire Alarm drawings - Fire alarm - not all of the drawings for the fire alarm system (e.g. security hut) have been issued to Crossrail. |  | Contr | VLK |  |  | 2017-09-30 | 2017-09-28 15:12 | -2 | 2016-09-22 08:50 | Fire - Fire Systems & General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | Missing Fire Alarm drawings - Fire alarm - not all of the drawings for the fire alarm system (e.g. security hut) have been issued to Crossrail.
| 01CV - Civils | Cxxx-NCR-000493 | NCR | CANCEL - DUPLICATE OF Cxxx-NCR-000492 |  | Contr | VLK |  |  | 2017-01-31 | 2017-02-01 16:59 | 1 | 2016-09-16 13:47 | Fire - Fire Systems & General | 500 |  | Documentation and Records | Reject | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Missing Fire Alarm drawings - Fire alarm - not all of the drawings for the fire alarm system (e.g. security hut) have been issued to Crossrail. mainly network schematic drawings was missing
| 01CV - Civils | Cxxx-NCR-000494 | NCR | in complete ITP deliverable pack for Logistic Builsing Lighting Pack |  | Contr | VLK |  |  | 2016-12-23 | 2017-01-11 15:47 | 19 | 2016-09-18 12:16 | Electrical - Lighting | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | Following comments to be addressed on ITP deliverables: • Is __ registered as CRE/CEM as he has signed the LV test sheets on behalf of __. • Lux level report does not clarify uniformity or reference lighting design (not the spec) and has not been verified by the designer. • Emergency lighting certs are not signed by a designer and reference design • We did the emergency lighting level check with an escape route drawing, this is essential but is not included
| 01CV - Civils | Cxxx-NCR-000495 | NCR | Automatic Barriers at the Western Crossing |  | Contr | VLK |  |  | 2017-02-28 | 2017-01-11 16:18 | -48 | 2016-09-18 12:20 | Electrical - General | 5000 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | Automated barriers - the automated barrier at the western crossing induces current from the OLE.
| 01CV - Civils | Cxxx-NCR-000496 | NCR | UTX1 and UTX2 - incomplete Form A to Gs |  | Contr | VLK |  |  | 2016-12-23 | 2016-10-11 14:46 | -73 | 2016-09-18 12:24 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Reject | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | UTX1 and UTX2 - the A to Gs have not been fully signed off and there is not evidence of the signatory's competence. Track to be re-checked/signed off.
| 01CV - Civils | Cxxx-NCR-000497 | NCR | Missing Gas main network diagrams - a statutory requirement under Gas Safety (Installation and Use) Regulations 1998 |  | Contr | VLK |  |  | 2017-05-21 | 2017-05-17 13:44 | -4 | 2016-09-18 12:29 | Mechanical - Mechanical Engineering General | 0 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Gas main network diagrams are not submitted ; which is a statutory requirement under Gas Safety (Installation and Use) Regulations 1998
| 01CV - Civils | Cxxx-NCR-000498 | NCR | Fire Hydrants - Flow of fire Hydrants is less than requirements |  | Contr | VLK |  |  | 2017-05-21 | 2017-05-21 15:12 | 0 | 2016-09-18 12:37 | Utilities Engineering - Utilities General | 4000 |  | Design | Use As-Is | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | The measured flow for the hydrants is 15l/s which equates to 900 l/minute. The minimum requirement is 1500 l/minute and the value assumed at design is 40l/s.
| 01CV - Civils | Cxxx-NCR-000499 | NCR | In correct installation of Fire Ring Main |  | Contr | VLK |  |  | 2017-05-21 | 2017-05-21 15:22 | 0 | 2016-09-18 12:43 | Utilities Engineering - Utilities General | 3000 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Fire Hydrants - The fire ring main share the same connection from the main as the main cold water supply to the buildings; where BS9990 requires these systems to be separate. In addition fire ring main is connected to the main at one point. BS9990 requires them to be fed at two points.
| 01CV - Civils | Cxxx-NCR-000500 | NCR | Missing Competency Matrix |  | Contr | VLK |  |  | 2016-12-23 | 2016-10-17 08:41 | -67 | 2016-09-18 12:56 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | There is no competency matrix for the project to sign various documents / check sheets etc
| 01CV - Civils | Cxxx-NCR-000501 | NCR | Reduced road width for fire tender access |  | Contr | VLK |  |  | 2017-04-30 | 2017-03-02 18:17 | -59 | 2016-09-18 12:59 | Civil - Civil Engineering General | 0 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Fire tender access – there is a requirement for fire tender access to the south of the logistics building. The access route provided does not meet the requirements of BS 9999, i.e. that the width of the route is a minimum of 3.1m at gates. There are pinch points on site of approximately 2.8m.
| 01CV - Civils | Cxxx-NCR-000502 | NCR | Ops & Welfare pilling foundation |  | Contr | VLK |  |  | 2017-05-31 | 2017-04-13 09:19 | -48 | 2016-09-22 10:06 | Geotechnical Engineering - Concrete - Bored Pile | 6000 |  | Supervision/Management | Use As-Is | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | The piles installed for the Ops & Welfare foundations have not reached design depth and are out of spec. Design depths of 14.0 - 16.5m were not reached despite the design report stating “the piles should be driven to at least the minimum depths…irrespective of reaching the ‘set’ criteria at a shallower depth”. The initial pile logs show detailed pile sets for each pile but have been removed from site on Sunday. The piling log now shows 8-10mm/blow sets achieved but piles P05, P09, P13, P17, P41, P45, P49, P53, P77 require 7mm or less.
| 01CV - Civils | Cxxx-NCR-000503 | NCR | Ops & Welfare pilling foundation |  | Contr | VLK |  |  | 2017-05-21 | 2017-04-11 14:06 | -40 | 2016-09-22 11:08 | Geotechnical Engineering - Concrete - Bored Pile | 6000 |  | Design | Use As-Is | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | The tolerance on plan for each pile is +/-75mm, due to the installation method not incorporating a pilot auger for the initial 1m the steel casing, which is then bouncing out of position and is bad practice .
| 01CV - Civils | Cxxx-NCR-000504 | NCR | ITP for WSA lighting for 6 & 7-Poor Submittal |  | Contr | VLK |  |  | 2017-03-30 | 2017-02-16 11:10 | -42 | 2016-10-05 08:33 | Electrical - Lighting | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | The ITP-326 submitted for WSA Lighting road 6 & 7 was observed as a poor quality submission by CRL.14 comments were raised regarding incorrect entries of design, parameters, specification, UPS, LUX level requirements etc.
| 01CV - Civils | Cxxx-NCR-000505 | NCR | ITP for WSA Fire Alarm for 6,7 & 8 -Poor Submittal |  | Contr | VLK |  |  | 2016-12-04 | 2017-02-01 21:58 | 59 | 2016-10-05 11:10 | Systems - Fire Detection systems and Mains | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | ITP 325 (Cxxx-VLK-N2-ITP-CR112_SD007-50253) - Workshop A Fire Alarm System - Roads 6,7 and 8 , was submitted but observed as a poor quality by CRL. 29 comments were raised regarding incorrect references of design ,specifications, parameters, Works information's etc.
| 01CV - Civils | Cxxx-NCR-000506 | NCR | ITP for WSA Compressed Air -Poor Submittal |  | Contr | VLK |  |  | 2016-12-04 | 2017-01-11 16:30 | 38 | 2016-10-05 11:19 | Electrical - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | ITP 330 (Cxxx-VLK-N2-ITP-CR112_SD007-50258) - Workshop A Roads 6,7 and 8 - Compressed Air, was submitted but observed as a poor quality by CRL. 19 comments were raised regarding incorrect references of design ,specifications, parameters, Works information's etc.
| 01CV - Civils | Cxxx-NCR-000507 | NCR | Main Blockade - Signalling works commenced without an approved ITP in place |  | Contr | VLK |  |  | 2016-12-31 | 2017-01-03 15:26 | 3 | 2016-10-17 14:50 | Systems - Signalling | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Main Blockade - Signalling works as part of the main blockade have commenced without an approved ITP in place.
| 01CV - Civils | Cxxx-NCR-000509 | NCR | Ops and Welfare building - lack of progressive drainage QA records |  | Contr | VLK |  |  | 2017-04-04 | 2017-02-23 16:45 | -40 | 2016-10-17 15:14 | Civil - Drainage | 0 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Procedure Problem - Lack of procedure | Completed |  | Ops and Welfare building - Foul Drainage QA – Foul drainage was installed along GLA of the Ops and Welfare during week 28 possession weekend. __ have not received any Work Inspection Sheets for the works. The works are at risk of not been signed off by CRL.
| 01CV - Civils | Cxxx-NCR-000510 | NCR | RMU base-Stage 3-6 |  | Contr | VLK |  |  | 2017-03-31 | 2017-01-11 16:32 | -79 | 2016-10-18 10:08 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | RMU base was poured over the weekend without assured design.
| 01CV - Civils | Cxxx-NCR-000511 | NCR | Chambers installations at country end of Ops &Welfare building-chambers are bearing onto formation rather than bases. |  | Contr | VLK |  |  | 2017-09-30 | 2017-06-29 08:07 | -93 | 2016-10-18 14:35 | Civil - Drainage | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Chambers are bearing onto formation rather than bases. Chambers installations stage 3-6 at country end of Ops &Welfare building was not carried out as per design Cxxx-VLK-U-DDD-CR112_SD007_1-15651 C01.
| 01CV - Civils | Cxxx-NCR-000512 | NCR | Utilities and drainage-works have been built to an unassured design that has not gone through the by exception process |  | Contr | VLK |  |  | 2017-10-31 | 2017-08-04 15:56 | -88 | 2016-10-20 09:05 | Civil - Civil Engineering General | 0 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | There appear to be more cable chambers & drainage connections than design drawings indicate - Stages 3-6 drawing needs to be updated with the Draw pits added for the Ops & Welfare building, but the number of draw pits is as per the construction issue Cxxx-VLK-D-DDA-CR112_SD007_2-15311 & Cxxx-VLK-D-DDA-CR112_SD007_2-15312 are not included in the By Exception that made those drawings construction issue.
| 01CV - Civils | Cxxx-NCR-000513 | NCR | Construction of slab in operations and welfare building without an assured design. |  | Contr | VLK |  |  | 2017-09-30 | 2017-05-23 12:00 | -130 | 2016-10-27 08:04 | Civil - Civil Engineering General | 0 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | The slab was constructed without an assured design or by exception signed off in operations and welfare building.
| 01CV - Civils | Cxxx-NCR-000514 | NCR | Back Road De-railer installed in incorrect position outside Paint Shop |  | Contr | VLK |  |  | 2016-02-29 | 2017-02-01 22:01 | 338 | 2016-11-14 12:37 | Civil - Track | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | Please cancel this NCR. not required
| 01CV - Civils | Cxxx-NCR-000515 | NCR | WSA Roads 6,7,8 - Installation of PA System |  | Contr | VLK |  |  | 2017-02-09 | 2017-02-01 22:03 | -8 | 2016-11-03 15:33 | Systems - Systems Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | The installation and test of the PA System has been done based on a code 3 ITP although the comments from previous revision have been addressed and ITP resubmitted.
| 01CV - Civils | Cxxx-NCR-000516 | NCR | Monorail hoist running rail |  | Contr | VLK |  |  | 2017-09-30 | 2018-02-12 09:39 | 135 | 2016-11-03 14:32 | Mechanical - Lifts | 3000 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During inspection from BT’s insurer, Zurich, a number of defects were identified including steps in the running rail. These defects were not picked up during the thorough examination.
| 01CV - Civils | Cxxx-NCR-000517 | NCR | CFA Piling Eastern Apron - Lack of MCr for Splicing Clamps |  | Contr | VLK |  |  | 2016-01-29 | 2017-01-11 16:38 | 348 | 2016-11-04 10:46 | Structural Engineering - Reinforcement | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | CFA Piling Eastern Apron - During the regular __ surveillance it was identified that there was no approved MCR for the Splicing Clamps used on the pile reinforcement cages.
| 01CV - Civils | Cxxx-NCR-000518 | NCR | Workshop A Rd 4,5 Bogie Turntables |  | Contr | VLK |  |  | 2017-02-28 | 2017-01-11 16:40 | -48 | 2016-11-08 17:00 | Electrical - Electrical Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | The information within the ITP 208 Bogie Turntable (Cxxx-VLK-N2-ITP-CR112_SD007-50175 @ code2) isn't sufficient to satisfy project requirements. Section 4.2 Dead Testing of site electrical wiring of the aforementioned ITP is yet to be confirmed.
| 01CV - Civils | Cxxx-NCR-000519 | NCR | Workshop A - Road 3 - DPS - Software changes without client approval |  | Contr | VLK |  |  | 2017-09-30 | 2017-08-07 14:06 | -54 | 2016-11-14 13:45 | Electrical - Electrical Engineering General | 0 |  | Software | Rework | 4 (0.5-3k) | Complete | Management Problem - Other management problem | Completed |  | Workshop A - Road 3 - DPS - Software changes without client approval During FAT testing; __ suggested various changes to DPS software (CRL also present during FAT testing) and B&P modified the software to suit __ requirements without going through change control process.
| 01CV - Civils | Cxxx-NCR-000520 | NCR | Incorrect wiring installation in Bulk Paint Store (in Logistics Building) |  | Contr | VLK |  |  | 2017-05-21 | 2017-04-27 10:19 | -24 | 2016-11-16 09:39 | Electrical - General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | It is observed that the wiring was incorrectly installed in Bulk Paint Store (in Logistics Building) by __ for Logistics Heater DB2 L1 & L2.
| 01CV - Civils | Cxxx-NCR-000521 | NCR | Ops and Welfare Containment Installation |  | Contr | VLK |  |  | 2017-02-28 | 2017-02-16 12:05 | -12 | 2016-11-23 09:13 | Mechanical - Mechanical Engineering General | 0 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Not Defined | Completed |  | No ITP available for the works to commence.
| 01CV - Civils | Cxxx-NCR-000522 | NCR | Not following the QSP 02 requirments |  | Contr | VLK |  |  | 2018-01-12 | 2018-01-22 10:02 | 10 | 2016-11-24 09:08 | Consents - General | 0 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Lack of approval Code 1 procedures excessive | Completed |  | • CVs have not been submitted for acceptance for all individuals responsible for undertaking design in accordance with QSP02 • ISO 9001 certificates for subcontractors/testing houses have not been submitted as ITP deliverables as stated in QSP02. In addition, competence records for individuals carrying out sampling, testing and inspection were not available for review. • Currently there is no system for showing the activities for which each member involved with testing and commissioning is certified to carry out as required by Volume 2A Part 28.
| 01CV - Civils | Cxxx-NCR-000523 | NCR | Turntable is out of alignment by 9mm on road 5 |  | Contr | VLK |  |  | 2017-03-31 | 2017-03-24 09:55 | -7 | 2016-11-29 16:19 | Mechanical - Mechanical Engineering General | 0 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The Turntable is out of alignment by 9mm.
| 01CV - Civils | Cxxx-NCR-000524 | NCR | L&S Western Car Park Slab Defects |  | Contr | VLK |  |  | 2018-03-16 | 2018-05-15 09:49 | 60 | 2016-12-09 14:20 | Civil - Civil Engineering General | 0 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | __ inspected the site on behalf of __ and informed in its report that one of the concrete bay out side western entrance of logistics building was cracked and the width of the crack in approximately 4mm (refer page 5, section 3.1 the attached report)
| 01CV - Civils | Cxxx-NCR-000525 | NCR | Paintshop DOORs - PSS-0352 |  | Contr | VLK |  |  | 2017-09-30 | 2017-06-08 16:02 | -114 | 2016-12-14 10:55 | Civil - Civil Engineering General | 0 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Further design and assurance evidence required to close the DOORs item PSS-0352
| 01CV - Civils | Cxxx-NCR-000526 | NCR | Paintshop DOORS requirements - Platforms |  | Contr | VLK |  |  | 2017-06-21 | 2017-07-28 09:59 | 37 | 2016-12-14 11:02 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | Further Design and assurance evidence required to close the following DOORs items for platforms in paint shop PSS-0151 PSS-0153 PSS-0154 PSS-0155 PSS-0157 PSS-0165 PSS-0219 PSS-0220 PSS-0221 PSS-0223 PSS-0225 PSS-0226 PSS-0227 PSS-0229 PSS-0231 PSS-0232 PSS-0236 PSS-0239 PSS-0313
| 01CV - Civils | Cxxx-NCR-000527 | NCR | Paint Shop DOORs Requirements - PSS 0363 (On Tool Dust Extraction) |  | Contr | VLK |  |  | 2017-06-21 | 2017-04-26 13:10 | -56 | 2016-12-14 11:07 | Civil - Civil Engineering General | 0 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Further Design and or assurance evidence to b provided to close DOORS item PSS 0363 (On Tool Dust Extraction) - On-tool dust extraction is required within the small parts paint shop, located towards the front of the booth to allow for working just outside.
| 01CV - Civils | Cxxx-NCR-000528 | NCR | Paint Shop DOORs - Noise reports of the air handling equipment for items PSS-0167 & PSS-0237 |  | Contr | VLK |  |  | 2017-04-13 | 2017-02-01 22:20 | -71 | 2016-12-14 11:30 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | Noise levels of the air handling equipment within the spray/bake & preparation booth shall be reduced to as low as reasonably practicable and a maximum 75dB are to be provided for the following DOORs items to close: PSS-0167 & PSS-0237
| 01CV - Civils | Cxxx-NCR-000529 | NCR | Paint Shop DOOrs Requirements - PSS-0106 & PSS-0171 (Fall Arrest System in shotblat and preparation booths) |  | Contr | VLK |  |  | 2017-06-21 | 2017-04-10 13:37 | -72 | 2016-12-14 11:37 | Civil - Civil Engineering General | 0 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Design and assurance documentation required to close the following DOORs items: PSS-0106 (The shot blasting area shall include a fall arrest system located at high level for roof working. This system shall have the capacity to cater for two people attached at any one time.) & PSS-0171 (The hydraulically operated gantry platforms shall include a fall arrest system that links the platform to the operator via a full body harness.)
| 01CV - Civils | Cxxx-NCR-000530 | NCR | Provision of an access control system is required for the paint shop building. The access control shall provide a uniform access arrangement across Bombardier’s estate. This will either be by new access control. |  | Contr | VLK |  |  | 2018-01-19 | 2018-01-26 09:44 | 7 | 2016-12-14 11:40 | Civil - Civil Engineering General | 0 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Provide Design and assurance evidence to lose the DOORs item PSS-0042 - Provision of an access control system is required for the paint shop building. The access control shall provide a uniform access arrangement across Bombardier’s estate. This will either be by new access control or integration with and replication of the existing.
| 01CV - Civils | Cxxx-NCR-000531 | NCR | Paint Shop Doors Requirements - PSS-0037 (The plant room housing the compressed air equipment shall be enclosed. The room will have lighting installed and a mechanical ventilation system) |  | Contr | VLK |  |  | 2017-04-13 | 2017-02-01 22:22 | -71 | 2016-12-14 11:44 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | Provide design and assurance documentation to close the DOORs Item PSS-0037 (The plant room housing the compressed air equipment shall be enclosed. The room will have lighting installed and a mechanical ventilation system)
| 01CV - Civils | Cxxx-NCR-000532 | NCR | Paint Shop Doors Requirements - PSS-0032 : Lighting within the shot blasting and spray booth areas shall utilise IP65 rated luminaires. |  | Contr | VLK |  |  | 2017-04-13 | 2017-04-04 10:27 | -9 | 2016-12-14 11:49 | Civil - Civil Engineering General | 0 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | Provide and design and assurance documentation to close DOORs item - PSS-0032 : Lighting within the shot blasting and spray booth areas shall utilise IP65 rated luminaires.
| 01CV - Civils | Cxxx-NCR-000533 | NCR | Paint Shop DOORs requirements - PSS-0045 (An emergency gas shut off valve shall be provided for the main gas supply to the paint shop. This shut off shall be linked to the fire alarm system within the paint shop building so the gas supply is terminated i |  | Contr | VLK |  |  | 2017-05-31 | 2017-04-11 14:15 | -50 | 2016-12-14 11:53 | Civil - Civil Engineering General | 0 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Provide design and assurance documentation evidence to close DOORs item PSS-0045 - An emergency gas shut off valve shall be provided for the main gas supply to the paint shop. This shut off shall be linked to the fire alarm system within the paint shop building so the gas supply is terminated in the event of a fire. The link to the fire alarm system shall provide the functionality of testing the fire alarm during routine procedures and not affect the gas supply.
| 01CV - Civils | Cxxx-NCR-000534 | NCR | Paint Shop DOORs Requirements - provide evidence against following DOOrs items: PSS-0031, PSS-0047, PSS-0091, PSS-0099, PSS-0173 & PSS-0243 |  | Contr | VLK |  |  | 2017-06-21 | 2018-03-14 14:49 | 266 | 2016-12-14 11:59 | Civil - Civil Engineering General | 0 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Provide evidence against DOORs items : PSS-0031, PSS-0047, PSS-0091, PSS-0099, PSS-0173 & PSS-0243 (Accessibility and Maintainability related issues)
| 01CV - Civils | Cxxx-NCR-000535 | NCR | Paint Shop DOORs Item - PSS -0017 (The paint shop building shall be installed on a prepared slab. This base will incorporate a service entry duct for incoming services at the southwest corner of the paint shop. This service area shall be separated from t |  | Contr | VLK |  |  | 2017-05-31 | 2017-04-21 15:09 | -40 | 2016-12-14 12:04 | Civil - Civil Engineering General | 0 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Provide design an assurance evidence against DOORs item PSS -0017 (The paint shop building shall be installed on a prepared slab. This base will incorporate a service entry duct for incoming services at the southwest corner of the paint shop. This service area shall be separated from the remaining paint shop area.
| 01CV - Civils | Cxxx-NCR-000536 | NCR | Paint Shop DOORs Requirements for items PSS-0009 & PSS-0073 |  | Contr | VLK |  |  | 2017-04-13 | 2017-02-23 16:30 | -49 | 2016-12-14 12:08 | Civil - Civil Engineering General | 0 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Provide design and assurance evidence against DOORs items PSS-0009 (The paint shop shall conform to Guidance Note PG6/41, Coating and Recoating of Railway Vehicles which states the concentration of total particulate matter must not exceed 50mg/m3 of extracted air.)& PSS-0073 (The shot blasting area within the proposed paint shop shall have a maintained average illumination level of 700lux with minimal lighting level reduction during the shot blasting process)
| 01CV - Civils | Cxxx-NCR-000537 | NCR | Paint Shop DOORs Requirements for DOORs Items - PSS-0003 (The paint shop construction shall be wholly within the Limits of Deviation (LOD) defined by the Crossrail Act.) |  | Contr | VLK |  |  | 2017-04-13 | 2017-02-01 22:27 | -71 | 2016-12-14 12:11 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | Provide design and assurance evidence against DOORs item PSS-0003 (The paint shop construction shall be wholly within the Limits of Deviation (LOD) defined by the Crossrail Act.)
| 01CV - Civils | Cxxx-NCR-000538 | NCR | Paint Shop DOORs Requirements for DOORs Item - PSS-0065 (Spares for paint shop maintenance shall be available for a life of 20 years.) |  | Contr | VLK |  |  | 2017-06-21 | 2017-07-17 13:49 | 26 | 2016-12-14 12:14 | Civil - Civil Engineering General | 0 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Provide assurance evidence against DOORs item PSS-0065 (Spares for paint shop maintenance shall be available for a life of 20 years.)
| 01CV - Civils | Cxxx-NCR-000539 | NCR | Paint Shop Doors Requirements for Small Parts Room |  | Contr | VLK |  |  | 2017-06-21 | 2017-04-26 13:14 | -56 | 2016-12-14 12:17 | Civil - Civil Engineering General | 0 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Provide design and assurance evidence against DOORs items PSS-0331 PSS-0334 PSS-0337 PSS-0340 PSS-0343 PSS-0346 PSS-0349 PSS-0355 PSS-0361
| 01CV - Civils | Cxxx-NCR-000540 | NCR | Paint Shop DOORs Requirement - DPS |  | Contr | VLK |  |  | 2017-09-30 | 2017-07-21 11:26 | -71 | 2016-12-14 12:22 | Civil - Civil Engineering General | 0 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Provide design and assurance documentation for the following DOORs Items: PSS-0307 PSS-0309 PSS-0311 PSS-0313 PSS-0315
| 01CV - Civils | Cxxx-NCR-000541 | NCR | Paint Shop DOORs Requirements - Shunter related |  | Contr | VLK |  |  | 2017-04-13 | 2017-02-01 22:29 | -71 | 2016-12-14 12:25 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | Provide design and assurance documentation for the following DOORs items: PSS-0289 PSS-0294 PSS-0295 PSS-0299 PSS-0301 PSS-0305 PSS-0306
| 01CV - Civils | Cxxx-NCR-000542 | NCR | Paint Shop DOORs Requirements - Paint Mixing Room |  | Contr | VLK |  |  | 2017-06-21 | 2017-07-13 10:43 | 22 | 2016-12-14 12:28 | Civil - Civil Engineering General | 0 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Provide design and assurance documentation for the following DOORS requirements: PSS-0277 PSS-0279 PSS-0281 PSS-0283 PSS-0285
| 01CV - Civils | Cxxx-NCR-000543 | NCR | Paint Shop Doors Requirements - Day Paint Store |  | Contr | VLK |  |  | 2017-06-21 | 2017-06-08 16:00 | -13 | 2016-12-14 12:30 | Civil - Civil Engineering General | 0 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Provide design and assurance evidence against the following DOORs requirements / items: PSS-0265 PSS-0269 PSS-0271 PSS-0273 PSS-0275
| 01CV - Civils | Cxxx-NCR-000544 | NCR | Paint Shop DOORS Requirements - Spray / Bake __ |  | Contr | VLK |  |  | 2017-06-21 | 2017-07-13 10:44 | 22 | 2016-12-14 12:35 | Civil - Civil Engineering General | 0 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Provide design and assurance documentation evidence against the following DOORs requirements / items: PSS-0187 PSS-0189 PSS-0191 PSS-0193 PSS-0195 PSS-0199 PSS-0201 PSS-0203 PSS-0205 PSS-0206 PSS-0209 PSS-0211 PSS-0213 PSS-0215 PSS-0217 PSS-0235 PSS-0241 PSS-0245 PSS-0249 PSS-0251 PSS-0259 PSS-0261
| 01CV - Civils | Cxxx-NCR-000545 | NCR | Paint Shop DOORs Requirements - Preparation __ |  | Contr | VLK |  |  | 2017-06-21 | 2017-07-12 16:34 | 21 | 2016-12-14 12:38 | Civil - Civil Engineering General | 0 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Provide design and assurance documentation evidence against the following DDORs requirements / items: PSS-0131 PSS-0133 PSS-0137 PSS-0141 PSS-0145 PSS-0169 PSS-0179
| 01CV - Civils | Cxxx-NCR-000546 | NCR | Paint Shop DOORs Requirements - PSS-0127 (Personnel doors around Traverser) |  | Contr | VLK |  |  | 2017-09-30 | 2017-07-17 15:58 | -75 | 2016-12-14 12:41 | Civil - Civil Engineering General | 0 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Provide design and assurance documentation evidence against DOORs item - PSS - 0127 (The traverser area shall incorporate a minimum of 3 personnel doors for staff access and egress. The doors shall be double skin insulated. These doors shall incorporate easily replaceable compression seals. These doors shall include vandal proof vision panels. These doors shall include facilities to be locked and be provided with a means of internal emergency egress from the shot blasting area in cases of fire evacuation. These doors shall incorporate automatic doors closing mechanisms)
| 01CV - Civils | Cxxx-NCR-000547 | NCR | Paint Shop DOORs Requirements - Shot Blast Area |  | Contr | VLK |  |  | 2017-06-21 | 2018-03-07 11:54 | 259 | 2016-12-14 12:44 | Civil - Civil Engineering General | 0 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Provide design and assurance documentation evidence against the following DOORs requirements / items: PSS-0069 PSS-0077 PSS-0085 PSS-0101
| 01CV - Civils | Cxxx-NCR-000548 | NCR | Paint Shop DOORs Requirements - Paintshop General |  | Contr | VLK |  |  | 2017-06-21 | 2017-09-28 08:55 | 99 | 2016-12-14 12:46 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Provide design and assurance documentation evidence against the following DOORs requirements / items: PSS-0023 PSS-0026 PSS-0035 PSS-0043 PSS-0046 PSS-0048 PSS-0051 PSS-0055 PSS-0057 PSS-0059 PSS-0061 PSS-0062 PSS-0063
| 01CV - Civils | Cxxx-NCR-000549 | NCR | Paint Shop DOORs Requirements - PSS-0105 & PSS-0124 - IP65 Requirement |  | Contr | VLK |  |  | 2017-09-30 | 2017-06-08 15:54 | -114 | 2016-12-14 12:50 | Civil - Civil Engineering General | 0 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Provide the design and assurance documentation evidence against the following DOORs requirements / Items: PSS-0105 (The electrical installation within the shot blasting area shall be rated as a minimum of IP65 as defined in IEC 60529.) PSS-0124 (The electrical installation within the shot blasting area shall be rated as a minimum of IP65 as defined in IEC 60529.)
| 01CV - Civils | Cxxx-NCR-000550 | NCR | Extend RRAP (Rail Road Access Point) to allow RRV (Rail Road Vehicle) to access the paintshop |  | Contr | VLK |  |  | 2017-09-30 | 2018-02-09 15:02 | 132 | 2016-12-15 15:07 | Civil - Civil Engineering General | 0 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Extend RRAP to allow RRV to access the paint shop
| 01CV - Civils | Cxxx-NCR-000551 | NCR | Troughing Installation to new switch room in Workshop A |  | Contr | VLK |  |  | 2017-05-31 | 2017-03-31 14:44 | -61 | 2016-12-15 17:13 | Civil - Civil Engineering General | 3000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | __ as part of trough installation from phase 3 to new switch room at WSA has installed the troughs to wrong alignment and level. On the drawing - Cxxx-VLK-U-DDA-CR112_SD007_1-15943 - Workshop A plan see C/1/43 troughing , this is the location where the alignment and level went wrong, similarly see detail on section A, where trough units going into the chamber at low level, however they are installed at cover level. (PK)
| 01CV - Civils | Cxxx-NCR-000552 | NCR | Water ingress to paintshop |  | Contr | VLK |  |  | 2017-05-31 | 2017-03-15 09:13 | -77 | 2016-12-15 15:14 | Civil - Civil Engineering General | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Water ingress was noticed in Paint Shop
| 01CV - Civils | Cxxx-NCR-000553 | NCR | WSA - Road 3 - Excessive Wide Gauge |  | Contr | VLK |  |  | 2017-03-31 | 2017-02-14 12:19 | -45 | 2016-12-15 16:54 | Civil - Track | 6000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | The Rail installed within Road 3 concrete 'Box Outs' is non-compliant with NR/L2/TRK/2102 - Design and Construction of Track. The Track Gauge is supposed to fall within the following dimensions: 1435-1438mm; however, the as-built gauge in it's widest position is 1444mm.
| 01CV - Civils | Cxxx-NCR-000554 | NCR | Paint Shop - 'C’ type standard BS EN 13355 - __ Equipment |  | Contr | VLK |  |  | 2017-09-30 | 2017-08-14 14:11 | -47 | 2016-12-16 14:32 | Mechanical - Mechanical Engineering General | 0 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | __ Engineering have referenced the ‘C’ type standard BS EN 13355 on their Declaration of Conformity, however there is a discrepancy between the some of the specific requirements given in the standard and the implementation, specifically the requirements for the architecture of safety-related controls that are detailed in clause 5.8.2.5.1 of the standard.
| 01CV - Civils | Cxxx-NCR-000555 | NCR | Competency Management is not as per QSP 02 |  | Contr | VLK |  |  | 2017-04-15 | 2017-03-16 10:59 | -30 | 2016-12-16 15:49 | Civil - Civil Engineering General | 0 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Not Defined | Completed |  | Competency management of project personnel is not managed as per QSP 02
| 01CV - Civils | Cxxx-NCR-000556 | NCR | Incomplete design for HV/LV distribution for sidings and WSA |  | Crossrail | XRL |  |  | 2017-09-28 | 2017-09-28 08:51 | 0 | 2016-12-20 09:49 | Electrical - General | 3000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | In line with Crossrail's RFI 374 sent to Andrew Mikol on 19/12/2016 Design submission Cxxx-VLK-C-XST-CR112_SD007-50011 has been issued to CRL in a Draft stage on Rev 1.0, dated 11 March 2016. Please submit within 14 days a revised, final document for WSA HV/LV distribution and __ RMUs design. Section 1.1 states "This report is to be used for tender purposes therefore further development will be required by the nominated contractor with __ and panel manufacturers to complete the design." In light of construction works progressing, __ is requested to provide complete design basis for construction work. Sections 4.2.11 and 4.2.12 state load calculations are preliminary. Please provide final coordinated load calculations. CRL comments have not been address on eB. Please address. Provision of fire alarms is subject to discussions with stakeholders. What has been agreed in those discussions? Sections 4.4.2 and 5.3.2 state cable routes are indicative. In light of site spatial constraints these need to be final and coordinated routes. Please supply. This detailed design submission is based on __ requirements, yet details of those requirements or evidence of __'s review and acceptance of the design is not included. Please supply. Section 6.9.2 advises cabling will be designed by . Please advise eB ref No and supply this design. Appendix B is missing, please supply. There is no indication of HV/LV cooling equipment. Please supply design detail. Please supply detail of earth rod inspection pit. Drg Cxxx-VLK-C-DDA-CR112_SD007_1-15212 calls for mesh & recess to be specified by __. Please confirm what has been specified by __. Drg Cxxx-VLK-C-DDA-CR112_SD007_1-15213 does not show coordinated slab openings for incoming and outgoing ducts. Please supply. Evidence the 100% IDC comments have been closed is missing or some comments have not been addressed or some have been deferred to FDS stage. Please supply close out evidence. Appendix E is First draft and incomplete. Please re-submit complete design calculations. Appendix F - load calculations is missing, please supply. Appendix F - luminaire schedule is missing, please supply. Survey around footbridge and OLE mast foundations is identified as required to confirm proximity of proposed excavations. Has this been undertaken and included in the final design of duct routes, bearing in mind congested area? Please supply. buried containment to CCTV and IR points seem to be missing from the coordinated containment layout. Please supply. Cl 4.2.9.2 states that confirmation that traction earth at this location can be connected to __ earth. Please supply. Lighting protection risk assessment is missing. Please supply. Please submit signed off IDC under a separate eB document number. There is overlap between the external areas and buried services in immediate vicinity of HV/LV substation and RMUs and the Stage 3-6 submission drawings. How is __ managing change to these drawings? Are both being updated following change?
| 01CV - Civils | Cxxx-NCR-000557 | NCR | Missing documentation for Signalling works (L5091) carried out in 2014 |  | Contr | VLK |  |  | 2017-12-22 | 2017-10-25 10:47 | -58 | 2017-01-17 17:41 | Systems - Signalling | 0 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Not Defined | Completed |  | Documentation related to Signalling works on signal L5091 during 2013 / 2014 (Christmas duration) were lost.
| 01CV - Civils | Cxxx-NCR-000558 | NCR | Utility requirements for the Project |  | Contr | VLK |  |  | 2017-09-30 | 2017-07-05 10:19 | -87 | 2016-12-21 12:45 | Civil - Civil Engineering General | 0 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Utility requirements for the whole of the project has not been calculated / identified. No evidence is available to check and ensure that whole of utility requirements are calculated and installed utilities are capable of meeting whole project requirements
| 01CV - Civils | Cxxx-NCR-000559 | NCR | Paint Shop - Lack of evidence of functional testing of Fan/Pressure switch alarm (__ Paint Kitchen) |  | Contr | VLK |  |  | 2017-03-30 | 2017-03-07 11:40 | -23 | 2016-12-21 15:27 | Civil - Civil Engineering General | 0 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Personnel Error - Not Defined | Completed |  | During review of certification documentation with CRL; it is noticed that document evidence for functional testing of Fan/Pressure switch alarm (__ Paint Kitchen) is missing.
| 01CV - Civils | Cxxx-NCR-000560 | NCR | Paintshop - Rewiring of paint kitchen |  | Contr | VLK |  |  | 2017-05-31 | 2017-03-21 12:58 | -71 | 2016-12-21 15:32 | Civil - Civil Engineering General | 0 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Evidence of functional testing of wiring is missing for Baldy Paint Kitchen
| 01CV - Civils | Cxxx-NCR-000562 | NCR | Failure to conduct periodic statutory tests of __ systems |  | Contr | VLK |  |  | 2017-04-19 | 2017-03-07 08:57 | -43 | 2017-01-13 09:41 | Civil - Civil Engineering General | 0 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | Periodic statutory tests of __ systems were not conducted as required.
| 01CV - Civils | Cxxx-NCR-000564 | NCR | WSA Eastern Apron - On-site concrete testing undertaken by not appropriately trained operatives |  | Contr | VLK |  |  | 2017-04-30 | 2017-04-03 15:38 | -27 | 2017-01-13 14:20 | Civil - Structural Engineering | 2000 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Training Deficiency - No training provided | Completed |  | WSA - RC works to Eastern Apron. During a regular __ surveillance, the activity of concrete sampling and cube making was observed being performed by two __ operatives and found to be in line with the requirements of BS EN 12350-2 (Slump Test and Cube Sampling). In addition to this, the operatives were able to correctly describe the whole process of concrete sampling and testing. However, when asked if they have been trained to perform such activity, they said they have been trained in the past but were not able to produce current certificates. Due to the positive finding of the observation and operatives' confirmation that they can do concrete testing correctly, they were allowed to continue with the concrete sampling and cube making.
| 01CV - Civils | Cxxx-NCR-000565 | NCR | Road 1 c/e track drainage |  | Contr | VLK |  |  | 2017-09-30 | 2018-01-26 14:37 | 118 | 2017-01-23 11:42 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Supervision - Other | Completed |  | Water main installation not in line as per design drawings.
| 01CV - Civils | Cxxx-NCR-000567 | NCR | Workshop A - Mechan lifting jacks truncking |  | Contr | VLK |  |  | 2017-09-30 | 2017-06-15 07:29 | -107 | 2017-01-30 11:01 | Electrical - Electrical Engineering General | 6000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | Workshop A - Mechan lifting jacks truncking The trunking installed at WSA Rd 3 to 5 to accommodate Mechan lifting jacks control cables has been found to be non-compliant (i.e. non-IP rated). The trunking runs are from GL 2-18 in the section's between RDs 4&5 (2 runs) and between RDs 3&4 (1 run) for approximately 160 M each run.
| 01CV - Civils | Cxxx-NCR-000568 | NCR | The OLE design for Road 12 |  | Contr | VLK |  |  | 2018-03-21 | 2018-03-09 16:36 | -12 | 2017-02-21 16:48 | Over Head Line Electrification - Over Head Line Electrification General | 0 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The OLE design for Road 12 has reduced OLE clearance to the lighting mast near to the eastern REB to sub 2.75m. As a result AGA have raised concern that they will no longer be able to lower the luminaires without requiring an isolation.
| 01CV - Civils | Cxxx-NCR-000569 | NCR | Ops & Welfare - Incorrect boards used in 1st floor female shower |  | Contr | VLK |  |  | 2017-09-29 | 2017-06-29 13:20 | -92 | 2017-03-10 15:24 | Civil - Civil Engineering General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | It was noted that within the Ops & welfare Female Locker / WC / Shower (first floor) the wall boards used are not the green moisture resistant boards used in all other ‘wet’ rooms.
| 01CV - Civils | Cxxx-NCR-000570 | NCR | PSS-0045 As built Gas drawings for Paintshop - Cxxx-VLK-M-DDE-CR112_SD007_Z-78018 (X02) |  | Contr | VLK |  |  | 2017-06-08 | 2017-05-10 11:56 | -29 | 2017-03-10 15:41 | Utilities Engineering - Gas | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | It is observed that Drawing Cxxx-VLK-M-DDE-CR112_SD007_Z-78018 X02 showing the GAS isolation valve has been marked up to mask the GAS SAFETY ISOLATION VALVE on the As built / redline. This is incorrect and needs to be revised to include correct information.
| 01CV - Civils | Cxxx-NCR-000572 | NCR | Section 61 consent application has been submitted to the council with no prior acceptance by CRL |  | Contr | VLK |  |  | 2017-07-04 | 2017-05-22 13:13 | -43 | 2017-03-30 16:20 | Environmental - Noise and Vibration | 0 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | A Section 61 application for Cxxx Ilford Depot works was issued by the Contractor to the local authority, Redbridge Council, on 27th March 2017. The Works Information requires prior approval of the consent paperwork by cross rail, under Parts 2A and 2B, clause 21.8.6.1: “The Contractor shall submit a control of construction noise and vibration plan to the Project Manager for acceptance prior to issuing a section 61 consent application to the local authority”. This required acceptance by the Project Manager has not been granted. Additionally, the Contractor’s current Section 61 consent expires on 31st March 2017. Therefore, the requirement for a completed and accepted consent to be issued to the Local Authority for their review no later than 4 weeks prior to the date of consent (if alternatively agreed that a draft will not be required, no later than 8 weeks before consent date sought) has not been met. The Contractor has fallen significantly short of this deadline.
| 01CV - Civils | Cxxx-NCR-000574 | NCR | Materials installed without an approved Material Compliance Record |  | Crossrail | XRL |  |  | 2017-08-13 | 2017-08-21 15:00 | 8 | 2017-05-16 10:05 | Electrical - General | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | A Quality Surveillance on MEP Material Compliance took place on the Operations and Welfare Building at Ilford Yard. Post site visit a check on documentation found that Swift Tray, 120mm Tri-rated Earth Cable and different types of Earth Bars had been installed without approved MCRs. The Contractor did produce two MCRs for different types of Earth Bar and Cable Tray installed.
| 01CV - Civils | Cxxx-NCR-000575 | NCR | Door Control Panel (DCP) fitness for purpose |  | Crossrail | XRL |  |  | 2018-05-31 | 2018-06-13 09:09 | 13 | 2017-06-28 14:21 | Human Factors - Human Factors General | 3000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Key switches on the DCP do not have feature to indicate which way these are pointing. As such the switches are not fit for purpose. In addition, the end user raised an issue of indication lights in operation not being suitable for the operations in its final setting, refer to the attached email.
| 01CV - Civils | Cxxx-NCR-000576 | NCR | WAS0412 & WAS0430 - the new bi-folding doors shall have a minimum width of 4.25m |  | Contr | VLK |  |  | 2017-12-22 | 2017-07-19 15:17 | -156 | 2017-07-05 14:02 | Architectural - Doors | 0 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | WAS0412 & WAS0430 - the new bi-folding doors shall have a minimum width of 4.25m not complied with
| 01CV - Civils | Cxxx-NCR-000577 | NCR | WAS0627 - The monorail hoists shall be stored at the east end of the workshop in their rest position. |  | Contr | VLK |  |  | 2017-08-31 | 2017-07-19 11:53 | -43 | 2017-07-05 14:22 | Mechanical - Mechanical Engineering General | 0 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | WAS0627 - The monorail hoists shall be stored at the east end of the workshop in their rest position, but are stored at the west end for Roads 3&4 and at both ends on Road 5.
| 01CV - Civils | Cxxx-NCR-000579 | NCR | CPFR 5882 and GRIP 4 wide walkways along Road H |  | Crossrail | XRL |  |  | 2017-10-31 | 2019-11-14 10:13 | 744 | 2017-07-21 13:28 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | FCD 381 requested approval for change of OLE pile and foundation. This FCD 381 has not been closed to date, due to information still outstanding from designers. In the FCD, concern was raised about introducing additional tripping hazard to the walkway by pile cap, if it was made proud of the walkway surface. Designer gave assurance this has been considered, however no evidence was provided to substantiate that claim. Works as constructed indicate the above concern was not addressed and pile caps have been installed such that they protrude above walkway surface, creating tripping hazard. Risk has been temporarily managed on site by fencing off the pile cap with a handrail, while bringing sidings into use on 21st May. Refer to the attached photograph. Works as installed are: - not in line with assured design (GRIP 5 design for walkways) - not in line with Works Information (GRIP 4 design for walkways) - not in line with functional requirement CPFR 5882. As such, this element of Works is considered defective and requires rectification. Contractor is required to submit proposals to Project Manager to address the above three shortcomings, in particular to provide wide walkways on both sides of stabling road H. Upon agreeing remediation proposal, Contractor is to submit design for approval and assurance, before progressing with works on site.
| 01CV - Civils | Cxxx-NCR-000580 | NCR | DOORs Item - Cxxx-WS-217 (the stabling of class 315 trains in an 8 car formation - no access platforms) |  | Contr | VLK |  |  | 2017-10-31 | 2018-02-14 16:36 | 106 | 2017-08-01 15:47 | Civil - Civil Engineering General | 0 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The requirements of Cxxx-WS-217 for the stabling of class 315 trains in an 8 car formation has not been met resulting in no access platforms for them. CRL can then get this closed out with GA, as the 315’s are only going to be in use for another 18 months and the walkways are already congested enough without more platforms.
| 01CV - Civils | Cxxx-NCR-000581 | NCR | Ops & Welfare Building - London-Facing (W8) Windows non-opening |  | Contr | VLK |  |  | 2017-10-31 | 2017-08-04 12:29 | -88 | 2017-08-01 15:51 | Civil - Civil Engineering General | 0 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | All windows installed in the Signal Control room were to be inward opening for cleaning purposes. On arrival to site, it was discovered that the 2 smallest London-facing windows were fixed and would not open at all. These were installed despite not being as per design - to weatherproof the room, with the intention of being replaced with the correct set at a later date. It has since been assessed that an alternative set which could be hinged would cause the viewing panels to be too narrow for operational purposes, and hence the proposal is for the windows to remain as fixed.
| 01CV - Civils | Cxxx-NCR-000582 | NCR | Ops & Welfare Builing - South-East Country-Facing (W7) Windows hung incorrectly |  | Contr | VLK |  |  | 2017-10-31 | 2018-01-18 16:58 | 79 | 2017-08-01 15:58 | Civil - Civil Engineering General | 0 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The Country-facing double-leaf window by the Signalling Panel was installed with the RH sash hung with RH opening, which led to it opening in to the Signal Control Panel. This prevented access to the outer pane for cleaning as the window opened no more than 15 degrees. The original design for this reason showed this sash to be hinged on the central mullion, rather than the outer frame. This requirement was missed by Thurston and the sash hung incorrectly prior to delivery on site.
| 01CV - Civils | Cxxx-NCR-000583 | NCR | Ops & Welfare Building - Chnage of SCR Carpet |  | Contr | VLK |  |  | 2017-10-31 | 2017-08-04 15:10 | -88 | 2017-08-01 16:02 | Civil - Civil Engineering General | 0 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The carpet specified in the previous design was no longer available, having been discontinued. __ and __ installed the suppliers recommended replacement for this product without CRL or stakeholder acceptance of the product.
| 01CV - Civils | Cxxx-NCR-000584 | NCR | Road 6&7 services |  | Contr | VLK |  |  | 2017-10-16 | 2017-08-14 15:16 | -63 | 2017-08-02 13:33 | Electrical - Power Distribution | 0 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The works information calls for a certain number of compressed air and electrical outlets to be supplied in the extending of Roads 6&7 as detailed below: WAS0334 - The extension of road 7 shall be provided with a minimum of 6 x compressed air outlets for every 20m vehicle position along the excavated pit. WAS0336 - A minimum of 6 x 415v, 3phase outlets shall be provided between the extensions of roads 6 and 7 equidistant along the hard standing. WAS0339 - The final locations of all maintenance pit services noted above (air, water and power) shall be fully determined at detailed design to suit the rolling stock being maintained. __ were unable to provide the requested number due to special constraints. In an effort to comply with the WI as best as possible, __ matched the spacing of the existing services in Roads 6&7. These spacings and quantities of the utilities were reviewed by __ during the interdisciplinary checks that __ attended and as the utilities matched what was already provided in the existing lengths of these roads, there was no request to increase the number to be installed.
| 01CV - Civils | Cxxx-NCR-000585 | NCR | Cxxx-WS-81 - Providing interlocking for the OLE in sidings |  | Contr | VLK |  |  | 2017-10-03 | 2018-02-14 16:50 | 134 | 2017-08-04 10:51 | Electrical - OHLE | 0 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | __ are unable to comply with Cxxx-WS-81: 4.5.12 Interlocking shall be an integral safety feature within the new Crossrail Stabling Sidings A to K and associated S&C to minimise the possibility of electrocution of staff while undertaking maintenance or cleaning. The interlocking system shall have an interlock panel; that will accept an interlock key that can be only removed from the OLE Switch Isolator when it is in the earthed position, and without which the OLE Switch Isolator cannot be moved from the earthed position. With the interlock key inserted in the interlock panel, the interlock key shall have the facility to be locked off with personal padlocks, to prevent its removal whilst maintenance staff are working in OLE areas. The Contractor shall submit the design of the OLE isolations, safety interlocking, and the relationship with signalling lockouts, to the Employer for Assurance Acceptance.
| 01CV - Civils | Cxxx-NCR-000586 | NCR | Minor cracks observed in drainage Catchpits |  | Contr | VLK |  |  | 2018-02-28 | 2018-03-23 11:56 | 23 | 2017-08-04 13:02 | Civil - Drainage | 0 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper handling of material | Completed |  | This NCR has been raised as a result of minor cracks being observed in some of the pre-cast concrete sections used to form drainage Catchpits
| 01CV - Civils | Cxxx-NCR-000587 | NCR | Cxxx-WS-259 - gate required on walkway east of O&W building |  | Contr | VLK |  |  | 2017-10-31 | 2017-08-14 15:26 | -78 | 2017-08-08 10:48 | Systems - Signalling | 0 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Cxxx-WS-259 was not complied with during the design & construction, text below: A gate on the walkway between the Operations & Welfare building and the east end of the Crossrail Stabling Sidings shall be interlocked with the depot protection system and shall be sprung closed. The gates shall be locked when it is not safe to access the sidings. The Contractor shall develop the design of the area to the north of siding K to include this gate, positioned such that a person would encounter the gate close to, but before, the point at which they would start to cross any sidings. The Contractor shall develop the design of the gate and local fencing in the vicinity such that persons would need to pass through the gate rather than finding a way around it. The Contractor shall submit the detail design for that area and the operation of the gate to Crossrail for Assurance Acceptance.
| 01CV - Civils | Cxxx-NCR-000588 | NCR | Paint Repairs to Ops & Welfare Building |  | Contr | VLK |  |  | 2018-04-09 | 2018-06-14 09:46 | 66 | 2017-09-18 15:21 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | It was identified that some area requiring painting repairs located at the strip of the building under the facia panel has not been repaired to the agreed Manor’s repair procedure. The attached letter from Thurston confirms in Item 2 that the area in question is adequately protected and has been repainted as per manufacturer's recommendations.
| 01CV - Civils | Cxxx-NCR-000589 | NCR | Incorrect Sealant used for Ops and Welfare Building |  | Contr | VLK |  |  | 2017-12-27 | 2020-03-27 16:58 | 821 | 2017-09-18 15:16 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | It was observed that the joint between the stacked units has not been sealed properly to prevent water ingress to the building.
| 01CV - Civils | Cxxx-NCR-000590 | NCR | Penetrations to Ops and Welfare Building |  | Contr | VLK |  |  | 2017-12-27 | 2020-06-22 15:01 | 908 | 2017-09-18 15:19 | Civil - Civil Engineering General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | It was observed that the penetrations to Ops and Welfare building were not properly closed
| 01CV - Civils | Cxxx-NCR-000592 | NCR | 3.2.4.1.g - Train lifting Jacks in WSA |  | Contr | VLK |  |  | 2018-01-19 | 2018-01-22 10:05 | 3 | 2017-09-21 09:00 | Civil - Civil Engineering General | 0 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | On site demonstration of lifting jacks could not complete site - waiting for Bombardiers availability.
| 01CV - Civils | Cxxx-NCR-000595 | NCR | COWL for SC 3 |  | Contr | VLK |  |  | 2018-05-31 | 2018-04-30 14:17 | -31 | 2017-09-21 10:41 | Civil - Civil Engineering General | 0 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | The following works and QA are outstanding for SC 3 - list attached for details
| 01CV - Civils | Cxxx-NCR-000596 | NCR | COWL for SC 4 |  | Contr | VLK |  |  | 2018-05-31 | 2018-04-30 14:18 | -31 | 2017-09-21 10:45 | Civil - Civil Engineering General | 0 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | The following works and QA are outstanding for SC 4 - list attached for details
| 01CV - Civils | Cxxx-NCR-000597 | NCR | COWL for SC 5 |  | Contr | VLK |  |  | 2018-05-31 | 2018-04-30 14:19 | -31 | 2017-09-21 10:49 | Civil - Civil Engineering General | 0 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | The following works and QA are outstanding for SC 5 - list attached for details.
| 01CV - Civils | Cxxx-NCR-000599 | NCR | Ops and Welfare Building - Pending DOORs item - C161-OWTS-81 |  | Contr | VLK |  |  | 2018-03-16 | 2018-03-19 15:51 | 3 | 2017-09-25 16:25 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The following DOORs item is still open - waiting for evidence for compliance: C161-OWTS-81
| 01CV - Civils | Cxxx-NCR-000600 | NCR | WSA Open DOORs items (WAS0257, WAS0283, WAS0521 & WAS0530) |  | Contr | VLK |  |  | 2018-03-22 | 2018-06-21 14:36 | 91 | 2017-09-25 16:29 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | The following DOORs items are still open - waiting for evidence to close: WAS0257, WAS0283, WAS0521 & WAS0530
| 01CV - Civils | Cxxx-NCR-000601 | NCR | Open DOORS items - DPSS - Cxxx.20, Cxxx.51, Cxxx.52, Cxxx.58, Cxxx.107, Cxxx.110 |  | Contr | VLK |  |  | 2018-03-22 | 2018-10-30 15:29 | 222 | 2017-09-25 16:34 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | The following DPSS DOORs items could not be closed due to lack of evidence: DPSS - Cxxx.20, Cxxx.51, Cxxx.52, Cxxx.58, Cxxx.107, Cxxx.110
| 01CV - Civils | Cxxx-NCR-000602 | NCR | Work Scopy DOORS items - Cxxx-WS-36, Cxxx-WS-314 |  | Contr | VLK |  |  | 2018-03-22 | 2018-10-30 15:30 | 222 | 2017-09-26 10:02 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | The following DOORs items are still open - waiting for evidence to close: Cxxx-WS-36, Cxxx-WS-314
| 01CV - Civils | Cxxx-NCR-000603 | NCR | Work Scope DOORS items - Cxxx-WS-37, Cxxx-WS-73, Cxxx-WS-81, Cxxx-WS-208, Cxxx-WS-211, Cxxx-WS-226, Cxxx-WS-279, Cxxx-WS-282 |  | Contr | VLK |  |  | 2018-01-24 | 2018-06-21 14:38 | 148 | 2017-09-26 10:06 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | The following DOORs items are still open - waiting for evidence to close: Cxxx-WS-37, Cxxx-WS-73, Cxxx-WS-81, Cxxx-WS-208, Cxxx-WS-211, Cxxx-WS-226, Cxxx-WS-279, Cxxx-WS-282
| 01CV - Civils | Cxxx-NCR-000604 | NCR | Work Scope DOORS items - Cxxx-WS-210, Cxxx-WS-217, Cxxx-WS-258, Cxxx-WS-272, Cxxx-WS-273, Cxxx-WS-347 |  | Contr | VLK |  |  | 2018-03-22 | 2018-06-18 14:03 | 88 | 2017-09-26 10:10 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | The following DOORs items are still open - waiting for evidence to close: Cxxx-WS-210, Cxxx-WS-217, Cxxx-WS-258, Cxxx-WS-272, Cxxx-WS-273, Cxxx-WS-347
| 01CV - Civils | Cxxx-NCR-000605 | NCR | Work Scope DOORS items - Cxxx-WS-317, Cxxx-WS-323, Cxxx-WS-324, Cxxx-WS-354, Cxxx-WS-459 |  | Contr | VLK |  |  | 2018-03-22 | 2018-06-18 14:04 | 88 | 2017-09-26 10:12 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | The following DOORs items are still open - waiting for evidence to close: Cxxx-WS-317, Cxxx-WS-323, Cxxx-WS-324, Cxxx-WS-354, Cxxx-WS-459
| 01CV - Civils | Cxxx-NCR-000606 | NCR | Work Scope DOORS items - Cxxx-WS-343 |  | Contr | VLK |  |  | 2018-01-01 | 2018-01-18 17:18 | 17 | 2017-09-26 10:15 | Civil - Civil Engineering General | 0 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | The following DOORs item is still open - waiting for evidence to close: Cxxx-WS-343
| 01CV - Civils | Cxxx-NCR-000607 | NCR | Work Scope DOORS items - Cxxx-WS-352, Cxxx-WS-353 |  | Contr | VLK |  |  | 2018-01-25 | 2018-03-09 09:38 | 43 | 2017-09-26 10:18 | Civil - Civil Engineering General | 0 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The following DOORs items are still open - waiting for evidence to close: Cxxx-WS-352, Cxxx-WS-353
| 01CV - Civils | Cxxx-NCR-000608 | NCR | Work Scope DOORS items - Cxxx-WS-363, Cxxx-WS-364, Cxxx-WS-365, Cxxx-WS-366, Cxxx-WS-370, Cxxx-WS-380 |  | Contr | VLK |  |  | 2018-03-22 | 2020-03-05 17:21 | 714 | 2017-09-26 10:20 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | The following DOORs items are still open - waiting for evidence to close: Cxxx-WS-363, Cxxx-WS-364, Cxxx-WS-365, Cxxx-WS-366, Cxxx-WS-370, Cxxx-WS-380
| 01CV - Civils | Cxxx-NCR-000609 | NCR | Work Scope DOORS items - Cxxx-WS-462, Cxxx-WS-464, Cxxx-WS-493, Cxxx-WS-500, Cxxx-WS-502, Cxxx-WS-503 |  | Contr | VLK |  |  | 2018-03-22 | 2019-01-18 13:58 | 302 | 2017-09-26 10:22 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | The following DOORs items are still open - waiting for evidence to close: Cxxx-WS-462, Cxxx-WS-464, Cxxx-WS-493, Cxxx-WS-500, Cxxx-WS-502, Cxxx-WS-503
| 01CV - Civils | Cxxx-NCR-000610 | NCR | Work Scope DOORS items - Cxxx-WS-326, Cxxx-WS-328, Cxxx-WS-332, Cxxx-WS-345, Cxxx-WS-463 |  | Contr | VLK |  |  | 2018-03-22 | 2018-06-29 09:49 | 99 | 2017-09-26 10:28 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Supervision - Other | Completed |  | The following DOORs items are still open - waiting for evidence to close: Cxxx-WS-326, Cxxx-WS-328, Cxxx-WS-332, Cxxx-WS-345, Cxxx-WS-463
| 01CV - Civils | Cxxx-NCR-000611 | NCR | RAM deliverables required prior to completion |  | Crossrail | XRL |  |  | 2018-02-22 | 2018-02-16 09:28 | -6 | 2017-09-26 16:10 | Systems - Systems Engineering General | 0 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | RAM evidence required prior to completion, under Part 30 of Vol 2A of Works Information, has not been made available to Project Manager for inspection and acceptance.
| 01CV - Civils | Cxxx-NCR-000613 | NCR | Road 1 limited clearances between kinematic envelope and NR palisade fence |  | Contr | VLK |  |  | 2018-04-06 | 2018-06-27 08:56 | 82 | 2017-09-28 15:03 | Health & Safety General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | The introduction of the NR owned palisade fence between the London and Country throats in the design has introduced limited clearances between Road 1 kinematic envelope and the fence.
| 01CV - Civils | Cxxx-NCR-000614 | NCR | Misting of SCR Windows |  | Contr | VLK |  |  | 2018-02-03 | 2018-03-07 17:37 | 32 | 2017-10-06 14:57 | Civil - Civil Engineering General | 0 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | it is observed that On several occasions the external face of the windows in the SCR, with the exception of the small windows which have the self-cleaning film applied, have misted up. This has prevented the yard controllers having a clear view of the yard out of the windows, which is a safety requirement of the contract.
| 01CV - Civils | Cxxx-NCR-000615 | NCR | Drainage run & connection to GA interceptor Country End |  | Crossrail | XRL |  |  | 2018-04-30 | 2018-06-29 10:04 | 60 | 2017-10-09 12:29 | Civil - Drainage | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Manhole SWMH12, the drain pipe down stream of this manhole and connection to the existing petrol interceptor have not been constructed in line with the Works Information requirement and it has not been captured in line with the established change management process.
| 01CV - Civils | Cxxx-NCR-000616 | NCR | Ops and Welfare Building - in correct installation of SCR door door closer |  | Contr | VLK |  |  | 2018-02-28 | 2018-02-02 10:57 | -26 | 2017-10-19 08:18 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Supervision - Other | Completed |  | it is observed that the control room door closer came off as long enough screws were not used.
| 01CV - Civils | Cxxx-NCR-000617 | NCR | Road A L/E insulator installed not in line with design |  | Crossrail | XRL |  |  | 2017-12-22 | 2018-03-09 10:20 | 77 | 2017-10-19 11:59 | Electrical - OHLE | 0 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The insulator of Road A contact wire for the permanently earthed section anchored on structure IL24B has been installed not in line with design drawings. As such a stagger has been introduced between section isolators on Road A and Roads B, C, D. This introduces staggered isolation limit within the same electrical section 361M. From discussions held on the Stage 4 Options Study to relocate SI on road B, it is clear that neither __'s designer, Mott's technical reviewer nor NR would endorse introducing such stagger. Depending on the proposed solution, the options study Cxxx-VLK-Y-RGN-CR112_SD007-50034 is to be updated such that there is no contradictory statements between the report and installed infrastructure.
| 01CV - Civils | Cxxx-NCR-000618 | NCR | Inconsistent illuminated fire signage in Paintshop Shotblast Bay |  | Contr | VLK |  |  | 2018-04-27 | 2018-04-30 12:43 | 3 | 2017-10-30 16:57 | Electrical - Lighting | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | installed illuminated Fire Exit signs at the north east and south east fire exits of the shot blast bay in the Paintshop and did not install an illuminated sign at the north west, despite this being marked on the fire strategy drawing as a Fire Exit.
| 01CV - Civils | Cxxx-NCR-000619 | NCR | DEFECTIVE FIXING TO MAGLOCK 002 - PAINTSHOP DOUBLE DOOR ADJACENT TO TRAVERSER. |  | Contr | VLK |  |  | 2018-03-30 | 2018-05-08 11:02 | 39 | 2017-10-30 17:06 | Civil - Civil Engineering General | 100 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | DEFECTIVE FIXING TO MAGLOCK 002 - PAINTSHOP DOUBLE DOOR ADJACENT TO TRAVERSER. - Maglock 002 has light duty fixings and is working loose
| 01CV - Civils | Cxxx-NCR-000620 | NCR | Security CCTV verification & validation |  | Crossrail | XRL |  |  | 2020-05-15 | 2020-09-07 08:54 | 115 | 2017-11-07 14:49 | Communications and Control Systems - CCTV | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Form B comment, relating to restricted views from some cameras, has been agreed to be resolved by __ via on site adjustments during installation, to optimise the view. Following site security review with CRL's __ it became apparent that 1) some of those adjustments either have not been done or an optimal viewing position has not been achieved. examples include cameras looking directly at OHLE stanchions, brackets limiting key view of PTZ camera 2) some of the signage has been installed after commissioning of the security system and its position has not been coordinated with security requirements 3) testing and commissioning has been undertaken without trains stabled within the roads
| 01CV - Civils | Cxxx-NCR-000621 | NCR | Redline drawings |  | Contr | VLK |  |  | 2018-04-09 | 2018-05-08 10:59 | 29 | 2017-11-17 14:20 | Civil - Civil Engineering General | 0 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | During a random joint review; it is noticed that some of the redline drawings are reflecting the as constructed information (didn't capture all changes).
| 01CV - Civils | Cxxx-NCR-000622 | NCR | Old YCO Fire Risk Assessment |  | Crossrail | XRL |  |  | 2018-05-31 | 2018-05-15 14:57 | -16 | 2017-12-04 12:35 | Fire - Fire Systems & General | 500 |  | Incomplete Works | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | FIRE RISK AS__MENT for OLD YCO has been completed at interim stage and needs to be re-visited, including site visit from competent person prior to updating the FRA, once all works covered under PMI 598 have been completed and tested. Please note specific wording of Fire Strategy regarding OYCO detection and connectivity and audible alarm.
| 01CV - Civils | Cxxx-NCR-000624 | NCR | Security snags |  | Crossrail | XRL |  |  | 2018-06-27 | 2020-06-08 13:19 | 712 | 2018-01-04 10:45 | Architectural - Security | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | In addition to defects specifically raised under NCR620, the CRL site security report appended to NCR 620 also highlights number of snags agreed by __ to be completed, as well as those which are contentious. The purpose of this NCR is to highlight at least two items deemed contentious which require evidence of either rectification or justification for keeping the asset as installed. These two items are: 1. no consideration of climbing aids on the NR side of the fence by the means of existing infrastructure and in particular use of unistrut bracket fixings for light fittings on Depot side on each fence post 2. height of the fence being less than 2.4m in number of places
| 01CV - Civils | Cxxx-NCR-000625 | NCR | Telecommunications link between Old YCO and O&W SCR |  | Contr | VLK |  |  | 2018-03-27 | 2020-06-23 12:39 | 819 | 2018-01-11 15:32 | Communications and Control Systems - Telephony | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | WI calls for a telephone link to be provided between the old YCO and the O&W SCR, this has not been provided by __, this is captured in the below: - The penetration point into the Old YCO is shown in 'Old YCO layout.png'. - The cable route to O&W building is shown in 'Stage 3-6 Utilities GA - new telecommunications route.pdf' - The cable route inside the O&W building will be as per the existing route utilised for all other communications/signalling and DPS containment as per existing containment drawing attached - The M&E Construction CRE has provided confirmation that there is space capacity in the troughing and O&W containment in the attached email 'Cable Routes.msg'. Cxxx-FCD-000475 -Telecommunications link from Old YCO to OandW SCR (linked) is approved
| 01CV - Civils | Cxxx-NCR-000626 | NCR | 'Electric Loco Stop Here' sign not installed on Road A as per Stage 4 OLE layout drawing |  | Contr | VLK |  |  | 2018-04-05 | 2018-06-13 09:03 | 69 | 2018-04-04 10:14 | Train - Signalling And Control | 500 |  | Incomplete Works | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | 'Electric Logo Stop Here' sign not install on Road A as per Stage 4 OLE layout drawing
| 01CV - Civils | Cxxx-NCR-000627 | NCR | Cxxx - COWL Items for WCC |  | Contr | VLK |  |  | 2021-01-19 | 2021-02-25 10:27 | 37 | 2018-01-08 12:16 | Civil - Civil Engineering General | 500 |  | Incomplete Works | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | COWL items for WCC are still to be closed
| 01CV - Civils | Cxxx-NCR-000628 | NCR | Cxxx - Outstanding Documents still at Code 3 |  | Contr | VLK |  |  | 2018-03-08 | 2018-06-27 08:58 | 111 | 2018-01-11 13:32 | Information Management | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | The Contractor does not comply with Works information Vol 2A,with regards to completion of outstanding documents still at code 3 post Whole Contract Completion.
| 01CV - Civils | Cxxx-NCR-000629 | NCR | Cxxx - Outstanding Documents still at Code 2 |  | Contr | VLK |  |  | 2018-03-08 | 2018-06-29 09:55 | 113 | 2018-01-11 13:57 | Information Management | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | The Contractor does not comply with Works information Vol 2A,with regards to completion of outstanding documents still at code 2 post Whole Contract Completion.
| 01CV - Civils | Cxxx-NCR-000630 | NCR | Cxxx - Outstanding As Builts |  | Contr | VLK |  |  | 2021-01-25 | 2021-02-26 16:59 | 32 | 2018-01-12 08:16 | Information Management | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | The Contractor does not comply with Works information Vol 2A,with regards to completion of outstanding As Builts post Whole Contract Completion.
| 01CV - Civils | Cxxx-NCR-000631 | NCR | Overall H&S file at completion and defects liability period |  | Crossrail | XRL |  |  | 2018-03-06 | 2018-03-06 15:10 | 0 | 2018-01-16 10:35 | Health & Safety General | 0 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | It is noted that Cxxx-VLK-Z7-GIN-CR112_SD007-50015 (Code 1) includes extract from CDM-RR in Appendix A. This does not represent the agreed final version of CDM RR. Contractor is required to update the content of the H&S file with the latest version of approved Integrated CDM Risk Register. It is recommended that a reference to the file is made or entire accepted document is included, rather than an extract, as that may cause issue with configuration control to the end users. Overall H&S file should be revised to its final version at the end of defects liability period, capturing all changes made while addressing NCRs, FCDs, defects etc.
| 01CV - Civils | Cxxx-NCR-000632 | NCR | Final Design Overview - close out of open deliverables |  | Crossrail | XRL |  |  | 2020-06-19 | 2020-08-12 08:32 | 54 | 2018-03-05 13:18 | Systems - Systems Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Final Design Overview process, in particular Final Design Overview Addendum report, has been concluded and signed off by CRL as Accepted (Code 1) on the basis that all engineering deliverables and in particular those open documents listed in Appendix L of Cxxx-VLK-Y-RGN-CR112_SD007-50035, have agreed path to closure. This NCR has been raised in order to ascertain that the above mentioned documents are all accepted by CRL (Code 1 or Code 4, where relevant). SC6 section completion certificate shall not be issued to the Contractor until such time when all the above are accepted by CRL Engineering team. A suitable file note shall be drafted by the Contractor logging close out of these deliverables and acceptance by CRL. This should be submitted and linked to FDO and FDOA reports.
|  | Cxxx-NCR-003010 | NCR | CMS installation in staircases at CHS & DSS do not comply with LUL Standards S1-371 & S1-133 |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2020-10-18 | 2022-03-15 09:43 | 513 | 2020-09-08 10:40 | Electrical - General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | some of the current CMS installation in staircases at CHS & DSS do not comply with LUL Standards S1-371 & S1-133.
|  | Cxxx-NCR-000118 | NCR | Crossrail Stainless Steel CCTV camera shroud discoloration |  | Crossrail | PDP | INT - Interfaces (Projectwide) |  | 2018-03-31 | 2019-08-12 16:21 | 499 | 2017-11-21 17:03 | Communications and Control Systems - CCTV | 500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Discoloration of stainless steel CCTV camera shrouds following failure to neutralise sufficiently the post-weld cleansing acid. Sample check at __ storage facility at Harlow revealed a near 100% defect rate.
|  | Cxxx-NCR-000122 | NCR | Naming convention and Designer's Alternative ID for Earthing cables below and within the Moorgate Shaft base slab |  | Crossrail | PDP | INT - Interfaces (Projectwide) |  | 2021-11-12 09:50 | 2021-10-22 09:53 | -21 | 2021-10-21 14:08 | Information Management - Asset Information | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The earth cables within and below the base slab, were installed by C501 and numbered and labelled by Crossrail in 2014. The naming convention is incorrect and no Designer's Alternative Asset ID has been assigned. The asset tags are as follows: M135-OLE-00001 L9 - EARTHWIRE 001 Earth Pit 1, Cable-E:, Base slab Earth mat M135-OLE-00002 L9 - EARTHWIRE 002 Earth Pit 1, Cable-E:, Base slab Earth mat M135-OLE-00003 L9 - EARTHWIRE 003 Earth Pit 1, Cable-E:, Base slab Earth mat M135-OLE-00004 L9 - EARTHWIRE 004 Earth Pit 2, Cable-E:, Base slab Earth mat M135-OLE-00005 L9 - EARTHWIRE 005 Earth Pit 2, Cable-E:, Base slab Earth mat M135-OLE-00006 L9 - EARTHWIRE 006 Earth Pit 2, Cable-E:, Base slab Earth mat M135-OLE-00007 L9 - EARTHWIRE 007 Earth Pit 3, Cable-E:, Base slab Earth mat M135-OLE-00008 L9 - EARTHWIRE 008 Earth Pit 3, Cable-E:, Base slab Earth mat M135-OLE-00009 L9 - EARTHWIRE 009 Earth Pit 3, Cable-E:, Base slab Earth mat M135-OLE-00010 L9 - EARTHWIRE 010 Earth Pit 4, Cable-E:, Base slab Earth mat M135-OLE-00011 L9 - EARTHWIRE 011 Earth Pit 5, Cable-E:, Base slab Earth mat M135-OLE-00012 L9 - EARTHWIRE 012 Earth Pit 6, Cable-E:, Base slab Earth mat M135-OLE-00013 L9 - EARTHWIRE 013 Earth Pit 6, Cable-E:, Base slab Earth mat M135-OLE-00014 L9 - EARTHWIRE 014 Earth Pit 6, Cable-E:, Base slab Earth mat M135-OLE-00015 L9 - EARTHWIRE 015 Earth Pit 7, Cable-E:, Base slab Earth mat M135-OLE-00016 L9 - EARTHWIRE 016 Earth Pit 7, Cable-E:, Base slab Earth mat M135-OLE-00017 L9 - EARTHWIRE 017 Earth Pit 7, Cable-E:, Base slab Earth mat M135-OLE-00018 L9 - EARTHWIRE 018 Earth Pit 8, Cable-E:, Base slab Earth mat M135-OLE-00019 L9 - EARTHWIRE 019 Earth Pit 8, Cable-E:, Base slab Earth mat M135-OLE-00020 L9 - EARTHWIRE 020 Earth Pit 8, Cable-E:, Base slab Earth mat M135-OLE-00021 L9 - EARTHWIRE 021 Earth Pit 9, Cable-E:, Base slab Earth mat M135-OLE-00022 L9 - EARTHWIRE 022 Earth Pit 9, Cable-E:, Base slab Earth mat M135-OLE-00023 L9 - EARTHWIRE 023 Earth Pit 9, Cable-E:, Base slab Earth mat
|  | Cxxx-NCR-000123 | NCR | Naming convention and Designer's Alternative ID for Earth Bars within the Moorgate Shaft base slab |  | Crossrail | PDP | INT - Interfaces (Projectwide) |  | 2021-11-19 20:55 | 2021-10-22 20:56 | -28 | 2021-10-22 10:54 | Information Management - Asset Information | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The earth bars within the Moorgate Shaft base slab, were installed by C501 and numbered and labelled by Crossrail in 2014. The naming convention is incorrect and no Designer's Alternative Asset ID has been assigned. The asset tags are as follows: Tag Code Name Description M135-ENB-00003 L9 - EARTH BAR 001 Moorgate Shaft, Level 9, Earth Bar M135-ENB-00004 L9 - EARTH BAR 002 Moorgate Shaft, Level 9, Earth Bar M135-ENB-00005 L9 - EARTH BAR 003 Moorgate Shaft, Level 9, Earth Bar M135-ENB-00006 L9 - EARTH BAR 004 Moorgate Shaft, Level 9, Earth Bar M135-ENB-00007 L9 - EARTH BAR 005 Moorgate Shaft, Level 9, Earth Bar M135-ENB-00008 L9 - EARTH BAR 006 Moorgate Shaft, Level 9, Earth Bar M135-ENB-00009 L9 - EARTH BAR 007 Moorgate Shaft, Level 9, Earth Bar M135-ENB-00010 L9 - EARTH BAR 008 Moorgate Shaft, Level 9, Earth Bar M135-ENB-00011 L9 - EARTH BAR 009 Moorgate Shaft, Level 9, Earth Bar
|  | Cxxx-NCR-000124 | NCR | C624 BUCF Asset Information: Naming non-conformance of grid references |  | Crossrail | XRL | INT - Interfaces (Projectwide) |  | 2022-03-14 08:38 | 2022-02-28 08:47 | -14 | 2022-02-01 11:32 | Information Management - Asset Information | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The attached 24 assets are unable to be named in conformance to Crossrail requirements as Crossrail cannot provide the 2x2 grid references required. In line with the intent of the naming convention, site grid references from site drawings have been used for the following asset tags.
|  | Cxxx-NCR-000125 | NCR | C624 Asset Information - Unavailable attributes |  | Crossrail | XRL | INT - Interfaces (Projectwide) |  | 2022-03-21 11:26 | 2022-03-15 13:08 | -6 | 2022-02-10 13:06 | Information Management - Asset Information | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Completion of the desktop and site activities are complete and there are a number of asset attributes outstanding that are not able to be collected. For EX-BCC-12-ME: There are 77 missing attributes affecting 33 assets (of the 225 total assets) across 6 systems For EX-BCC-03-ME: There are 820 missing attributes affecting 168 assets (of the 385 total) across 16 systems. There is no further works planned to source the outstanding information. This NCR is to approve that the undocumented attributes are acceptable and do not adversely impact on RFLi's ability to carry out it's asset management obligations.
|  | Cxxx-NCR-000126 | NCR | C624 Asset Information - Incorrect use of Sounder L-Class for Speaker assets |  | Crossrail | XRL | INT - Interfaces (Projectwide) |  | 2022-03-21 12:03 | 2022-03-15 13:15 | -6 | 2022-02-01 11:55 | Information Management - Asset Information | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The contractor has labelled speaker assets under the Sounder L-class (L76254). This NCR is raised to confirm this non-conformance is acceptable and the assets are not required to be corrected to the Speaker L-Class (L76116). The following assets are applicable to this NCR.
|  | Cxxx-NCR-000127 | NCR | C624 Asset Information - Use of LVD functional code instead of LTG for Lighting wiring |  | Crossrail | XRL | INT - Interfaces (Projectwide) |  | 2022-03-07 14:24 | 2022-02-21 16:26 | -14 | 2022-02-10 12:31 | Information Management - Asset Information | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The following wiring cables relating to the lighting system have been raised using the LVD functional code in the asset tag, instead of the required LTG functional code. This NCR is raised to allow the acceptance of this non-conformance to limit the rework to the asset information.
|  | Cxxx-NCR-000128 | NCR | C624 Asset Information - Access Door Control PC raised under incorrect L-Class |  | Crossrail | XRL | INT - Interfaces (Projectwide) |  | 2022-03-21 12:00 | 2022-03-15 13:16 | -6 | 2022-02-02 15:16 | Information Management - Asset Information | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The PC that controls the Access Control software/system for the BUCF was raised under the incorrect L-Class of L76133 - AV Recording Equipment. A more appropriate L-class for this asset is L7642 - Head end computer. This NCR has been raised to accept this non-conformance in naming as the Access Control System at the BUCF is planned to be replaced by the TfL access control system, and there is no adverse affect in allowing this non-conformance in the interim period. The asset tag for the PC is: CR527-__-00128 AV RECORDING EQUIPMENT 002 BUCF, Lvl 1, Store G005, PC
|  | Cxxx-NCR-000129 | NCR | C624 Asset Information - Missing Equipment - BUCF 012 High |  | Crossrail | XRL | INT - Interfaces (Projectwide) |  | 2022-03-08 13:45 | 2022-03-15 13:11 | 7 | 2022-02-15 06:34 | Information Management - Asset Information | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | There are a total of 24 items cannot be raised as equipment in AIMS due to insufficient information. This NCR is to confirm that the absence of equipment iDs for these assets can be managed by RFLi and no further works are necessary to correct this non-conformance. LClass # Info on item L746211 Wiring cables 19 All wiring cables as no manufacturer information. Cable schedule exists. L76133AV Recording Equipment 1 PC is not given a specific make and model L762203 Micro Switch Contacts for Doors And Windows 4 No confirmation of manufacturer make/model. See doc reference for more information : C624-XRL-Z3-RGN-CR527-50004
|  | Cxxx-NCR-000130 | NCR | C624 Asset Information - Missing equipment information for BUCF non-critical |  | Crossrail | XRL | INT - Interfaces (Projectwide) |  | 2022-03-21 09:10 | 2022-03-15 13:12 | -6 | 2022-02-16 14:46 | Information Management - Asset Information | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | There are a total 94 items that cannot be raised as equipment in AIMS due to insufficient information (86 assets affected) or due to a technical issue (8). This NCR is to confirm that the absence of equipment iDs for these assets can be managed by RFLi and no further works are necessary to correct this non-conformance. L746211 Wiring cables: 26 All wiring cables have no manufacturer information. Cable schedule exists. L746291 Control Cables: 14 All control cables have info on size and type but no manufacturer information L743343: Earthwire 10 Unknown manufacturer and model L74341: Earth Bar 2 Unknown manufacturer and model L74344: Earth Rods 2 Unknown manufacturer and model L76264 Data/Telephone Point: 17 Manufacturer is known, model number is not, there is not a direct match in the MCR containing similar product so cannot raise equipment L75611 Dampers: 5 No info has been sourced through site visits or documentation on the Volume control dampers. Sizes are known from the drawings L747352 Plate Switches & Multi Gang Grid: 3 Manufacturer is known, model number is not, there is not a direct match in the MCR containing similar product so cannot raise equipment L7453Test Point: 7 Manufacturer is known, model number is not, there is not a direct match in the MCR containing similar product so cannot raise equipment L76254 Sounders: 8 These assets were raised as sounders, and due to this we are unable to assign the equipment id: EQ00005913 as this is linked to speakers. So this is a technical allocation issue over an absence of product knowledge. Note: CRL1-NCR-000126 was raised relating to the use of the Sounder L-Class for a speaker asset. Total 94
|  | Cxxx-NCR-000131 | NCR | Incorrect Functional code used to create assets. |  | Crossrail | XRL | INT - Interfaces (Projectwide) |  | 2022-03-21 09:07 | 2022-03-15 13:17 | -6 | 2022-02-15 13:19 | Information Management - Asset Information | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | In correcting the L-Class for 6 motion detectors that form part of the intruder alarm system, the new assets iDs were incorrectly raised using the LTG function code instead of the SEC function code. CR527-LTG-00198 GAP MONITOR 005 CR527-LTG-00199 GAP MONITOR 006 CR527-LTG-00200 GAP MONITOR 007 CR527-LTG-00201 GAP MONITOR 008 CR527-LTG-00202 GAP MONITOR 009 CR527-LTG-00203 GAP MONITOR 010
|  | Cxxx-NCR-000132 | NCR | Over-length CCTV CAT 6 cables at Liverpool Street |  | Crossrail | PDP | INT - Interfaces (Projectwide) |  | 2022-03-24 | 2022-03-11 10:00 | -13 | 2022-03-10 14:09 | Communications and Control Systems - CCTV | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | The following CCTV camera CAT6 cables fall outside of the 90m limit for CAT 6 cabling and do not have ethernet extenders installed. The numbers below are the camera numbers from their CAM-XXX designation on the design. These are recorded on the red-line as built schedule : Cxxx-SMN-R3-LST-C101-50011 rev X01. Code 1 on eB. Greater than 120m: 226 227 229 230 232 335 336 233 165 331 Greater than 90m , less than 120m: 118 119 122 123 136 173 210 159 216 220 222 224 225 231 164 166 166 163
|  | Cxxx-NCR-000133 | NCR | BUCF - M26 Asset Label Information Recorded: Tags without label (CRL1-PWK-00394, CRL1-PWk-00403, CRL1-PWK-00433 & __-00243) |  | Crossrail | XRL | INT - Interfaces (Projectwide) |  | 2022-09-26 10:38 | 2022-09-12 10:42 | -14 | 2022-09-08 10:57 | Information Management - Asset Information | 0 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | NCR raised to close-out CRL1-PWK-00394, CRL1-PWK-00403 & CRL1-PWK-00433, the three PWKs relates to tags without asset label at BUCF. RfLi to acceptance the assets as is, this will remove the need for __-00243.
|  | Cxxx-NCR-000352 | NCR | __R Supplies A & B Not Cordinated between Station and Systemwide (__-00274) |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2023-06-30 |  | -144 | 2022-07-11 11:16 | Electrical - Power Distribution | 500 |  | System Defect | Use As-Is | 4 (0.5-3k) | Open |  | REVIEW |  | During the Scenario 9 tests it was found that when the A supply was lost there was an alarm on the signalling switchboard that showed a fault on the 'B' supply not 'A'. This was demonstrated two times during the Scenario 9 tests held on 26th June and 10th July.
|  | Cxxx-NCR-000395 | NCR | Busbar Support Remidal Works Following __ Report (__-00274) |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2023-06-30 |  | -144 | 2022-10-28 11:52 | Electrical - General | 500 |  | Incorrect Installation |  |  | Open |  | PROPOSE ACTION |  | The busbars at the ETH require remedial works to the support systems as they have been found to fail which is confirmed in the __ support bracketry calculations report (see references). Remedial works are required on the BOS/LV/E/A to Transformer busbar and BOS/LV/E/A to BOS/LV/E/B busbar. Specific details can be found in the __ reports (see references). Location: ETH -4 LVSRA & LVSRB
|  | Cxxx-NCR-000062 | NCR | WTH DCP124 in LCR room 5/776 does not allow multicontrol of local dampers (__-00274) |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2023-06-30 |  | -144 | 2022-09-28 09:20 | Fire - Fire Systems & General | 2000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Open |  | IMPLEMENTATION |  | WTH Damper Control Panel (DCP124) located in the LCR room 5/776 is currently a 12-way DCP with single control from the fire panel but needs to be a multicontrol panel
|  | Cxxx-NCR-000010 | NCR | WTH -3 Bench Install - Wrong Colour Grout Used (__-00274) |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2023-06-30 |  | -144 | 2022-10-20 14:33 | Architectural - General | 500 |  | Incorrect Installation |  |  | Open |  | PROPOSE ACTION |  | Instructed works under Cxxx-PMI-00129. On final inspection of the WTH -3 Bench, it appears that the wrong colour grout has been installed. This must be removed and reinstated to the correct colour
|  | Cxxx-NCR-002561 | NCR | Ommission of easy clean-dust free sockets from Door thresholds |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2022-11-11 | 2022-10-07 08:56 | -35 | 2020-06-04 21:11 | Architectural - Doors | 3000 |  | Design | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On Various locations around the station where a shoot-bolt forms part of the installed Ironmongery, an easy clean floor socket has not been fitted as identified on the door schedule. This applies to both suppliers of this project. However, the majority of __ doors are only securely fixed (bolted) to the top frame so no hole has been formed on the floor. On many locations, although the door schedule does not call for an easy clean socket, there are holes in the threshold as the installed Ironmongery consists of floor restrained bottom shoot-bolts on either the passive or active leaf of the door.
|  | Cxxx-NCR-002240 | NCR | PAD Balustrading Architectural Issues - AP5 Staircase |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2021-07-31 | 2020-07-10 14:33 | -386 | 2019-04-08 17:08 | Architectural - Balustrade | 500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | There are a number of Architectural issues with the PAD installed BAL-112 glazed balustrades across the station. Cxxx-NCR-002198 has been cancelled and the associated issues split into the 3 station areas. Cxxx-NCR-002238 - PAD Balustrading Architectural Issues - Moorgate Ticket Hall Cxxx-NCR-002239 - PAD Balustrading Architectural Issues - PRM Corridor Cxxx-NCR-002240 - PAD Balustrading Architectural Issues - AP5 Staircase (this NCR) These NCR’s also cover issues raised within CRL-OBS-27320 and CRL-OBS-27792 which all relate to Architectural issues with the balustrades. Cxxx-NCR-002429 - captures missing benchmarks for the PAD balustrades BAL-112 and CRL-OBS-27230 photo 11 also relates to a missing benchmark. Cxxx-NCR-002549 - captures all design related issues for the balustrades including CRL-OBS-27341 on security. This NCR covers - AP5 Staircase: 1. Quality issues with supporting baseplates identified in CRL-OBS-27320 and CRL-OBS-27792 - During installation or transportation of the materials there has been damage done to the exposed finished surface of the baseplates. - The large amount of welding required to hold the base plates together has distorted the finished surface so that there are noticeable bumps/warping. - The gaps between installed baseplates are inconsistent - Termination of not all finished satisfactorily - Some panels not fully adhered to structural baseplate - Finish / polishing of overcladding plates not all finished satisfactorily - Some baseplates appear out of tolerance with visible gaps - Some areas of __ resin poured low and required “topping up” 2. Glass quality issues identified in the attached spreadsheet - Missing Kite Marks - Glass panels of incorrect thickness - Manifestation patterns/provisions incorrect/misaligned - Glazing specification incorrect (2xtoughened panes) not as per WI requirement Note: This design item is addressed under design NCR Cxxx-NCR-002549 3. Installation concerns resulting from design change to 2 toughened glass panes and resin bonded base - Glass MCR not accepted ahead of installation – Address under Cxxx-NCR-002549 for design - Installation quality risk – use of accredited __ installer - Potential for warranty from manufacturer/installer due to reliance on bonded base - Need to ensure a high level of installation checking is completed - __ pour heights not achieved in single pour - Reduced glass embedment depths Note: there are also missing hard/soft body impact test results, these have been raised as part of the quality pack review. Recording as non-conforming to the WI requirements but to be addressed as part of the quality pack.
|  | Cxxx-NCR-002435 | NCR | BTH - hidden recess between entrance portal and canopy glazing |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2020-12-31 | 2020-04-24 08:48 | -251 | 2019-09-26 10:27 | Architectural - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | __ have built to the gated design. The I__ have agreed to Use as Is - __ to reallocate to ADM. It will remain at implementation stage post revenue.
|  | Cxxx-NCR-002444 | NCR | Platform end_Ruggedised phone access LU Human Factors assesment compliance |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2020-09-30 | 2020-10-22 08:40 | 22 | 2019-10-15 13:04 | Architectural - General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The Ruggedised phone door is not as per Works Information as constructed and designed by Cxxx. A LU human factors assessment was carried out on the Platform. See below Observations: Below are some considerations with respect to the current Telephone installation, which contains features that encroach into the area where both hands are to be used (resulting in both of the wrists deviating from a neutral wrist posture): 1. The “European Agency for Health and Safety at Work - Research - Work-related Neck and Upper Limb - Musculoskeletal Disorders (ISBN 92-828-8174-1)” report includes findings that indicate that pain is experienced when there is a wrist deviation of greater than 20 degrees (Hunting et al, 1981). 2. e Health and Safety Executive (HSE) Assessment of Repetitive Tasks (ART) Tool includes the following with respect to wrist posture: - C4 Wrist posture - The wrist is considered to be bent or deviated if an obvious wrist angle can be observed. - Almost straight/in a neutral position (Green / 0 = Low-risk) - Bent or deviated part of the time (Amber / 1 = Medium risk) - Bent or deviated more than half of the time (Red / 2 = High-risk) 3. “The Rules of Work: A Practical Guide to Ergonomics – Second Edition (ISBN-13: 978-1138424647)” states “Provide hand clearance – equally important is having sufficient space for the hands in order to avoid ‘knuckle-buster’ injuries” 4. In numerous different contexts, best practice is to provide 50mm clearance for the hands (e.g. BS EN ISO 2867).
|  | Cxxx-NCR-000567 | NCR | Inconsistant CE Marking stamps on the glass wall panels in the ticket hall |  | Contr | __R | WOO - Woolwich Station (East) |  | 2019-11-29 | 2020-07-02 16:03 | 216 | 2019-08-02 14:38 | Architectural - Glazing | 500 |  | Material | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | CE marking stamps are inconsistent across the system (different stamps and different print out quality) on the glass wall panels in the ticket hall. The marked up elevations attached, show where the 2 different types of marks occur. Out of the 5 elevations, only 2 are either all __ or all __ (Benchmark wall).
|  | Cxxx-NCR-000616 | NCR | Paint Flaking on Louvres - East Box |  | Contr | __R | WOO - Woolwich Station (East) |  | 2020-04-06 | 2020-06-12 09:42 | 67 | 2020-01-07 15:24 | Architectural - Finishes | 500 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Evidence of paint flaking on the External Louvres outside the TVF (901) room in the East box.
|  | Cxxx-NCR-000140 | NCR | Bronze External Cladding at Entrance Gates __-00253 |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2022-09-04 |  | 155 | 2022-02-23 08:17 | Architectural - Finishes | 500 |  | Damaged | Repair | 4 (0.5-3k) | Open | Management Problem - Inadequate supervision | IMPLEMENTATION |  | Bronze cladding to side gates on Weighhouse Street. __ fixings have penetrated the face of the bronze cladding. At gridline L (gate 1) 6 penetrations, and gridline J (gate 6) 9 penetrations. (See attachment for details.) Solution required to remove Tech Screws fixings and make good Bronze panels.
|  | Cxxx-NCR-000169 | NCR | WTH L0 Tech Wall LV Sockets __-00269 |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-12-07 15:41 | 94 | 2022-06-01 14:07 | Electrical - LV Equipment | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The WTH Tech Walls do not have sufficient space to install the __ LV9 110V sockets. See attached sketch (1. Ticket Hall 110V Socket Installation) for details of the dimensional clashes.
|  | Cxxx-NCR-000175 | NCR | ETH LIN-403 Precast Panels Damages __-00253 |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2022-07-30 |  | 191 | 2022-07-16 14:22 | Architectural - Finishes | 500 |  | Damaged | Repair | 4 (0.5-3k) | Open | Design Problem - Not Defined | IMPLEMENTATION |  | Damages to 2 No's precast panels and difference in colour from the adjacent LIN 403 precast panels, as shown in the attached pictures.
|  | Cxxx-NCR-000176 | NCR | WTH LIN 409 Precast skirting misalignment __-00253 |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2022-07-30 |  | 191 | 2022-07-16 14:39 | Architectural - Finishes | 500 |  | Design | Repair | 4 (0.5-3k) | Open | Design Problem - Not Defined | IMPLEMENTATION |  | It was identified that the joints between the LIN 409 precast skirting panels and the tech. wall are not aligned (attached pictures). The area is marked on the Cxxx-SKC-A-DWG-Cxxx-51268 drawing
|  | Cxxx-NCR-000016 | NCR | WO-00297, AIMS Missing EQ Numbers - __ 00229 |  | Contr | COF | CWS - Canary Wharf Station |  | 2022-12-02 | 2022-12-08 11:51 | 6 | 2022-04-20 12:44 | Information Management - Asset Information | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Regarding WO-297, The following items cannot be raised as equipment (EQ) in AIMS due to unknown manufacturer and model. The attachment to this NCR contains the current equipment Information and the asset tags effected by this.
|  | Cxxx-NCR-000019 | NCR | Asset missing label information - __ 00223 |  | Crossrail | XRL | CWS - Canary Wharf Station |  | 2022-12-02 | 2023-01-13 16:03 | 42 | 2022-07-12 10:53 | Information Management - Asset Information | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Canary Wharf asset information team confirmed that Cxxx asset missing label information in the Cxxx-PWK-00197 cannot be labelled due to various issues such as location and access. The team are requesting RfL to accept data as is.
|  | Cxxx-NCR-003591 | NCR | Water Ingress in Sub Platform - Design and Implementation of a Permanent Solution __-00141 |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2023-09-25 |  | -231 | 2021-07-08 14:00 | Civil - Drainage | 500 |  | Incorrect Installation |  |  | Open |  | REVIEW |  | Further to Cxxx-PWK-01889, the Contractor is required to develop and implement a permanent solution to the water ingress in sub-platform level. Solution to be agreed with CRL prior to implementation. Monitoring and temporary mitigation measures (as outlined in Cxxx-PWK-01889 and Cxxx-SKC-B-RGN-B071_WS077-50013) to continue until the permanent solution is satisfactorily implemented.
|  | Cxxx-NCR-003600 | NCR | Gap in Floor Next to Escalator at Platform Level |  | Contr | ATK | PAD - Paddington Station (West) |  | 2021-10-08 | 2022-04-25 14:59 | 199 | 2021-09-24 11:51 | Architectural - Flooring | 5000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | At platform level there is a gap between the edge of the pit of escalator 7 and the cladding to the side of the escalator. The gap at its widest is approximately 20mm wide, as seen on the attached photos. This is not in compliance with the F1 works information.
|  | Cxxx-NCR-003601 | NCR | Platform Roundel Spacing __-00143 |  | Contr | ATK | PAD - Paddington Station (West) |  | 2023-12-31 |  | -328 | 2021-09-24 12:07 | Architectural - Signage | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Open |  | IMPLEMENTATION |  | In response to PMI 1836 the contractor has checked the positions of the roundels at platform level and issued the information as a marked-up pdf file in Cxxx-CCM-08192. The result of this check shows that some of the roundels are too widely spaced and do not comply with the LU requirement. The London Underground Signs Manual Issue 4 requires roundels spacing not to exceed 15 metres apart, but six spaces at Paddington exceed this – 16.9m, 24.42m, 23.24m, 29.4m, 16m, 25m.
|  | Cxxx-NCR-000494 | NCR | Western Ticket Hall - Material Installation Rails (__ Rails) __-00253 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2022-09-04 |  | 155 | 2018-05-03 17:27 | Civil - Civil Engineering General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Open | Material/Preservation Problems - Improper preservation of material after installation | IMPLEMENTATION |  | RS162 material installation rails have surface marks caused during the anodising process. These occur at the ends of each rails where they were clamped during the coating process. This NCR cover the repairs to these marks.
|  | Cxxx-NCR-001038 | NCR | WTH L0 W14 LIN-403 Panel Water Stain - GL 2 - G and J __-00269 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-12-07 15:05 | 94 | 2019-11-14 09:33 | Architectural - General | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | WTH L0 Wall 14 located Grid 2/G-L; 2 x panels Located Grid 2/G have water stains due to leakage from +1 slab above. Photos and mark up clarify specific location. The precast panels were installed prior to completion of the level +1 protection slab and waterproofing. As a result a water path into the station above the precast panels, the water has run down and stained.
|  | Cxxx-NCR-000174 | NCR | ETH Level 0 CMS - Less than 25% spare capacity __-00253 |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-09-04 |  | 155 | 2022-03-08 16:09 | Electrical - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Open | Design Problem - Other | IMPLEMENTATION |  | Please see SAP report attached, marked up drawings and FCD within contract communications to support this NCR. On the ETH Level 0 there is one area (circ area 1/073) in which Cxxx are in breach off the 25% spare capacity requirement. This is highlighted in red on attachment '2 of 6'. Specifically within the L&SP compartments (Observations 9, 10, 12 & 17).
|  | Cxxx-NCR-000176 | NCR | ETH Level -4 CMS - less than 25% spare capacity __-00253 |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-09-04 |  | 155 | 2022-03-11 11:24 | Electrical - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Open | Design Problem - Other | IMPLEMENTATION |  | Please see SAP report attached which identifies areas/sections of CMS (Ladder Rack and/or tray) in which Cxxx are in breach of the 25% spare capacity requirement. These areas are on ETH Level -4 within Switch Rooms LVA 5/668, LVB 5/669, Circ Areas 5/093 and 5/073. The SAP report also gives evidence of no spare capacity issues in Fan Room 5/775.
|  | Cxxx-NCR-000177 | NCR | ETH Level -4 CMS - Limited access and maintanance. __-00253 |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-09-04 |  | 155 | 2022-03-09 13:53 | Electrical - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Open | Design Problem - Other | IMPLEMENTATION |  | 1.Access and maintenance for future works etc are achievable via maintenance windows (unrestricted sections of CMS), rodding points etc. The obstruction (luminaries or unistruts) causes particular sections of CMS to be out of reach whilst using safe means of access equipment. Please refer to observations 5, 14, 17, 18, 19, 20 & 21 within the SAP report attached. For these observations Cxxx would like the opportunity to demonstrate to CRL that access for future cabling is suffice and can be achieved without a change or removal of assets. 2.Severe obstruction to access and maintain CMS routes. The obstruction (ie; luminaries, unistruts, other types of CMS) causes sections of CMS to be completely out of reach whilst using safe means of access equipment. Please refer to observations 15, 16, 22, 23 and 25 within SAP report attached. These observations refer to areas which will require assets to be removed to facilitate access. Please also refer to observations 26, 27, 28 and 29. These observations require Cxxx to propose either utilising existing CMS routes and/or space allocation for additional CMS as a mitigation for not being able to gain access to particular sections. There are no areas of concern identified in relation to 25% spare capacity however, if it so happens that the areas which cannot be accessed due to other disciplines installation (like in access issue No.3), then the proposed mitigation of further CMS will mitigate both A&M and lack of 25% spare capacity.
|  | Cxxx-NCR-000178 | NCR | ETH Level -2 CMS - Limited access and maintenance __-00253 |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-09-04 |  | 155 | 2022-03-15 11:37 | Electrical - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Open | Design Problem - Other | IMPLEMENTATION |  | 1.Access and maintenance for future works etc are achievable via maintenance windows (unrestricted sections of CMS), rodding points etc. The obstruction (luminaries, conduits, etc) causes particular sections of CMS to be out of reach whilst using safe means of access equipment. Please refer to observations 15, 19, 21, 22, 23 & 35 within the SAP report attached. For these observations Cxxx would like the opportunity to demonstrate to CRL that access for future cabling is suffice and can be achieved without a change or removal of assets. 2.Obstruction to access and maintain CMS routes. The obstruction (ie; luminaries, unistruts, other types of CMS) causes sections of CMS to be out of reach whilst using safe means of access equipment. Please refer to observations 4, 5, 17, 18, 20, 26, 27, 28, 29, 31 & 32 within SAP report attached. These observations refer to areas which will require assets to be removed to facilitate access. 3. Please also refer to observation 25. This observation requires Cxxx to propose either utilising existing CMS routes and/or space allocation for additional CMS as a mitigation for not being able to gain access to particular sections. If it so happens that the area which cannot be accessed due to other installations (like in access issue No.25), then the proposed mitigation of further CMS will mitigate both A&M and lack of 25% spare capacity. The attached SAP report also captures areas in which there is no access and maintenance issue but have been recorded to give assurance that a comprehensive check has been undertaken (observations 1-3 , 6-14, 16, 24, 30, 33 & 34).
|  | Cxxx-NCR-000180 | NCR | ETH Level -3 CMS - less than 25% spare capacity __-00253 |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-07-07 |  | 214 | 2022-06-23 10:48 | Electrical - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Open | Design Problem - Other | IMPLEMENTATION |  | 25% Spare capacity has been maintained in the CMS shown in attached SAP report under observations 1, 2, 3, 4, 5, 6, 7, 8, 9 & 10
|  | Cxxx-NCR-000181 | NCR | ETH Level-3 CMS - limited access and maintenance __-00253 |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-09-04 |  | 155 | 2022-03-07 11:53 | Electrical - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Open | Design Problem - Other | IMPLEMENTATION |  | 1.Access and maintenance for future works etc are achievable via maintenance windows (unrestricted sections of CMS), rodding points etc. The obstruction (luminaries or unistruts) causes particular sections of CMS to be out of reach whilst using safe means of access equipment 2.Severe obstruction to access and maintain CMS routes. The obstruction (ie: other CMS & Bracketry as per observations 6,7,8,9,11&15 within the SAP report attached) causes sections of CMS to be completely out of reach whilst using safe means of access equipment A SAP report has been produced and attached in conjunction with marked up CMS layout drawings to identify the areas which require mitigation for adequate A & M. There are no areas of concern identified in relation to 25% spare capacity however, if it so happens that the areas which cannot be accessed due to other CMS and Bracketry (observations 6,7,8,9,11&15 ), then the proposed mitigation of further CMS will mitigate both A&M and lack of 25% spare capacity (as per proposed answer number 2).
|  | Cxxx-NCR-000209 | NCR | ETH Level -2 CMS -25% Spare Capacity __-00253 |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-09-04 |  | 155 | 2022-03-16 11:12 | Electrical - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Open | Design Problem - Other | IMPLEMENTATION |  | Please see SAP report attached noting observation 15 in which Cxxx are in breach of the 25% spare capacity requirement. The SAP report also gives evidence of no spare capacity issues through the majority of the floor identified in observations 1-14.
|  | Cxxx-NCR-000218 | NCR | ETH Level 0.5 CMS - Less than 25% spare capacity __-00253 |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-09-04 |  | 155 | 2022-03-22 13:56 | Electrical - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Open | Design Problem - Other | IMPLEMENTATION |  | Please see SAP report attached which identifies a particular section of CMS (Tray) in which Cxxx are in breach of the 25% spare capacity requirement. This area is on ETH Level +0.5 within corridor A/073. The SAP report also gives evidence of no spare capacity issues in all other areas (captured in observations 1-14 and 16-18).
|  | Cxxx-NCR-000219 | NCR | E1WTH Level -3 CMS Less than 25% Spare Capacity __-00253 |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-09-04 |  | 155 | 2022-03-23 14:46 | Electrical - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Open | Design Problem - Other | IMPLEMENTATION |  | Please see SAP report attached which identifies an section of CMS (trunking) in which Cxxx are in breach of the 25% spare capacity requirement. The trunking does not have 25% spare capacity for the emergency compartment only. This is only apparent in lobby 4/085 as this is where the circuits are fed from the floor below. Once the trunking continues throughout Level -3, 25% spare capacity is achieved as the SAP report states. The SAP report also gives evidence of no spare capacity issues in all other areas (observations 2-5) and the report summarised in observation no.6..
|  | Cxxx-NCR-000220 | NCR | WTH Level -3 CMS Limited access and Maintenance __-00253 |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-09-04 |  | 155 | 2022-03-23 15:12 | Electrical - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Open | Design Problem - Other | IMPLEMENTATION |  | 1. Access to CMS for future cabling and/or maintenance is currently possible. However, upon completion of the suspended ceiling, access will be restricted via a MEWP or platform as the ceiling would impede the handrail of the MEWP/tower elevating any further and so limiting the height at which a maintainer could reach. Please refer to observations 2 and 6 within the SAP report attached. 2. Severe obstruction to access and maintain CMS routes. The obstruction (ie; ceiling trims, unistruts, other types of CMS) causes sections of CMS to be out of reach whilst using safe means of access equipment. Please refer to observations 1, 3 & 9 within SAP report attached. The SAP report also captures areas of compliance in which no action is needed (observations 4, 5 & 7). Observation 8 refers to the requirement to remove the Architectural finish however, there are no access constraints upon this being facilitated.
|  | Cxxx-NCR-000225 | NCR | WTH X/799 & X/798 -Limited Access & Maintenance __-00253 |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-09-04 |  | 155 | 2022-03-29 12:08 | Electrical - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Open | Design Problem - Other | IMPLEMENTATION |  | Although there are no instances of constrained access typically caused by lack of space or congested areas, it has been noted that in particular areas of X/799 & X/798 there are sections of CMS which would be difficult to access using standard ‘off the shelf’ access equipment due to narrow floor area and/or stairs. These instances are identified within the 2 SAP reports attached. The SAP reports also capture all other areas of compliance in which no action is needed.
|  | Cxxx-NCR-000250 | NCR | ETH Riser 927 and 683 Less than 25% spare capacity. __-00253 |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-09-04 |  | 155 | 2022-04-19 09:38 | Electrical - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Open | Design Problem - Other | IMPLEMENTATION |  | During a site inspection of ETH Riser 927 and 683 it was evident that any future cabling would be constrained on particular levels due to lack of spare capacity. A survey has been undertaken by Jake Parsons (CRL Electrical Package Manager) and __ (CRL Lead Field Assurance Engineer) and the below narratives give support to the attached SAP report. Riser 927 • Level+0.5 – 60% spare capacity on the left hand wall containment (allocated to UPS) and 30% spare capacity on the back wall containment (allocated to LV). Right hand wall has no containment installed however, space available for further containment should there be a requirement. Level deemed suffice in terms of spare capacity • Level 0 - 30% spare capacity on the left hand wall containment (allocated to UPS) and 30% spare capacity on the back wall containment (allocated to LV). Right hand wall has no containment installed however, space available for further containment should there be a requirement. Level deemed suffice in terms of spare capacity • Level -1 - 10% spare capacity left hand wall containment (allocated to UPS) and 40% spare capacity on back wall containment (allocated to LV). Right hand wall has no containment installed however, space available for further containment should there be a requirement. Level deemed suffice in terms of spare capacity • Level -2 - 10% spare capacity left hand wall containment (allocated to UPS) and 0% spare capacity on back wall containment (allocated to LV). Right hand wall has 40% spare capacity (allocated to LV). Both the right hand wall and back wall are both allocated to LV and has an estimate of 15-20% spare capacity combined • Level -3 - 0% spare capacity on back wall containment (allocated to LV). Back wall also now contains brackets to support UPS cables which transition between Level -2 and Level -3 (left wall to back wall). There is 25% spare capacity for future UPS cabling . Right hand wall has 15% spare capacity (allocated to LV). Both the right hand wall and back wall are both allocated to LV and has an estimate of 5% spare capacity combined • Level -4 – This is the bottom of Riser 927 and houses the distribution boards. There is adequate spare capacity in all types of CMS on this level Riser 683 • Level +0.5 – 25% spare capacity available and further space available should further CMS/cabling be required • Level 0 – 5% spare capacity on the left hand wall containment (allocated to UPS). Space available on the right hand wall for further cabling/trunking should there be a requirement • Level -1 - 5% spare capacity on the left hand wall containment (allocated to UPS). Back wall has tray for BMS LV cabling with adequate spare capacity. Space available on the back wall and right hand wall for further cabling/trunking should there be a requirement • Level -2 – 80% spare capacity on the left hand wall containment (allocated to UPS). Back wall tray allocated to BMS LV cabling has adequate spare capacity
|  | Cxxx-NCR-000252 | NCR | ETH Riser 927 and 683 CMS Access & Maintenance Issues __-00253 |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-09-04 |  | 155 | 2022-04-20 12:39 | Consents - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Open | Design Problem - Other | IMPLEMENTATION |  | During a site inspection of ETH Riser 927 and 683 it was evident that access to 2 particular sections within Riser 927 are constrained and may prove to be difficult for the maintainer to gain access for cabling activities. A survey has been undertaken by Jake Parsons (CRL Electrical Package Manager) and __ (CRL Lead Field Assurance Engineer) and the below narrative describes the constraints and supports the attachments. 1) ETH Riser 927 Level -3 (4/927) - There is a 300mm LVE tray which penetrates into riser 927 at high level (3085mm above the riser grating) and immediately turns 90 degrees. There are some services that would restrict access to the tray from beneath. The same tray is an estimated 1800mm below the riser grating if you were to stand on level -2 and so access from above looks impracticable too. For straight lengths of CMS (ladder rack/tray/trunking) lack of access can be mitigated simply by proving that cables can easily be installed/rodded however, the 90 degree bend would need to be accessible to dress and secure any future cabling 2) ETH Riser 927 Level -4 (5/927) – This is the lowest point of the riser and houses 4no Distribution Boards and an earth bar. The attached SAP report includes 2 photos highlighting the congestion at high level which will impact accessibility to both the trunking and tray (observations 4 & 5)
|  | Cxxx-NCR-000258 | NCR | WTH Level -4 CMS Limited access and Maintenance __-00253 |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-09-04 |  | 155 | 2022-04-27 12:24 | Electrical - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Open | Design Problem - Other | IMPLEMENTATION |  | 1. Access and maintenance for future works etc are achievable via maintenance windows (unrestricted sections of CMS), rodding points etc. The obstruction (luminaries or unistruts) causes particular sections of CMS to be out of reach whilst using safe means of access equipment. Please refer to observations 6, 7, 8, 9, 11 & 12 within the SAP report 480 and observation 1 & 2 in SAP report 481 attached. For these observations Cxxx would like the opportunity to demonstrate to CRL that access for future cabling is suffice and can be achieved without a change or removal of assets. 2. Severe obstruction to access and maintain CMS routes. The obstruction (ie; luminaries, unistruts, other types of CMS) causes sections of CMS to be completely out of reach whilst using safe means of access equipment. Please refer to observation 3 within SAP report 481 attached 3. Observations 4 & 5 identify that primary CMS has been encapsulated within fire rated boarding in the vicinity of lift lobby 8 and therefore not accessible on an immediate basis *Note – Observations 1, 2, 10 & 13 – 30 in SAP report 480 confirm no other access issues
|  | Cxxx-NCR-000260 | NCR | WTH Level -4 CMS Less than 25% Spare Capacity __-00253 |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-09-04 |  | 155 | 2022-04-27 12:38 | Electrical - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Open | Design Problem - Other | IMPLEMENTATION |  | There is a section of ladder rack CMS installed in WTH Level -4 5/667 in which has a high number of SWA cables spread across the width thus posing difficulty in the future should further cables need to be installed on this section. This defect is identified within SAP 479 observation 24.
|  | Cxxx-NCR-000261 | NCR | ETH - Limited Access and maintenance Risers 913, 912, 919 & 920 __-00253 |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-09-04 |  | 155 | 2022-05-05 13:16 | Electrical - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Open | Design Problem - Other | IMPLEMENTATION |  | Identified in observations 2, 6, 7 & 9 there are sections of CMS (both tray and trunking) with restricted access that may prove difficult for the maintainer to install and/or dress future cabling. This is due to multiple CMS and bracketry installed in close proximity
|  | Cxxx-NCR-000262 | NCR | ETH Risers 913, 912, 919 & 920 CMS - Less than 25% spare capacity. __-00253 |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-09-04 |  | 155 | 2022-05-05 11:34 | Electrical - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Open | Design Problem - Other | IMPLEMENTATION |  | Riser 912 (spans between level -5 and level -3) • Level -4 (LV B) - As seen in observations 6 & 7 the manner in which the LV A SWAs have been dressed/supported on the ladder rack would constrain any future cabling by the maintainer. There is approximately 20mm-30mm spacings between each cable and so no further cables can be installed • Level -4 (Radio) – As seen in observation 8 the manner in which the Radio cables have been dressed on the tray would constrain any future cabling by the maintainer. There is approximately 15mm-20mm spacings between each cable and so no further cables can be installed SR 3/913 • No issues Riser 919 (spans between level -5 and level -4) • Level -4 – As seen in observations 9 & 10 the manner in which the LV B SWAs have been dressed/supported on the 2no. ladder racks would constrain any future cabling by the maintainer. There is approximately 20mm-30mm spacings between each cable and so no further cables can be installed. This level also has an additional ladder rack for UPS cables on the LHS which does not have any spare capacity for future cabling and have minimal spacing in-between each one Riser 920 (spans between level -4 and level -2) • Level -2 – As seen in observation 22 the manner in which the LV B SWAs have been dressed/supported on the ladder rack would constrain any future cabling by the maintainer. There is approximately 20mm-30mm spacings between each cable and so no further cables can be installed • Level -3 – As seen in observations 16 & 17 the manner in which the LV B SWAs have been dressed/supported on the ladder rack would constrain any future cabling by the maintainer. There is approximately 20mm-30mm spacings between each cable and so no further cables can be installed
|  | Cxxx-NCR-000266 | NCR | WTH Risers 680 and 681- CMS Less than 25% spare capacity __-00253 |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-09-04 |  | 155 | 2022-05-10 12:11 | Consents - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Open | Discipline/Workmanship - Other | IMPLEMENTATION |  | 1. Level -4 (5/680) - As seen in observations 1 & 2 the manner in which the LV SWAs have been dressed/supported directly by __ framework would constrain any future cabling by the maintainer. There is approximately 15mm-20mm spacings between each cable and so only a further 1-2 cables could be installed by the maintainer should they be required 2. Level -4 (5/681) - As seen in observation 6 the manner in which the LV SWAs have been dressed/supported directly by __ framework would constrain any future cabling by the maintainer. There is approximately 20mm-30mm spacings between each cable and so no further cables can be installed 3. Level -2 (3/680) – As seen in observation 8, 9 & 10 the manner in which the LV SWAs have been dressed on the tray would constrain any future cabling by the maintainer. There is approximately 15mm-30mm spacings between each cable and so only a further 1-2 cables could be installed by the maintainer should they be required 4. Level -1 (2/680) – As seen in observation 15 the manner in which the LV SWAs have been dressed/supported on the ladder rack would constrain any future cabling by the maintainer. There is approximately 15mm-20mm spacings between each cable and so only a further 1-2 cables could be installed by the maintainer should they be required 5. Level -1 (2/681) – As seen in observation 21 the manner in which the LV SWAs have been dressed/supported on the ladder rack would constrain any future cabling by the maintainer. There is approximately 15mm-20mm spacings between each cable and so only a further 1-2 cables could be installed by the maintainer should they be required 6. Further observations 8, 12 &18 give visibility of sections of CMS which currently do not conform with the requirement to have 25% SC however, once the temporary cables are removed there will be adequate available SC
|  | Cxxx-NCR-000267 | NCR | WTH Risers 680 and 681- CMS Limited Access & Maintenance __-00253 |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-09-04 |  | 155 | 2022-05-09 11:40 | Electrical - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Open | Design Problem - Other | IMPLEMENTATION |  | 1. Riser 680 - Between level -4 (5/680) and level -2 (3/680) there is a large distance between floors and therefore would be extremely difficult for the Maintainer to gain access from Level -4 to the highest section of CMS/cabling. This can be seen in observation 1 and 3 within the attached SAP report 2. Riser 681 - Between level -4 (5/681) and level -2 (3/681) there is a large distance between floors and therefore would be extremely difficult for the Maintainer to gain access from Level -4 to the highest section of CMS/cabling. This can be seen in observation 2 and 5 within the attached SAP report 3. Observation 4 refers to a straight run of CMS (looking up from 3/680) which again poses a similar challenge to those above however, the difference being that this run could be cabled the full length with ease but dressing of the cables would be restricted using ordinary mobile access equipment 4. Observation 6 highlights inadequate access to a particular tray however, the lower tray can be utilised for future cabling should it be required
|  | Cxxx-NCR-000274 | NCR | ETH -5 CMS Less than 25% Spare Capacity __-00253 |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-09-04 |  | 155 | 2022-05-25 11:54 | Electrical - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Open | Design Problem - Other | IMPLEMENTATION |  | 25% Spare capacity has been maintained in the CMS shown in attached SAP report under observations 1, 2, 3, 4, 5, 6, 8, 9, 10, 11, 12, 13, 14, 18 & 19 No spare capacity as shown in observations 7, 17 & 20 Areas unaccusable in this location are shown under observation 15 CMS that will have 25% spare capacity if the cables are re-dressed are covered under observation 16
|  | Cxxx-NCR-000275 | NCR | ETH Level-5 CMS Limited Access & Maintenance __-00253 |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-09-04 |  | 155 | 2022-05-17 14:45 | Electrical - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Open | Design Problem - Other | IMPLEMENTATION |  | 1.Out of reach access to sections of CMS. The restrictions are identified in the attached SAP report under observations 1, 14, 15, 16, 17, 20, 21, 22, 23, 25, 29 & 39 along with locations shown on the attached drawing. 2.Access is limited but still maintainable in SAP observations 2 along with locations shown on the attached drawing 3.Access and maintained for future works etc using rodding points or carried out within maintained windows. Removal of the luminaire shown in observations 24, 28, 31, 32 36 & 37 to gain access are shown in the SAP and on the attached drawings. 4.The SAP report also provides assurance that all other areas have adequate access to maintain and/ or install further services at a later date (Observations 3, 4, 5, 6, 7, 8, 9, 10, 11, 12, 13, 18, 19, 26, 27, 30, 33, 34, 35, 38)
|  | Cxxx-NCR-000277 | NCR | WTH Level -2 CMS Limited access & Maintenance __-00253 |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-09-04 |  | 155 | 2022-05-16 14:52 | Electrical - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Open | Design Problem - Other | IMPLEMENTATION |  | 1.Access and maintained for future works etc using rodding points or carried out within maintained windows. Removal of the luminaire shown in observations 5, 6, 11, 12, 14 & 15 to gain access are shown in the SAP and on the attached drawings. 2.No access to CMS due to ductwork as shown in observation 16, however access to CMS in observation can be maintained ether side of the ductwork as shown in attached SAP report under observation 4, 13 & 18 along with attached drawing. 3.Out of reach access to sections of CMS. The restrictions are identified in the attached SAP report under observations 7, 9 & 17 along with locations shown on the attached drawing. 4.Access is limited but still maintainable in SAP observations 3 & 8 along with locations shown on the attached drawing. 5.The SAP report also provides assurance that all other areas have adequate access to maintain and/ or install further services at a later date (Observations 1, 2 & 10)
|  | Cxxx-NCR-000278 | NCR | WTH Level - 2 CMS Less than 25% Spare capacity __-00253 |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-09-04 |  | 155 | 2022-05-17 10:05 | Electrical - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Open | Design Problem - Other | IMPLEMENTATION |  | NCR Details Please see SAP report attached which identifies a section of CMS (Tray) in which only 15% spare capacity is available as shown on observations 6 & 7. Observations 1-5 & 7-11 shows there are no other issues in this area.
|  | Cxxx-NCR-000289 | NCR | WTH Level -5 CMS Less than 25% spare capacity __-00253 |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-09-04 |  | 155 | 2022-05-30 12:38 | Electrical - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Open | Design Problem - Other | IMPLEMENTATION |  | 25% Spare capacity has been maintained in the CMS shown in attached SAP report under observations 1, 2, 3, 4, 5, 6, 7, 8, 9, 13, 15, 16 & 17 No spare capacity as shown in observations 10, 11, 14 Observation 12 only has one of the trays located to the left side
|  | Cxxx-NCR-000293 | NCR | WTH -5 CMS Limited Access & Maintenance __-00269 |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-09-04 |  | 155 | 2022-05-30 12:39 | Consents - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Open | Design Problem - Other | IMPLEMENTATION |  | 1. Out of reach access to sections of CMS. The restrictions are identified in the attached SAP report under observations 1, 5, 6, 18, 21, 22, 23, 24, 26, 27 & 28 and observations 1, 2, 3, 4,5 ,6 & 7 as shown in SAP report titled “-5 SAP Additional Points” 2. Access and maintained for future works etc using rodding points or carried out within maintained windows. Removal of the luminaire shown in observations 2, 3, 4, 7 & 20 3. Access and maintained for future works etc using rodding points or carried out within maintained windows. Removal of ceiling shown in observations 13, 14 & 15 4. The SAP report also provides assurance that all other areas have adequate access to maintain and/ or install further services at a later date (Observations 8, 9, 10, 11, 12, 16, 17, 19, 25, 29, 30, 31, 32, 33, 34, 35)
|  | Cxxx-NCR-000295 | NCR | WTH Level -1 CMS Less than 25% spare capacity __-00253 |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-09-04 |  | 155 | 2022-06-08 14:12 | Consents - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Open | Design Problem - Other | IMPLEMENTATION |  | 1. 25% Spare capacity has been maintained in the CMS shown in attached SAP report under observations 1, 2, 3, 4, 5, 6, 7 & 8 2. Areas unaccusable in this location are shown under observation 9, 10, 11 & 12
|  | Cxxx-NCR-000296 | NCR | WTH -1 CMS Limited Access & Maintenance __-00253 |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-09-04 |  | 155 | 2022-06-08 13:33 | Electrical - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Open | Design Problem - Other | IMPLEMENTATION |  | 1. Out of reach access to sections of CMS. The restrictions are identified in the attached SAP report under observations 1, 2, 7 8, 10, 11, 12, 13, 17, 20 & 22 and observations 1, 2,3 &4 in attachment "WTH -1 SAP report 2" 2. Access and maintained for future works etc using rodding points or carried out within maintained windows. Removal of ceiling shown in observation 14 3. The SAP report also provides assurance that all other areas have adequate access to maintain and/ or install further services at a later date (Observations 3, 4, 5, 6, 9, 15, 16, 18, 19, 21, 23)
|  | Cxxx-NCR-000303 | NCR | P&T - CH2 & CH3 - Chipped Glazing Panels __-00268 |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-09-04 |  | 155 | 2022-06-06 15:21 | Architectural - Glazing | 500 |  | Damaged | Rework | 4 (0.5-3k) | Open |  | INITIATE |  | Glazing panel has been chipped at the rear and is visible from the front. Concerns are both aesthetic and structural - as to the long term stability of the glazing panel.
|  | Cxxx-NCR-000312 | NCR | DB's Installed At Low Level - ETH & WTH (Elec VIRS 63) __-00268 |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2022-09-04 |  | 155 | 2022-06-10 11:36 | Electrical - Power Distribution | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Open | Design Problem - Other | IMPLEMENTATION |  | Distribution Boards have been installed at low level within the rooms below, see attached photos. These DB's need to be raised 1m from the ground. Location: WTH 2/907 and ETH 3/772 Electrical VIRS item 63
|  | Cxxx-NCR-000323 | NCR | Fire Damper GE-W-FD132 blocked by false ceiling panel and services 2-318 - WTH Gen Ex. IRN-M-50032 __-0268 |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2022-07-12 10:09 |  | 209 | 2022-06-28 10:09 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Design |  |  | Open |  | PROPOSE ACTION |  | Fire Damper FD 132 blocked by false ceiling panel and services in LU Locker room Male 2-318 see Drawing: Cxxx-XRL-M-DDA-Cxxx-11112_P01
|  | Cxxx-NCR-000335 | NCR | ETH - Minor Dali Changes & Redlines __-00269 |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-07-11 |  | 210 | 2022-06-27 14:40 | Electrical - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Open | Discipline/Workmanship - Other | IMPLEMENTATION |  | This NCR needs to cover all the minor changes made to Dali orientation/minor layout changes. The changes that will be picked up do not require any close out paperwork (QA Checksheets or Test sheets) but will require updated redlines for each level.
|  | Cxxx-NCR-000336 | NCR | WTH - Minor Dali Changes & Red Line Drawings __-00269 |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-07-11 |  | 210 | 2022-06-27 14:39 | Electrical - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Open | Discipline/Workmanship - Other | IMPLEMENTATION |  | This NCR needs to cover all the minor changes made to Dali orientation/minor layout changes. The changes that will be picked up do not require any close out paperwork (QA Checksheets or Test sheets) but will require updated redlines for each level.
|  | Cxxx-NCR-000356 | NCR | Generic VIRS- Approved as built MCC schematics need to be fitted in any room that an MCC panel is installed. __-00269 |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2022-07-28 11:34 |  | 193 | 2022-07-14 11:34 | Electrical - Power Distribution | 500 |  | Documentation and Records |  |  | Open |  | PROPOSE ACTION |  | Approved as built MCC schematics need to be fitted in any room that an MCC panel is installed.
|  | Cxxx-NCR-000378 | NCR | Lack of Access into Sumps __-00268 |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2022-09-01 10:58 |  | 158 | 2022-08-18 10:58 | Mechanical - Public Health Engineering | 500 |  | Design |  |  | Open |  | PROPOSE ACTION |  | There are no permanent access ladders for entry into the following sump pits: WTH -6/SP003 WTH -6/SP005 ETH -6/SP003 Currently only temporary access via scaffold/scaffold ladder is available. A permanent access arrangement (ie.CAT ladder) is required for sump pump inspections and maintenance.
|  | Cxxx-NCR-000400 | NCR | BOS - AP1 GFRC Panel Finger Traps (__-00292) |  | Contr | COF | BOS - Bond Street Station (West) |  | 2023-06-30 |  | -144 | 2022-11-09 15:54 | Architectural - Walls | 500 |  | Design | Repair | 4 (0.5-3k) | Open | Design Problem - Not Defined | IMPLEMENTATION |  | CRL's Architect has highlighted finger traps between joints of the AP1 GFRC cladding panels
|  | Cxxx-NCR-000401 | NCR | Fire detection additions and ammendments (__-00292) |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2023-02-16 09:43 |  | -10 | 2022-11-18 09:43 | Fire - Detection | 500 |  | Design |  |  | Open |  | REVIEW |  | Additional Multi detectors required in the 3x locations and relocation on 1 multi detector where this is now unmaintainable location 1 1/MA1 inside the electrical cupboard location 2 5/411 in a void area at the back of the room location 3 3/681 Electrical riser relocation 1 5/777 Pipe and laggin installed below the detector- Detector to be relocated adjacent to the Pipework
|  | Cxxx-NCR-000402 | NCR | Faulty Fire Dampers LC-W-FD054 (__-00292) |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2023-06-30 |  | -144 | 2022-11-24 15:52 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Damaged |  |  | Open |  | PROPOSE ACTION |  | During damper drop testing Fire dampers it was discovered that LC-W-FD054 in room 5/776 has been disconnected due to electrical fault. A new Actuator is required.
|  | Cxxx-NCR-000006 | NCR | MCC Schematics not Displayed in Live Plant Rooms __-00269 |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2022-09-04 | 2023-01-25 11:00 | 143 | 2022-02-15 14:29 | Electrical - General | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The below MCC panels have been live for a long period of time without displaying the required schematics/signage within the plant rooms. Refer to CRL1-CEC-00654 where this requirement was instructed. MCC-W-06 MCC-W-05 MCC-E-06 MCC-E-05
|  | Cxxx-NCR-000015 | NCR | Damage to MCC-W-04 __-00269 |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2022-09-04 |  | 155 | 2022-05-03 10:15 | Mechanical - Mechanical Engineering General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Open | Management Problem - Inadequate supervision | IMPLEMENTATION |  | Control panel 001 L7864-MCC-W-04 was found to have substantial damage to all panels as well as lagging tape covering several areas
|  | Cxxx-NCR-000009 | NCR | WTH 3/778 Remedial Works - Over-cladding & Identification Label (__-00292) |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2023-06-30 |  | -144 | 2022-11-15 14:24 | Mechanical - Public Health Engineering | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Open |  | IMPLEMENTATION |  | "1. All low level domestic pipework in this room is to be cladded for protection. 2. All pipework is to be fitted with identification label. "
|  | Cxxx-NCR-000012 | NCR | WTH duckwork thermal insulation incomplete (__-00292) |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2023-06-30 |  | -144 | 2022-11-13 17:01 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Incomplete Works |  |  | Open |  | INITIATE |  | Sections of ductwork thermal insulation is incomplete or damaged and need completing and labelling (with service identification labels). The rooms are: 1. 5/777 Insulation needs completing (square patch of 400mmx400mm insulation missing on duct by the back of the MCC-W-04). 2. 6/777 Insulation missing 3meter length but this duct can stay as is - 'use-as-is' - no need to insulate this now. 3. WTH 2/907 - CCU lagging badly applied and now damaged - requires repairs (photos attached to EOWL CRL-OBS-36392)
|  | Cxxx-NCR-000014 | NCR | Aluminium cladding incomplete - for thermal insulation on ductwork, CHW pipework, domestic pipework (__-00292) |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2023-06-30 |  | -144 | 2022-11-13 17:31 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Incomplete Works |  |  | Open |  | REVIEW |  | Aluminium cladding incomplete - for thermal insulation on ductwork, CHW pipework, domestic pipework. The Thermal Insulation specification is part of the __ works information. It includes Aluminium Cladding – Page 6 Clause JY50.1311 Cxxx-SKC-M-RSP-Cxxx-50056 4.0 Cxxx MEP Fit-Out Specification Section JY50 - Thermal Insulation The expectation is that all thermal insulation applied by __ to ductwork, CHW pipework, Domestic pipework, and Fire Main pipework, in risers, plant rooms, corridors, bin stores, cleaning stores, circulation areas and BOH accommodation etc that could be damaged from buckets, tool boxes, ladders, MEWPS and maintenance staff climbing over low level services to get to other services would be cladded up to height of 2.5 meters. CRL also expected the cladding applied to pipework in Local cooling rooms. These rooms fall under plant room and risers.
|  | Cxxx-NCR-000015 | NCR | Incomplete works - __ Remaining Asset Labelling/Issues (__-00292) |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2023-06-30 |  | -144 | 2022-11-13 18:59 | Information Management - Asset Information | 500 |  | Incomplete Works |  |  | Open |  | PROPOSE ACTION |  | The Crossrail asset labelling team has identified asset labels that are yet to be installed, or corrected, that was __ scope. please see attached email for details of asset labels considered outstanding works '__ Remaining Asset Labelling Issues for NCR.msg'.
|  | Cxxx-NCR-000019 | NCR | Domestic Cold Water Tanks ETH & WTH (__-00292) |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2023-06-30 |  | -144 | 2022-11-15 15:30 | Mechanical - Public Health Engineering | 500 |  | Incomplete Works |  |  | Open |  | REVIEW |  | ETH Non-potable Water Tank: 1. Bacnet module is to be labelled WTH Potable Water Tank: 1. Bacnet module is to be labelled 2. The tank lid clips are to be fixed/secured. 3. The keraflo float valve is to be set lower in a such a way that the high level sensor is not triggered before the water shuts off. At the moment, the BMS is sending daily nuisance alarms as a result of this issue. 4. All exposed holes in tank are to be plugged.
|  | Cxxx-NCR-000021 | NCR | WTH 2/084 Drainage Pipework (__-00292) |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2023-06-30 |  | -144 | 2022-11-15 17:06 | Mechanical - Public Health Engineering | 500 |  | Incomplete Works |  |  | Open |  | PROPOSE ACTION |  | Remove redundant gravity drainage pipework and cap end, install is not currently as per design.
|  | Cxxx-NCR-000022 | NCR | WTH Chilled water pipework alterations - repair leaks, remove redundant sections (__-00292) |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2023-06-30 |  | -144 | 2022-11-16 12:52 | Mechanical - Piping | 500 |  | Incorrect Installation |  |  | Open |  | PROPOSE ACTION |  | The WTH chilled water pipework flushing connections require removal. Take these off and provide a cap at the largest diameter isolation valve. See attached pictures 'WTH room flushing pipework to be removed and capped at isolation valves.msg'. The WTH chilled water dosing pot bleed valve is leaking when CHW is directed through the dosing pot. Seal the thread, which is where is appears to be leaking from. See attached pictures 'WTH chiller room dosing pot bleed valve leaking thread needs PTFE tape applied.msg'.
|  | Cxxx-NCR-000023 | NCR | WTH 2/402 - Bin Store - Cladding and redundant __ (__-00292) |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2023-06-30 |  | -144 | 2022-11-18 13:33 | Mechanical - Public Health Engineering | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Open |  | IMPLEMENTATION |  | 1. Low level domestic pipework is to be cladded for protection. 2. Remove redundant __ glands in room.
|  | Cxxx-NCR-000024 | NCR | WTH 4/083 - Incomplete Insulation (__-00292) |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2023-06-30 |  | -144 | 2022-11-18 13:44 | Mechanical - Public Health Engineering | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Open |  | IMPLEMENTATION |  | Incomplete insulation on the domestic cold water pipe in WTH 4/083.
|  | Cxxx-NCR-000025 | NCR | WTH 4/407 - Incomplete insulation& Pipework Identification labels (__-00292) |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2023-06-30 |  | -144 | 2022-11-18 13:57 | Mechanical - Public Health Engineering | 500 |  | Incomplete Works |  |  | Open |  | PROPOSE ACTION |  | Complete Aluminium cladding on domestic pipework and apply identification labels to drainage pipework in 4/407.
|  | Cxxx-NCR-000027 | NCR | ETH Faulty Water Conditioner Controller (__-00292) |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2023-06-30 |  | -144 | 2022-11-21 16:32 | Mechanical - Hot & Cold Water Supplies | 500 |  | Equipment Breakdown | Repair | 4 (0.5-3k) | Open |  | ENGINEERING ROUTING |  | The Powermag control box for ETH water conditioner is faulty. When energised the internal PCB started smoking/sparking and had to be isolated.
|  | Cxxx-NCR-000028 | NCR | Hydrocarbon Sensor Cleaning (__-00292) |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2023-06-30 |  | -144 | 2022-12-02 17:19 | Mechanical - Pumps | 500 |  | Supervision/Management |  |  | Open |  | REVIEW |  | The hydrocarbon sensor installed within -5/SP001 detected the presence of hydrocarbons, causing the pumps to become inhibited. Investigation was carried out by taking water samples for laboratory analysis: 1) The initial samples taken from -5/SP001 at the time of the first hydrocarbon alarm were all within acceptable limits, except a slightly high trace of mercury was identified which may have initially set off the sensor. 2) A second round of samples were taken from all sumps which feed into -5/SP001. No hydrocarbons or high mercury levels were detected. 3) A third round of samples taken from -5/SP001. No hydrocarbons or high mercury levels were detected. Multiple attempts to re-set the sensor have proved unsuccessful, with the system remaining in alarm even after the on-site testing (using hydrocarbon test strips) and off-site testing (above samples sent for laboratory analysis) have not detected hydrocarbons within the sampled water. This is therefore believed to be caused by residual oil contamination on the TRM-CC-35 sensor and the sensor has been temporarily disconnected to enable normal pump operation.
|  | Cxxx-NCR-000002 | NCR | Damages caused to WTH External Bronze cladding __-00269 |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2022-09-04 |  | 155 | 2021-11-16 17:48 | Architectural - General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Open | Supervision - Insufficient supervision | IMPLEMENTATION |  | The New employer raises this NCR to record the damages caused on 2 separate occasions in 2 locations. Both incidents were caused by __ install operatives and witnessed by CRL's Supervisor (__) and __'s Supervisor. The first incident happened 11/9/2021 and the second on the 13/9/2021. The New Employer notifies his concerns over the amount of potentially corrosive cements and grouting compound's that have been left by Subcontractor covering the Bronze surface of finished cladding elements.
|  | Cxxx-NCR-001919 | NCR | GFRC - Acoustic Panel Boroscope Position __-00139 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2023-12-31 | 2022-12-20 09:50 | -376 | 2017-09-19 14:44 | Architectural - General | 2500 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | Boroscope holes have been installed to various panels site wide in the wrong location.
|  | Cxxx-NCR-002176 | NCR | MTH - Ground Floor Level - Water/weather Proofing __-00139 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2023-12-31 | 2022-12-20 11:16 | -376 | 2020-07-09 14:02 | Architectural - Roofing & Exterior Treatment | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | CRL-OBS-26107 - __e During a Quality Surveillance site walk we observed the installation of the glazed rain screen cladding for the Moorgate Ticket Hall. The façade design is made up of number of components or systems each with a differing performance requirement: EWS-115, EWS-220 and EWS -910. The water proofing behind the cladding has not been installed using a single water proofing system – sheet membrane and liquid applied systems have both been installed. In some areas there is no evidence of waterproofing being in place (around Bostwick Gate floor/jamb and head details) and how this has been coordinated with adjacent finishes/types of façade (Tag sheet references noted above). If water does penetrate the façade in some areas this will require an outlet again, this is not evident in what has been installed on site. Fire separation is also to be provided between the station and OSD/Adjacent Buildings. There is no evidence that this has been considered based on what can be seen on site.
|  | Cxxx-NCR-002263 | NCR | Tun - CMS install multi comp trunking capacity __-00139 |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2023-12-31 | 2022-12-20 09:52 | -376 | 2019-04-25 09:08 | Electrical - Cable Management | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | multi comp comms trunking/ installed in switchroom 8/668 has been installed and now cabled, the trunking transition from vertical to horizontal has been installed by use of 'top hat' joint with a cut out section for cables to transition, it was noted that there is no capacity through the comms cable compartment for any further cabling to be installed through this junction, further more the cabling installed through the cut out appears to be damaged. note; the full route of this cms should be checked to ensure there is adequate capacity for future cabling to be installed.
|  | Cxxx-NCR-002289 | NCR | ESC - Tunnel Decking out of tolerance __-00139 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2023-12-31 | 2022-12-20 09:53 | -376 | 2019-05-08 16:06 | Mechanical - Escalators | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Further to a 3D scan produced by Cxxx for interrogation of escalator barrels 2 and 3, __ have identified external decking lines are not linear and straight. This out-of-tolerance installation is producing issues with Robert Stevens cabinet installation and subsequent design rationale advertising screen install.
|  | Cxxx-NCR-002294 | NCR | MShaft - Cracking in screed to Street level - 1 corridor and rooms __-00139 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2023-12-31 | 2022-12-20 09:54 | -376 | 2019-05-10 08:58 | Architectural - Flooring | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | surface cracking has appeared to the screen in various areas on level Street -1. Generally in corridors
|  | Cxxx-NCR-002343 | NCR | __X - Back Entrance - Security Fence and Ladder - Wrong Installation __-00139 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2023-12-31 | 2022-12-20 11:17 | -376 | 2019-06-19 14:45 | Architectural - Security | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Cxxx have been instructed with Cxxx-PMI-00535 Blomfield Box Proposed Revision to N.E. Core in May 2015. Cxxx failed to comply to the PMI instructions: Item 1.b. - The twin decks to be enclosed to the north and east by a metal fencing not less than 1800mm above deck level, to prevent objects being accidentally dropped to the MCL railway below. As it stands, the fence on the East Elevation is 2.4m and on the North Elevation is 4.0m. Both from slab level. This was identified on a LUL VAP Report on 26/04/2018 - LUL VAP Report 518, item 20.
|  | Cxxx-NCR-002390 | NCR | P&T - NLL - Lean Bars - Broken Infill Strips __-00139 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2023-12-31 | 2022-12-20 09:55 | -376 | 2019-09-13 08:48 | Architectural - Finishes | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | GFRC infill strips damaged
|  | Cxxx-NCR-002412 | NCR | BTH - Bedlam Memorial - Interface Works __ / __ __-00139 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2023-12-31 | 2022-12-20 09:59 | -376 | 2019-09-09 09:59 | Architectural - Finishes | 500 |  | Incomplete Works | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Bedlam Memorial (__ Package 25a) was offered to CRL inspection on Tuesday 3rd September 2019. The following issues were identified as missing scope / incomplete works / damage are due to be completed by __. - Floor mastic: not installed between the floor plates and adjacent finishes. - Flooring / baseplate: damage flooring adjacent to baseplate forming part of floor - interface issues to be resolved. - BTH paid side: flooring missing. - BTH paid side: florring and baseplate are at different levels - confirmation required that both scopes are within tolerances.
|  | Cxxx-NCR-002440 | NCR | P&T - Eastbound and Westbound Platforms - PES/Terrazzo Flooring Interface - Localized Gaps |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2023-12-31 |  | -328 | 2019-10-11 12:46 | Architectural - Flooring | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Open | Discipline/Workmanship - Other | IMPLEMENTATION |  | Location description: PES/Flooring interface Eastbound and Westbound Platforms. Localized gaps between the manufactured floor joints and the frame / threshold to the PES. To note: this is an interface between __ and CRL contractor.
|  | Cxxx-NCR-002451 | NCR | __ Portland Stone panel damaged in MTH - 4A - GL.7 __-00139 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2023-12-31 | 2022-12-20 10:00 | -376 | 2019-10-31 09:47 | Architectural - General | 6000 |  | Damaged | Rework | 3 (3-6k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | Damaged occurred to 1no Portland stone panel in MTH along GL7 - South Elevation. The bottom panel, installed by __, has been damaged .
|  | Cxxx-NCR-002456 | NCR | BTH - Glass Canopy - S/S Joints __-00139 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2023-12-31 | 2022-12-20 10:01 | -376 | 2019-11-06 08:52 | Architectural - Finishes | 6000 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Further to CRL observation, it has been raised that the joints to the internal south collaspible enclosure are non-consistent. It is apparent that the Tier 2 contractor has not issued drawings for this to review. Historically this area was a door arrangement, however under PMI-1448 this was changed to a collapsible gate. However, CRL approved drawings Cxxx-LAO-A-DDD-C101_Z-47643 shows the panel and joint arrangement. Furthermore drawing Cxxx-LAO-A-DDD-C101_Z-47642 Detail 02 reflects this. This panel arrangement is as per installed on site. See attached drawing.
|  | Cxxx-NCR-002459 | NCR | Terrazzo Flooring / Tile Shading / Moorgate Ticket Hall __-00139 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2023-12-31 | 2022-12-20 10:02 | -376 | 2019-11-12 10:32 | Architectural - Flooring | 500 |  | Material | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During site inspection of the Terrazzo floor tiles in Moorgate Ticket Hall with __, CRL (Neil Sharpe) and HB it was noted that the area to the north side of the Ticket Hall had different shading to the floor tiles. Note; Attached Observation report carried out by CRL architects high lights the issue and also contains photographs of the effected area / tiles.
|  | Cxxx-NCR-002460 | NCR | BTH - L+E - Bimetallic Fixings __-00139 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2023-12-31 | 2022-12-20 10:03 | -376 | 2019-11-12 17:18 | Mechanical - Lifts | 4000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Mixture of zinc, stainless and galvanised fixings for landing frame install for L8+9 top and bottom landing frames. No separation / isolation through nylon washers or similar. No protection of steelwork cut on site.
|  | Cxxx-NCR-002469 | NCR | Damaged comm's assets site wide. __-00139 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2023-12-31 | 2022-12-20 10:04 | -376 | 2019-11-28 08:07 | Communications and Control Systems | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | This NCR has been raised to highlight the fact that there are various comm's assets site wide that are damaged and will require repair or replacement. We intend to do a full site survey of these assets at the end of January 2020 and either instruct contractors to repair damage or request replacement assets from __ Cxxx.
|  | Cxxx-NCR-002481 | NCR | MSH - Level 0 - Moorgate Elevation - __ Louvres __-00139 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2023-12-31 | 2022-12-20 10:07 | -376 | 2020-01-20 12:41 | Architectural - Finishes | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | This NCR is an extract from Cxxx-NCR-002360. The items below only refer to __ Package. Photo 14 & 15: Moorgate – __ Louvres – Header detail The trim at the top of the louver appears to have been added in because the louvres have both been made to correct opening height of the opening in the concrete structure. Photo 16: Moorgate – __ Louvres – Bottom detail Bottom flashing detail does not appear on Cxxx drawing Cxxx-LAO-A-DDD-C101-_Z-24101. Cxxx to confirm if the bottom flashing has been approved as a design by Crossrail and has it been co-ordinated with the urban realm finishes and finishes levels to provide the required level of waterproofing to the building envelope. Photo 18: Moorgate – __ Louvres – Sealant and Staining a) Louvre frame is stained and grimy and the paint finish to the louvre has been damaged b) Hole in concrete: is the Cxxx proposal to fill this hole or to leave it as is? Photo 20: Moorgate – __ Louvres – Door hardware Door to __ transformer secured by padlock. Cxxx to confirm if this is compliant with the security requirements. Additional item: Skirting trim and floor interface – a gap between the two results in an area of waterproofing being exposed and susceptible to damage – propose detail to address issue.
|  | Cxxx-NCR-002491 | NCR | MTH – __ Tiling – Unpaid Side – 13. Movement joint stops before hatch – Occurred on 2 occasions - Reoccurs along the gate line __-00139 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2023-12-31 | 2022-12-20 10:08 | -376 | 2020-01-25 14:15 | Architectural - Flooring | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Movement joint sevres no functionality within hatch cover purpose. Floor tling has been installed as per Cxxx drawing. No objection from __\Brown on as built installation
|  | Cxxx-NCR-002526 | NCR | BTH - Damage to stone cladding of __ glass canopy __-00139 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2023-12-31 | 2022-12-20 10:09 | -376 | 2020-02-25 15:09 | Architectural - Walls | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper storage of material | Completed |  | Damage to stone noted on Cxxx-NCR-002222, along with other, non-physical issues. This is a separate NCR to deal with the damage issue only.
|  | Cxxx-NCR-002530 | NCR | Totem Signs - Louvred Shroud __-00139 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2023-12-31 |  | -328 | 2020-03-09 12:34 | Architectural - Signage | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Open | Discipline/Workmanship - Defective construction | IMPLEMENTATION |  | The louvre shroud on totems with small projecting signs, antenna and CCTV cameras are not as per the works information or the approved prototype details. The shrouds should be complete above and below the projecting equipment bracket and there should be a blanking plate behind the louvre fins.
|  | Cxxx-NCR-002551 | NCR | BTH - North Canopy Wall Waterproofing (Further to VAP492 & PWK3248) __-00139 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2023-12-31 | 2022-12-20 11:18 | -376 | 2020-04-29 06:55 | Civil - Civil Engineering General | 2000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Further to VAP 492 Item 19 and PWK 3248, the contractor is unable to raise the level of the waterproofing to the required 225mm above FFL due to clashes with containment of the uplighters within the BTH canopy. The contractor has been able to raise the level of the __ of the waterproofing to approximately 100mm above FFL.
|  | Cxxx-NCR-002552 | NCR | Blomfield Box - Bronze over-clad exit and maintenance doors - operation restrictions. __-00139 |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2023-12-31 | 2022-12-20 10:12 | -376 | 2020-05-14 15:28 | Architectural - Doors | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | As identified in CRL-OBS-30514 - a number of issues have been raised associated with the operation of the large maintenance doors forming part of the façade. Right hand Fan removal door - Clashes with services – Cxxx to advise on proposed mitigation/re-location of services. - Bolt – confirm depth requirement (security) is achieved. - Door clashes with ramped floor (ramp towards outside) in open position. Right hand Fan removal door - Clashes with flood barrier – Cxxx to advise on proposed mitigation/re-location of services. - Bolt – confirm depth requirement (security) is achieved. Confirmation that doors in restricted position (clash with flood barrier) meets requirements of the Access and Maintenance Strategy.
|  | Cxxx-NCR-002566 | NCR | __ - SOR glazing __-00139 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2023-12-31 | 2022-12-20 10:13 | -376 | 2020-06-15 12:23 | Architectural - Glazing | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Some glazing units have some powder / dust inside. This is very unsightly as facing the public at eye level. Please refer to attached photos for clarity.
|  | Cxxx-NCR-002590 | NCR | Anti drumming to ironman cladding __-00139 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2023-12-31 | 2022-12-20 10:14 | -376 | 2020-11-13 09:53 | Architectural - Finishes | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | During final inspection its was identified that the design of the __ cladding failed to incorporate sufficient anti drumming measures as per section JK17.1206 (f) of the specification. Remedial work is required to bring the cladding up to the correct specification.
|  | Cxxx-NCR-002595 | NCR | Anti drumming to ironman cladding AP5 __-00139 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2023-12-31 | 2022-12-20 10:14 | -376 | 2020-11-27 09:45 | Architectural - General | 500 |  | Incomplete Works | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During final inspection its was identified that the design of the __ cladding failed to incorporate sufficient anti drumming measures as per section JK17.1206 (f) of the specification. Remedial work is required to bring the cladding up to the correct specification.
|  | Cxxx-NCR-002630 | NCR | Platform Projecting Help Point Signs - Wrong Colour Down Light __-00139 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2023-12-31 |  | -328 | 2021-05-21 10:00 | Architectural - Signage | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Open | Discipline/Workmanship - Other | INSPECTION |  | The colour of the down lights in the platform projecting help point signs is incorrect. It is currently 3000K but it should be 5000K.
|  | Cxxx-NCR-000498 | NCR | Damaged (7 0ff) Escalator Panels - West Box __-00075 |  | Contr | __R | WOO - Woolwich Station (East) |  | 2023-12-31 | 2023-01-13 15:50 | -352 | 2018-07-16 13:52 | Architectural - Finishes | 3000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | Location: West Box Escalator Area Side Panels – A joint inspection on the 12/07/18 by __ led to findings of damaged/scratched/bent panels on __’s installed cladding and inspected by CRL on the 18/08/2017. By then the only damage identified was a scuff mark which is part of NCR with ref. Cxxx-NCR-000412. See attached IRF and work acceptance record of final inspection done on the 18/08/2017 (Cxxx-QUAL-SF-4003-CL-0005 – Work acceptance record). The panels were protected immediately with correx sheets after final inspection took place (see pics taken on the 21-08-2017). During the period of time since 18/08/2017 the correx protection was removed by others (see pics taken on the 24-10-2017 and 05-01-2018). Seven panels were found scratched and 1 panel bent on the underside. See attached markup with joint inspection findings (Escalator Side Panels damage_Markup.pdf) and pictures taken on the 12-07-2018.
|  | Cxxx-NCR-000580 | NCR | Damaged Water Heater - Rm 48 West Box Platform Level __-00075 |  | Contr | __R | WOO - Woolwich Station (East) |  | 2023-12-31 | 2023-01-13 15:54 | -352 | 2019-09-16 10:03 | Mechanical - Hot & Cold Water Supplies | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | A water heater in Rm 48 has incurred damage to the outter casing.
|  | Cxxx-NCR-000170 | NCR | Accommodation Building Ventilation Issues __-00113 |  | Contr | __ |  |  | 2023-09-23 |  | -229 | 2020-05-06 13:24 | Mechanical - Heating Ventilation & Air Conditioning | 700000 |  | Design | Repair | 1 (>60k) | Open | Design Problem - Other | INSPECTION |  | The Contractor has been notified by the end user that buildings internal temperature during periods of hot weather exceeds comfortable levels. The Contractor has reviewed the installation of the works and believes that the works comply to the Works Information, as detailed in Cxxx-CCM-01402.
| 03SR - Stations (RfL) | T142-Cxxx-NCR-000001 | NCR | Station Entrance Maintainability Issue |  | Crossrail | XRL | CWS - Canary Wharf Station |  | 2018-04-13 | 2018-05-25 10:53 | 42 | 2016-08-24 12:56 | Logistics - Logistics - General | 0.1 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Maintainability issue in the Station Entrance when needing to arrange lifting for Tunnel Vent Fans, Transformers and other heavy equipment from within the plant areas, as the whole roof has to be taken out, before the gantry crane can be assembled and certificated, and a crash deck installed beneath the floor planks before they can be removed. Looks like many shifts required prior to any maintenance operation involving lifting equipment in or out, and therefore will necessitate always needing to be done at a possession weekend - there are only two of these per year, and this seems far too onerous a limitation for routine maintainability.
| 03SR - Stations (RfL) | T142-Cxxx-NCR-000002 | NCR | CWG D33 Missing Mastic on Smoke Downstand |  | Crossrail | XRL | CWS - Canary Wharf Station |  | 2019-07-22 13:57 | 2019-04-30 08:33 | -83 | 2018-10-30 08:30 | Fire - Compartmentation | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | CWG design calls for high temperature silicone between smoke downstand panels to achieve a smoke stop. This is missing.
| 03SR - Stations (RfL) | T142-Cxxx-NCR-000003 | NCR | CWG D01 and D02 CMS hanging system / undercut anchors |  | Crossrail | XRL | CWS - Canary Wharf Station |  | 2019-01-28 | 2019-07-19 08:39 | 172 | 2018-10-30 09:04 | Electrical - Cable Management | 200000 |  | Incorrect Installation | Repair | 1 (>60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The CMS hanging system installed by CWG (T142 contract) has not been provided with design calculations/certificate to confirm it can survive a 2hr fire for life critical systems. A back calculation by __ (Cxxx) commissioned by the Cxxx team has identified that drop rods are insufficiently sized (eg 8mm where should be 112-14mm dia). A defect notice has been served to CWG but they have not responded. Additionally, the Cxxx team pull tested 6No. undercut anchors supporting the drop rods and the majority of these failed. CWG witnessed these tests.
| 03SR - Stations (RfL) | T142-Cxxx-NCR-000004 | NCR | Ceiling anchors |  | Crossrail | XRL | CWS - Canary Wharf Station |  | 2018-12-13 | 2019-07-19 09:33 | 218 | 2018-11-22 14:15 | Architectural - Ceilings & Soffits | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - NCR excessive closure due to design issue | Completed |  | The -1, -4 and -5 __ ceiling hangers are installed with 32mm long 4mm __ screws that fail to provide the required pull out load and as they are carbon steel the fail to comply with durability requirement for the use of stainless steel fixings into concrete. Failure of pull tests (circa 0.1kN) Non stainless steel fixings. Inadequate capacity to meet FOS 4 Anchors do not tally with as-built drawing information, or provided calculations Cxxx agreed with CEG / CCSC that this presented a safety concern and the Cxxx team removed and swapped anchors for __ HST3 M8/10 anchors -For record purposes this NCR records this.
| 03SR - Stations (RfL) | T142-Cxxx-NCR-000005 | NCR | D04 Cable lugs |  | Crossrail | XRL | CWS - Canary Wharf Station |  | 2019-07-22 13:53 | 2019-07-18 07:34 | -4 | 2018-11-22 17:01 | Electrical - Electrical Engineering General | 50000 |  | Workmanship | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Cable lugs installed by CWG have been found to be incorrectly sized, been cut and splayed to fit bolts, and have had excessive sheathing cut back.
| 03SR - Stations (RfL) | T142-Cxxx-NCR-000006 | NCR | D14 Vinyl Tiles - smoke emissions |  | Crossrail | XRL | CWS - Canary Wharf Station |  | 2018-12-25 | 2019-07-19 09:49 | 206 | 2018-11-22 17:21 | Materials - General | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Vinyl tiles installed by CWG which do not have MCR approval. Tiles with approved MCR / material properties readily available and in fact installed elsewhere in the station. In rooms of various sizes. Material Details __ Location: Level -4 Rooms: 4205, 4206, 4207, 4208, 4461, 4466 See also attached emails
| 03SR - Stations (RfL) | T142-Cxxx-NCR-000009 | NCR | Hydrant and Watermist Supports |  | Contr | DRN | CWS - Canary Wharf Station |  | 2019-08-07 16:40 | 2019-07-24 16:48 | -14 | 2019-07-19 11:48 | Fire - Suppression | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The Hydrant and Watermist pipes are not supported correctly at Level -2 East back of house, in corridor 2/236. The pipes should be supported independently from the structure, not supported from the CMS or other services.
| 03SR - Stations (RfL) | T142-Cxxx-NCR-000010 | NCR | BMS Panel - Main Labels |  | Crossrail | XRL | CWS - Canary Wharf Station |  | 2019-08-31 | 2019-07-28 13:22 | -34 | 2019-07-22 08:43 | Communications and Control Systems - Station Management System | 40000 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Supervision - Supervisor not familiar with the work | Completed |  | It has come to our attention that every BMS Panel has a fixed label stating where the panel is fed from. Every one of them is incorrect.
| 03SR - Stations (RfL) | T142-Cxxx-NCR-000011 | NCR | No Pull Test Assurance for Fire Main Installation |  | Contr | DRN | CWS - Canary Wharf Station |  | 2019-08-09 15:22 | 2019-07-26 15:31 | -14 | 2019-07-25 12:48 | Mechanical - Public Health Engineering | 4000 |  | Documentation and Records | Use As-Is | 3 (3-6k) | Complete | Supervision - Insufficient supervision | Completed |  | During a Crossrail Surveillance at Canary Wharf Station by Oliver Mark it was found that fixings had been installed within the concrete ceiling outside 3462 on level -3. Pull test records were not available for these when requested from the contractor. This was raised as an NCR against Cxxx (Cxxx-NCR-000043). The contractors replied to the NCR stating that as the pipework had passed pressure testing and had been signed off by CWG the supports were adequate.
|  | TCxxx-NCR-000031 | NCR | GYB Level -5 Drainage - Blocked Gully drain branch GYB Level -5 Drainage - Blocked Gully drain branch GYB Level -5 Drainage - Blocked Gully drain branch |  | Stakeholder - LU | LU | INT - Interfaces (West) |  | 2014-04-15 | 2015-09-23 10:35 | 526 | 2014-04-01 16:24 | Civil - Drainage | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During the pour of the Area A of the level -5 floor slab, a short branch of drain pipe has incurred concrete ingress. This has blocked the drain pipe from one of the floor gully's as shown on attached highlighted drainage plan and sketches. The blockage has been attempted to be cleared by way of water jetting and electro-mechanical means. Both have proved unsuccessful. The blocked floor gully has 3 other floor gully's in close proximity. The blocked gully does not appear to be segregated from these by any walls on current plans". __ therefore request confirmation from Crossrail and their drainage designer that the floor gulley can be made redundant, with the drainage system utilising adjacent gully's to absorb the catchment. This will allow them to complete the Non-Conformance Report.
|  | TCxxx-NCR-000032 | NCR | Goslett Yard Box Buttress Wall |  | Stakeholder - LU | LU | INT - Interfaces (West) |  | 2014-04-17 | 2016-09-20 15:18 | 887 | 2014-04-03 14:38 | Mechanical - Lifts | 10000 |  | Incorrect Installation | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The Buttress wall has been constructed out of tolerance with the wall projecting into the lift shaft approximately 28mm, (see Plan and sketch within attached NCR Report VBN-TCR-8742-NCR-000748). The Defect occurred during the set-up of the pour when the carpenters installed the shutter incorrectly. The buttress wall now projects into the shaft a maximum of 28mm at a height of approximately 3m. The TCRSU Project Requires confirmation from Crossrail lift contractor that this 'bulge' does not affect the lift's installation or operation to allow the Defect to be uncorrected.
|  | TCxxx-NCR-000033 | NCR | Goslett Yard Box Level 3.5 Slab (Level +104.500m) |  | Stakeholder - LU | LU | INT - Interfaces (West) |  | 2014-04-16 | 2014-06-02 15:30 | 47 | 2014-04-02 12:47 | Civil - Civil Engineering General | 0 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | The level 3.5 slab has been constructed out of permitted tolerance by 4mm. During construction of the +104.500m (level 3.5 slab), the soffit was lowered by 20mm to suit the cast-in sockets in the connections in the diaphragm walls. This increased the thickness of the slab from 600mm to 620mm. The soffit was lowered in order to ensure the correct cover was achieved to the B1 reinforcement. Therefore the slab thickness exceeds the permitted tolerance [+/-16.5 mm] by 4 mm, (see attached sketches). __ therefore request confirmation from Crossrail that this does not impact on any future fit out works. This will allow them to complete the Non-Conformance Report.
|  | TCxxx-NCR-000034 | NCR | Goslett Yard Box HD Bolts reduced tie force capacity |  | Stakeholder - LU | LU | INT - Interfaces (West) |  | 2014-06-17 | 2014-06-03 12:45 | -14 | 2014-06-03 10:26 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | __ have informed London Underground that some holding down bolts for the Crossrail OSD into the GYB Decline North Capping Beam were not cast in when the beam was originally cast. The locations of the omitted bolts are shown yellow on the attached sketch 001, relating to the details on drawing ATK-N105-8742-STR-D-GAR-0-31605. One cluster detail 51 and one cluster detail 53 have been remediated using a drilled fixing. The detail 51 now complies fully with the original design requirements. The remedial action of drilling and fixing the bolts has resulted in the tie force design capacity for cluster detail 53 being reduced from 2145KN (ULS) to 1046KN (ULS). In addition, __ have confirmed that the ‘Z’ level on the Sketch 001 refers to the top of the bolts and that it had been grouted below the plate. Moreover, with reference to the attached detail section 52, (ATK-N105-8742-STR-DET-X-34410) that the temporary bolt and bolt coupler are not galvanised. __ have advised __ that they are unable to produce a post-fixed detail that achieves the full design capacity. __ therefore request acceptance of the reduced load capacity for this cluster detail.
|  | TCxxx-NCR-000035 | NCR | Goslett Yard Lift Shaft Lifting Eyes Level 0 |  | Stakeholder - LU | LU | INT - Interfaces (West) |  | 2015-01-02 | 2016-09-14 10:59 | 621 | 2014-12-19 12:27 | Civil - Civil Engineering General | 10000 |  | Incorrect Installation | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Other | Completed |  | "The approved design includes four Rd30 lifting sockets cast into the Level +0 slab soffit to serve the lift shaft between Level -1 of the escalator decline and Level -4 of the box. Three of the lifting eyes were omitted when the level +0 slab was poured in 2011, as shown on ATK-VBN-8742-STR-D-GAR-0-31603 X01 (attached). Discussions with Crossrail, and the information subsequently provided with PMI1175, indicate that the locations of the lifting sockets in the approved design no longer suit the lift contractor's design for the lift".
69867161.58

## Summary Total
1. Total No. of NCRs Raised as at 04/02/2023 | 25232
2. Total Raised by Contractor | 22521 | 89%
3. Total Partial Rework Cost | 69867162 | 0.8292%
4. Total Actual Cost of Work Performed | 8425690625