| 02SL - Stations (LUL) | Cxxx-NCR-001242 | NCR | WTH Level +1 Cast In Steel Plate Survey - Position & Level Deviations |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-08-31 | 2021-06-30 07:51 | 303 | 2020-05-14 13:54 | Civil - Civil Engineering General | 14345 |  | Incorrect Installation | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A survey of the WTH L+1 Cast in steel plates was carried out for both level & position. Analysis has confirmed a number of cast in plates have deviated outside of specified tolerances in both level and position under KF10.3222 n) i). The plates outside of tolerances are clouded in red on attachments 'WTH Level 1 Steel plates - Levels Rev.3.0' and 'WTH Level 1 Steel plates - Position Rev.3.0'
| 02SL - Stations (LUL) | Cxxx-NCR-001243 | NCR | FFL design levels beneath WTH Side Gates - Error in 3D Modelling |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-06-15 | 2022-03-18 14:22 | 641 | 2020-06-01 11:18 | Architectural - General | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Urban realm FFLs provided by __ Highways, used to coordinate __ and __ designs - see __-SUBRFI-000244 - SK1995 were not aligned with levels provided by __ in response to __-RFI-005972 - TCS RFI - Matwell Levels - SK2236.
| 02SL - Stations (LUL) | Cxxx-NCR-001244 | NCR | Mixed Cable Manufacturers |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-06-16 | 2021-06-29 14:06 | 378 | 2020-06-02 12:03 | Electrical - Electrical Engineering General | 0 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The M&W Specification Cxxx-SKC-M-RSP-Cxxx-50063 - MEP Fit-Out Specification Section JY61 - LV Cables and Wiring states the following: JY61.1401 System Characteristics o) The cable type and manufacture shall be consistent throughout each wired system. All cable utilised must be continuously run from source to termination, without any through joints unless agreed in writing by the Project Manager.The contractor has identified the use of mixed cable manufacturers used in the same circuit across multiple distribution boards across the site. The M&W Specification Cxxx-SKC-M-RSP-Cxxx-50063 - MEP Fit-Out Specification Section JY61 - LV Cables and Wiring states the following: JY61.1401 System Characteristics o) The cable type and manufacture shall be consistent throughout each wired system. All cable utilised must be continuously run from source to termination, without any through joints unless agreed in writing by the Project Manager. The cable manufacturers and MCRs are as follows: CRL-MCR-004094 - Firetec Tubesafe Cable CRL-MCR-003943 - Exane PC Class 2 Cable CRL-MCR-005621 - Exane Circuit safe The contractor shall provide the number of affected DB's / CCT's to the Project Manager for further discussion at the weekly Legacy Issues meeting. This affects Normal and Emergency circuits and the mixed cables will be identified with the test sheets submitted within the IRN SAF packs.
| 02SL - Stations (LUL) | Cxxx-NCR-001245 | NCR | WTH L-3 4_212, Cxxx Damaged Fibre Cxxx-DAT-00193, between roomm 4_407 and 4_083 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-12-10 | 2020-11-26 13:42 | -14 | 2020-11-26 10:56 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | On investigation of fault between DC3&4 we found the fiber cable between the cabs has been chopped in the trunking outside the room. Cxxx-DAT-00193 goes from BOS-03-CAB-4790AU1 to BOS-02-CAB-3747U1 Please note that this cable is an SC1 requirement and has been handed over to __. Please also be aware that this cable traverses between WTH L-3 over to the ETH L-2 Cable length is excess of 700m.
| 02SL - Stations (LUL) | Cxxx-NCR-001246 | NCR | Low RC upstand - WTH L+0 - Gridline J1 to L1 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-06-24 | 2021-07-02 16:08 | 373 | 2020-06-10 11:02 | Structural Engineering - Concrete Member | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | The levels for the RC upstand in the WTH L+0 6no. bays J1 to L1 (between the precast column beneath the __ Side gates) are between 96mm and 38mm below the required levels. See 'Cxxx-__-S-DDL-Cxxx-11103 Rev X03_OH Markup of upstands.pdf'
| 02SL - Stations (LUL) | Cxxx-NCR-001247 | NCR | DB-E-EL07 16WAY TP&N installed instead of 18WAY TP&N |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-06-25 | 2021-02-02 16:09 | 222 | 2020-06-11 11:50 | Electrical - Electrical Engineering General | 0 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | DB-E-EL07 is referenced as 18WAY TP&N on __ DB Schedule but a 16 way TP&N was installed. ETH Level -5, SRIII/ESRIII 6/672
| 02SL - Stations (LUL) | Cxxx-NCR-000028 | NCR | Support Fluid |  | Contr |  | TCR - Tottenham Court Road Station (West) |  | 2011-08-08 | 2011-08-24 09:36 | 16 | 2011-07-25 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | During piling of pile 30, pile bore found dry to the toe and no evidence of any water ingress. __ decided to carry on as a dry pile and not to use support fluid and monitoring the bore constantly for any collapse. No collapsed observed until completion of concreting.
| 02SL - Stations (LUL) | Cxxx-NCR-000029 | NCR | Concrete cover zone to geothermal pipe - piles 28, 31, 33 |  | Contr |  | TCR - Tottenham Court Road Station (West) |  | 2011-08-08 | 2011-08-23 16:59 | 15 | 2011-07-25 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Design | Reject |  | Complete |  | Completed |  | As built cover is between 100 and 104mm.
| 02SL - Stations (LUL) | Cxxx-NCR-000030 | NCR | Piling not completed within 24 hours - Pile 27 |  | Contr |  | TCR - Tottenham Court Road Station (West) |  | 2011-08-08 | 2011-08-03 16:31 | -5 | 2011-07-25 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Planning | Use As-Is |  | Complete |  | Completed |  | Piling of pile 27 not completed within the specified 24 hours or 18 hours from the Lambeth. Pile excavation started in the London Clay at 12:20pm on Wednesday 20th of July and completed at 18:30pm on Thursday 21st of July. Concrete commenced at 10:26am on Thursday 21st of July.
| 02SL - Stations (LUL) | Cxxx-NCR-000031 | NCR | Top of the reinforcement higher than specified on Pile 27 |  | Contr |  | TCR - Tottenham Court Road Station (West) |  | 2011-08-08 | 2011-08-03 16:22 | -5 | 2011-07-25 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | As built of pile reinforcement on Pile 27 is 372mm higher. This is 222mm out of tolerance. NCR caused by tremie lendth reduced on time resulting in the cage lifting.
| 02SL - Stations (LUL) | Cxxx-NCR-000032 | NCR | Coupler Connection of the Pile Reinforcement Cage on Pile 28. |  | Contr |  | TCR - Tottenham Court Road Station (West) |  | 2011-08-08 | 2011-08-03 16:35 | -5 | 2011-07-25 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | On pile 28 five no of coupler connection could not be connected as per the manufacturer's specification as the cage's shape deformed due to longer storage period and number of moves within the site.
| 02SL - Stations (LUL) | Cxxx-NCR-000033 | NCR | Particulate Filters |  | Contr |  | TCR - Tottenham Court Road Station (West) |  | 2011-08-08 | 2011-09-30 15:59 | 53 | 2011-07-26 | Environmental - Air Quality | 500 |  | Material | Reject |  | Complete |  | Completed |  | 4 pieces of equipment on site over the 37Kwatt limit, not fitted with the stated device.
| 02SL - Stations (LUL) | Cxxx-NCR-000034 | NCR | Top of the reinforcement cage level on P31 |  | Contr |  | TCR - Tottenham Court Road Station (West) |  | 2011-08-16 | 2011-08-08 08:54 | -8 | 2011-08-02 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Reinforcement cage raised 577mm during concreting operation and the asbuilt level is 121.402mod and out of tolerance of 407mm.
| 02SL - Stations (LUL) | Cxxx-NCR-000035 | NCR | Top of the reinforcement cage level on P2 |  | Contr |  | TCR - Tottenham Court Road Station (West) |  | 2011-08-03 | 2011-08-08 08:57 | 5 | 2011-08-02 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Due to cage was lifed by 525mm during concrete operation asbuilt level of top of the reinforcement is 115.420mod, 375mm out of tolerance.
| 02SL - Stations (LUL) | Cxxx-NCR-000036 | NCR | Joining Sacrificial reinforcement cage to Structural cage on pile 2. |  | Contr |  | TCR - Tottenham Court Road Station (West) |  | 2011-08-03 | 2011-08-08 09:01 | 5 | 2011-08-02 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Planning | Use As-Is |  | Complete |  | Completed |  | Non described method of using wire rope grips used to join sacrificial cage to the structural cage as this is low cost method and also common practice. But not included in the work Method Statement and the design informatin of the wire rope grip not submitted to Crossrail.
| 02SL - Stations (LUL) | Cxxx-NCR-000042 | NCR | Bentonite testing |  | Contr |  | TCR - Tottenham Court Road Station (West) |  | 2011-08-17 | 2011-08-17 10:43 | 0 | 2011-08-10 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Filter cake thickness not been tested for piles P33 and P27, as on the the old test record sheet this test was not stated.
| 02SL - Stations (LUL) | Cxxx-NCR-000043 | NCR | Bentonite testing |  | Contr |  | TCR - Tottenham Court Road Station (West) |  | 2011-08-15 | 2011-08-17 10:49 | 2 | 2011-08-10 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The following tests have not been carried out for all the piles constructed up to date as __ do not have the facility and experience. a) Plastic viscosity b) Yield stress c) Consistency index d) Flow index f) Gel strength.
| 02SL - Stations (LUL) | Cxxx-NCR-000044 | NCR | Concrete |  | Contr |  | TCR - Tottenham Court Road Station (West) |  | 2011-08-15 | 2011-08-17 10:53 | 2 | 2011-08-10 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Due to major break down at the __ batching plant at 1/3 of the way of concreting pile no 4, and no other plants have the facility supply the recycled aggregate, alternate mix without the recycled aggregate used to complete the pile from the same batching plant but different mix unit. sample cubes taken for strength test.
| 02SL - Stations (LUL) | Cxxx-NCR-000047 | NCR | Pile 37 top of steel |  | Contr |  | TCR - Tottenham Court Road Station (West) |  | 2011-08-19 | 2011-08-17 13:49 | -2 | 2011-08-16 | Geotechnical Engineering - Concrete - Driven Pile | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Asbuilt top of steel is 190mm too high (121.015), 40mm out of tolarance due to error in calculation of cage feet length, the shortest bar should be taken into the calculation.
| 02SL - Stations (LUL) | Cxxx-NCR-000048 | NCR | Pile 4 Top of steel level |  | Contr |  | TCR - Tottenham Court Road Station (West) |  | 2011-08-19 | 2011-08-17 14:18 | -2 | 2011-08-16 | Geotechnical Engineering - Concrete - Driven Pile | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Asbuilt top of steel level of this pile is 585mm too high (115.480mod) 435mm out of tolerance. This is caused by cage lifted during the concreting operation.
| 02SL - Stations (LUL) | Cxxx-NCR-000049 | NCR | Pile 6 top of steel too high |  | Contr |  | TCR - Tottenham Court Road Station (West) |  | 2011-08-23 | 2011-08-17 14:16 | -6 | 2011-08-16 | Geotechnical Engineering - Concrete - Driven Pile | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Asbuilt top f the steel level of this pile is (115.155mod) 110mm out of tolerance. This is the fifth pile cage lifted as proposed on the last NCR for the same reason (P4) proposed to use cage feet this cage has the cage feet still lifted but only by 260mm compared with previous lifts between 400-500mm.
| 02SL - Stations (LUL) | Cxxx-NCR-000051 | NCR | D-Wall Panel 13, Fabrication of sonic tubes |  | Contr |  | TCR - Tottenham Court Road Station (West) |  | 2011-09-12 | 2011-09-07 16:16 | -5 | 2011-09-07 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Two number of sonic tubes out of six did not marry while joining the cages together, this lead the panel completion delayed by 4 hours on Saturday (permitted working hours till 1pm) and one of the two relocated tube is blocked too. Additional work carried out, lay the cahe flat removed the sonic tube and re located. Also one load of concrete rejected as it was waited more than two hours.
| 02SL - Stations (LUL) | Cxxx-NCR-000052 | NCR | Pile 7, Concrete Test Limit out of Spec. |  | Contr |  | TCR - Tottenham Court Road Station (West) |  | 2011-09-12 | 2011-09-12 12:08 | 0 | 2011-09-08 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | One load of 6m3 concrete out of 55m3 on pile 7 had the slump value of 250mm, this was allowed to use by the concrete technician on the basis of visual observation this non conforming the specification by 20mm higher slump value.
| 02SL - Stations (LUL) | Cxxx-NCR-000053 | NCR | Inner hanging bars not de-bonded on Panel 5. |  | Contr |  | TCR - Tottenham Court Road Station (West) |  | 2011-09-16 | 2011-09-22 16:36 | 6 | 2011-09-13 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Inner hanging bars on panel 5 do not have the de-bonding foam and not de-bonded.
| 02SL - Stations (LUL) | Cxxx-NCR-000054 | NCR | Low Concrete Cube Strength on Pile 5 |  | Contr |  | TCR - Tottenham Court Road Station (West) |  | 2011-09-20 | 2011-11-28 16:36 | 69 | 2011-09-16 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | 28 Day strength 36.5N. Pile 5 concreted on the 10-08-2011 Ticket number 552980.
| 02SL - Stations (LUL) | Cxxx-NCR-000055 | NCR | None reycled concrete used partially on Pile 23 from Back up batching plant |  | Contr |  | TCR - Tottenham Court Road Station (West) |  | 2011-09-26 | 2011-09-28 09:12 | 2 | 2011-09-21 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Due to usual supply batching plant King Cross broke down, concrete supplied from the back up plant in Paddington which dont have the facility of recycled aggregate. 28.5m3 of Concrete with None recycled aggregate and 21.5m3 of Concrete with recycled aggregate used, total volume used 50m3.
| 02SL - Stations (LUL) | Cxxx-NCR-000056 | NCR | Uncompleted Pile 25 |  | Contr |  | TCR - Tottenham Court Road Station (West) |  | 2011-09-27 | 2011-10-10 09:07 | 13 | 2011-09-23 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Workmanship | Reject |  | Complete |  | Completed |  | Pile completed short of 7.35m from the cut off level, this due to the blockage in the concrete placement tube at the first load this lead further delay of pouring each load from the batch time.
| 02SL - Stations (LUL) | Cxxx-NCR-000057 | NCR | Lack of sound concrete in pile 4 |  | Contr |  | TCR - Tottenham Court Road Station (West) |  | 2011-10-07 | 2012-01-25 16:13 | 110 | 2011-10-03 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Less than 3m of tremie embedded in the last 5m of pile 4 during concreting this caused by lack of concrete flow, resulting pile integrity test shows lack of sound concrete within this zone. Affected zone 2.5m below cut off level.
| 02SL - Stations (LUL) | Cxxx-NCR-000059 | NCR | Insufficient length of Concrete placement tube used on pile 28. |  | Contr |  | TCR - Tottenham Court Road Station (West) |  | 2011-10-10 | 2011-12-20 16:48 | 71 | 2011-10-05 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Concrete fallen through 11.9m through any reinforcement cage.
| 02SL - Stations (LUL) | Cxxx-NCR-000060 | NCR | Controlling and Communicating of the latest drawing revisions and the register |  | Contr |  | TCR - Tottenham Court Road Station (West) |  | 2011-10-14 | 2011-10-18 12:24 | 4 | 2011-10-10 | Geotechnical Engineering - Concrete - Driven Pile | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Panel 61 cage delivered to site with the pre inspection check pack the drawing attached with the pack was incorrect revision, even though the cage fabricated and checked against he correct drawing rev 03.
| 02SL - Stations (LUL) | Cxxx-NCR-000062 | NCR | Panel 30, Use of out of spec concrete. |  | Contr |  | TCR - Tottenham Court Road Station (West) |  | 2011-10-21 | 2011-10-24 17:12 | 3 | 2011-10-14 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | One load of concrete with tkt number 598246 poured with the slump value of 245mm.
| 02SL - Stations (LUL) | Cxxx-NCR-000063 | NCR | Gel Strength Test not carried out |  | Contr |  | TCR - Tottenham Court Road Station (West) |  | 2011-10-21 | 2011-10-18 12:18 | -3 | 2011-10-14 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Equipment Breakdown | Use As-Is |  | Complete |  | Completed |  | 10MIN Gel Strength test not carried out on the followings all the LDA piles 1-39 except pile 40 and D-Wall Panels 1-8 & 12-19.
| 02SL - Stations (LUL) | Cxxx-NCR-000064 | NCR | D-Wall Panel 61 Floor slab couplers are Incorrect. |  | Contr |  | TCR - Tottenham Court Road Station (West) |  | 2011-10-24 | 2011-10-18 12:20 | -6 | 2011-10-17 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Panel 60 is constructed on the 14th of October 2011 with 32 number of 40mm couplers instead of 32mm, this cage was fabricated as per rev 01 of the above drawings on the above floor slab levels.
| 02SL - Stations (LUL) | Cxxx-NCR-000065 | NCR | Panel 62 not concreted within the specified time of 48 hours. |  | Contr |  | TCR - Tottenham Court Road Station (West) |  | 2011-10-28 | 2011-10-27 12:31 | -1 | 2011-10-21 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Equipment Breakdown | Use As-Is |  | Complete |  | Completed |  | Due to the plant breakdown panel 62 connot meet the above requirement and current condition as follows. Panel excavation commenced on the 19th at 14.45pm Top of Raft level excavation (28m from the guide wall) commenced at 19.40pm. Plant breakdown on 20th 8.00am depth at the depth of 36m on the virgin dig (2700mm) and 30m on the stop end side (750mm). Plant will be fixed and the earliest concreting will be on Monday the 24th (120hrs).
| 02SL - Stations (LUL) | Cxxx-NCR-000066 | NCR | Panel 63 not completed within 48 hours |  | Contr |  | TCR - Tottenham Court Road Station (West) |  | 2011-11-11 | 2011-11-17 17:39 | 6 | 2011-11-03 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Equipment Breakdown | Use As-Is |  | Complete |  | Completed |  | Excavation commenced on Panel 63 on Thursday 27th and excavated to the depth of 27m, at this depth we have experienced difficulity with removing the stop end, on Friday the 28th the virgin side excavated to the depth of 31m, Monday 31st up to 36m and Tuesday 1st of November panel excavated to full depth, the stop end removed and concreted on Wednesday 2nd.
| 02SL - Stations (LUL) | Cxxx-NCR-000068 | NCR | Tremie embedment length on every piles exept piles 28 and 30. |  | Contr |  | TCR - Tottenham Court Road Station (West) |  | 2011-11-25 | 2011-11-18 17:29 | -7 | 2011-11-15 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | All the LDA piles except piles 28 and 30 had the maximum embedment of more than 6m.
| 02SL - Stations (LUL) | Cxxx-NCR-000070 | NCR | Cage lift on Panel 21 |  | Contr |  | TCR - Tottenham Court Road Station (West) |  | 2011-12-02 | 2012-02-15 12:37 | 75 | 2011-11-16 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Reinforcement cage on panel 21 rised by 195 mm during concreting, top f the reinforcement and box out couplers for slab connections are higher and out of tolerance by 145mm.
| 02SL - Stations (LUL) | Cxxx-NCR-000071 | NCR | Top of steel level on Pile 39 |  | Contr |  | TCR - Tottenham Court Road Station (West) |  | 2011-11-25 | 2011-11-18 17:26 | -7 | 2011-11-16 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Top of steel as built recorded as 121.012mOD, 13mm out of tolerance.
| 02SL - Stations (LUL) | Cxxx-NCR-000072 | NCR | Bentonite testing on Pile 35 and Pile 2 |  | Contr |  | TCR - Tottenham Court Road Station (West) |  | 2011-11-25 | 2011-11-18 17:58 | -7 | 2011-11-18 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Marsh cone viscosity tested value for pile 35 was 32s and PH Value on pile 2 was 9. These two resulte does not conform with the requirements.
| 02SL - Stations (LUL) | Cxxx-NCR-000073 | NCR | Blocked Sonic Tubes on LDA Piles |  | Contr |  | TCR - Tottenham Court Road Station (West) |  | 2011-11-25 | 2011-11-18 17:24 | -7 | 2011-11-18 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | Deep cut off piles 07, 09, 10, 13, 14, 15 and 17 sonic tubes were damaged while back filling the piles. Piles 03, 26, 32, 33 and 34 one or more tubes partially blocked where sufficient testing cannot be achieved.
| 02SL - Stations (LUL) | Cxxx-NCR-000080 | NCR | Panel 36 Concrete Slump test |  | Contr |  | TCR - Tottenham Court Road Station (West) |  | 2012-01-03 | 2012-01-12 12:07 | 9 | 2011-12-05 | Geotechnical Engineering - Concrete - Driven Pile | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Two number of loads in panel 36 with the ticket numbers 599716 and 599717 was slumped 250mm, which were 10mm out of spec.
| 02SL - Stations (LUL) | Cxxx-NCR-000082 | NCR | Panel 57 Out of Spec Concrete used |  | Contr |  | TCR - Tottenham Court Road Station (West) |  | 2012-01-06 | 2012-02-08 15:52 | 33 | 2011-12-19 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Panel 57 concreted on 14-12-2011 and 6 loads of out of spec concrete poured in, the slump test values were 245mm and 260mm. information on the attached concrete pour record. On the same panel also 6 loads were rejected as high slumps.
| 02SL - Stations (LUL) | Cxxx-NCR-000084 | NCR | Concrete Testing on Grout Shaft 7 |  | Contr |  | TCR - Tottenham Court Road Station (West) |  | 2012-01-13 | 2012-01-09 17:21 | -4 | 2012-01-09 | Shafts - Excavation | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Concrete poured in the collar not have been tested.
| 02SL - Stations (LUL) | Cxxx-NCR-000085 | NCR | Cracked pre cast segmental rings |  | Contr |  | TCR - Tottenham Court Road Station (West) |  | 2012-01-16 | 2012-02-13 10:59 | 28 | 2012-01-09 | Shafts - Shafts General | 500 |  | Planning | Repair |  | Complete |  | Completed |  | Some of the rings are cracked and damaged, asbuilt survey and the locations of the these rings will be submitted.
| 02SL - Stations (LUL) | Cxxx-NCR-000087 | NCR | Site perimeter hoarding |  | Contr |  | TCR - Tottenham Court Road Station (West) |  | 2012-01-03 | 2012-02-15 12:39 | 43 | 2012-01-31 | Civil - Civil Engineering General | 500 |  | Design | Repair |  | Complete |  | Completed |  | Following investigation it was discovered that the dowel bars between the existing concrete blocks and the new beam had, in some instances, not been installed correctly, they either had been not installed with the correct embedment or fixing adhesive. Although this is suspected to have been the case on the hoarding between gate 3 and the extreme southerly section of the hoarding adjacent to the Hostel, without further investigation this can not be proven. Thus, to provide certainty to our customer (CRL) we will provide the solution detailed on every connection, new to old concrete, along the whole western side of the site, i.e. from gate 2 past gate 3 to the south end adjacent to the hostel
| 02SL - Stations (LUL) | Cxxx-NCR-000082 | NCR | Kickers cast without MCR approval |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2014-09-05 | 2014-08-27 13:38 | -9 | 2014-07-22 14:05 | Materials - Approval | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | The kickers for: Level -5 Buttress 9-EE Level -5 500 thick wall GL (5-6)-(A+4m) Were poured on 17/7/14 without CODE 1 approval of the MCRs: Cxxx-LAO-O4-LRC-N105_WS089_Z-50012 - Tying Wire Cxxx-LAO-O4-XDS-N105_WS089_Z-50009 - Concrete Design MIX 2
| 02SL - Stations (LUL) | Cxxx-NCR-000083 | NCR | MCR / ITP Approval - Lattice Planks |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2014-08-20 | 2014-08-05 16:16 | -15 | 2014-07-23 10:31 | Materials - Approval | 0 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Lattice PLanks at -5 Level in Western Ticket Hall installed without a Code 1 MCR/ITP.
| 02SL - Stations (LUL) | Cxxx-NCR-000084 | NCR | Concrete Cubes - Storage |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2014-09-04 | 2014-08-27 13:39 | -8 | 2014-07-24 10:19 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Concrete Cubes not being stored in accordance with BS EN 12390-2. Cube tank not opperational during first two concrete pours. Cubes being struck and stored under hessian sacks.
| 02SL - Stations (LUL) | Cxxx-NCR-000085 | NCR | Commencement of d-wall repairs without approved method statement or ITP |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2014-11-07 | 2014-10-15 10:09 | -23 | 2014-07-25 16:59 | Civil - Geotechnical Engineering | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | The Contractor has already commenced the repair of the d-wall panels on the -5 level without an approved method statement or ITP. The repair of d-wall panels is as a result of PMI-00165.
| 02SL - Stations (LUL) | Cxxx-NCR-000086 | NCR | Commencement of d-wall repairs utilising Brokk Drill without accepted method statement or ITP |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2014-11-07 | 2014-10-15 10:11 | -23 | 2014-08-07 14:41 | Civil - Geotechnical Engineering | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Diaphragm Wall repairs commenced utilising a Brokk Drill to alleviate the need for MEWPs and hand break out using jack hammers without an accepted Method Statement or ITP. A Task Briefing Record was produced for this work and briefed by the engineer to the operatives prior to commencement of the Method Statement compilation. The Method Statement once written was discussed with the PFE and minor amendments were made.
| 02SL - Stations (LUL) | Cxxx-NCR-000087 | NCR | Northside of Doorway in Core 4 Wall 1 (Grid Line EE-DD / 9-10) |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2014-10-09 | 2014-09-25 12:50 | -14 | 2014-08-28 11:11 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Supervision - Other | Completed |  | The north side of the doorway in core 4 wall 1 (grid lineEE-DD/9-10) has been cast too far north by 40mm.
| 02SL - Stations (LUL) | Cxxx-NCR-000088 | NCR | Core 4 Wall at the North of the Vent Opening cast with a 25mm Step 700mm above slab level |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2015-02-13 | 2015-03-06 14:04 | 21 | 2014-08-28 14:44 | Civil - Civil Engineering General | 1000 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The wall at the north of the vent opening in core 4 has been cast with a step of 25mm in it at a position of 700mm above the slab level. The sketches attached show location, as-built position and photograph of the wall.
| 02SL - Stations (LUL) | Cxxx-NCR-000089 | NCR | CH1 reinforcement dowel bars through waterproofing layer |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2014-11-21 | 2014-11-03 12:04 | -18 | 2014-09-03 17:51 | Civil - Civil Engineering General | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | The Contractor, in following the Code 1 approved reinforcement drawing for CH1 lining wall collar dowel bars (Cxxx-LAO-C-DWG-N105_WS089_6-50089) has drilled through, what appears to be, the Vandex Flextape positioned on the external face of the diaphragm wall. The site engineers instructed the operatives to commence drilling for dowel bars, following the Code 1 status drawing and Method Statement (Cxxx-LAO-O1-GMS-N105_WS089-50003), however the engineers were alerted by the operatives when the material was struck. In response to this, the site engineers reviewed the reinforcement drawing stated above and found that bars were detailed through the Vandex location. The works were then stopped with 4no. bars drilled, no further drilling took place.
| 02SL - Stations (LUL) | Cxxx-NCR-000090 | NCR | Blocked Geothermal Loops in Piles P30 and P31 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2014-09-19 | 2014-09-08 15:30 | -11 | 2014-09-05 14:46 | Civil - Civil Engineering General | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Previous Construction - Problems based on previous construction errors | Completed |  | Cxxx have encountered blockages on 3no. loops on pile 30 and 3no. Loops on pile 31. In accordance with G I Energy procedure Cxxx have attempted: -flushing -using compressed air -using the ‘Cobra’ system to attempt to clear the pipes.
| 02SL - Stations (LUL) | Cxxx-NCR-000091 | NCR | TC3 Base Poured without eB approval |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2014-09-24 | 2014-09-15 15:17 | -9 | 2014-09-10 10:31 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | The TC3 base foundation has been poured without the relevant design approval on eB. The TCR-EDB-161 which applies to the lowering of the base by 300mm to avoid permanent works was agreed in a meeting held on 11/8/14 with: Cxxx - __ Cxxx - __ Cxxx - __ CRL - __ The design brief was submitted on 8/8/14 The design calculations were submitted on 11/8/14
| 02SL - Stations (LUL) | Cxxx-NCR-000092 | NCR | WTH Core 4 wall reinforcement lap length too short GL DD/9 -5 to -4 level |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2014-09-30 | 2014-09-29 14:40 | -1 | 2014-09-16 07:45 | Structural Engineering - Reinforcement | 500 |  | Manufacturing Defect | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Whilst constructing Core 4 walls at -5 to -4 and using __ Pull out bars (used for reinforcement continuity), the Contractor has determined that 4no. B12 horizontal bars are short by 70mm with bar lengths at 680mm rather than the specified 750mm (drawing Cxxx-LAO-C-DWG-N105_WS089_6-50094). Bars are located in the upper quarter of the wall height, with 2no. FF1 and 2no. NF1. Bar lap lengths have assumed 'poor bond' conditions.
| 02SL - Stations (LUL) | Cxxx-NCR-000093 | NCR | Plastic Cube Moulds |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2014-10-03 | 2014-11-27 11:04 | 55 | 2014-09-16 11:30 | Civil - Civil Engineering General | 0 |  | Material | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | During a planned Crossrail surveillance it was noted that the Contractor was using plastic cube moulds. A post review found that the plastic moulds did not comply with the Company procedure Cxxx-LAO-O7-GMS-N105_WS089_Z-50003 rev 2.0 section Making and Curing Specimens for Strength Tests states; “The moulds must be steel or cast iron, never of wood or polystyrene. A cube mould is usually in two halves that are bolted together and fastened by clamps to a metal base plate”.
| 02SL - Stations (LUL) | Cxxx-NCR-000094 | NCR | Temporary Works Design for Diadem Court Cabins |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2014-10-22 | 2014-10-15 11:49 | -7 | 2014-09-25 12:12 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | Temporary Works Design for Diadem Court site cabin foundations (Cxxx-LAO-Y-XCL-N105_WS089_Z-50066 Rev 1.0) was submitted on 5th September 2014 and returned Code 3 on 29th September 2014. No Design Brief has been submitted for these works, as required by WI Vol 2B Cl 22.5. Work has commenced on site prior to acceptance of the Temporary Works Design, as required by WI Vol 2B Cl 22.4.
| 02SL - Stations (LUL) | Cxxx-NCR-000095 | NCR | Shear Studs - Incorrect MCR submitted |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2014-11-10 | 2014-10-15 11:45 | -26 | 2014-09-29 09:08 | Structural Engineering - Steel Member | 2500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Structural Steel members used within the series of trusses and composite columns at the Western Ticket Hall require a series of Shear Studs. The Shear Studs Material Compliance Record (MCR) that was submitted and accepted is not the same as the Shear Studs currently contained on the steel members. The accepted Shear Studs are Scholer & Bolte and the Shear studs on site currently are from Tru-Weld.
| 02SL - Stations (LUL) | Cxxx-NCR-000097 | NCR | Tunnel S4 opening oversized - inherited from others |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2014-11-11 | 2015-01-08 10:54 | 58 | 2014-10-28 14:06 | Civil - Drainage | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Previous Construction - Other | Completed |  | The Contractor, Cxxx, upon handover of the tunnel opening has set out where the opening should be. It has become apparent that the opening is oversized, as can be seen from the attached photo. After the engineering issues meeting on 28 October 2014 it was agreed that the Contractor would mass fill this resulting gap. One of the affects of this change is on the waterproofing detail; this now cannot sit on the face of the diaphragm wall as there is no wall to place it onto. Therefore the __ product must sit within the arch. Cxxx will need to inspect and approve this installation prior to pouring.
| 02SL - Stations (LUL) | Cxxx-NCR-000098 | NCR | Temporary Works Design TCR-EDB-174 |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2014-12-09 | 2015-08-07 12:50 | 241 | 2014-11-25 16:40 | Structural Engineering - Structural Engineering - General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Temporary Works Design TCR-EDB-174 Rev 1.0 submitted on 27/10/2014 includes a copy of Engineering Design Brief EDB-174 Rev 1.0 which does not match the version accepted by the Project Manager and held on eB (also at Rev 1.0). In particular the version included with the design submission is unsigned and states that a Cat 1 check is required, whereas the approved version is signed and states that a Cat 2 check is required. It is unclear whether there are any other differences between the two versions. Works Information Vol 2B Clause 22.6 states that 'The Contractor’s design of a Temporary Works scheme shall base the design on the design brief accepted by the Project Manager'.
| 02SL - Stations (LUL) | Cxxx-NCR-000099 | NCR | Starter bars bent horizontally around insufficent radius |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2015-01-15 | 2015-06-02 09:11 | 138 | 2014-11-28 15:27 | Structural Engineering - Reinforcement | 1000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | The Contractor wishes to inform the PM that the 36no B12 starter bars, cast into the -5 UPD trench covering slab, detailed on drawing Cxxx-LAO-C-DWG-N105_WS089_6-50095, have been bent over to allow for plant mobility throughout CH1 lining wall construction. This was an oversight by the Contractor at time of detailing, with coupler bars a better option. This NCR replaces FCD 163.
| 02SL - Stations (LUL) | Cxxx-NCR-000100 | NCR | WTH - wall 2 WTH level -5 reduced cover GL10 DD-EE |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2014-12-17 | 2015-01-08 09:30 | 22 | 2014-12-03 15:04 | Civil - Civil Engineering General | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Management Problem - Inadequate supervision | Completed |  | One of the internal walls of core 4 on GL10 between DD and EE has been poured with reduced cover on the Northern face, see attached photos
| 02SL - Stations (LUL) | Cxxx-NCR-000101 | NCR | Masterseal damage at the rear of PTE |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2015-01-28 | 2015-01-08 10:29 | -20 | 2014-12-03 15:03 | Civil - Civil Engineering General | 5000 |  | Damaged | Repair | 3 (3-6k) | Complete | Supervision - Insufficient supervision | Completed |  | The Masterseal cover to the vandex strip at the rear of the PTE liner wall (inside the tunnel opening) was damaged at the crown by __ during the removal of the rear shutter. The Vandex strip is in the joint between the SCL and D-wall. The rubber protective strip over the Vandex strip is still in place and in-tact. A marked up copy of drawing Cxxx-OVE-S-DDD-N105_Z-24327 attached shows the areas in which the Masterseal was damaged. Photos PTE_001 to 004 show the extent of the damage.
| 02SL - Stations (LUL) | Cxxx-NCR-000102 | NCR | PTE Opening Size |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2015-01-28 | 2015-03-27 09:39 | 58 | 2014-12-03 15:31 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The opening size of PTE was cast using a RMD/Cordek drum shutter. Due to the complicated nature of the opening and the shutter it was extremely difficult to get the shutter in exactly the correct position. A best fit was achieved, however the opening is out of tolerance in places. A highlighted copy of the as-built of the opening is attached with the out of tolerance dimensions highlighted.
| 02SL - Stations (LUL) | Cxxx-NCR-000103 | NCR | -5 to -4 Composite column concrete cover |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2014-12-19 | 2015-02-03 14:33 | 46 | 2014-12-05 13:15 | Structural Engineering - Concrete Member | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Previous Construction - Other | Completed |  | Concrete cover for the -5 to -4 composite column, GL 8/D/C, was found to be excessive to an extent of 40mm. The Contractor therefore positioned additional B20 vertical bars in front of the horizontal links to reduce the cover down to 50mm (maximum). The Contractor requests confirmation that this is satisfactory and that no further action is required?
| 02SL - Stations (LUL) | Cxxx-NCR-000104 | NCR | Level -4 Service Riser Doorway GL 9.5-10/DD |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2015-12-31 | 2016-01-05 11:18 | 5 | 2014-12-23 11:09 | Civil - Civil Engineering General | 5000 |  | Supervision/Management | Repair | 3 (3-6k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | The level -4 slab has been cast with the door way starter bars in the wrong place, please see the attached sketch showing the existing location highlighted in red of the doorway after main slab poured.
| 02SL - Stations (LUL) | Cxxx-NCR-000105 | NCR | Wall 9 - Kicker |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2015-02-19 | 2015-02-04 08:38 | -15 | 2015-01-08 10:23 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Wall 9 kicker was cast without the Rookwool between S4 and Wall 9, frost blanket was used instead. The position of this is shown in the attached annotated sketch extracted from drawing Cxxx-OVE-S-DDA-N105_6-21123.
| 02SL - Stations (LUL) | Cxxx-NCR-000106 | NCR | Omission of 1no coupler bar for -4 slab tie into CH1 lining wall |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2015-02-05 | 2015-02-05 09:07 | 0 | 2015-01-08 14:16 | Civil - Civil Engineering General | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Previous Construction - Problems based on previous construction errors | Completed |  | Following a conversation with Cxxx, the Contractor wishes to confirm the omission of 1no B20 coupler bar into the CH1 lining wall at -4 level GL DD/10 due to a defective cast in female coupler.
| 02SL - Stations (LUL) | Cxxx-NCR-000107 | NCR | WTH - S4 tunnel opening poured 200mm short of crown |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2015-01-26 | 2015-01-20 14:34 | -6 | 2015-01-12 16:06 | Civil - Civil Engineering General | 2000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The final pour of the tunnel opening S4 has resulted in the concrete being poured up to 200mm too low, at the centre of the crown. This was the result of the uneven surface being cast against making it difficult to seal the shutter. The opening is 200mm high at the centre of the crown, 1800mm wide and 250mm deep.
| 02SL - Stations (LUL) | Cxxx-NCR-000108 | NCR | WTH - Service Opening in Wall 9 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2015-03-12 | 2015-02-09 08:43 | -31 | 2015-01-15 08:22 | Civil - Civil Engineering General | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | The service opening in Wall 9, see attached drawing showing exact location (Cxxx-OVE-S-DDA-N105_6-21123 and extract from Cxxx-OVE-S-DDC-N105_Z-22155), has been cast with a 20mm step in the wall. This is due to the movement of the box out shutter during the pour. Upon carrying out a dimensional as-built for the box out the top and bottom of the opening are in the correction position however the middle of this side is out. See attached photograph
| 02SL - Stations (LUL) | Cxxx-NCR-000109 | NCR | Cut starters GL B / 9 (14 No.) |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2015-03-13 | 2015-02-26 13:38 | -15 | 2015-01-16 16:41 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | starters from the top of the wall along GL B / 9 at level -5 above the doorway have been cut to allow access to the carpenters to erect the deck.
| 02SL - Stations (LUL) | Cxxx-NCR-000111 | NCR | WTH - Concrete finishing to rear of S4 tunnel opening |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2015-02-04 | 2015-01-26 14:51 | -9 | 2015-01-21 08:50 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | After striking the shutter at the rear of S4 it was noticed that there were some imperfections in the concrete finish, see attached photos. It was agreed to leave this in the current state as the follow on contractor will be applying a sprayed concrete finish to this area.
| 02SL - Stations (LUL) | Cxxx-NCR-000113 | NCR | CH1 High Couplers into -4 slab |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2015-03-25 | 2015-03-31 14:10 | 6 | 2015-01-28 13:48 | Civil - Civil Engineering General | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 15No couplers were cast too high, approximately 20mm, and would reduce the cover of the slab
| 02SL - Stations (LUL) | Cxxx-NCR-000114 | NCR | Non Approved Concrete Mix Used |  | Crossrail | PDP | TCR - Tottenham Court Road Station (West) |  | 2015-02-12 | 2015-03-27 09:38 | 43 | 2015-01-29 12:12 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | Self Compacting Concrete was used for -4 levels walls to core 4 on 22 January 2015. This was not an approved mix. The MCR for the mix had been returned Code 3 on 13 January 2015.
| 02SL - Stations (LUL) | Cxxx-NCR-000115 | NCR | Records |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2015-03-26 | 2015-04-21 14:18 | 26 | 2015-01-29 13:08 | Civil - Civil Engineering General | 1000 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Personnel Error - Other human error | Completed |  | During a planned CRL led surveillance,whilst witnessed the concrete placement on core wall 4, it was noted that in a number of places on the East elevation, tying wire was encroaching into the concrete cover area, It was also noted that on the West elevation several vertical lengths of reinforcement were not adequately tied and out of position. ITP Cxxx-LAO-O4-ITP-N105_WS089_Z-50001 item 5.1.11 pre pour inspection record document number Cxxx-LAO-XXX-T-00011 had been signed off with outstanding defects.
| 02SL - Stations (LUL) | Cxxx-NCR-000116 | NCR | concrete placement |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2015-02-12 | 2015-08-24 13:23 | 193 | 2015-01-29 13:04 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Whilst witnessing the concrete placement on core walls 4, it was noted that the pipe attached to the concrete skip was approximately 3.0 m long and the wall pour height 6m; thus on the initial placement, the concrete was free falling in excess of 2.5 m which is outside of the maximum 2 m stated in method statement
| 02SL - Stations (LUL) | Cxxx-NCR-000117 | NCR | Storage of concrete Cubes |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2015-02-12 | 2015-06-17 08:32 | 125 | 2015-01-29 13:19 | Civil - Civil Engineering General | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | During a planned CRL led surveillance the Contractor stated that the cube storage facility had been moved but had no power at this time, as a result the concrete test cubes for the Core 4 wall pour will be wrapped in hessian and stored in the staff drying room. On inspection of the drying room it was found that the temperature of the room was not regulated and extremely hot.
| 02SL - Stations (LUL) | Cxxx-NCR-000119 | NCR | WTH - Buttress B3 Level -4 to -3 GL EE/10 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2015-02-12 | 2015-02-02 15:59 | -10 | 2015-01-29 15:06 | Civil - Civil Engineering General | 1000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | The reinforcement drawing states that there should be a 1500mm lap of the 32mm reinforcement bars in buttress B3 on GL 10/EE as highlighted on the attached drawing. The measure on site shows only 1350 is left protruding.
| 02SL - Stations (LUL) | Cxxx-NCR-000120 | NCR | Eazistrip in Core 4 construction joints for walls W6 and W7 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2015-03-27 | 2015-02-09 16:14 | -46 | 2015-01-30 13:24 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Not Defined | Completed |  | Eazistrip in Core 4 construction joints for walls W6 and W7 12mm starters are too short to get correct splice. -4 slab level GL 9 – DD. Starters bars are 300mm long and splice needs to be a minimum of 450mm
| 02SL - Stations (LUL) | Cxxx-NCR-000121 | NCR | WTH - Circular columns GL B 7.5, 8.5 + 9 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2015-02-16 | 2015-03-04 14:35 | 16 | 2015-02-02 15:58 | Civil - Civil Engineering General | 5000 |  | Supervision/Management | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The circular columns along GLB 7.5, 8.5 and 9 are scheduled as 850mm diameter columns for the lower 2600mm, above SSL, and then 900mm diameter above this point. The reinforcement has been installed incorrectly for a 900mm diameter column for the entire column. There are spots where the cover is as low as 16mm to the main bar, which could mean 0mm cover after the concrete has been cast.
| 02SL - Stations (LUL) | Cxxx-NCR-000122 | NCR | WTH - Buttress B1 reduced cover level -4 GL A |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2015-02-19 | 2015-02-09 17:21 | -10 | 2015-02-05 16:59 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The 2No B1 type buttresses on GL A / 7.5 and 8.5 both have reduced cover on the East face. There is 45mm cover to the main 40mm reinforcement within the buttress. Once the link has been installed this will be reduced to 29mm.
| 02SL - Stations (LUL) | Cxxx-NCR-000123 | NCR | WTH - CH1 - Couplers Installed |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2015-04-06 | 2015-02-26 09:38 | -39 | 2015-02-09 14:19 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | CH1 Concrete Wall - Couplers installed not in accordance to the design.
| 02SL - Stations (LUL) | Cxxx-NCR-000124 | NCR | PTE GL8 Concrete Wall |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2015-04-06 | 2015-04-07 11:10 | 1 | 2015-02-09 14:24 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | PTE GL8 Concrete Wall - Couplers installed not in accordance to the design.
| 02SL - Stations (LUL) | Cxxx-NCR-000125 | NCR | Core 4 Chamfers |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2015-04-07 | 2015-02-25 17:05 | -41 | 2015-02-10 11:22 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Core 4 Chamfers omitted as required in drawing Cxxx-OVE-S-DDD-N105_Z-44003
| 02SL - Stations (LUL) | Cxxx-NCR-000126 | NCR | WTH Level -5 - South East Corner - Buttress |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2015-07-31 | 2015-06-15 14:38 | -46 | 2015-02-11 11:18 | Civil - Civil Engineering General | 2000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Level -5 SE Corner Buttress should be isolated from the diaphragm wall, dywidag bars in the buttress prevent this. Dywidag bar left in place negates the independence of the buttress and the diaphragm wall. The dywidage bar has also been cut off flush with the wall and requires remedial work.
| 02SL - Stations (LUL) | Cxxx-NCR-000127 | NCR | Small level of breaking out of platform wall to accomodate platform wall / shear dowels -4 level WTH |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2015-03-06 | 2015-03-31 14:09 | 25 | 2015-02-20 09:14 | Structural Engineering - Concrete Member | 5000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Due to an error made on site with the setting out, of the 250mm thick platform support wall at -5 to -4 level (GL 7/A-B) where it interfaces with the -4 700mm propping slab, we need to carry out a small amount of concrete breaking out to accommodate the 700mm slab and shear dowels required at the top of the wall. What this means is that we need to cut back reinforcement beyond the movement joints and treat accordingly.
| 02SL - Stations (LUL) | Cxxx-NCR-000128 | NCR | fresh concrete testing training |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2015-10-31 | 2015-10-14 10:18 | -17 | 2015-02-20 10:37 | Civil - Civil Engineering General | 1000 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Training Deficiency - No training provided | Completed |  | A post surveillance review of the training records for the Contractor responsible for the slump flow test was carried out during the surveillance, found the operative had been trained to BS EN 12350; 2009/2010 parts 1, 2, 5 and 8, sampling, slump, flow, slump-flow and cube manufacture by __ (UKAS accreditation number 2581). On reviewing the accreditation schedule for __ (UKAS accreditation number 2581), found that the testing facility is not accredited for slump flow testing of fresh concrete and as such not able to train for this activity. The Contractor made a proposal, to utilise his own staff to carry out the on site concrete testing, submitted under CCM-733. The Project Manager accepted the Contractor's proposal submitted under Cxxx-PMC-00855 quoting Works Information Volume 2B - Clause 20.8; The Project Manager accepts the Contractor's proposal, submitted under CCM-733, to utilise his own staff to carry out the on site concrete testing. This acceptance is made on the basis that those persons will be accredited to UKAS or a similar standard and that accreditation will be appropriately maintained. The Contractor is to keep evidence of all those trained and provide that evidence to the PM. The PM will monitor the Contractor's progress on site during his regular site visits to ensure the testing is being carried out in accordance with the requirements of the Contract. It must be noted that as the __ site personnel do not form part of the __ UKAS laboratories staff, the site persons will not be UKAS accredited under the __ schedule, only trained by UKAS accredited persons. As such, the __ UKAS laboratory should seek to maintain a schedule of re-assessment dates for all site personnel trained
| 02SL - Stations (LUL) | Cxxx-NCR-000129 | NCR | ITP for Platform and Tunnels Dowel Bar Drilling and Installation |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2015-04-21 | 2015-04-01 09:01 | -20 | 2015-02-24 12:49 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | ITP - Cxxx-LAO-O4-ITP-N105_WS089_Z-50008 - Platform and Tunnels Dowel Bar Drilling and Installation was submitted on 12th February 2015. Work subsequently commenced on site without the ITP being accepted.
| 02SL - Stations (LUL) | Cxxx-NCR-000130 | NCR | -4 Circular column (bottom portion) GL 9/B excessive concrete blow holes |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2015-07-31 | 2015-07-06 17:14 | -25 | 2015-02-27 10:28 | Structural Engineering - Concrete Member | 2000 |  | Material | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Following the removal of the circular column shuttering, required to form the bottom portion of the composite column upon GL 9/B, the Contractor discovered that many blow holes were present on the face (see photos attached) and due to entrapted air against the shutter. The concrete used was a self compacting (SCC) mix, which is designed to not need vibrating. The mix was tested on site by the Contractors concrete technision at the time of the load being dispatched into the skip. As the mix was SCC, a slump/ flow test is required, with a SF2 class specified. In accordance with EN 12350-8, the diameter of the flow required was 660 to 750mm. 660mm was mesured by the Contractors concrete technition and recorded prior to the concrete being used
| 02SL - Stations (LUL) | Cxxx-NCR-000131 | NCR | WTH -4 level soffit cracking (GL A-B/10-9) |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2015-03-31 | 2015-04-07 15:25 | 7 | 2015-03-02 09:52 | Structural Engineering - Concrete Member | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Following the pouring (and formwork striking) of -4 level propping slab GL A-B/9-10 using concrete MIX 1 (Cxxx-LAO-O4-XDS-N105_WS089_Z-50008), the Contractor has discovered several cracks (<1mm wide) running diagonally from slab supports (see attached plot). This appears to be due to shrinkage. Water has been leaking through the cracks due to the -4 SSL being temporarily exposed to the wet weather.
| 02SL - Stations (LUL) | Cxxx-NCR-000132 | NCR | Acoustic Design Statement inputs and outputs not complete |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2015-03-19 | 2015-08-12 12:32 | 146 | 2015-03-05 08:08 | Communications and Control Systems - Public Address Systems | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | Platform Tunnels Fit Out Acoustic Design Statement Cxxx-LAO-M-XST-N105_WS089-50006 rev 2.0 documents only 7 out of the 20 requirements for inputs and outputs specified by WIv2B part 7.7.3
| 02SL - Stations (LUL) | Cxxx-NCR-000133 | NCR | Comprehensive design programme |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2015-03-19 | 2015-08-21 08:50 | 155 | 2015-03-05 08:17 | Communications and Control Systems - Public Address Systems | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The requirement of WIv2B part 7.5.1 is for the Contractor to submit a comprehensive design programme and maintain it.Programme Cxxx-LAO-M-XST-N105_WS089-50001 revision 34 did not documnet the acoustic design activity.
| 02SL - Stations (LUL) | Cxxx-NCR-000134 | NCR | Software validation |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2015-03-19 | 2015-09-02 12:55 | 167 | 2015-03-05 08:28 | Communications and Control Systems - Public Address Systems | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | WIv2B part 20.2 specifies; “The Quality Management System is to be capable of demonstrating by Contractor self certification that all the requirements of the contract and all relevant standards, regulations etc. are being met.” It could not be demonstrated that the Acoustic Modelling Software was validated.
| 02SL - Stations (LUL) | Cxxx-NCR-000135 | NCR | Design Competency |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2015-03-19 | 2015-08-21 09:00 | 155 | 2015-03-05 08:37 | Communications and Control Systems - Public Address Systems | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The Contractor maintains duly signed competency assessment records .Records were only avaialbe for one of the two acoustic engineers. The requirement is defined in Works Information volumne 2B part 7.1.4 " evidence that design has been prepared by experienced and competent staff"
| 02SL - Stations (LUL) | Cxxx-NCR-000136 | NCR | Testing light drums |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2015-03-19 | 2015-09-08 09:45 | 173 | 2015-03-05 08:42 | Communications and Control Systems - Public Address Systems | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | RIBA Stage E :Station Acoustics Cxxx-OVE-E-RGN-N105-00010 rev 1.0 clause 4.3 Light Drums specifies “Current architectural designs are for drums of the following dimensions: TCR West Ticket Hall = 800mm diameter x 1000mm heightLevel -1 Concourse = 800mm diameter x 300mm height TCR East Level -1 Concourse = 800mm diameter x 300mm height Each drum variant will be tested in an acoustic laboratory to measure sound absorption performance.” In lieu of the above tests the drum sink was tested in flat configuration (Cxxx – Acoustic Modelling Progress Report - Ticket Halls and Platform Areas Cxxx-LAO-T1-RGN-N105_WS089_Z-50005 rev 1.0 refers).
| 02SL - Stations (LUL) | Cxxx-NCR-000138 | NCR | Circular Column GLB-9 - Concrete Finish |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2015-09-21 | 2015-07-21 13:40 | -62 | 2015-03-10 11:59 | Civil - Civil Engineering General | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | Concrete finish (blowholes) to Column located at GLB-9
| 02SL - Stations (LUL) | Cxxx-NCR-000139 | NCR | CH1 Spine Wall Opening Opposite AP1 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2015-06-30 | 2015-06-22 14:21 | -8 | 2015-03-10 14:24 | Civil - Civil Engineering General | 2000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A section of the CH1 Spine Wall kicker (100mm high) opposite AP1 has been cast where an opening in the wall occurs (see attached sketch Cxxx/ENG/SK/141). Detail H in Drawing Cxxx-OVE-S-DDB-N105_Z-43002 shows 2No openings (2500 x 1100mm each) from tunnel base slab level. These openings did not get detailed on the reinforcement detailing drawing (Cxxx-LAO-C-DWG-N105_WS089_6-50053), which had been accepted Code 1.
| 02SL - Stations (LUL) | Cxxx-NCR-000141 | NCR | WTH - Core 1 poor quality concrete on some panels |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-05-31 | 2016-05-16 15:56 | -15 | 2015-03-16 13:34 | Civil - Civil Engineering General | 5000 |  | Workmanship | Rework | 3 (3-6k) | Complete | Management Problem - Inadequate supervision | Completed |  | After striking the shutters for core 1 on the WTH it has become apparent that some of the concrete is not of the required standards with large numbers of blow holes present on some panels.
| 02SL - Stations (LUL) | Cxxx-NCR-000142 | NCR | PTE GL:6-7 Concrete Wall - Concrete cover 130 mm |  | Crossrail | PDP | TCR - Tottenham Court Road Station (West) |  | 2015-03-30 | 2015-03-25 14:05 | -5 | 2015-03-16 16:05 | Civil - Civil Engineering General | 1000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | PTE GL:6-7 Concrete Wall - Concrete cover 130 mm Excessive cover to face of Headwall.
| 02SL - Stations (LUL) | Cxxx-NCR-000143 | NCR | Running Tunnel : Excessive Cover to Concrete Wall. |  | Crossrail | PDP | TCR - Tottenham Court Road Station (West) |  | 2015-03-30 | 2015-04-17 08:31 | 18 | 2015-03-16 16:17 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | RT- Running Tunnel Concrete Wall - Shutter had excessive coverat 85 mm. Also incorrect sized spacers fitted to face rebar. Refer to item 31 in Piotr's tracker
| 02SL - Stations (LUL) | Cxxx-NCR-000144 | NCR | Damage to -2 under slab drainage pipe due to Windpost starter bar drilling |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-06-30 | 2016-06-13 12:54 | -17 | 2015-03-17 19:03 | Civil - Drainage | 10000 |  | Damaged | Rework | 2 (6-60k) | Complete | Previous Construction - Interfacing issues | Completed |  | The Contractor has inadvertently damaged a drainage pipe located within the -2 raft slab immediately below a reinforced concrete windpost located upon GL B/2-3. The Contractor was drilling into the -2 raft slab to install starter bars required for an RC windpost. The size of the hole drilled was 18mm in diameter. Whilst drilling, resistance to the drill suddenly stopped and the drill dropped down through what appeared to be a void in the slab. The drill was extracted where water then filled the hole. The Contractors site engineer then reviewed drawings and determined that a 100mm diameter drainage pipe was present below at an approximate depth of 250mm (to pipes crown).
| 02SL - Stations (LUL) | Cxxx-NCR-000145 | NCR | NCR review |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2015-07-31 | 2015-06-17 08:44 | -44 | 2015-03-24 09:44 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | During the post preparation the NCR’s from the previous quality surveillance QS422-04 (22/01/2015), eB document number Cxxx-XRL-O4-RGN-CR001-50004 rev 01 were reviewed and found; Cxxx-NCR-000117 raised 29/01/2015 had not been actioned. NCR Details The Contractor stated that the Concrete compression test cube sample storage facility had been moved but had no power at this time, as a result the concrete test cubes for the Core 4 wall pour will be wrapped in hessian and stored in the staff drying room. On inspection of the drying room it was found that the temperature of the room was not regulated and extremely hot. During the surveillance the facility for the storage of Concrete compression test cube samples was inspected and found; the cubes have been stored in a cupboard along with concrete testing equipment and empty moulds. The cupboard, which was situated in the Dean Street loading area, was not insulated and the temperature could not be regulated, as such, it is susceptible to temperature fluctuation. It was also noted that the cube specimens had not been stored as per the Contractors procedure Cxxx-LAO-O7-GMS-N105_WS089_Z-50003 Rev 6.0 appendix C Curing of test pieces
| 02SL - Stations (LUL) | Cxxx-NCR-000146 | NCR | calibration of plastic cube moulds |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2015-04-21 | 2015-04-24 10:31 | 3 | 2015-03-24 09:54 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | During a post review of concrete cube compressive strength testing reports issued by __, and supplied by the Contractor, found that there is no evidence that dimensional checks have been carried out to ensure dimensional compliance of the plastic cubes that are in use on site. This requirement is detailed under FCD 130 that formed part of the close out of NCRCxxx-NCR-000093 FCD 130 Detail: “The Contractor intends to utilise Plastic Cube Moulds in their works, in accordance with BS EN 12390-1:2012 Testing Hardened Concrete Part 1: Shape, dimensions and other requirements for specimens and moulds. Clause 5.1.2 states “Moulds, other than calibrated moulds in accordance with 5.2, may be made from any material which is suitable for producing concrete specimens”. Clause 5.2.1 states: “Calibrated moulds shall be made of steel or cast-iron, which shall be the reference materials. If moulds are manufactured from other materials, in-use performance test data shall be available which demonstrates long-term equivalence with steel or cast-iron calibrated moulds” FCD 130 Proposed Answer: “The moulds will be checked upon arrival to the works to ensure initial dimensional compliance and thereafter the reports on compressive strength testing will identify the dimensions of the specimen thus indicating dimensional compliance and in-use performance data as required by BS EN 12390-1:2012.
| 02SL - Stations (LUL) | Cxxx-NCR-000147 | NCR | CON-103 Fairfaced Concrete Cylindical Column located -4 level Gridline 9B |  | Crossrail | PDP | TCR - Tottenham Court Road Station (West) |  | 2016-01-31 | 2016-02-18 08:03 | 18 | 2015-03-24 14:29 | Architectural - General | 5000 |  | Workmanship | Rework | 3 (3-6k) | Complete | Supervision - Not Defined | Completed |  | Column should be to CON-103 Fairfaced concrete. Referring to Architectural Specification Cxxx-OVE-A-XDS-N105-50009. The column does not achieve the requirements of: JE20:1206 sections b)iii, b)iv, b)vi ,b)xii, d), e)iii, e)iv, e)v, e)vi, and h)iv. JE20.1404 sections a), b), c), d) and f). It should be noted that there is no accepted benchmark for these works. The submitted benchmark exhibiting most of the problems of this finished column.
| 02SL - Stations (LUL) | Cxxx-NCR-000148 | NCR | ITP Not Followed: Material Approval Required. |  | Crossrail | PDP | TCR - Tottenham Court Road Station (West) |  | 2015-06-30 | 2015-06-22 11:37 | -8 | 2015-03-25 17:09 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Works installing Combined Spacer Blocks to the -1 slab were carried out without the MCR being approved to Code 1. The works were started on or before 16 March, the MCR was returned Code 2 on 20th March. It should also be noted that the spacers have not been installed in accordance with the spacing that was detailed in communications between __ and Alex Fleming on 18 March which was an undertaking to space them at 500mm which enabled the spacers to be approved.
| 02SL - Stations (LUL) | Cxxx-NCR-000149 | NCR | AP2W Corbel - 135mm too long through SMJ |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2015-04-10 | 2015-04-15 11:07 | 5 | 2015-03-27 08:35 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | The Corbel on the West face has been cast 135mm to long through the SMJ (See attached Drawing)
| 02SL - Stations (LUL) | Cxxx-NCR-000150 | NCR | -4 to -3 level Buttress B6 GL 9/A |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2015-07-31 | 2015-05-15 15:04 | -77 | 2015-03-30 14:31 | Structural Engineering - Reinforcement | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | The Contractor has determined a reduced lap length with B40 starter bars within the -4 to -3 buttress (B6) located upon GL 9/A. The length of the lap is 1945mm, rather than the specified 2025mm length shown on drawing Cxxx-LAO-C-DWG-W105-WS089_5-50001 C02. Please can confirmation be given on whether the 80mm reduction is satisfactory in this instance?
| 02SL - Stations (LUL) | Cxxx-NCR-000151 | NCR | Structural Cracks on Track foundation Slabs - PTE |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-02-20 | 2016-02-09 10:24 | -11 | 2015-04-02 14:52 | Structural Engineering - Concrete Member | 10000 |  | Design | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Other | Completed |  | The track foundation slabs (bays 1 and 2) poured in the Eastbound tunnel have exhibited signifcant cracking in both the top surface and in some cases these propogate through to the wall. Some of the cracks on the top surface of the track foundation are in excess of 1mm wide. Cracks started to appear approximately 24 hours after each pour and have been increasing in width since. The Contractor attaches thermal maturity information for the pour, as well as a survey of the most significant cracks (those which extend across the full width of the slab and onto the face of the wall) and photos of some of the cracks.
| 02SL - Stations (LUL) | Cxxx-NCR-000152 | NCR | Concrete Cube Storage |  | Crossrail | PDP | TCR - Tottenham Court Road Station (West) |  | 2015-07-31 | 2015-06-15 14:45 | -46 | 2015-04-07 13:46 | Civil - Civil Engineering General | 5000 |  | Supervision/Management | Rework | 3 (3-6k) | Complete | Management Problem - Other | Completed |  | Cubes continue not to be stored in accordance with BS EN 12390-2. NCR 000084, 000117, 00145 also refer to this subject.. Cubes are being struck and left dry on the shelf for periods up to 7 days. There is no Cube tank. The cube 'hut' has a heater and a thermometer, but there is no control over temperature.
| 02SL - Stations (LUL) | Cxxx-NCR-000153 | NCR | Concrete CON 104 |  | Crossrail | PDP | TCR - Tottenham Court Road Station (West) |  | 2015-12-31 | 2016-01-26 14:45 | 26 | 2015-04-07 17:15 | Civil - Civil Engineering General | 10000 |  | Workmanship | Rework | 2 (6-60k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Core 2 -4 to -3 level concrete does not comply to CON-104 specification, including, but not inclusive of JE20.1207 b) i), ii), iii), vi), vii), viii), ix), x), xi), xii), xiii) c), d) i), ii), iii), iv), v), vi), vii), viii), ix), x), xi), xii), xiii), xiv).
| 02SL - Stations (LUL) | Cxxx-NCR-000154 | NCR | Concrete Placement: Excessive freefall. |  | Crossrail | PDP | TCR - Tottenham Court Road Station (West) |  | 2015-07-31 | 2015-08-24 13:18 | 24 | 2015-04-09 13:22 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | While carrying out the inspection to close out NCR 000116 concerning measures to prevent excessive freefalling of concrete, we observed the column at Gridline 6/B was being concreted. We noted that concrete was being freefalled from an excessive height of approximately 4.0 to 4.5m where the maximum allowed is 2.0m.
| 02SL - Stations (LUL) | Cxxx-NCR-000155 | NCR | Concrete Delivery: Out of Time |  | Crossrail | PDP | TCR - Tottenham Court Road Station (West) |  | 2015-07-03 | 2015-07-02 09:02 | -1 | 2015-04-09 15:43 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Concrete delivery 8 April 2015 Batched 11.31 had exceeded the allowable time from batching when discharge did not start until 13.35.
| 02SL - Stations (LUL) | Cxxx-NCR-000156 | NCR | CH1 crown - excessive crack widths |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-01-31 | 2016-02-15 15:46 | 15 | 2015-04-09 15:55 | Structural Engineering - Concrete Member | 10000 |  | Damaged | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Other | Completed |  | Upon gaining access to view the condition of the CH1 crown at -3 soffit level, 1no. crack has been observed at a width of 0.6mm. The location of the crack is ploted upon the drawing attached. The width specified within the NSCS is 0.3mm for superstructures.
| 02SL - Stations (LUL) | Cxxx-NCR-000157 | NCR | Dywidag Fixed into the Tunnel Lining Wall |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2015-06-09 | 2015-07-10 11:38 | 31 | 2015-04-10 19:53 | Civil - Civil Engineering General | 5000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | Within the temporary works design for the corbel structure within the tunnels a Dywiday is required to be drilled and fixed into the tunnel lining at the top to hold the shutter in place. This bar should be installed no more than 200mm above the corbel reinforcement so that following striking it can be cut flush with the tunnel lining. When the 250mm slab is poured above the corbel the bar is the encased within the slab. Within AP2E a number of Dywidag bars have been drilled and fixed higher than the SSL. Please note attached images showing the bars in the SCL.
| 02SL - Stations (LUL) | Cxxx-NCR-000158 | NCR | -4 to -3 level buttress column concrete segragation GL A/8 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-01-31 | 2015-12-15 15:21 | -47 | 2015-04-14 18:36 | Structural Engineering - Concrete Member | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | Concrete segragation has been identified within the -4 to -3 buttress located upon GL A/8. The defect appears to be located at the bottom of the buttress (to 1m above -4 waler beam level) and confined to the corner of the buttress at the north east side. Please see photos illustating the defect
| 02SL - Stations (LUL) | Cxxx-NCR-000159 | NCR | PTE Track Slab Concrete Pour Incomplete |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2015-04-29 | 2015-05-06 15:57 | 7 | 2015-04-15 13:08 | Civil - Civil Engineering General | 5000 |  | Equipment Breakdown | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | During the concrete pour to PTE track slab between CH 4836 and 4860 on 13/04/15 there was a blockage in the concrete pipeline towards the end of the pour which prevented the last section of track slab being completed. A 3.8m long section of track slab between the drainage channel and the 350 wall was left between 50mm and 150mm low resulting in the top mat of reinforcement being exposed - see attached photos.
| 02SL - Stations (LUL) | Cxxx-NCR-000160 | NCR | Mis-aligned couplers in CH1 lining wall at -3 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2015-07-31 | 2015-05-19 12:26 | -73 | 2015-04-20 11:18 | Structural Engineering - Reinforcement | 5000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | Further to FCD 253, the Contractor has carried out an As-built survey of coupler bars cast into the CH1 lining wall at -3 level. Concrete cover to the couplers is to a maximum of 210mm. The specified cover (to the main vertical bar) is 45mm + hz bar diameter = 61mm (drawing number Cxxx-LAO-C-DWG-N105_WS089_4-50007).
| 02SL - Stations (LUL) | Cxxx-NCR-000161 | NCR | Incorrect cover on reinforcing for 200 thick wall (-5) |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2015-07-28 | 2015-06-09 12:13 | -49 | 2015-04-29 15:52 | Civil - Civil Engineering General | 5000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | As shown on reinforcement drawing Cxxx-LAO-C-DWG-N105_WS089_6-50048 the cover on F1 bar, with __ lock channel is required to be 50mm. The wall has been poured to a level of 100mm above maintenance slab with 35mm cover to F1 bars. This has occured in multiple locations from chainage 4772.488 to 4887.935
| 02SL - Stations (LUL) | Cxxx-NCR-000162 | NCR | Concrete windpost constructed too high |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2015-08-31 | 2015-08-27 08:08 | -4 | 2015-04-30 07:45 | Structural Engineering - Concrete Member | 5000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | At -2 level, with windpost number 5, the element has been constrcted too high by 70mm. The reduced level should have been 119.29m however has been cast to 119.36m, resulting in reinforcement being positioned to the incorrect height also. The windpost should be postioned to 50mm below the -1 soffit only, and not interect with it.
| 02SL - Stations (LUL) | Cxxx-NCR-000163 | NCR | Missing __ Shear dowel within -2 to -1 windpost 4 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2015-05-14 | 2015-05-19 12:07 | 5 | 2015-04-30 08:06 | Structural Engineering - Inserts | 2000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | 1no. RC windpost, located at -2 level (denoted as windpost 4), has been cast without an __ Shear Connector, which is required at the top of it (drawing Cxxx-LAO-C-DWG-N105_WS089_3-50022).
| 02SL - Stations (LUL) | Cxxx-NCR-000164 | NCR | -3 Downstand beams GL 9-10/A-D - Excessive Blow holes |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-04-15 | 2016-02-16 10:32 | -59 | 2015-05-11 10:28 | Structural Engineering - Finishes | 10000 |  | Material | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The Contractor has determined, upon removing -3 downstand beam formwork, an excessive amount of concrete blow holes on the beams poured face. Blow holes do not ahere to that defined in Architectural Specification: Cxxx-OVE-A-XDS-1025-50009, clause JE20.1206 e), with many hole exceeding the 20mm2 limit. (please see photos for clarity)
| 02SL - Stations (LUL) | Cxxx-NCR-000165 | NCR | Missed cavity drain pipe in -4 propping slab GL A/7-8 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2015-12-31 | 2015-11-30 13:52 | -31 | 2015-05-11 11:03 | Mechanical - Public Health Engineering | 10000 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The Contractor has missed one number 100mm diameter cavity drain pipe required to be located through the -4 raft slab GL A/7-8 as per drawing Cxxx-LAO-P-DDA-N015_5-31171.
| 02SL - Stations (LUL) | Cxxx-NCR-000166 | NCR | Construction Issue Drawings |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2015-08-21 | 2015-06-01 10:06 | -81 | 2015-05-13 11:04 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | The following drawings were being utilised on site that were not Construction Issue: Cxxx-LAO-C-DWG-N105-WS089_6-50026; Cxxx-LAO-C-DWG-N105-WS089_6-50022
| 02SL - Stations (LUL) | Cxxx-NCR-000167 | NCR | Omitted starter bars for AP2W Type 1 Beam |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2015-06-03 | 2015-06-16 11:04 | 13 | 2015-05-13 13:13 | Civil - Civil Engineering General | 1000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | The starter bars for AP2W beam type 1 at the opening to PTW were missed from one side of the corner corbel pour.
| 02SL - Stations (LUL) | Cxxx-NCR-000168 | NCR | Missing starter bars wall 2, core 4, level -3 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2015-05-29 | 2015-05-29 13:58 | 0 | 2015-05-15 18:11 | Civil - Civil Engineering General | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 20no. starter bars were missed out of wall 2, core 4, level -3 above the box out before pouring the bottom 600mm of the waling beam. See attached sketch for exact location.
| 02SL - Stations (LUL) | Cxxx-NCR-000169 | NCR | PTE lining wall crown - Ecessive crack widths |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-01-31 | 2017-01-31 11:21 | 0 | 2015-05-19 18:41 | Structural Engineering - Concrete Member | 1000 |  | Material | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Upon gaining access to view the condition of the PTE lining wall crown at -3 soffit level, 1no. crack has been observed at a width of 1mm. The location of the crack is ploted upon the drawing attached. The wall was poured using the C32/40 micro-synthetic fibre mix (MIX 4 -Cxxx-LAO-O4-XDS-N105_WS089_Z-50011) and cast with reinforcement to drawings: Cxxx-LAO-C-DWG-N105_WS089_6-50019 and Cxxx-LAO-C-DWG-N105_WS089_6-50020. The crack at its worst is 1m and can be seen on the top corner of the wall and gradually reduces in size the lower it is down the wall (photos). The crack can also be seen on top of the wall however appears to curtail at the FF reinforcement position.
| 02SL - Stations (LUL) | Cxxx-NCR-000171 | NCR | GYB - Lift 10 level -5 to -4 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2015-06-15 | 2015-08-03 14:04 | 49 | 2015-06-01 17:55 | Civil - Civil Engineering General | 10000 |  | Workmanship | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A cold joint has been formed on the first pour between level -5 and level -4. This was caused by the second load of concrete being very late to site. All efforts were made to keep the joint live but not successfully. There are also a couple of areas of poor compaction.
| 02SL - Stations (LUL) | Cxxx-NCR-000172 | NCR | 28 day cube result failure - Shear wall, level -5 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2015-08-01 | 2015-06-09 08:30 | -53 | 2015-06-02 14:23 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | The 28 day cube results for mix 1B, level -5 shear wall have failed with an average of 59.6N/mm2 (individual results are 60.3N/mm2 and 58.9N/mm2), 0.4N/mm2 below the required 60N/mm2. The 56 day result gives a strength of 63.5N/mm2. The cube test reports are attached.
| 02SL - Stations (LUL) | Cxxx-NCR-000173 | NCR | Shear Wall missalignment |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2015-06-17 | 2015-07-21 12:40 | 34 | 2015-06-03 10:16 | Civil - Civil Engineering General | 2000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | The SCL side shear wall located at chainage 4936.7 has had its reinforcement installed approximately 0.5m out of position (see attached photo). This has meant 4 bars in the shear wall will have to be removed and an additional 4 bars will have to be post drilled and fixed in the correct location.
| 02SL - Stations (LUL) | Cxxx-NCR-000174 | NCR | PTE Bay 8 Track Slab Pour Incomplete |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2015-06-23 | 2015-06-17 15:29 | -6 | 2015-06-09 14:25 | Civil - Structural Engineering | 5000 |  | Incomplete Works | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | The pour of Bay 8 track slab in the PTE tunnel, carried out during the backshift on 8/6/15, was incomplete. An additional load of concrete was anticipated as per the total quantity shown on the concrete tickets, however the final wagon did not arrive. When this was realised, the batching plant had already closed so another load could not be provided. As a result a stopend was put in 7.3 - 6.2m from the end of the pour, leaving the final section with concrete 100-300mm below the finished level.
| 02SL - Stations (LUL) | Cxxx-NCR-000175 | NCR | Formwork Tie Bars |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2015-06-29 | 2015-07-21 12:04 | 22 | 2015-06-15 15:46 | Civil - Civil Engineering General | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The tie bars used on the trackside corbel have been installed with a gap between the sleeve and the formwork. This allowed cement grout to enter the sleeve and make it impossible to un-do the tie bar from its connector.
| 02SL - Stations (LUL) | Cxxx-NCR-000176 | NCR | Finishing of concrete |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2015-07-03 | 2015-08-05 16:33 | 33 | 2015-06-15 17:44 | Civil - Civil Engineering General | 1000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Concrete finish to platform walls and corbels is not up to standard, as per attached photos.
| 02SL - Stations (LUL) | Cxxx-NCR-000177 | NCR | GYB - Lift 11 level -4 to -3.5 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2015-06-30 | 2015-07-07 08:14 | 7 | 2015-06-16 15:13 | Civil - Civil Engineering General | 10000 |  | Workmanship | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | After completing the post pour inspection of the riser walls from level -4 to level -3.5 it has been noticed that errors, outside tolerances within the ITP, have occurred on walls 1, 2 and 7. Wall 7 has areas where it is out of plumb by 24mm over the pour height.
| 02SL - Stations (LUL) | Cxxx-NCR-000178 | NCR | Concrete sample panel |  | Contr | OVE | TCR - Tottenham Court Road Station (West) |  | 2016-01-15 | 2016-02-16 10:47 | 32 | 2015-06-17 09:16 | Architectural - General | 5000 |  | Incomplete Works | Rework | 3 (3-6k) | Complete | Supervision - Other | Completed |  | The contractor has not provided The Concrete sample panel for Con 103. please see Cxxx Tottenham Court Road Architectural Specification Cxxx-OVE-A-XDS-N105-50009 extract below (read in conjunction with JA and JE20 sections) ;- "The proposed concrete mix shall be cast in a sample panel to prove the integrity of the concrete mix, the framework system, and workmanship in meeting the requirements. b) Refer to the Design Drawings showing the exact size and profile of the overall prototype to be cast. c) The concrete shall incorporate the full reinforcement as required for the actual construction. d) Details to be cast in shall be as indicated on the Design Drawings and all construction joints identified under "Types of Construction Joints" above. e) Contractor to ensure mock-ups / prototypes can be viewed in natural and artificial lighting conditions."
| 02SL - Stations (LUL) | Cxxx-NCR-000179 | NCR | MEP Design Verification Plan incomplete |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2015-11-30 | 2015-12-09 11:21 | 9 | 2015-06-17 10:41 | Electrical - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | MEP Design Verification Plan Cxxx-LAO-E-RGN-N105_WS089_Z-50001 Revision 2.0 provided as evidence of compliance for surveillance QS422-06 was incomplete. Design Verification work had at this stage already been undertaken. For details please refer to the report.
| 02SL - Stations (LUL) | Cxxx-NCR-000181 | NCR | Dywidag bar fixed above trackside corbel in PTE |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2015-07-08 | 2015-09-01 11:46 | 55 | 2015-06-22 15:25 | Civil - Civil Engineering General | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Dwyidag bars have been fixed above the trackside corbel in PTE over a length of 25m for use in the temporary works (see attached photo). Due to there being no slab being constructed on the trackside corbel, these Dywidag bars would be exposed if left in place.
| 02SL - Stations (LUL) | Cxxx-NCR-000182 | NCR | Level -3 slab edge GL B |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-09-30 | 2016-10-14 15:54 | 14 | 2015-06-25 17:18 | Civil - Civil Engineering General | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The slab edge shutter moved during the slab pour resulting in a large step in the joint on the seen face. On initial inspection there was also what appeared to be a cold joint at the corner of the slab pour.
| 02SL - Stations (LUL) | Cxxx-NCR-000184 | NCR | Works commencing without an approved Quality Plan in place |  | Crossrail | PDP | TCR - Tottenham Court Road Station (West) |  | 2015-07-16 | 2015-08-24 13:30 | 39 | 2015-07-02 09:51 | Mechanical - Platform Edge Doors | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Lack of approval Code 1 procedures excessive | Completed |  | __ Quality Management Plan Cxxx-LAO-Y-STP-N105_WS089_5-50001 rev 1.0 was returned code 3 on 30 June 2015. Works have since commenced on PES Bolt installation to Platform Tunnel Soffit.
| 02SL - Stations (LUL) | Cxxx-NCR-000185 | NCR | PES __ bolt installation: Not in accordance with ITP. |  | Crossrail | PDP | TCR - Tottenham Court Road Station (West) |  | 2015-07-16 | 2015-07-23 14:43 | 7 | 2015-07-02 10:06 | Mechanical - Platform Edge Doors | 1500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Not Defined | Completed |  | Works to the __ PES bolts have commenced. Cxxx - ITP - Setting Out, Drilling and Installation of __ Bolts Cxxx-LAO-Y-ITP-N105_WS089_5-50005 is not being followed. Paricularly Section 4 of the ITP.
| 02SL - Stations (LUL) | Cxxx-NCR-000186 | NCR | Working to invalid drawings on site. |  | Crossrail | PDP | TCR - Tottenham Court Road Station (West) |  | 2015-07-16 | 2015-08-05 15:53 | 20 | 2015-07-02 11:32 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | An inspection on Wed 17 June found that drawing Cxxx-LAO-C-DWG-N105_WS089_6-50046 1.0 ‘For CRL Acceptance’ was in use on site. The current edition is C01 at IFC and coded on 21 May.
| 02SL - Stations (LUL) | Cxxx-NCR-000187 | NCR | Working to unapproved ITP |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2015-09-20 | 2015-10-22 15:26 | 32 | 2015-07-02 13:24 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | ITP Cxxx-LAO-Y-ITP-N105_WS089_5-50002 for the Off-Site Steel fabrication is Code 3 and work in the fabrication facilities has begun
| 02SL - Stations (LUL) | Cxxx-NCR-000188 | NCR | Working to an unapproved MCR |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2015-09-20 | 2015-10-02 10:37 | 12 | 2015-07-02 13:25 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | MCR Cxxx-LAO-O4-XDS-N105_WS089_5-50005 for the Prescast works at __ is currently at Code 3 and works within the factory on the design and moulds has begun.
| 02SL - Stations (LUL) | Cxxx-NCR-000189 | NCR | Working to an unapproved ITP |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2015-09-20 | 2015-10-20 09:53 | 30 | 2015-07-02 13:24 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | ITP Cxxx-LAO-Y-ITP-N105_WS089_5-50003 for the Precast Panel manufacture at __ has commented without an approved ITP
| 02SL - Stations (LUL) | Cxxx-NCR-000190 | NCR | Missing cubes - Windposts level -2 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2015-07-18 | 2015-08-05 08:10 | 18 | 2015-07-04 12:59 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | We are missing cubes for 2no wind post pours on 21/04/15 and 14/04/2015. The cube numbers referenced on the pour histories are for tunnels pours or non-existent. Both loads of concrete passed the consistency test. See attached pour histories.
| 02SL - Stations (LUL) | Cxxx-NCR-000192 | NCR | Water addition to Concrete for second Level -3 Slab pour on the 19/06/15 |  | Crossrail | PDP | TCR - Tottenham Court Road Station (West) |  | 2015-07-31 | 2015-07-21 13:22 | -10 | 2015-07-07 13:31 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | It was observed, during a surveillance of the certification records, that the second Level -3 Slab pour on the 19/06/15 had a number occasions were additional water was added to the concrete truck mixer drum before discharge on site In total, water was added to 5 no loads under the instruction of the batcher. The ticket numbers of these loads are: 31712815263 31712815307 31712815362 31712815373 3171281544X The addition of water did not follow the Crossrail guidance detailed in CRL1-XRL-C-GPD-CR001-50001. a) At the time of the surveillance, the water addition was covered under the __ method statement for general concreting, Cxxx-LAO-O7-GMS-N105_WS089_Z-50003. BS EN 206: 2013 7.5 states that any water addition is ‘under the responsibility of the producer’ and that ‘there is a documental procedure for undertaking this process in a safe manner within the factory production control’ (i.e. a Heidelberg Cement Group procedure). b) Water addition is generally not allowed but, as an exception, can only be added to bring the concrete to within the limiting values permitted by the specification. If the concrete is within the tolerances specified by the mix design, no more water can be added at site. In all occurrences during Pour 2 water was added to a conforming mix to take the slump to the top end of the range 230-240mm. This contravened section 3.4 of Cxxx-LAO-O7-GMS-N105_WS089_Z-50003. c) Four of the loads did not have any cubes taken from a concrete sample, following the addition of the water. The NSCS Standard states that, where water addition occurs, “concrete shall be deemed non-conforming – until identity testing for strength shows that the concrete is acceptable. NSCS is referenced in the design specification KF11 – In Situ Concrete for Buildings, Cxxx-OVE-S-RSP-N105-50001.
| 02SL - Stations (LUL) | Cxxx-NCR-000193 | NCR | Deformation of stopend at movement joint |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2015-07-23 | 2015-08-06 14:56 | 14 | 2015-07-09 17:59 | Civil - Civil Engineering General | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The stopend at the Movement Joint at the East End of PTE has deformed, which may reduce the effectiveness of the movement joint. in order to remove the timber from the joint, the area has had to be partially broken out.
| 02SL - Stations (LUL) | Cxxx-NCR-000194 | NCR | GYB - Secondary walls level -5 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2015-07-24 | 2015-08-06 08:08 | 13 | 2015-07-10 12:14 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | After striking the secondary walls at level -5 it was noticed that around the pump connection the shutter had been overtightened and hence kicked in 15mm. The carpenters had overtightened the shutter in this area as they were concerned over the pressure being generated by the pump.
| 02SL - Stations (LUL) | Cxxx-NCR-000195 | NCR | Incomplete concrete pour |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2015-07-28 | 2015-08-05 08:15 | 8 | 2015-07-14 11:36 | Civil - Civil Engineering General | 10000 |  | Incomplete Works | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the track corbel (PTW Bay 2) pour on the 11/7/15 there was a blockage in the concrete pipe line. The result of this meant the pour was stopped prematurely, leaving an area of incomplete, uncompacted concrete.
| 02SL - Stations (LUL) | Cxxx-NCR-000196 | NCR | Cracks in platform structure propagating from service openings |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2015-11-30 | 2015-12-21 14:40 | 21 | 2015-07-16 09:49 | Structural Engineering - Concrete Member | 10000 |  | Design | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Other | Completed |  | The Contractor has become aware that there are cracks appearing in the platform wall (350/250mm wall connected to the track foundation slab) that propagate from the UPE extract openings. These cracks have appeared on several of the UPE extract holes and has occured within wall pours of varying lengths (between 12 and 25m long). The attached photos show examples of this cracking. The majority of these cracks are minor and are expected to seal over time but some appear to be greater than 0.3mm wide. Following meetings with the Employers Designer and Project Manager (see work task notes below and attached emails), it was agreed cracks above 0.6mm wide above the UPE openings only would be repaired. Material approvals, ITP and Method Statement have all been accepted code 1 and are attached for information.
| 02SL - Stations (LUL) | Cxxx-NCR-000197 | NCR | WTH & Track Slab interface |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2015-10-31 | 2015-09-17 16:32 | -44 | 2015-07-22 17:18 | Civil - Civil Engineering General | 2000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Upon setting out the track foundation slab and shear walls within the WTH box, the Contractor has become aware of a discrepancy between the setting out using the tunnel setting out system and the WTH local grid. The difference between the two setting out's has resulted in the couplers for the shear walls being at least 50mm out of position. Looking at the wall from the track slab (see also attached photos); - The left of the left shear wall concrete edge falls directly over the heads fo the couplers cast in to the wall. - The right side of the left shear wall has 100mm cover. - The left of the right shear wall's couplers will fall outside of the concrete. - The right of the right shear wall's couplers are 650mm away from the left instead of 930mm. - The step up is 50mm too far east.
| 02SL - Stations (LUL) | Cxxx-NCR-000198 | NCR | During the Quality Focus Meeting site walk, __ and CRL observed: The drawing number Cxxx-LAO-C-DWG-N105_WS089_6-50026 Rev.2 Title: Cxxx- Eastbound Platform Reinforcement Details of Track FDN Shear Wall ‘A’ & Corbel (Level -5) found marked for `CRL Acce |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2015-08-10 | 2015-08-11 10:40 | 1 | 2015-07-27 15:44 | Civil - Civil Engineering General | 1000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | During the Quality Focus Meeting site walk, __ and CRL observed: The drawing number Cxxx-LAO-C-DWG-N105_WS089_6-50026 Rev.2 Title: Cxxx- Eastbound Platform Reinforcement Details of Track FDN Shear Wall ‘A’ & Corbel (Level -5) found marked for `CRL Acceptance'. The current edition is C01 at IFC and coded on 22/05/2015 – Refer observation CRL-OBS-04464.
| 02SL - Stations (LUL) | Cxxx-NCR-000199 | NCR | Hole below UPE Opening in the 350/250 Wall Pour - PTW Bay 10 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2015-08-19 | 2015-09-01 11:57 | 13 | 2015-07-29 07:41 | Civil - Civil Engineering General | 5000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Upon removal of the shuttering for the 350/250 wall PTW Bay 10 there is an area under the UPE opening where the concrete has not being placed and compacted correctly. See attached photos.
| 02SL - Stations (LUL) | Cxxx-NCR-000200 | NCR | As-built position of the UTX Ducting |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-06-30 | 2016-06-14 09:47 | -16 | 2015-07-29 08:01 | Civil - Civil Engineering General | 10000 |  | Incorrect Installation | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The Contractor raised FCD 00268 with regards to the Level -5 Platform UTX Ducting and attached Cxxx-LAO-E-DWG-N105_WS089_6-50001, Revision P03 on 13/05/15 requesting that the Project Manager confirm the location of the UTX ducting within the slabs where it had deviated from the Works Information. The Contractor received a response on the 10/07/15 from the Project Manager. The Contractor has been progressing the works and at the Westbound West End the Contractor has installed the UTX ducting to P05 and has an as-built chainage 4750.916. The opening in the floating track slab is at 4752.1 therefore there is a difference of 1.18m. At the Westbound East End the Contractor has installed the UTX ducting at CH 4988.676 (both P03 and P05) and the opening in the FTS is at CH 4986.1 therefore there is a difference 2.576m.
| 02SL - Stations (LUL) | Cxxx-NCR-000201 | NCR | GYB Level -2 Wind Post Not Cast to Front Face of Upstand |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-02-18 | 2016-02-12 10:09 | -6 | 2016-02-04 08:10 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | At GYB Level -2 along the walling down the side of the escalator and in particular at the stairs between the two levels in this location the wind post highlighted on the mark-up has not been completed to the front face of the upstand. It has been positioned to the edge of the chamfer. The blockwork has been completed to the front face of the upstand as per the drawing.
| 02SL - Stations (LUL) | Cxxx-NCR-000202 | NCR | Missing Cubes |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2015-08-13 | 2015-08-04 13:00 | -9 | 2015-07-30 11:20 | Civil - Civil Engineering General | 2000 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Training Deficiency - Insufficient practice or hands -on experience | Completed |  | We are missing cubes for PTE Maintenance Slab Bay 3. All loads of concrete passed the consistency test. See attached pour history.
| 02SL - Stations (LUL) | Cxxx-NCR-000203 | NCR | PTP- Corbel couplers in WTH track Slab |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2015-08-14 | 2015-09-02 16:02 | 19 | 2015-07-31 15:10 | Civil - Civil Engineering General | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the first track slab pour in WTH (18/3/15) it appears that the couplers for the corbel moved. On setting out the concrete line for the corbel, we found the couplers have extremely limited cover between GL DD and the East liner wall within the western ticket hall. At the worst case, the coupler edge is on the line of the concrete (see attached photos).
| 02SL - Stations (LUL) | Cxxx-NCR-000204 | NCR | WTH -windpost level -2 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-05-27 | 2016-04-13 11:03 | -44 | 2015-11-09 09:18 | Civil - Structural Engineering | 2000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | WTH, level, wind post (WP-8), GL 4-5/D-E - As-built survey shows that top section of wind post ( 1.5 m from top of a wind post) is in tolerance (9mm out of position) referring to ITP Cxxx-LAO-O4-ITP-N105_WS089_Z-50002
| 02SL - Stations (LUL) | Cxxx-NCR-000205 | NCR | Crack in VWW liner wall |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-02-23 | 2016-03-04 11:02 | 10 | 2015-08-07 08:51 | Civil - Civil Engineering General | 5000 |  | Design | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | A crack has been observed down the face of the VWW liner wall. The crack also extends part way across the top of the liner wall (see attached photos). The crack is 4.5m from the east end of the wall.
| 02SL - Stations (LUL) | Cxxx-NCR-000206 | NCR | PTE Track Foundation Slab out of level tolerance |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2015-11-05 | 2015-12-04 12:07 | 29 | 2015-08-07 10:08 | Structural Engineering - Concrete Member | 10000 |  | Workmanship | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following a level survey of the track foundation slab in PTE, it has been found that some of the slab levels are outside of the tolerances stated in the works information (+0/-10mm). The attached survey shows these areas. After discussions with Cxxx regarding FTS installation, they will require these areas to be ground down and then a repair material used to create a smooth casting surface for the FTS.
| 02SL - Stations (LUL) | Cxxx-NCR-000207 | NCR | TCR, Tunnel PTW. PES galvanized steel material. Steel beams – abrasion/chips. |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2015-08-21 | 2015-12-17 08:53 | 118 | 2015-08-07 16:05 | Civil - Civil Engineering General | 10000 |  | Material | Rework | 2 (6-60k) | Complete | Management Problem - Inadequate supervision | Completed |  | During the site inspection CRL, __ and __ noticed: The galvanized steel beams, material for PES - Platform Edge Screen has got abrasions and chips (galvanized surface damage – see attached photos) According to the ITP: Cxxx-LAO-Y-ITP-N105_WS089_5-50006 Material should be checking, inspection number: 4.1 The all material, which coming from supplier is not protected in any way against damages.
| 02SL - Stations (LUL) | Cxxx-NCR-000208 | NCR | -3 to -2 deep beam starter bars missed in -3 level slab GL 8/A-B |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2015-11-18 | 2015-11-24 14:40 | 6 | 2015-08-10 16:11 | Structural Engineering - Reinforcement | 5000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Procedure Problem - Lack of procedure | Completed |  | The Contractor has determined an error made with continuity reinforcement required to be cast into the -3 horizontal elements for a deep beam upon GL 8/A-B. Reinforcement starter bar detailed on drawings Cxxx-LAO-C-DWG-N105_WS089_4-50017 under bar mark 06 and Cxxx-LAO-C-DWG-N105_WS089_4-50008 under bar mark 64 have been missed throughout the 1.05m length of waler beam adjacent to GL A between buttress and edge of beam.
| 02SL - Stations (LUL) | Cxxx-NCR-000209 | NCR | Missing cubes, wall 4 pour 3, level -4 to -3 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2015-11-18 | 2015-09-23 14:17 | -56 | 2015-08-10 16:17 | Civil - Civil Engineering General | 500 |  | Testing and Commissioning | Repair | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | We are missing cube results for wall 4, pour 3, level -4 to -3. Cubes were taken but results from __ cannot be found.
| 02SL - Stations (LUL) | Cxxx-NCR-000210 | NCR | Incomplete concrete pour |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-01-30 | 2016-02-11 13:09 | 12 | 2015-08-13 07:57 | Civil - Civil Engineering General | 10000 |  | Supervision/Management | Repair | 2 (6-60k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | During the pour for CH3 slab there was a miscommunication between the contractor and the batching plant. This resulted in the required quantity not being delivered and a section of the slab left unpoured.
| 02SL - Stations (LUL) | Cxxx-NCR-000211 | NCR | GYB - Superstructure cover |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-08-15 | 2016-05-16 15:59 | -91 | 2015-08-13 08:24 | Civil - Civil Engineering General | 5000 |  | Incorrect Installation | Use As-Is | 3 (3-6k) | Complete | Previous Construction - Problems based on previous construction errors | Completed |  | Please see attached a full cover survey of the walls at stub wall level (1.060m above ground level). There is reduced cover in some areas due to the coupler position in the slab below that were inherited from the previous contractor
| 02SL - Stations (LUL) | Cxxx-NCR-000213 | NCR | GYB - lift 11 -1 to ground lacers on inside face |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2015-09-01 | 2015-09-01 12:04 | 0 | 2015-08-18 14:20 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | On the western face of the inside of lift 11 from level -1 to ground the first few lacesr were placed on the inside of the verticals rather than external as there would have been insufficient cover otherwise. This was completed and concreted before asking for permission to compelte the work in this manner. It was only for a few bars as it was possible to bring the bars over to generate the cover after this point.
| 02SL - Stations (LUL) | Cxxx-NCR-000214 | NCR | AP7a West Corbel |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2015-09-02 | 2015-09-10 12:01 | 8 | 2015-08-19 10:56 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On the East Side of AP7a the Contractor has cast the corbel upto the S3 head wall when it should be finshed short of the head wall. See attached mark-up.
| 02SL - Stations (LUL) | Cxxx-NCR-000215 | NCR | Trunking type used in MEP Modules |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2015-09-02 | 2015-10-12 17:14 | 40 | 2015-08-19 16:13 | Electrical - Cable Management | 5000 |  | Material | Rework | 3 (3-6k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | During the factory visit to the __ Manufacturing facility it was noted that an incorrect type of trunking was fixed within the modules. The runking type installed, utilised the turnbuckle method for securing the trunking lid however the project requires the use of a screw fixed trunking lid. As such the trunking must be replaced.
| 02SL - Stations (LUL) | Cxxx-NCR-000216 | NCR | Cover at PTE Liner wall level -3 to -2 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2015-09-02 | 2015-09-04 11:42 | 2 | 2015-08-19 17:29 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | There are 2 issues with cover to the reinforcement in the PTE liner wall, level -3 to -2: Issue 1 - The front of the PTE liner wall at the bottom 600mm is short of cover to the starter bars Issue 2 - The centre 2m of the liner wall there is up to 360mm gap between the reinforcement cage which is greater that the 275mm cover given by the D-wall position (75mm cover + 200mm D-wall tolerance).
| 02SL - Stations (LUL) | Cxxx-NCR-000217 | NCR | Missing Cubes for tunnel pour on 22/4/15 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2015-09-03 | 2015-09-03 13:20 | 0 | 2015-08-20 12:43 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | We are missing cubes for the pour that occured on 22/4/15, cube references T0021A-D. This affects PTE Bay 4 Maintenance Slab and PTE Bay 1 350/250 wall. All loads of concrete passed the consistency test. See attached pour history.
| 02SL - Stations (LUL) | Cxxx-NCR-000218 | NCR | Alignment Beam and Grouting Installation ITP Not Accepted by Crossrail |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2015-09-04 | 2015-09-14 15:25 | 10 | 2015-08-21 09:30 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | During a planned Crossrail surveillance undertaken on 13th August 2015 which looked at PES bolt and structural steelwork installation, it was identified that the Inspection and Test Plan (ITP) for the Installation of Alignment Beams and Grouting (Cxxx-LAO-Y-ITP-N105_WS089_5-50006) was still at Decal Code 3, with Revision 1 being the most ‘Current’ version on eB. Revision 2 was visible on eB, however this was identified as being ‘Draft’ and ‘Not Approved’. As the alignment beam installation started on site on 06th August, the works to date have been undertaken without an accepted ITP in place; as such this NCR was raised resulting from the surveillance visit. A Code 3 Decal stands for “Not Accepted. Revise and resubmit. Work may not proceed” as detailed in Crossrail Document Management Procedure. Works Information Volume 2B Part 20.8 Inspection and Testing states “The Contractor and his subcontractors and suppliers of any tier engaged in supplying, manufacturing, construction, installation, commissioning and testing or any other service connected with the works, shall maintain ITPs appropriate for the services they provide that are accepted by the Supervisor”; and “The Contractor shall not start the relevant works until the Supervisor has accepted the ITP.” Part 20.4 Contract Quality Plan states “The Contractor shall not start any activity on any part of the works for which the Contract Quality Plan, applicable QSPs or ITPs, are not accepted by the Project Manager.”
| 02SL - Stations (LUL) | Cxxx-NCR-000219 | NCR | PES structural steelwork MCR not accepted by Crossrail |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2015-09-04 | 2016-01-18 11:16 | 136 | 2015-08-21 09:32 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | During a planned Crossrail surveillance undertaken on 13th August 2015 which looked at PES bolt and structural steelwork installation, it was identified that the __ Structural Steelwork (Cxxx-LAO-O4-XDS-N105_WS089_5-50006) and Cahill Structural Steelwork (Cxxx-LAO-O4-XDS-N105_WS089_5-50007) MCRs, which are being used to construct the PES alignment beams, were still at a Decal Code 3 and not accepted by Crossrail. As the alignment beam installation started on site on 06th August, the works to date have been undertaken with non-accepted structural steelwork; as such this NCR was raised resulting from the surveillance visit. A Code 3 Decal stands for “Not Accepted. Revise and resubmit. Work may not proceed” as detailed in Crossrail Document Management Procedure. Works Information Volume 2B Part 13.3.8 Materials Compliance Record states “The Contractor shall utilise the template attached in Appendix 13J (MCR) for the purpose of recording material and product acceptances for the works and submit such records to the Project Manager for acceptance.”
| 02SL - Stations (LUL) | Cxxx-NCR-000220 | NCR | Missing Cubes- PTE Bay 4 Track Slab |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2015-09-23 | 2015-09-03 13:09 | -20 | 2015-08-24 08:59 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | During the the pouring of PTE Bay 4 Track slab, only one set of cubes were made. As the pour was 88m3 two sets should have been taken. The set that was taken (T0028, attached) shows that the concrete exceeded the required strength at 28 days.
| 02SL - Stations (LUL) | Cxxx-NCR-000221 | NCR | Missing __s in PTW Platform Edge |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-01-23 | 2015-11-24 12:38 | -60 | 2015-08-26 10:58 | Civil - Civil Engineering General | 5000 |  | Supervision/Management | Repair | 3 (3-6k) | Complete | Management Problem - Other | Completed |  | 8No halfens within the platform edge slab have been missed out (not installed) - see attached as-built survey of missing halfens (clouded).
| 02SL - Stations (LUL) | Cxxx-NCR-000222 | NCR | Missing Cubes: Tunnel Pour 27/3/15 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2015-09-25 | 2015-09-03 13:12 | -22 | 2015-08-26 10:33 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | e are missing cubes for the pour that occured on 27/3/15. This affects portions of CH1 Spine Wall, AP1 Spine Wall, AP2W Spine Wall and AP2E Corbels. All loads of concrete passed the consistency test. See attached pour history.
| 02SL - Stations (LUL) | Cxxx-NCR-000223 | NCR | Concrete Delivery: Out of Time |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2015-09-28 | 2015-11-20 13:44 | 53 | 2015-08-26 13:55 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Concrete delivery 22 August 2015 Batched 11:09 had exceeded the allowable time from batching when discharge did not start until 13:20. PTW East end platform. (Please hold correct record of pour locations sheet.)
| 02SL - Stations (LUL) | Cxxx-NCR-000224 | NCR | __ drawings for Alignment Beam installation still at preliminary status and have not been accepted by Crossrail as required |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2015-09-24 | 2016-01-04 09:14 | 102 | 2015-08-27 15:03 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | During a planned Crossrail surveillance undertaken on 13th August 2015 which looked at PES bolt and structural steelwork installation, whilst reviewing the __ construction issue drawings ‘specification drawings – Cxxx-LAO-Y-DWG-N105_WS089_5_500(35-37)’ it was identified that the drawings were still P0X coded (preliminary status) and not accepted on eB (Code 1) with the cover sheet left blank (dated April 2015). Additionally ‘setting out drawings - Cxxx-LAO-Y-DWG-N105_WS089_5_500(56-63) had not been submitted on eB, with the eB reference numbers being a placeholder since April 2015, with the drawings P0X coded and not IFC (C0X status). ITP, Cxxx-LAO-Y-ITP-N105_WS089_5-50006 inspection number 1.2 states ‘IFC –Drawings’ should be accepted by __ and Crossrail with a Decal Code 1 issued. Furthermore, Design Management Plan, Cxxx-LAO-C-STP-N105_WS089-50001 (Rev 5) Code 2 states “On completion of the Cxxx design, including completion of the sub-contractor and specialist supplier design, where applicable to the Stage F submission, Cxxx will provide Contractor’s Design Submissions to the Project Manager for acceptance.” As the Alignment Beam fabrication drawings were either not present (placeholder), at P0X status (not IFC ‘C0X’ status) or had been used with no CRL Decal Code 1 acceptance this NCR was raised resulting from the surveillance.
| 02SL - Stations (LUL) | Cxxx-NCR-000225 | NCR | Concrete Delivery: Out of Time |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2015-11-13 | 2015-11-25 13:25 | 12 | 2015-08-28 09:04 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Concrete delivery 28 August 2015 Batched 11:36 had exceeded the allowable time from batching when discharge for lift 11 ended 13:55. + additional time to compact (vibration method) the concrete.
| 02SL - Stations (LUL) | Cxxx-NCR-000226 | NCR | Cube Failure - Tunnel Pour 28/7/15 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2015-10-03 | 2015-09-14 14:06 | -19 | 2015-09-03 11:38 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | The strength of cubes T0095 A-D did not reach the required 40N/mm2 in 28 days, see attached record sheet. This affects PTW East End Track Slab and PTW Bay 10 Corbel. The consistence was within specification, see attached pour history.
| 02SL - Stations (LUL) | Cxxx-NCR-000227 | NCR | Platform Structure Movement Joints |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2015-11-07 | 2015-11-25 10:13 | 18 | 2015-09-08 13:42 | Civil - Civil Engineering General | 2000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | On initial casting of the platform structure the movement joints had a rough finish and and varying width of joint.
| 02SL - Stations (LUL) | Cxxx-NCR-000228 | NCR | Blockwork Walls Mortar Joint Quality |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2015-09-23 | 2015-09-23 12:54 | 0 | 2015-09-09 12:31 | Architectural - Brickworks/Blockworks | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Upon a site visit and inspection of the cavity blockwork walls it has been highlighted that in some of the joints, in particular the vertical joints, the blocks have not been prepared sufficiently to ensure a full and consistent mortar joints. Following the laying of the blocks the joints at the back have not been pointed suficiently. The particular area highlighted in Level -5 has been amended.
| 02SL - Stations (LUL) | Cxxx-NCR-000229 | NCR | Cover of Reinforcement W3 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-01-07 | 2015-12-09 12:59 | -29 | 2015-09-09 14:36 | Structural Engineering - Reinforcement | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Upon completion of pouring the concrete at W3 the cover of the reinforcement did not deemed to be as per design (varying between 25-35mm over a distance of 3m from W5). See attached photos.
| 02SL - Stations (LUL) | Cxxx-NCR-000230 | NCR | GYB - Truss 3 top and bottom chords |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2015-09-24 | 2015-09-14 15:00 | -10 | 2015-09-10 13:20 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Contractor carried out an as built survey of the existing steel plates at the top and bottom of Truss 3 diagonals and found that plates on -1 slab are not in line with the plates in the soffit above. Relative difference is upto 40mm (see attached survey) Gap between parallel plates is not unform either.
| 02SL - Stations (LUL) | Cxxx-NCR-000231 | NCR | __ Channels not installed |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2015-10-14 | 2015-10-29 14:40 | 15 | 2015-09-14 17:16 | Civil - Civil Engineering General | 5000 |  | Supervision/Management | Use As-Is | 3 (3-6k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | __ Channels were not installed in the 200 wall in PTE Bays 1+2, and not in the soffit of Bay 1.
| 02SL - Stations (LUL) | Cxxx-NCR-000232 | NCR | Cracks in grout |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-03-30 | 2016-02-15 09:55 | -44 | 2015-09-16 10:18 | Civil - Civil Engineering General | 10000 |  | Design | Use As-Is | 2 (6-60k) | Complete | Material/Preservation Problems - Not Defined | Completed |  | Cracking has been obsierved in the grout placed between crown alignment beam and the SCL. The crack widths vary, as shown on attached reports.
| 02SL - Stations (LUL) | Cxxx-NCR-000233 | NCR | Commencement of works without approved ITP |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2015-09-29 | 2015-09-30 12:35 | 1 | 2015-09-16 16:13 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Works have commenced on installation of extract ductwork in Platform inverts without an approved. ITP Cxxx-LAO-04-ITP-N105_WS089-50010 Rev 2 was returned code 3 on the 11th September 2015 (Rev 1 30th July 2015). This contravenes Works Information Vol 2B, Part 20, Cl20.8 and Section 1.3 Hold point of the ITP submitted.
| 02SL - Stations (LUL) | Cxxx-NCR-000234 | NCR | Cutting Vertical Bars in W2 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-01-19 | 2015-11-18 15:35 | -62 | 2015-09-21 10:02 | Structural Engineering - Reinforcement | 2000 |  | Planning | Repair | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | 4No. Vertical B16 Bars were cut on internal Wall W2 in order to fix erect the shutters for the external wall. This was not agreed with Crossrail in advance.
| 02SL - Stations (LUL) | Cxxx-NCR-000235 | NCR | Cut Verical Bars in W10 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-01-19 | 2015-11-18 15:37 | -62 | 2015-09-21 10:03 | Structural Engineering - Reinforcement | 2000 |  | Planning | Repair | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | 4No. B16 vertical bars were cut in W10 to enable instalation of the shutter of the external wall. This was not discussed/approved with Crosrail in advance of the works.
| 02SL - Stations (LUL) | Cxxx-NCR-000236 | NCR | Defective windpost at -2 GYB |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2015-11-14 | 2015-12-04 14:52 | 20 | 2015-10-15 13:31 | Civil - Civil Engineering General | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | An defective wind post has been spotted at -2 level GYB (opposite Fan room 3/916). The connection between the in situ cast and the pre cast part seems to be twisted. Also on both sides the block work anchor channels are missing.
| 02SL - Stations (LUL) | Cxxx-NCR-000237 | NCR | Concrete Delivery: Out of Time |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2015-11-13 | 2015-11-27 15:00 | 14 | 2015-09-21 14:04 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Concrete delivery 07.09.15 batched: 0907 & 08.09.15 batched: 0859 & 08.09.15 batched: 0949 & 10.09.15 batched: 0817 had exceeded the allowable time of 120min from batching to discharge finish from 16min to 78min. Concrete for VentTower and Secondary walls at GYB. Concrete cubes have been found in unlabelled moulds in the cube shed. The concrete ticket from the 11/09/15 got lost and is missing since.
| 02SL - Stations (LUL) | Cxxx-NCR-000238 | NCR | Concrete Delivery: Out of Time |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2015-11-12 | 2015-11-24 09:48 | 12 | 2015-10-15 13:36 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Concrete delivery 16 September 2015 Batched 13:09 had exceeded the allowable time of 120min from batching when discharge did not start until 17:10. Concrete used for VentTower or secondary walls - No correct record of pour locations made. Total overtime of the pour: 133min.
| 02SL - Stations (LUL) | Cxxx-NCR-000239 | NCR | Concrete Delivery: Out of Time |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2015-11-13 | 2015-11-25 13:29 | 12 | 2015-09-21 16:24 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Concrete delivery 16 September 2015 Batched 13:09 had exceeded the allowable time of 120min from batching when discharge did not start until 17:10. Concrete used for VentTower or secondary walls - No correct record of pour locations made. Total overtime of the pour: 133min.
| 02SL - Stations (LUL) | Cxxx-NCR-000240 | NCR | Missing chamfers WTH |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-07-31 | 2016-04-08 10:27 | -114 | 2015-09-23 13:36 | Civil - Structural Engineering | 10000 |  | Incorrect Installation | Rework | 2 (6-60k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | During the CRL and __ inspection (08/07/2015) observed that missing chamfers at level -5 and -4 have not been installed yet as per agreed benchmark. Please see attached DWG.
| 02SL - Stations (LUL) | Cxxx-NCR-000241 | NCR | WTH - Spray Paint on Completed Wall |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-04-10 | 2015-10-12 08:19 | -181 | 2015-09-23 14:40 | Civil - Civil Engineering General | 1000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Western Ticket Hall - Level -5 (GL:9-10/D-E) - Yellow Spray paint has been applied to a completed wall
| 02SL - Stations (LUL) | Cxxx-NCR-000242 | NCR | Inadequate notice, works not ready for inspection: Missing rebar, insufficient concrete cover and not cleaned. |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2015-10-07 | 2015-11-09 12:00 | 33 | 2015-09-23 16:05 | Civil - Civil Engineering General | 1000 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | I was asked to come out 1 hour before for the pre pour inspection of the +1 slab at GYB VentTower (23/09/15 between axis F/E at 2). The contractor agreed with the client a fair notice of min 24 h. The WI requires more. I was asked to come out a 11:00 because __ "will be ready then and start concreting". At the Inspection at 11:00 it was found that it was not ready for inspection: 1.The decking was not cleaned. 2.Bars were missing and needed to be drilled into the wall 13 next to it which was not fully accessible for a drill machine anymore. 3. Too little cover on top bars. 4. Thread bars were not screwed/tight fully 100% onto the couplers. The concrete wagon was already on site waiting while the steel fixer came back from break. They started in presence of the concrete wagon to solve the problems.
| 02SL - Stations (LUL) | Cxxx-NCR-000243 | NCR | Pourform ply in GYB Superstructure |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-06-05 | 2016-05-26 15:02 | -10 | 2015-09-23 16:28 | Civil - Civil Engineering General | 1000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | White ply has been used on the level +1 slab soffit in the GYB superstructure. The architectural specification clause JE20.1401 part i states that ply with a phenolic resin coating will be used (pourform) therefor the white ply is non-conforming.
| 02SL - Stations (LUL) | Cxxx-NCR-000244 | NCR | PES Top Support Brackets |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-01-07 | 2016-03-22 12:09 | 75 | 2015-09-29 08:31 | Civil - Structural Engineering | 100000 |  | Incorrect Installation | Repair | 1 (>60k) | Complete | Management Problem - Inadequate administrative control | Completed |  | The top bracket should have 5 stiffeners as shown in detail 02g on drawing number Cxxx-ATK-S-DDD-CR001_Z-43053 (copy attached above). There should be 3 stiffeners at the front/platform side of the bracket and 2 on the back/track side. The fabricators have installed 3 stiffeners on the front and 3 instead of 2 on the back. The additional stiffener on the back clashes with the support bracket & its central stiffener at the top of the PES truss hangers; see detail 02c on above drawing.
| 02SL - Stations (LUL) | Cxxx-NCR-000245 | NCR | GFRC __ Cladding Mock-Up Prototype Constructed Without Approved Quality Paperwork |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-04-15 | 2016-04-07 11:14 | -8 | 2015-09-30 15:18 | Architectural - Walls | 5000 |  | Documentation and Records | Rework | 3 (3-6k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | The Contractor progressed with the manufacture and build of the GRC cladding mock-up prototype without the quality paperwork in place including Inspection & Test Plans, Material Compliance Records, and Quality Plan. These documents are work in progress and the ITPs and Quality Plan have been informally reviewed with CRL __.
| 02SL - Stations (LUL) | Cxxx-NCR-000246 | NCR | GFRC __ Cladding Mock-Up Prototype Constructed with Code 3 drawings |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-01-08 | 2016-01-12 14:59 | 4 | 2015-09-30 16:39 | Architectural - Walls | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | The Contractor progressed with the manufacture and build of the GFRC / GRC Cladding mock-up prototype without Code 1 'Accepted' drawings: Cxxx-LAO-Y-DWG-N105_WS089_6-50011 Cxxx-LAO-Y-DWG-N105_WS089_6-50012 Both drawings recieved a Code 3 on eB upon review by the Cxxx Project Manager.
| 02SL - Stations (LUL) | Cxxx-NCR-000247 | NCR | Concrete failed Flow test for secondary walls |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2015-10-28 | 2015-11-27 10:38 | 30 | 2015-09-30 17:08 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | 2 concrete deliveries at 30/09/15 of self compacting concrete SF2 failed the slump-flow test. The concrete was nevertheless used for the secondary walls GL 2-3 C-D at GYB -3 level. The slump-flow readings were 500mm and 610mm.
| 02SL - Stations (LUL) | Cxxx-NCR-000248 | NCR | Concrete delivery out of time |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2015-11-13 | 2015-11-25 13:32 | 12 | 2015-09-30 17:18 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | The following concrete deliveries have been out of time: 30/09/15 Batching time: 09:50 / Total Overtime: 60min / GYB secondary walls - 3 1.5h late 25/09/15 Batching time: 13:48/ Total Overtime: 12min / VentTower&Secondary walls 22/09/15 Batching time: 13:23/ Total Overtime: 1h27min / VentTower&Secondary walls 23/09/15 Batching time: 10:10/ Total Overtime 20min / VentTower&Secondary walls
| 02SL - Stations (LUL) | Cxxx-NCR-000249 | NCR | Cracks in platform structure |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2015-10-30 | 2015-12-21 14:46 | 52 | 2015-10-02 13:04 | Civil - Civil Engineering General | 10000 |  | Design | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Other | Completed |  | Cracks over 0.3mm have been found in the platform concrete structure, this includes the platform slab, 200 thick wall, 350/250 thick wall and platform corbel. cracks are not numerous, but do need to be addressed. This NCR is a duplicate of NCR 196
| 02SL - Stations (LUL) | Cxxx-NCR-000250 | NCR | -3 to -2 secondary wall issues (GL A-B/9) |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-02-29 | 2016-02-09 10:57 | -20 | 2015-10-02 18:22 | Structural Engineering - Concrete Member | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Management Problem - Inadequate supervision | Completed |  | With regards to the secondary wall located within the WTH at GL A-B/9, several issues have been determined upon carrying out the post pour inspection. These are listed here: 1) Lack of cover to reinforcement at construction joint, 2) Wall thickness. Wall, at its extreme, is 45mm too slim (see as-built), 3) No chamfer to external corner (GL A)
| 02SL - Stations (LUL) | Cxxx-NCR-000251 | NCR | Missed coupler bar reinforcement for downstand beam at -2 level GL 9-10/B |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-01-31 | 2015-11-25 14:44 | -67 | 2015-10-05 09:13 | Structural Engineering - Reinforcement | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Couplers bars detailed on Cxxx-LAO-C-DWG-N105_WS089_4-50019 were not cast into the wall located on GL B and between 9-10. Coupler bars are required for the 1.3m downstand beam intersecting with the wall with 2no. B32 and 4no. B25 bars required. Wall is cast to the soffit of the 700mm slab, therefore through the top 700mm thick slab bars can be positioned as per design (Cxxx-LAO-C-DWG-N105_WS089_3-50012).
| 02SL - Stations (LUL) | Cxxx-NCR-000252 | NCR | TCR, WTH, Level -2, GL: 8/A-B, Wall (Top of Beam) - Concrete beam, has not constructed according to the design. Part of the concrete beam was demolished. |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2015-10-26 | 2016-01-12 09:35 | 78 | 2015-10-05 11:30 | Civil - Civil Engineering General | 1000 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | TCR, WTH, Level -2, GL: 8/A-B, Wall (Top of Beam) Concrete beam, poured not according to the design, No space for the perpendicular concrete beam. Part of the concrete beam was demolished. For more details see attached observation report.
| 02SL - Stations (LUL) | Cxxx-NCR-000253 | NCR | WTH missing reinforcement for beam tie into column at -2 GL 9/B |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2015-10-19 | 2015-11-25 14:37 | 37 | 2015-10-05 11:37 | Structural Engineering - Reinforcement | 2000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | No coupler bars have been cast into a 1m x 0.85m column at grid line 9/B level -2 of the WTH. Continuity reinforcement is required for anchoring the 1.3m deep beam (denoted as B22 on drawing Cxxx-C-DWG-N105_WS089_3-50012) with the column. Top bars (2no. 32mm bars and 5no. 25mm bars) will be fixed as per drawing Cxxx-C-DWG-N105_WS089_3-50012.
| 02SL - Stations (LUL) | Cxxx-NCR-000255 | NCR | Start work without answered FCD. FCD was reviewed and not accepted. Missing couplers at W1 +1 level. |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2015-10-19 | 2015-12-15 10:20 | 57 | 2015-10-05 15:42 | Civil - Civil Engineering General | 5000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | At wall 1 between axis D-E at +1 level. Two 16mm lacer bars have been cut off in order to have enough space to install the stop ends with waler beams designed by formwork sub contractor. The contactor raised an FCD (370) proposing to drill and fix afterwards. This has been rejected as unacceptable by the structural department (D.Marlow). The cut out bars will take loads. The contractor can foresee his action and with appropriate planning this can be avoided.
| 02SL - Stations (LUL) | Cxxx-NCR-000256 | NCR | Changing wall 5 +1 level design without notice or approval by CRL. |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2015-10-19 | 2015-12-22 16:34 | 64 | 2015-10-05 16:17 | Civil - Civil Engineering General | 10000 |  | Supervision/Management | Repair | 2 (6-60k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | At Wall 5 at the VentTower at height 132.360m additional temporary concrete has been poured into the wall opening to give enough strength for the temporary formwork anchor on the outside. The concrete/rebar is intended to be cut back later. There is no procedure in place how to cover the bars to permanently rust proof the cut ends. The contractor did this without notice to the structural engineer or to the architect. (This is a CON103.)
| 02SL - Stations (LUL) | Cxxx-NCR-000257 | NCR | Concrete cut out of finished outside CON103 Wall 9/10 corner at +1 level without notice. |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2015-10-19 | 2015-11-18 15:42 | 30 | 2015-10-05 16:41 | Civil - Civil Engineering General | 1000 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | Because of wrong setting at Vent Tower +1 level w9/10 corner at the outside of w9 concrete and rebar has been cut off and exposed. This has been done without notice to the client. The remedial rebar (attached picture) is not anchored in the concrete at all. This is a CON103 architectural surface.
| 02SL - Stations (LUL) | Cxxx-NCR-000258 | NCR | Changing wall 14 to 7 rebar design without notice or approval by CRL. |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2015-11-25 | 2015-11-24 09:56 | -1 | 2015-10-05 16:41 | Civil - Civil Engineering General | 10000 |  | Supervision/Management | Use As-Is | 2 (6-60k) | Complete | Management Problem - Inadequate administrative control | Completed |  | At the corner of wall 14 to wall 7 at the Vent Tower from GF to the second floor instead of u-bars to tie into the lift wall 7, the contractor decided to use couplers. This is to attach L-bars at a later stage and bend into the wall 7. It has been no notice given to the client.
| 02SL - Stations (LUL) | Cxxx-NCR-000259 | NCR | Contractor not ready for inspection. Re-welding inspection for truss -1 GYB. |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2015-10-19 | 2015-12-08 16:42 | 50 | 2015-10-05 16:47 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | The contractor has not been ready for inspection IRF 043 as the works delayed. The contractor did not give notice.
| 02SL - Stations (LUL) | Cxxx-NCR-000260 | NCR | Incorrect manufacture of MEP modules |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2015-10-23 | 2015-12-01 08:46 | 39 | 2015-10-09 11:12 | Electrical - Cable Management | 8000 |  | Manufacturing Defect | Rework | 2 (6-60k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | 1: 3: Tray CMS cut on unistrut bracket subsequently producing sharp edges. The issue is requiring rework on manufactured modules that have been already delivered and installed on site. 2: Galvanised fixings for CMS used. As per Works Information these should be BZP coating. Rework required to change to the specified fixing type.
| 02SL - Stations (LUL) | Cxxx-NCR-000261 | NCR | GYB - Section of secondary wall 1F out of position |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2015-10-26 | 2015-12-01 16:11 | 36 | 2015-10-12 14:08 | Civil - Civil Engineering General | 5000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Part of wall 1F was constructed to the alignment given in superseded drawing Cxxx-OVE-S-DDD-N105_2-34611 Rev P03. Drawing was revised to C02 status on 16th of July 2015 which shows different alignment. See attached highlighted drawing Cxxx-OVE-S-DDD-N105_2-34611 Rev C02
| 02SL - Stations (LUL) | Cxxx-NCR-000262 | NCR | Concrete Delivery: Out of Time (GYB) |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2015-10-26 | 2015-12-14 12:58 | 49 | 2015-10-12 16:03 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Concrete delivery 07/10/15 Batched:16:15 End of discharge:18:50 Total delay: 35min 07/10/15 Batched:13:50 End of discharge:16:30 Total delay: 40min 07/10/15 Batched:13:23 End of discharge:15:40 Total delay: 17min 09/10/15 Batched:15:09 End of discharge:17:30 Total delay: 21min had exceeded the allowable time of 120min from batching to discharge finish from 17min to 40min. Concrete for VentTower and Secondary walls at GYB. Keep in mind concrete not finished build in when concrete lorry is washing out.
| 02SL - Stations (LUL) | Cxxx-NCR-000263 | NCR | GYB Superstructure - Broken concrete surface |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-01-20 | 2016-02-22 15:31 | 33 | 2015-10-12 17:49 | Civil - Civil Engineering General | 2000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | A section of the concrete surface on the construction joint, level +1 to +2 in wall 1, has broken off after the shutter was struck. See attached photographs
| 02SL - Stations (LUL) | Cxxx-NCR-000264 | NCR | Under Platform Module Benchmark |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2015-10-27 | 2015-11-26 08:25 | 30 | 2015-10-13 14:07 | Electrical - Cable Management | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Please note that numerous meetings and correspondence have taken place between the Project Manager and the Contractor, in relation to the Quality and Installation of the Under Platform Module Installation. The Project Manager is unable to secure a Benchmark Inspection date from the Contractor, despite numerous requests, dating from the 18/09/2015 to the 13/10/2015 on a weekly basis at the MEP meetings. The Project Manager requires the Contractor to demonstrate a series of modules installed and containing coupled/linked CMS as a benchmark, to ensure the Contractors Installation can meet the Specification requirements. The current site activities are contrary to the Works Information Volume 2B – Part 20 – Quality Management 20.7 , that clearly indicates a Benchmark Inspection will be offered to the Project Manager from the Contractor to ensure the Quality of the Installation prior to installation continuity. This is also detailed within the Contractors Cxxx Tottenham Court Road Mechanical, Electrical and Public Health Specification Volume 1 – General Requirements-MEP Cxxx-LAO-M-RSP-N105_WS089-50002 Rev 1.0 JA.4006.
| 02SL - Stations (LUL) | Cxxx-NCR-000265 | NCR | Spring washers on modules |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2015-11-10 | 2015-11-25 08:19 | 15 | 2015-10-20 11:24 | Electrical - Cable Management | 1500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | It has been identified by the Contractor that spring washers were not used during the manufacturing of the under-platform modules. As such none of the CMS installed has spring washers fixing the equipment in place.
| 02SL - Stations (LUL) | Cxxx-NCR-000266 | NCR | WTH - Level -4 - Cavity Drainage - Sealed Joints with Silicone |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2015-12-03 | 2015-12-17 08:25 | 14 | 2015-10-14 17:21 | Civil - Civil Engineering General | 2000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Cavity Drainage on Level -4 North box and Level-4 between Mezzanine at Core 4 had sealed joints with silicone instead of a normal push fitting with no jointing material required
| 02SL - Stations (LUL) | Cxxx-NCR-000267 | NCR | Misalignment of PTW East End platform end walls |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-02-12 | 2016-02-15 15:07 | 3 | 2015-10-15 12:49 | Civil - Civil Engineering General | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Management Problem - Inadequate supervision | Completed |  | There is a misalignment of PTW East End platform end walls (Wall C) and making good to the concrete is required. Please refer to drawing number Cxxx-LAO-C-DWG-N105_WS089_5-50038 and attached photos.
| 02SL - Stations (LUL) | Cxxx-NCR-000268 | NCR | GYB VentTower: Reinforcement spacers sticking out of the external walls on CON 103 architectural concrete. |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2015-11-14 | 2015-12-15 10:13 | 31 | 2015-10-15 13:53 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Reinforcement spacers sticking out of the external wall 5 and wall 3 at +1 level VentTower on CON 103 architectural concrete. This will influence the architectural surface and the concrete cover. On wall 5 one bit is sticking out 5 mm.
| 02SL - Stations (LUL) | Cxxx-NCR-000269 | NCR | Escalator Assurance |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-11-13 | 2016-10-04 11:30 | -40 | 2015-10-15 17:11 | Mechanical - Escalators | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | __ have progressed procurement of components and associated assurance inspections and collation of certification in advance of Code 1 acceptance of the Inspection Test Plan.
| 02SL - Stations (LUL) | Cxxx-NCR-000270 | NCR | Out of position Shear Walls in PTE |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-01-27 | 2015-11-30 15:05 | -58 | 2015-10-16 09:42 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following an as-built survey of the shear walls, it has been identified that 1No shear wall at CH 4966.400 and 2No shear walls at CH 4969.000 within PTE are out of positional tolerance along the longitudinal length of the track slab. The shear wall on the corbel side of the track slab at CH 4966.400 is out of position by 15-20mm. Both shear walls on both sides of the track slab at CH 4969.000 are out of position by 35-40mm. The size of shear walls are as per design and all faces plumb. As-built survey of shear walls attached.
| 02SL - Stations (LUL) | Cxxx-NCR-000271 | NCR | Missing Movement Joint in PTW Platform Corbel |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2015-12-23 | 2015-11-02 16:58 | -51 | 2015-10-16 14:00 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | It has been identified that the movement joint within the platform corbel at CH 4772.488 between Bays 1 and 2 in PTW has not been formed. See attached photo. The movement joint has been constructed within the platform slab and platform walls.
| 02SL - Stations (LUL) | Cxxx-NCR-000272 | NCR | Bulging of alignment beam grout |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2015-11-02 | 2015-11-02 16:59 | 0 | 2015-10-19 16:27 | Civil - Civil Engineering General | 5000 |  | Material | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The grout installed above alignment beams has bulged out beyond the line of the alignment beam by up to 40mm. This has occured in multiple locations where the finger shuttering system was used.
| 02SL - Stations (LUL) | Cxxx-NCR-000273 | NCR | Reduced cover GYB superstructure, Column C2 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-06-30 | 2016-07-19 10:55 | 19 | 2015-10-20 13:37 | Civil - Civil Engineering General | 6000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Management Problem - Inadequate supervision | Completed |  | There is reduced cover on one of the columns level +0 to +1 (+125.06 to +126.06). It is column C2 GL G/2. The column has been surveyed and on the external face it has cover of 38mm on one face and 14mm on another. See attached sketch.
| 02SL - Stations (LUL) | Cxxx-NCR-000274 | NCR | Missing starter bars level +1 slab, Wall 13 and 17 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-03-18 | 2016-01-07 08:41 | -71 | 2015-10-20 14:13 | Civil - Civil Engineering General | 2000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Starter bars for Wall 17 and a section of Wall 13 are missing from the level +1 slab
| 02SL - Stations (LUL) | Cxxx-NCR-000275 | NCR | GYB Concrete cracks on the architectural external walls at VentTower wall3/+1 Level |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2015-11-20 | 2015-11-30 15:33 | 10 | 2015-10-21 16:38 | Civil - Civil Engineering General | 5000 |  | Manufacturing Defect | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 4 x Concrete cracks on the architectural external walls at VentTower wall3/+1 Level have been spotted. They are up to 4m long. In some parts they are up to 0.4mm wide. The with can be tested with a fine mechanical drill bit in size 0.4mm. Please find attached pictures.
| 02SL - Stations (LUL) | Cxxx-NCR-000276 | NCR | Concrete delivery out of time |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2015-11-18 | 2015-12-15 10:14 | 27 | 2015-10-21 16:37 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Concrete delivery 20/10/15 2015 Batched 12:38 had exceeded the allowable time of at least 60min from batching when discharge did not start until 15:00. Concrete used for second lift on secondary wall1K -1 GYB .
| 02SL - Stations (LUL) | Cxxx-NCR-000277 | NCR | GYB Honey combing on external architectural walls5/3 at VentTower +1 Level & Steps in formwork panels greater than 3mm |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2015-11-20 | 2015-12-22 11:29 | 32 | 2015-10-21 16:35 | Civil - Civil Engineering General | 5000 |  | Manufacturing Defect | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | GYB Honey combing on external architectural walls5/3 at VentTower +1 Level
| 02SL - Stations (LUL) | Cxxx-NCR-000279 | NCR | Concrete cubes not covered up and not stored in water. |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2015-11-19 | 2015-12-04 14:51 | 15 | 2015-10-22 12:31 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Concrete cubes taken at the 20/10/15 for secondary walls were found 2 days later in the mould not covered up and not stored in water.
| 02SL - Stations (LUL) | Cxxx-NCR-000280 | NCR | Drill and Fixed bars level +2 landing |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-03-25 | 2015-12-08 13:35 | -108 | 2015-10-27 10:54 | Civil - Civil Engineering General | 6000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Management Problem - Inadequate supervision | Completed |  | Couplers for the landing slab at level +2 in Wall 2 have been cast too high.
| 02SL - Stations (LUL) | Cxxx-NCR-000281 | NCR | WTH -2 to -1 wall upon GL B/8-9 construction issues |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2015-11-30 | 2015-12-16 15:17 | 16 | 2015-10-29 11:50 | Structural Engineering - Concrete Member | 10000 |  | Planning | Repair | 2 (6-60k) | Complete | Supervision - Insufficient supervision | Completed |  | The Contractor has encountered an issue with a concrete wall pour at -2 level within a WTH. The wall concerned is located: -2 level GL B/8-9 The wall was incorrectly poured before shuttering and reinforcement was correctly vertically positioned. This resulted in the following being incorrect: - Face off the concrete (east side) out of verticality by up to 23mm determined by as-built survey (attached) - Reinforcement out of verticality. The pour was stopped due to the above, therefore concrete did not get finished correctly (see attached photos).
| 02SL - Stations (LUL) | Cxxx-NCR-000282 | NCR | 28 day cubes - crushed too early, Wall 2 GYB +1 to +2 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-02-10 | 2015-11-09 12:44 | -93 | 2015-11-02 16:38 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | The 28day concrete cubes for the wall 2 pour level +1 and +2 on the 12/10/2015 were crushed at 7days and not 28 days, due to the incorrect manufacture date being issued on the collection receipt to the testing lab. The pour history, cube sheet and returned test certificate are all attached.
| 02SL - Stations (LUL) | Cxxx-NCR-000283 | NCR | GYB L-1 Decline Walkway CON-103 Graffiti |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2016-06-15 | 2016-06-09 06:15 | -6 | 2015-11-03 11:23 | Architectural - Ceilings & Soffits | 2000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | External Phenomenon - Theft, tampering, sabotage, or vandalism | Completed |  | Graffiti assumed to be made by black marker pen has been drawn onto the ceiling in the GYB L-1 decline walkway (CON-P 2/3). The area affected by the graffiti is an exposed concrete soffit in the finished station and is required to be CON-103 Insitu concrete. This was constructed by Others but is the responsibility of the Cxxx Contractor.
| 02SL - Stations (LUL) | Cxxx-NCR-000285 | NCR | No valid Welding Procedure and other documents for on site welding in place (GYB trusses and couplers). |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2015-11-30 | 2015-11-27 12:34 | -3 | 2015-11-03 14:22 | Structural Engineering - Welding | 1000 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | After the on site welding of the trusses in -1 level GYB (diagonals at wall 1f), the contractor has been asked to forward several documents for the quality process. The required documents have been specified. The contractor forwarded some documents, but not the required ones stated in the National Structural Steelwork Specification. Also for the upcoming works, the welding of the couplers for the secondary walls at the GYB box, the documents are not in place. These documents (see below in technical requirements) are to be present before the welding works start.
| 02SL - Stations (LUL) | Cxxx-NCR-000286 | NCR | UTX Duct Termination |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2016-01-15 | 2016-02-10 09:06 | 26 | 2015-11-03 15:24 | Civil - Civil Engineering General | 10000 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | The UTX’s, at trackside, have been terminated at the First Stage Concrete level. However, in order to allow for the Systemwide cabling to extend along the tunnel, the UTX is required to extend through the corbel.
| 02SL - Stations (LUL) | Cxxx-NCR-000287 | NCR | GYB Superstructure - Reduced cover to lacers W3, LVL +132.660 to +133.960 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-04-02 | 2015-11-24 10:53 | -130 | 2015-11-04 08:09 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Reduced cover of 30-35mm on 10no. lacers in Wall 3, level +132.66 to +133.96. See attached photos.
| 02SL - Stations (LUL) | Cxxx-NCR-000288 | NCR | Wind Posts WTH Level -3 Position and Alignment |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2015-11-18 | 2015-11-24 10:56 | 6 | 2015-11-04 09:16 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Upon an as-built check of the wind posts the Contractor has found 2 wind posts that aren't correctly installed. The first wind post on GL 7 between GL D & E has not been centred on the centre line of the blockwork as shown on drawing Cxxx-LAO-A-DDD-N105_4-2204. Instead the wind post's West Face has been aligned with the west face of the wall and thus 25mm further east. See attached sketch. The second wind post is between GL 7-8 and on the perimeter wall (GL E). The verticality is incorrect with a difference of 24mm between the base and the head of the wind post. Blockwork tolerances allow for +-10mm over 3m height and +-14mm over 7m height. This wind post is 4.6m high.
| 02SL - Stations (LUL) | Cxxx-NCR-000289 | NCR | Closed up shutters at inspection - not providing witness point according to ITP |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2015-11-22 | 2015-11-24 14:37 | 2 | 2015-11-04 13:47 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | At the 30/10/15 the client field engineer __ has been called in for pre pour inspection by Site Engineer __ at wall 1f at -1 Level GYB. No correct drawings have been presented to him. No relevant FCD has been shown to him (which is recorded on the pre pour by the field eng). And the item to be inspected was covered up by form work. An adequate inspection was impossible.
| 02SL - Stations (LUL) | Cxxx-NCR-000290 | NCR | Out of tolerance track slab levels in PTE and PTW |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2015-12-23 | 2015-11-27 17:08 | -26 | 2015-11-04 15:28 | Civil - Civil Engineering General | 5000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The track slab level has a tolerance of +0mm/-10mm. Attached is the track slab as-built survey for both PTE and PTW. The as-built shows the AOD level as well as indicating the difference between design level and as-built level as + or - Xmm. As can be seen on the as-built survey, there are a number of points which fall outside of the +0mm/-10mm tolerance, either being greater then 0mm high or greater than 10mm low. The majority of the track slab is within the +0mm/-10mm tolerance.
| 02SL - Stations (LUL) | Cxxx-NCR-000291 | NCR | GYB -1 The client has been not invited for pre pour inspection. |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2015-11-19 | 2015-11-24 14:37 | 5 | 2015-11-05 13:06 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | On GYB -1 level wall 1f, the client received no pre pour inspection request for the second lift pour at the 051115. The contractor should do that as per ITP General Concreting Cxxx-LAO-O4-ITP-N105_WS089-50002. Also the Site Engineer __ did not know about this requirement. He should be briefed to this procedure.
| 02SL - Stations (LUL) | Cxxx-NCR-000292 | NCR | Columns out of plumb WTH, Level -1 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-06-01 | 2016-03-24 10:23 | -69 | 2016-01-13 11:08 | Civil - Structural Engineering | 2000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | 500sq column GL B/4 and column C-1-C GL B/3 at level -1 WTH have been cast out of plumb ( out of tolerance) referring to ITP Cxxx-LAO-O4-ITP-N105_WS089_Z-50002 . Please see attached as built survey DWG.
| 02SL - Stations (LUL) | Cxxx-NCR-000294 | NCR | Use normal ply wood instead of "pour form" and steps in the form work GYB -1. |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2015-11-23 | 2015-12-01 16:09 | 8 | 2015-11-09 16:25 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | At the -1 GYB secondary wall 1A the contractor uses normal ply wood instead of "pour form" for finish type CON-104.
| 02SL - Stations (LUL) | Cxxx-NCR-000295 | NCR | No as build information provided by the contractor for the VentTower (GYB). |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2015-11-13 | 2015-12-22 11:04 | 39 | 2015-11-09 16:24 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | __ Method Statement states “As built surveys will be carried out progressively to ensure that workmanship complies to tolerance required." Despite requests for sight of these over a period in excess of 3 weeks, none have been provided. The assumption is that none have been carried out contrary to the requirements of the MS.
| 02SL - Stations (LUL) | Cxxx-NCR-000296 | NCR | Concrete cover issue Wall 1F -1 Level GYB |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2015-11-24 | 2016-01-08 15:57 | 45 | 2015-11-10 11:50 | Civil - Civil Engineering General | 2000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | There is only max 10mm distance form the bars to the mineral (movement joint at column side). Please see attached. Specified cover is 30mm. Please see attached.
| 02SL - Stations (LUL) | Cxxx-NCR-000297 | NCR | Mezzanine slab Core 4 - post drilled bars |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-05-29 | 2016-02-15 12:50 | -104 | 2015-11-11 14:03 | Civil - Structural Engineering | 2000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | 16no couplers for bars highlighted on DWG Cxxx-LAO-C-DWG-N105_WS089_5-50012 have been installed on incorrect height - below level of mezzanine slab behind Core 4 at level -4.
| 02SL - Stations (LUL) | Cxxx-NCR-000298 | NCR | CON-103 finish level +1 to +2 phase 1 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-04-11 | 2015-11-26 13:29 | -137 | 2015-11-13 14:20 | Civil - Civil Engineering General | 5000 |  | Workmanship | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | There are stepped joints in the level +1 to +2 that do not conform to the CON-103 specification. See the attached sketch showing where the joints are out of tolerance.
| 02SL - Stations (LUL) | Cxxx-NCR-000300 | NCR | WTH PES Support Reactions - interface with platform nosing |  | Crossrail | PDP | TCR - Tottenham Court Road Station (West) |  | 2017-01-31 | 2016-07-01 13:15 | -214 | 2015-11-13 13:52 | Civil - Structural Engineering | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | The Project Manager has been advised that the loading from the PES support posts through the extent of the Western Ticket Hall exceeds the allowable loading for which the platform nosing was designed. The loading constraints were set out in drawing Cxxx-ATK-S-DDD-CR001_Z-45001 issued to the Contractor in PMI-00148 on 23rd May 2014. The Contractor has not incorporated this loading constraint within his design for the PES. Additionally the Contractor has already built the platform nosing to the original Cxxx loading constraints. The PES design has not been coordinated with the platform nosing and therefore the platform nosing is not capable of supporting the WTH PES as currently designed. The Project Manager awaits a proposal from the Contractor to rectify this design defect in the PES including any remedial works that are necessary to accommodate his proposal.
| 02SL - Stations (LUL) | Cxxx-NCR-000302 | NCR | Comfort Cooling Late Design Change Submission |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2015-11-30 | 2015-12-03 12:46 | 3 | 2015-11-16 16:43 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | DX Cooling Unit selection RFI-000526 stating that the stage E design should not be progressed and another solution should be proposed was issued on the 11th November 2014. Cxxx-CCM-01671 was issued on the 16 October 2015 proposing a VRF system and asking for a PMI to instruct the change however the Western Ticket Hall gate was first issued in 2015 and again on the 29th October 2015 with the Stage "E" DX cooling units still specified. The PM is concerned due to the length of time that elapsed in providing a compliant, workable solution.
| 02SL - Stations (LUL) | Cxxx-NCR-000303 | NCR | GYB - Wall 1 level +2 - +3. Incorrect cubing |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-01-31 | 2016-02-05 15:02 | 5 | 2015-11-16 16:48 | Civil - Civil Engineering General | 5000 |  | Supervision/Management | Use As-Is | 3 (3-6k) | Complete | Management Problem - Inadequate supervision | Completed |  | Due to a mistake cubing up the wall 1 pour for level +2 to +3 there was insufficent concrete to complete the pour and it was not completed to the horizontal construction joint. The cube up had been checked by 2 site engineers. The mistake was realised at 1815 on Friday 13/11/2015 at which point the batching plant and back-up batching plant were both contacted but both were closed. The pour was then left between 200-400mm low along the length of wall 1. On the following day Saturday 14/11/2015 the joint was jet washed, the sand, water and laitance removed and the pour completed up to the construction joint line.
| 02SL - Stations (LUL) | Cxxx-NCR-000304 | NCR | Buttress reinforcement mis-alignment -2 to -1 level GL 6-7/A, 7/A and 8/A |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2015-11-30 | 2015-12-16 15:19 | 16 | 2015-11-16 17:37 | Structural Engineering - Reinforcement | 5000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | With 3no. R.C. buttresses at -2 level grid lines 6-7/A, 7/A and 8/A, main bar reinforcement has been positioned out of place (see attached sketch of As-built). This has resulted in bars being offset to link positions. Buttresses are denoted as: - B14 (GL 8/A): Where an additional line of links have been positioned due to main bars being too far away from each other, - B10 (GL 6-7/A): Where internal main bars where offset to the link by 100mm. B25 bars have been placed in line with the sketch. Also owed to a large gap between main bars (320mm) an additional B20 bar was installed. - B10 (GL 7/A): Where various bars have are offset to link. Additional bars have been installed as per sketch
| 02SL - Stations (LUL) | Cxxx-NCR-000305 | NCR | Brass Bonding Bolts |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-03-15 | 2016-03-14 09:14 | -1 | 2015-11-17 10:56 | Electrical - Cable Management | 6000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | There are no brass bolts used on the cable tray earth braid connections
| 02SL - Stations (LUL) | Cxxx-NCR-000306 | NCR | Incorrect setting out of recess in Wall 9 Level +2 to Level +3 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-01-16 | 2015-12-08 16:12 | -39 | 2015-11-17 11:48 | Civil - Civil Engineering General | 10000 |  | Supervision/Management | Repair | 2 (6-60k) | Complete | Management Problem - Inadequate supervision | Completed |  | The 100mm recess in Wall 9 between Gridline 1 & 2 at between Level +2 and Level +3 has been incorectly extended up to the Column while it should stop 1200mm before the column (see attached drawing). The recess is 1200mm long, 400mm height and 100mm thick.
| 02SL - Stations (LUL) | Cxxx-NCR-000307 | NCR | PES interface with SCL transititions (east of E/B & west of W/B) |  | Crossrail | PDP | TCR - Tottenham Court Road Station (West) |  | 2015-12-16 | 2015-12-11 10:05 | -5 | 2015-11-18 11:26 | Civil - Civil Engineering General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | It has come to the Project Managers attention that the design for the PES as submitted by the Contractor at SC1 Gate has not been adequately coordinated with the geometry of the SCL tunnels with specific reference to the eastern extent of the eastbound tunnel and the western extent of the westbound tunnel over the extent of the transition between the standard SCL profile and the bored tunnel interface. The Works Information contain a generic design by Cxxx, as set out in table 7.1 and clause 7.1.2 states that no further Employer design will be issued. The Project Manager reminds the Contractor that the Works Information Volume 2A Part 7 requires the following from the Contractor; - the contractor to complete the structural steelwork detailing and connections; - for generic details, resolve the particular condition and its application in completing Stage F2; and - RIBA F design for the platform structure overhead steelwork to support ventilation ducts, CMS and cladding. The Project Manager additionally issued PMI-00019 in February 2013, instructing the Contractor of the following: - progress their station detailed design of civil, architectural, MEP and structural elements of the Platform Edge Screen (PES) bespoke to Tottenham Court Road Station in accordance with the Cxxx RIBA Stage F1 design information for civil/structural and architectural elements and the updated RIBA Stage E design for MEP identified on the Volume 2C Document List Revision 6.0 (by reference to PMI-00019); - to incorporate the final structural fixing details, applying the generic Employer's design; and - completing the final detail of the architectural and MEP design to enable the PES to be incorporated into and coordinated with the particular station arrangement, condition and interfaces. It is apparent that the contractor has not adequately completed the above prior to submission of the PES design for Assurance Gate Review (SC1) on 20th July 2015 as the PES does not coordinate with the SCL geometry. The Project Manager advises this is considered a defect in the Contractors design and awaits the contractors proposal to address.
| 02SL - Stations (LUL) | Cxxx-NCR-000308 | NCR | GYB - Lift 11 wall-5 shutter kicked in by upto 22mm |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2015-12-02 | 2015-12-10 10:30 | 8 | 2015-11-18 16:35 | Civil - Civil Engineering General | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | After striking formwork from lift 11 at -4 it was noticed that wall 5 (north of the lift shaft had kicked in by approx. 22mm, probably because of the over tightened shutters.
| 02SL - Stations (LUL) | Cxxx-NCR-000309 | NCR | GYB - Exposed reinforcement in lift 11 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2015-12-02 | 2016-01-07 08:37 | 36 | 2015-11-18 17:22 | Civil - Civil Engineering General | 10000 |  | Damaged | Repair | 2 (6-60k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Additional pockets were cut to support Peri platform inside the lift 11 during construction. This process exposed the reinforcement within two walls at four locations (please see attached photographs). Any other areas where reinforcement has been exposed will be repaired as below.
| 02SL - Stations (LUL) | Cxxx-NCR-000311 | NCR | GYB VT "Eazystrip" dimension unsuatable for wall/slab dimensions of 300mm |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2015-12-04 | 2015-12-24 11:24 | 20 | 2015-11-20 10:54 | Civil - Civil Engineering General | 5000 |  | Supervision/Management | Use As-Is | 3 (3-6k) | Complete | Supervision - Insufficient supervision | Completed |  | At pre pour inspection at 16/11/15 at +3level Vent Tower GYB it has been discovered that EAZYSTRIP pre fab starter bar modules available on site are only 270mm wide. If these are used for slabs and walls with dim 300mm, it is questionable to provide cover requirements - 30/35mm inside face. (Please see for clarification attached "1.jpg". At this particular inspection it has been found too little cover at the transition point to the wall/slab of 10mm.
| 02SL - Stations (LUL) | Cxxx-NCR-000312 | NCR | Design Managment Plan's compliance with Works Information v2B |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2015-12-04 | 2016-01-27 08:10 | 54 | 2015-11-20 11:14 | Systems - Other | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | This NCR has been raised to ensure the following items are satisfactorily addressed in a timely manner: • There is no section on ROLES AND RESPONSIBILITIES within the document. Therefore, it is unclear who is responsible for various aspects of the plan and design elements e.g. who is responsible for the verification and validation process, interfaces, environmental issues, etc, • There is no reference to the Mini-Gate Risk Assessment in the document. This is a requirement of Engineering Design Assurance Gates Procedure and should be clearly addressed in DMP, • There is no mention about the design planning or programme and how this is to be achieved by the Contractor, • No Design Validation Reports have been found on eB at the time of surveillance which have been referred to in DMP, • There is no mention about manufacturing and fabrication certification in accordance with the requirements of the Works Information. For details refer to the surveillance report ref. no. Cxxx-XRL-O4-RGN-CR001-50012.
| 02SL - Stations (LUL) | Cxxx-NCR-000313 | NCR | Design Management Plant late revision |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2015-12-04 | 2016-01-27 08:11 | 54 | 2015-11-20 11:30 | Systems - Other | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | This NCR has been raised for the late issue (after 457 days) of the revised Design Management Plan as described in the surveillance report ref. no. Cxxx-XRL-O4-RGN-CR001-50012.
| 02SL - Stations (LUL) | Cxxx-NCR-000314 | NCR | Surveillance QS422-11: Documentation not provided within agreed timeframe. |  | Crossrail | PDP | TCR - Tottenham Court Road Station (West) |  | 2016-12-12 | 2016-12-22 11:20 | 10 | 2015-11-20 12:50 | Architectural - General | 5000 |  | Documentation and Records | Rework | 3 (3-6k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | Further to Surveillance QS422-11 held 11 November 2015 Documentation that was listed as being required for Post Surveillance Review on 16 November 2015 were not supplied within this timeframe.
| 02SL - Stations (LUL) | Cxxx-NCR-000316 | NCR | GYB - Shrikage crack in wall 3H |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2015-12-04 | 2015-12-08 09:38 | 4 | 2015-11-20 16:20 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A shrinkage crack has appeared in top corner of door opening in wall 3H. crack seems to be approx. 0.4mm (measured by Crossrail field Engineer). Please see attached photograph and drawing for location.
| 02SL - Stations (LUL) | Cxxx-NCR-000317 | NCR | Omit 1no. B40 starter bar -4 composite circular column GL B/7-8 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2015-12-11 | 2015-12-16 15:26 | 5 | 2015-11-23 08:11 | Structural Engineering - Reinforcement | 1000 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The Contractor has determined a clash with one of the B40 starter bars for the circular composite column upon GL B/7-8 at -4 level. The bar, in its current position shall be in the way of the 40mm thick structural steel splice plate required here to connect the structural steelwork UC sections together (drawing Cxxx-LAO-C-DWG-N105_WS089_Z-50003).
| 02SL - Stations (LUL) | Cxxx-NCR-000318 | NCR | Truss 1 diagonal splice Gap's GL 3/B-D |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-01-12 | 2016-01-04 12:39 | -8 | 2015-11-23 08:55 | Structural Engineering - Steel Member | 2000 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Similar to FCD 327, the Contractor has encountered an issue with closing a gap beteen two spliced UC members within the truss 1 structure located within the WTH at -1 level. In positioning the diagonal members between -1 and +0, a gap has opened between two abutting flanges at locations highlighed attached. The gaps have been measured on site to be: - GL 3B = 1.5mm - GL 3D = 1.2mm. The Contractor can however confirm that all bolts/ splice plates are correctly installed as per design.
| 02SL - Stations (LUL) | Cxxx-NCR-000320 | NCR | Post Pour Inspection: TCR, WTH, -2 Level. Inspection according to Cxxx-LAO-O4-ITP-N105_WS089-50002 and Cxxx-LAO-O7-ITP-N105_WS089_Z-50001 . 19 no. couplers missing. |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2016-06-05 | 2016-05-18 14:06 | -18 | 2015-11-23 15:11 | Civil - Civil Engineering General | 10000 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Management Problem - Inadequate supervision | Completed |  | Further to Site Observation CLR observed: TCR, WTH, -2 Level. 19 numbers of couplers missing. Main contractor has to drill and glue new rebar's - instead to use couplers. For more details go to attached Site Observation.
| 02SL - Stations (LUL) | Cxxx-NCR-000321 | NCR | TCR, WTH, -3 Level. Site Inspection: Precast Stair Installation on Site. Accepted with comment - Lack of protection. |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2016-01-22 | 2016-02-22 15:34 | 31 | 2015-11-23 15:21 | Civil - Civil Engineering General | 5000 |  | Damaged | Repair | 3 (3-6k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | Further to Site Observation 17.11.2015 Location: TCR, WTH, -3 Level. CRL and __ have been checked the precast stairs installation an according to the Cxxx-LAO-O4-ITP-N105_WS089_Z-50011 CRL Comment: Lack of proper protection caused the damages. For more details go to attached Site Observation.
| 02SL - Stations (LUL) | Cxxx-NCR-000322 | NCR | TCR, WTH,- 3 Level. A numbers of windpost demolished. |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2016-01-22 | 2016-02-09 10:48 | 18 | 2015-11-23 15:34 | Civil - Civil Engineering General | 10000 |  | Design | Rework | 2 (6-60k) | Complete | Design Problem - Approval of Design Change Notice (FCN/FCR) in CTI excessive | Completed |  | Further to Site Observation 10.11.2015 CLR comments: A numbers of windpost demolished. Main Contractor is dealing with the designer to clarify this issue. Location TCR, WTH,- 3 Level, GL: a/10-8 For more details go to attached Site Observation.
| 02SL - Stations (LUL) | Cxxx-NCR-000323 | NCR | TCR, WTH, Level -2, GL: 5-6/B-DD, Demolition of the concrete beam. |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2016-01-22 | 2016-02-10 15:02 | 19 | 2015-11-23 15:53 | Civil - Civil Engineering General | 10000 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Further to Site Observation 09.10.2015, CLR observed: Due to lack of quality (horizontal deflection 20 to 30 mm) the concrete beam was demolished. For more details go to attached Site Observation.
| 02SL - Stations (LUL) | Cxxx-NCR-000325 | NCR | TCR, WTH, Level -3, According to Post Pour Inspection: Some of the walls, they do not have correct dimensions and positions. The full as built survey required for ALL concrete structure at all levels. |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2016-03-31 | 2016-03-23 08:59 | -8 | 2015-11-23 16:09 | Civil - Civil Engineering General | 3000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Further to Site Observation 05.10.2015 CLR observed: Location: TCR, WTH, Level -3, According to comments from Post Pour Inspection: Some of the walls, they do not have correct dimensions and positions. The full as built survey required for ALL concrete structure at all levels. For more details go to the attached Site Observation.
| 02SL - Stations (LUL) | Cxxx-NCR-000326 | NCR | WTH,- 3 level, Core 4 According to Post Pour Inspection: Concrete Wall, 28 mm deviation from the vertical. |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2016-02-28 | 2016-03-08 08:49 | 9 | 2015-11-23 16:18 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Supervision - Other | Completed |  | Further to Site Observation 23.10.2015 CLR observed: Concrete Wall, 28 mm deviation. The thickness in the central part of the wall is larger 28mm from rest of the wall. For more details go to the attached Site Observation.
| 02SL - Stations (LUL) | Cxxx-NCR-000327 | NCR | Additional links to buttress B1 Gl 8-9/A |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-05-12 | 2016-03-17 12:43 | -56 | 2016-01-13 11:45 | Civil - Structural Engineering | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | B12 Links BM 309 highlighted on attached DWG have been fixed around 2nd vertical bar instead middle bar due to incorrect spacing between second and first bar bigger than 150mm - additional row of B12 links required.
| 02SL - Stations (LUL) | Cxxx-NCR-000328 | NCR | Openings with GYB Level -2 alignment with Wind Post and Walling below |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2015-12-08 | 2015-12-10 11:53 | 2 | 2015-11-24 08:44 | Archaeology - General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Previous Construction - Problems based on previous construction errors | Completed |  | At GYB Level -2 the openings within the structural slab cast by others is out of position by 4 to 12mm. The blockwork and wind post below at Level -3 are set out to align to the edge of this opening thus to not impede services going through the opening.
| 02SL - Stations (LUL) | Cxxx-NCR-000329 | NCR | Not sufficient cover for Slab Level +3 (Section along W1) |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-02-22 | 2015-12-08 09:55 | -76 | 2015-11-24 11:03 | Structural Engineering - Reinforcement | 5000 |  | Incorrect Installation | Use As-Is | 3 (3-6k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | 4No. B16 bars from eazistrip along Wall 1 have 15-20mm cover on the underide of slab Level +3 in the section shown on the attached drawing. The 15-20mm cover extends for approximately 20mm from the face of the wall and after this, sufficient cover is provided.
| 02SL - Stations (LUL) | Cxxx-NCR-000331 | NCR | Clash between the platform builder's works and the GRC support system. |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-05-05 | 2017-04-26 15:31 | -9 | 2015-11-30 12:06 | Architectural - General | 10000 |  | Incorrect Installation | Rework | 2 (6-60k) | Complete | Design Problem - Inadequate or defective design | Completed |  | It has been identified that the builders works carried out on site, based on drawing Cxxx-LAO-Z-DWG-N105_WS089_5-50007, clash with the support frames for the platform GRC cladding. The level of clashes is identified in document 104014-BW-SK-068 "Platform As-Built Service Penetrations Analysis". Additionally the relocation of 2 platform cabinets in PTE has resulted in further clashes with GRC frames.
| 02SL - Stations (LUL) | Cxxx-NCR-000332 | NCR | Failure in following the quality process outlined within the ITP |  | Contr | TWC | TCR - Tottenham Court Road Station (West) |  | 2015-12-15 | 2015-12-08 15:38 | -7 | 2015-12-01 11:01 | Mechanical - Platform Edge Doors | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | The pre-cast concrete panels have been installed and grouted into position prior to the electrical continuity testing having taken place. This has been undertaken out of sequence from the ITP and contradicts the information given within the contract specification.
| 02SL - Stations (LUL) | Cxxx-NCR-000333 | NCR | Installation of unique, indelible identification number on pre-cast panels |  | Contr | TWC | TCR - Tottenham Court Road Station (West) |  | 2017-02-20 | 2017-03-03 12:11 | 11 | 2015-12-01 12:33 | Architectural - Signage | 5000 |  | Documentation and Records | Rework | 3 (3-6k) | Complete | Management Problem - Other | Completed |  | The pre-cast concrete panels have been installed without the unique, indelible identification number required as part of the specification and for future maintenance records. These numbers are also required for referencing the locations of the electrical continuity testing carried out on site.
| 02SL - Stations (LUL) | Cxxx-NCR-000334 | NCR | Electrical continuity of the rebar in GYB. |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-02-28 | 2017-02-27 16:59 | -1 | 2015-12-02 12:28 | Civil - Structural Engineering | 10000 |  | Incorrect Installation | Rework | 2 (6-60k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | The GYB shaft has been constructed up to L3 however the rebar has not been connected together in accordance with the requirements of the lightning protection specification CRL1-XRL-M-RSP-CR001-50052.
| 02SL - Stations (LUL) | Cxxx-NCR-000335 | NCR | Diaphragm Wall - Coring of adjacent Vertical bar |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2015-12-16 | 2015-12-18 09:26 | 2 | 2015-12-02 15:17 | Civil - Structural Engineering | 1000 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | During vertical coring of 52mm diameter holes, 2no locations where currently cast-in reinforcing steel was found to have been cored. The reinforcing steel affected appears to be the remainder of the B40/B50 starter bars which have been cut off during the wire sawing of d-wall operations and not the continuous bar into the remainder of the d-wall. In the 2no. core holes the bar appears to be 'grazed' from a depth of 300mm from cut off to approx. 600mm from cut off where the bar appears to terminate. Please refer to the attached sketches and photos.
| 02SL - Stations (LUL) | Cxxx-NCR-000336 | NCR | Diaphragm Wall - Coring of 2no. links on one core |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2015-12-17 | 2015-12-18 09:24 | 1 | 2015-12-03 08:08 | Civil - Structural Engineering | 1000 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | During vertical coring of 52mm diameter holes, in one core, it appears that 2no. horizontal links were cored, losing approximately 5mm of their diameter in cross section. The first link was 'grazed' at a depth of 500mm below cut off level and is on the 'hook' side. The second link was 'grazed' at a depth of 650mm on the 'main bar' side Please refer to attached sketches for further detail
| 02SL - Stations (LUL) | Cxxx-NCR-000337 | NCR | Incorrect Door Opening |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2015-12-17 | 2015-12-10 12:59 | -7 | 2015-12-03 14:33 | Architectural - Brickworks/Blockworks | 5000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Management Problem - Inadequate supervision | Completed |  | In setting out the walling within the WTH Level -4 North box for the door openings D2-5/004 (TR 1) and D2-5/006 (SR HV 1) the Contractor did not check the height of the door and in setting out the courses assumed a 2260mm height. Upon review and inspection this was picked up as incorrect.
| 02SL - Stations (LUL) | Cxxx-NCR-000338 | NCR | Access Hatch Opening WTH Level -4 Northbox |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2015-12-17 | 2015-12-17 13:07 | 0 | 2015-12-03 17:14 | Architectural - Brickworks/Blockworks | 1000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | The Contractor reviewed the position of the access panel which was adjacent to the wind post, note that it had moved from its original Cxxx opening position due to the ductwork that comes down through this space and opening in the slab, and believed that structurally fixing the galvanized steel cleat in this location would not be the correct method of installation as it would be against a chamfered column and the omega channel for ties was already installed so drilling fixings for the cleat would be difficult. Therefore a reduced access panel of 685mm x 485mm (wide) would be left to enable a 200m blockwork wall to support the lintel. This decision was mis-communicated between the Package Manager (__) and the Supervisor (__) and the opening was built 685mm x 685mm and moved 200mm to the right rather than reduced by 200mm. The Contractor extended the blockwork into the opening to reduce its width as planned.
| 02SL - Stations (LUL) | Cxxx-NCR-000339 | NCR | Precast Panel Cracking |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-04-30 | 2017-03-31 12:43 | -30 | 2015-12-03 17:38 | Civil - Civil Engineering General | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Cracking has been found in the PES precast sofit panels in PTW. Crack widths vary
| 02SL - Stations (LUL) | Cxxx-NCR-000340 | NCR | Cracking to PC panel beneath truss connection bracket |  | Contr | TWC | TCR - Tottenham Court Road Station (West) |  | 2017-05-05 | 2017-04-26 11:14 | -9 | 2015-12-04 11:29 | Architectural - Ceilings & Soffits | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | A significant sized crack has been identified protruding from the beneath truss connection bracket at PTW- W8 following torqueing of the FX20 bolt.
| 02SL - Stations (LUL) | Cxxx-NCR-000341 | NCR | Grouting within plenum movement joints |  | Contr | TWC | TCR - Tottenham Court Road Station (West) |  | 2016-02-15 | 2016-03-03 09:22 | 17 | 2015-12-04 11:47 | Architectural - Ceilings & Soffits | 10000 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | PTW - The plenum section movement joints located between the pre cast panels have been grouted in at platform side. This will need to be removed to enable the design intent.
| 02SL - Stations (LUL) | Cxxx-NCR-000342 | NCR | Works progressing without the approved documentation |  | Contr | TWC | TCR - Tottenham Court Road Station (West) |  | 2015-12-18 | 2015-12-08 15:41 | -10 | 2015-12-04 13:40 | Architectural - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | On numerous occasions works have been progressing on site without the relevant documentation having been submitted to and approved by Crossrail. This includes the following; Cxxx-LAO-Y-ITP-N105_WS089_5-50008 - Installation of precast soffit panels, duct lining panels, VCD's and access hatches. (Approved 27/11/15) Cxxx-LAO-O4-XDS-N105_WS089_5-50025 - Bolts, Nuts and Washers (No code) Cxxx-LAO-O4-XDS-N105_WS089_5-50024 - PTFE Shims (No code) Cxxx-LAO-O4-XDS-N105_WS089_5-50012 - __ Intumescent Acrylic Sealant (No code) Cxxx-LAO-O4-XDS-N105_WS089_5-50022 - C144 Firestop Strips & Blocks (No code) Cxxx-LAO-O4-XDS-N105_WS089_5-50010 - Mica glass- Mycalex MM60-75-M16 (Code 2 - Not accepted 02/12/15) The Project Manager requires the Contractor to submit the relevant documentation in a timely manner, to ensure the Contractors installation can meet the Specification requirements. The current site activities are contrary to the Works Information Volume 2B – Part 20 – Quality Management, that clearly indicates the Contractor shall not start on any activity on any part of the works for which the relevant QSP's and ITPs have not been accepted by the Project Manager.
| 02SL - Stations (LUL) | Cxxx-NCR-000343 | NCR | Bending starter bars at supended slab +1 VentTower |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2016-01-01 | 2016-01-14 09:23 | 13 | 2015-12-04 15:59 | Civil - Civil Engineering General | 3000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Starter bars for the suspended slab level on top of stub walls have been bended down at the transition point. The couplers have been set out at the wrong level. 30% have been replaced.
| 02SL - Stations (LUL) | Cxxx-NCR-000344 | NCR | GYB Escalator holes to close (30mm - 50mm) to slab edge -4 and -3 / outside slab cover |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2016-04-15 | 2016-02-26 14:29 | -49 | 2015-12-04 16:00 | Civil - Civil Engineering General | 5000 |  | Supervision/Management | Repair | 3 (3-6k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | At level -3 and -4 works have been started to install the escalator surrounding walls without approved design. Shear dowel holes have been drilled along one side parallel to the escalator on two levels. The steel in the slabs are designed with 50mm cover and 2 x 16mm bars. The holes are at some areas as close as 30mm which is deemed to be not suitable.
| 02SL - Stations (LUL) | Cxxx-NCR-000345 | NCR | RC repair works necessary in GYB -2 level wall2A. |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2015-12-18 | 2016-02-12 09:53 | 56 | 2015-12-04 16:00 | Civil - Civil Engineering General | 10000 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | At Wall 2A two layers of mineral are overlaying and therefore are reducing the cover zone. It is suspected there is no cover for the steel and needs to be repaired.
| 02SL - Stations (LUL) | Cxxx-NCR-000346 | NCR | GYB Concrete repair works needs to be done without ITP / MS. |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2015-12-24 | 2016-01-11 12:03 | 18 | 2015-12-04 16:00 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | At several locations at the VentTower and the Box concrete needs to be repaired including pre treatment of exposed steel. There is no Method Statement or ITP in place which gives the client the option to check the works been done correctly.
| 02SL - Stations (LUL) | Cxxx-NCR-000347 | NCR | GYB as build surveys for -5 and -4 level showing walls out of tolerance. |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2016-03-18 | 2016-03-09 09:36 | -9 | 2015-12-04 16:13 | Civil - Civil Engineering General | 10000 |  | Incorrect Installation | Use As-Is | 2 (6-60k) | Complete | Supervision - Insufficient supervision | Completed |  | At location -5 and -4 at the riser walls (see attached) a out of tolerance curvature/inclination has been spotted in the as builds presented by the contractor. At -4 level the tolerance will exceed into the staircase room. It needs to be also clarified why as builds have been issued on such a late date.
| 02SL - Stations (LUL) | Cxxx-NCR-000348 | NCR | GYB Crack detected at slab +1 in the fan rooms B769 at the first opening at north side |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2016-05-28 | 2016-05-03 11:56 | -25 | 2015-12-04 16:33 | Civil - Civil Engineering General | 5000 |  | Damaged | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A crack has been detected at the front face of the a slab. The steel will be effected and needs to be repaired. This will include the erection of a platform to gain access. There is currently no access. Therefore it needs to be investigated for structural condition once current platform has been build back.
| 02SL - Stations (LUL) | Cxxx-NCR-000349 | NCR | PES Trusses: Connection Brackets incorrect installation. |  | Crossrail | PDP | TCR - Tottenham Court Road Station (West) |  | 2017-03-21 | 2017-03-30 12:45 | 9 | 2015-12-07 13:35 | Archaeology - General | 50000 |  | Manufacturing Defect | Rework | 2 (6-60k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | 1. In the permanent condition, the weight of the truss is taken by the PES posts. 2. The fixings to the SCL are slotted in order that any tunnel movement can be absorbed. (For the temporary condition, there are two additional temporary bolts fixed at the crown bracket to prevent any movement – these will be removed when the PES posts are fitted). 3. I understand that the Cxxx design is for the PES post closest to the end of the 15m section (eg the right hand truss in the photo), is situated up to 1.6m away from the movement joint so that the end of the RH truss is cantilevered off the post in the permanent condition. 4. The end of the next truss, eg the left hand truss in the photo, is designed to sit on the cantilevered end of the RH truss, so that the PES post takes the load from some of the RH truss and some of the LH Truss. 5. However, in the photo, you can see that at the movement joint, the left hand truss is NOT sitting on the bracket of the right hand truss. This is incorrect. 6. This means that in the permanent condition, the end of the left hand truss is only being supported by the 55mm movement joint bolts which is not the design intent. 7. If you compare this to the Cxxx drawing (which is handed from the photo) you can see that the right hand truss is supported by PES post and the short cantilevered section.
| 02SL - Stations (LUL) | Cxxx-NCR-000350 | NCR | GYB CON-103 Finish level +132.24 to +134.9 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-03-17 | 2016-01-06 12:54 | -71 | 2015-12-08 11:08 | Civil - Civil Engineering General | 10000 |  | Workmanship | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | After an inspection between __ (H Fletcher) and CRL (__) minor defects were picked up in the CON-103 finish between +132.24 to +134.9. See marked up sketches showing the steps in joints, steps between ply lines above and below the CJ and corners that needed making good.
| 02SL - Stations (LUL) | Cxxx-NCR-000351 | NCR | PTW / PTE - Out of tolerance PSD cast in channels |  | Contr | TWC | TCR - Tottenham Court Road Station (West) |  | 2017-05-31 | 2017-03-14 15:32 | -78 | 2015-12-08 12:09 | Civil - Civil Engineering General | 10000 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Various PSD cast in channels along the platform nosing in both PTE and PTW have been surveyed as out of tolerance. This ranges between 10mm – 25mm in the worst instance. Drawing Cxxx--C-DWG-CR001-50003 details the tolerances for the PSD cast in channels as; 1) +/-20mm on positional dimensions between any __ channel along the platform edge. These are non cumulative. 2) +/- 10mm from track centre line. 3) +/- 10mm vertically As a result, the Contractor is to propose a solution to rectify this issue.
| 02SL - Stations (LUL) | Cxxx-NCR-000352 | NCR | GYB - level -3, water added to load and no cubes taken |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-03-17 | 2015-12-14 13:14 | -94 | 2015-12-08 18:19 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Water was added to a load of concrete to bring it into consistency. The water addition procedure from s was followed, however cubes were not taken from the load.
| 02SL - Stations (LUL) | Cxxx-NCR-000353 | NCR | GYB - Connection of Beam C31 to Wall 3 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-02-15 | 2017-01-17 10:22 | -29 | 2015-12-09 11:09 | Civil - Civil Engineering General | 5000 |  | Planning | Repair | 3 (3-6k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | Due to the sequence of constructing the GYB Superstructure (Phase 1 & Phase 2) the Beam C31 will be boxed out in W3 so that the B32 U-Bars are installed when the beam is constructed (FCD 419). The soffit of the beam is at the same level as the soffit of the slab in Level +3. During the construction of the slab at Level +3, the box out of the slab was missed out and therefore breaking out 300mm of the slab over a length of 1200mm is required in order to install the U-Bars at the end of the beam. During breaking out of the slab, no reinforcement will be cut or removed. This is shown on the sketch attached.
| 02SL - Stations (LUL) | Cxxx-NCR-000354 | NCR | Drill and fix 4 x snapped eazi-strip starter bars in W6 kicker at level +3 (136.860m) |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-03-18 | 2016-03-22 10:54 | 4 | 2015-12-09 16:01 | Civil - Civil Engineering General | 5000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Management Problem - Inadequate supervision | Completed |  | 12mm Eazi-strip bars snapped whilst being bent out of the way to accommodate a through shutter for the perpendicular walls.
| 02SL - Stations (LUL) | Cxxx-NCR-000357 | NCR | GYB - W2, level +1 to +2 pour 3, Cubes crushed at incorrect dates |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-03-18 | 2015-12-14 13:13 | -95 | 2015-12-09 11:07 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | Cubes GYBMC58A to D were sent to the lab with the incorrect cast date on. They were cast on the 14/10/15 and the date on the request sheet read 14/09/2015. The cubes have therefore been crushed at 3no at 9 days and 1no at 25days
| 02SL - Stations (LUL) | Cxxx-NCR-000358 | NCR | (To clarify incomplete ncr 354 from contractor) GYB Cut Verical & Horizontal Bars in W6 and offered for pre pour inspection. This is a repetitive issue (NCR 234/235). |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2015-12-23 | 2016-01-11 12:05 | 19 | 2015-12-09 17:08 | Civil - Civil Engineering General | 5000 |  | Incorrect Installation | Use As-Is | 3 (3-6k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Vertical 16mm structural tension bars have been cut. In addition as stated in NCR 354 12mm horizontal pull out bars have been cut/snapped as well. 1. Warnings from the past (NCR 234/235) from Cxxx structural engineers to not drill and fix structural steel have been ignored. Also statements to avoid recurrence have been ignored. 2. In this condition the wall has been offered for pre pour inspection.
| 02SL - Stations (LUL) | Cxxx-NCR-000359 | NCR | LYTAG used in concrete Mix 3F - Wall 1, level +3 to +4 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-03-30 | 2016-01-04 09:17 | -86 | 2015-12-21 17:38 | Civil - Civil Engineering General | 10000 |  | Material | Use As-Is | 2 (6-60k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | LYTAG has been found at the top of Wall 1, level +3 to +4. The wall has been poured using mix 3F.
| 02SL - Stations (LUL) | Cxxx-NCR-000361 | NCR | GRC replacement panel |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-04-10 | 2017-03-09 11:41 | -32 | 2015-12-15 10:26 | Civil - Civil Engineering General | 5000 |  | Material | Repair | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | Steel backing panels have been installed in the PES and in some areas the gap between panel and truss in greater than 3mm.
| 02SL - Stations (LUL) | Cxxx-NCR-000362 | NCR | Buttress at -1 level GL 10/A unusable B40 bar |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-03-24 | 2016-02-09 10:35 | -44 | 2015-12-15 17:02 | Structural Engineering - Reinforcement | 2000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | The Contractor has determined that 2no. B40 main bar starters for a buttress column upon GL 10/A at -1 level have been positioned too close to each other therefore neither can be used. The above means 2no. out of the 20no. B40's cannot be installed in line with drawing: Cxxx-LAO-C-DWG-N105_WS089_2-50001
| 02SL - Stations (LUL) | Cxxx-NCR-000363 | NCR | PES alignment beam clash with PTE tunnel liner wall |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-06-30 | 2017-01-11 11:39 | -170 | 2015-12-16 11:56 | Civil - Civil Engineering General | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | The PES corbel side alignment beam will clash with the PTE tunnel liner wall, heading East from WTH. This clash is not with the SCL, but with the tunnel liner wall cast by Cxxx.
| 02SL - Stations (LUL) | Cxxx-NCR-000364 | NCR | Core 4 Void between levels -2 and -1 box out deflection |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-03-25 | 2016-02-19 14:57 | -35 | 2015-12-16 13:07 | Structural Engineering - Concrete Member | 10000 |  | Equipment Breakdown | Repair | 2 (6-60k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | There has been a temporary works failure with forming a void within a Core 4 wall between levels -2 and -1 (GL 8/DD-EE) North side. The centre of the box has deflected due to concrete pressure and therefore is smaller than defined on builders work drawings (Cxxx-LAO-Z-DWG-N105_WS089_3-50003).
| 02SL - Stations (LUL) | Cxxx-NCR-000365 | NCR | Various gullies cast into the -2 slab clashing with perimeter concrete upstand |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-03-25 | 2016-01-04 11:24 | -81 | 2015-12-16 14:10 | Civil - Drainage | 5000 |  | Design | Use As-Is | 3 (3-6k) | Complete | Management Problem - Inadequate supervision | Completed |  | Due to clashes with heavy reinforcement within the -2 propping slab, the Contractor could not install cavity drain points close enough to the diaphragm wall in two locations denoted attached. This has lead to them clashing with the concrete upstand located around the perimeter by 60mm. The 200mm wide upstand in these locations is therefore reduced to 140mm, however cast with the correct amount of reinforcement given on design drawings.
| 02SL - Stations (LUL) | Cxxx-NCR-000366 | NCR | Missing concrete sampling cubes for -3 secondary walls between GL D-A/6-7 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-03-25 | 2016-01-04 11:21 | -81 | 2015-12-16 15:32 | Structural Engineering - Testing | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | 2no. -3 to -2 secondary walls (highlighted attached) were poured with no compressive strength sampling cubes taken as required in the ITP (Cxxx-LAO-O4-ITP-N105_WS089-50002). The concrete mix used to pour these walls was: MIX 1B, which is a C50/60 mix (MCR: Cxxx-LAO-O4-XDS-N105_WS089_Z-50008). This therefore has a greater characteristic strength than that specified in the specification (C32/40).
| 02SL - Stations (LUL) | Cxxx-NCR-000367 | NCR | -2 slab and waler beam pour 1 - cube sample testing frequency not conforming to ITP |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-03-25 | 2016-01-04 09:22 | -81 | 2015-12-16 16:18 | Structural Engineering - Testing | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Whilst concreting the -2 slab and waler beam (pour 1), compressive strength sample cubes were not taken to the frequency as defined in the General Concrete ITP (Cxxx-LAO-O4-ITP-N105_WS089-50002), which states, every 50m3. 3no. sets were made, however 5no. should have been made with the volume of concrete poured (232.5m3).
| 02SL - Stations (LUL) | Cxxx-NCR-000368 | NCR | -2 slab and waler beam pour 3 - cube sample testing frequency not conforming to ITP |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-03-25 | 2016-01-04 12:44 | -81 | 2015-12-16 18:46 | Structural Engineering - Testing | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Whilst concreting the -2 slab (pour 3), compressive strength sample cubes were not taken to the frequency as defined in the General Concrete ITP (Cxxx-LAO-O4-ITP-N105_WS089-50002), which states, every 50m3. 3no. sets were made, however 4no. should have been made with the volume of concrete poured (195m3). Although the pour history sheets state that reference W0087 A-D was taken, this was not sent to __.
| 02SL - Stations (LUL) | Cxxx-NCR-000369 | NCR | Wind Post and Upstand Alignment WTH Level -3 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2015-12-31 | 2016-01-26 15:46 | 26 | 2015-12-17 10:52 | Civil - Civil Engineering General | 10000 |  | Design | Repair | 2 (6-60k) | Complete | Management Problem - Other | Completed |  | Upon review of the structural and architectural drawings (see attached mark-up) there is a discrepancy of 40mm between the positioning of the wind post on the architectural drawing and opening aligned above on the structural drawing. The Contractor installed the wind post and as per the architectural drawing. Upon preparation for the precast stairs the Contractor recognized this discrepancy that the stairs would not fit without repositioning the wind post which the Contractor did. In doing this to accommodate the stairs the line of the upstand and wind posts along the north face was not aligned.
| 02SL - Stations (LUL) | Cxxx-NCR-000370 | NCR | Decoration works - sealing of WTH/GYB lower levels and changes to Room Data Sheets |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-02-21 | 2016-01-18 11:37 | -34 | 2015-12-23 10:41 | Architectural - Finishes | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Sealing has commenced on levels -1, +0 and +1 of the Goslett Yard Box tunnel ventilation rooms. These works have commenced prior to design being gated and furthermore the Room data sheets that will be gated on 21 Dec 2015 are no longer current due to late changes that are being captured on a number of FCD's changing the finishes on all levels of both boxes (including FCD-422,423 and 427) that have been agreed in principle between the Contractor, the PM and Cxxx but have not been formally closed out yet.
| 02SL - Stations (LUL) | Cxxx-NCR-000371 | NCR | Mass concrete/hydroduct commenced at WTH level -5 ahead of Gate 3 design |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-01-06 | 2016-01-04 09:25 | -2 | 2015-12-23 12:25 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | Mass concrete installation has commenced at WTH level -5 ahead of a gated design. However the relevant RFI's, FCD's and PMI's have been raised to cover the changes which will be implemented post gate.
| 02SL - Stations (LUL) | Cxxx-NCR-000372 | NCR | Windpost -1 level GL A/5-4 starter bars missing in slab |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-05-31 | 2016-05-18 14:22 | -13 | 2016-01-03 13:12 | Structural Engineering - Reinforcement | 5000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Supervision - Insufficient supervision | Completed |  | In place of FCD 265, the Contractor has not cast in the required reinforcement starter bars detailed within the Cxxx reinforcement detail drawings for a Windpost located at -1 level GL A/4-5.
| 02SL - Stations (LUL) | Cxxx-NCR-000373 | NCR | Scabble back of Door openings at WTH level -4 trackside area |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-07-23 | 2017-01-12 14:51 | -192 | 2016-01-05 12:21 | Civil - Civil Engineering General | 1000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Door openings at WTH level -4 do not allow sufficient space for installation of intumescent around the door frames.
| 02SL - Stations (LUL) | Cxxx-NCR-000374 | NCR | PES - Out of tolerance horizontal struts in PTW / PTE |  | Contr | TWC | TCR - Tottenham Court Road Station (West) |  | 2016-08-15 | 2016-06-28 16:10 | -48 | 2016-01-05 14:59 | Archaeology - General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The PES Horizontal Strut position has a tolerance of +/- 3mm. Attached is the PES Horizontal Strut as-built survey for both PTE and PTW. The as-built survey shows the design position as well as indicating the deviation between design level and as-built level. This is indicated as + or - Xmm. As shown on the as-built survey, there are a number of points which fall outside of the +/- 3mm tolerance. This ranges between +10mm to -8mm.
| 02SL - Stations (LUL) | Cxxx-NCR-000375 | NCR | Cracking to internal walls |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-02-02 | 2016-02-02 14:12 | 0 | 2016-01-05 15:29 | Civil - Civil Engineering General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | Cracking has been located on internal walls on minus 5 GYB. Crack widths vary, with the largest being 0.5mm wide.
| 02SL - Stations (LUL) | Cxxx-NCR-000376 | NCR | Works Commenced Without Relevant Accepted ITP in place: Concrete Surface Sealing. |  | Crossrail | PDP | TCR - Tottenham Court Road Station (West) |  | 2016-01-20 | 2016-01-27 08:19 | 7 | 2016-01-06 10:12 | Architectural - Finishes | 10000 |  | Supervision/Management | Rework | 2 (6-60k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Works have commenced without an accepted ITP in place.
| 02SL - Stations (LUL) | Cxxx-NCR-000377 | NCR | Cable Management system installation |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-01-21 | 2016-01-18 11:43 | -3 | 2016-01-07 11:01 | Electrical - Cable Management | 50000 |  | Documentation and Records | Use As-Is | 2 (6-60k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Works have commenced on installation of cable management systems without an approved ITP Cxxx-LAO-O4_ITP-N105_WS089_Z-50036 was returned code 3 on the 11th December 2015 (Rev 1 Issued 03.12.2015). This contravenes Works Information Vol 2B, Part 20, Cl20.8 and Section 1.3 Hold point of the ITP submitted.
| 02SL - Stations (LUL) | Cxxx-NCR-000378 | NCR | Buttress reinforcement -1 to +0 GL 8/EE |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-02-27 | 2016-02-09 10:31 | -18 | 2016-01-08 17:56 | Structural Engineering - Reinforcement | 5000 |  | Incorrect Installation | Use As-Is | 3 (3-6k) | Complete | Supervision - Insufficient supervision | Completed |  | The buttress at -1 level upon GL 8/EE has reinforcement out of position. The main bar starters (B40) are not positioned in a regular arrangement, therefore has larger spacing's than that given on the Cxxx detail drawing. In order to ensure lapping bars are positioned back to the correct arrangement they are required to be offset in 2no. locations. This has resulted in an offset of 110mm (maximum). Each bar has a containment link around it.
| 02SL - Stations (LUL) | Cxxx-NCR-000379 | NCR | Upstand WTH Level -3 Installed Out of Line |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-01-25 | 2016-01-27 08:40 | 2 | 2016-01-11 08:01 | Architectural - Brickworks/Blockworks | 10000 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Upon review of the line of blockwork the Contractor identified that the concrete upstand has been cast out of position by 104mm. See attached mark-up.
| 02SL - Stations (LUL) | Cxxx-NCR-000380 | NCR | Damage to concrete finish when drilling for Unistut Installation within GYB Vent Tower due to Re-Bar collision with SDS Hammer drill |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2016-08-30 | 2016-08-26 06:30 | -4 | 2016-01-11 12:24 | Electrical - Electrical Engineering General | 6000 |  | Damaged | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Insufficient information made available to the worker. | Completed |  | The Contractor has damaged the concrete fascia, when drilling fixing holes for vertical wall mounted __ that will support the perimeter CMS, due to drill bit collision with sub surface reinforcing bars. The Contractor was made aware of this issue by the Project Manager, prior to commencing the works and the high risk of this occurrence when using 70-100mm fixings within a concrete shuttered wall with only 40-50mm of concrete over cover on top of the recessed reinforcing bars gridded to aprox 150x150mm. As a result of these discussions, the Project Manager recommended the Contractor carried out Reinforcing Bar drawing checks for setting out and obtained a datum identifying the reinforcing location from a set start point and also as an advisory suggestion, Ferro Scan the walls to identify the location of the bars.
| 02SL - Stations (LUL) | Cxxx-NCR-000381 | NCR | Cube Failure - WTH 10/09/2015 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-04-01 | 2016-03-07 09:03 | -25 | 2016-01-11 14:04 | Civil - Structural Engineering | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | The strength of cubes W0063B did not reach required 60N/mm2 in 28 days, see attached record sheet. This affect column C-3-A at level -3. The consistence was within specification for used concrete mix.
| 02SL - Stations (LUL) | Cxxx-NCR-000384 | NCR | Lightning Protection ITP |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2017-01-31 | 2017-05-19 09:33 | 108 | 2016-01-12 09:24 | Electrical - General | 50000 |  | Documentation and Records | Rework | 2 (6-60k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | The Contractor has installed Lightning Protection Components embedded within the GYB Vent Tower Superstructure walls without an associated Method Statement or ITP. Furthermore, whilst the components have been submitted under the MCR process, the components currently being used are still outstanding acceptance (Code 1) from CRL. Due to the nature of the installation and the fact the Contractors current installation process is not in accordance with the Works Information, Crossrail are unable to formally recognise/acknowledge the current works being undertaken, which runs the future risk of installing un-assured works, which may require further future re-works.
| 02SL - Stations (LUL) | Cxxx-NCR-000385 | NCR | Nib steel detail |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-01-26 | 2016-01-27 15:55 | 1 | 2016-01-12 09:32 | Civil - Civil Engineering General | 5000 |  | Supervision/Management | Use As-Is | 3 (3-6k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | FCD 000437 detailed a NIB for precast stairs. The Nib steel was installed prior to the FCD being confirmed which has caused the installed detail being different to the FCD.
| 02SL - Stations (LUL) | Cxxx-NCR-000386 | NCR | Reduced cover 250 Seconary Wall at -3 level |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-02-09 | 2016-02-15 13:29 | 6 | 2016-01-12 10:50 | Civil - Civil Engineering General | 2000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | Reduced cover of 10-15mm of 6no. __ Eazi Strip starter bars in 250mm secondary wall at level -3. See attached photos.
| 02SL - Stations (LUL) | Cxxx-NCR-000387 | NCR | Commencement of Hydroduct GYB L-5 Prior to Design Assurance |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2016-01-27 | 2016-01-29 15:29 | 2 | 2016-01-13 15:57 | Architectural - Flooring | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Non conformance with the approved ITP and design assurance procedure. Installation of permanent works commenced ahead of IFC drawing and/or 'By Exception' pre gate approval procedure.
| 02SL - Stations (LUL) | Cxxx-NCR-000388 | NCR | GYB - No Lightning protection installed from level +0 to +3 as per ITP |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2017-03-30 | 2017-02-01 10:03 | -57 | 2016-01-14 09:12 | Civil - Civil Engineering General | 5000 |  | Supervision/Management | Rework | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | No lightning protection elements/components have ben installed within the GYB Vent Tower from level +0 to +3. There is a clearly defined hold point within the General concreting ITP, that clearly identifies this Hold Point and the Contractor has failed to stop works at this point to ensure these elements were installed within the internal reinforcing steel bars prior to final concrete pour. This will now result in additional re-work and introduces the risk of delay/additional cost to the project
| 02SL - Stations (LUL) | Cxxx-NCR-000389 | NCR | PES - Out of tolerance alignment beam in PTW / PTE |  | Contr | TWC | TCR - Tottenham Court Road Station (West) |  | 2016-08-15 | 2016-06-28 16:13 | -48 | 2016-01-14 10:08 | Architectural - General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The position of the PES alignment beams have a tolerance of +/- 3mm. Attached is the PES alignment beam as-built surveys for both PTE and PTW. The as-built surveys show the design position as well as indicating the deviation between alignment, design level and chainage. This is indicated as + or - Xmm. As shown on the as-built survey, there are a number of points which fall outside of the +/- 3mm tolerance. This ranges between +10mm to -8mm.
| 02SL - Stations (LUL) | Cxxx-NCR-000390 | NCR | PES - Damaged Mica glass - Mycalex MM60 |  | Contr | TWC | TCR - Tottenham Court Road Station (West) |  | 2017-08-31 | 2017-06-21 15:13 | -71 | 2016-01-14 11:10 | Archaeology - General | 5000 |  | Damaged | Repair | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | During temporary installation of the Mica Glass - Mycalex MM60-75-M16’s along both PTW and PTE, it has been noted that 20no + have been broken. It appears as though they have been snapped in half during the torqueing stage (208Nm). See attached photos. All of the Mycalex MM60-75-M16 have now been removed in line with the handover of the platform edge to Cxxx and shall not be re-installed for a number of months. In the meantime, it is important to understand why and how these have been damaged in order to prevent this from occurring again. A secondary installation with a reduced torque of 136Nm led to further breakages, which necessitated the need for further investigations, carried out in accordance with PMI 1200 and 1202
| 02SL - Stations (LUL) | Cxxx-NCR-000391 | NCR | Repeatedly LYTAG used in concrete Mix 3F - Wall 1 & escalator walls |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2016-02-13 | 2016-02-18 16:25 | 5 | 2016-01-14 11:45 | Civil - Civil Engineering General | 10000 |  | Supervision/Management | Use As-Is | 2 (6-60k) | Complete | Material/Preservation Problems - Lack or improper material identification and traceability | Completed |  | LYTAG has been used in concrete Mix 3F - Wall 1 +4 level & escalator walls -4 level. This is a repetitive issue. And strictly the wrong concrete to what has been designed in the WI. This issue has been first recorded in NCR-359, the corrective actions have patently not been either effective, or adhered to. The contractor to survey concrete poured since last NCR, and report on exact locations where this remains a problem..
| 02SL - Stations (LUL) | Cxxx-NCR-000392 | NCR | W3 level +4 to +5 and W3/W9 Level +3 to +4 External Finish |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-06-13 | 2016-01-20 11:40 | -145 | 2016-01-15 08:47 | Civil - Civil Engineering General | 10000 |  | Workmanship | Repair | 2 (6-60k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | After inspection a few non-conforming parts blemishes on the external walls CON-103 have been picked up. See attached sketch
| 02SL - Stations (LUL) | Cxxx-NCR-000393 | NCR | -3 level secondary wall (SW1) horizontal splicing bar lack of cover GL D-B/7 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-02-15 | 2016-02-15 15:58 | 0 | 2016-01-19 12:21 | Structural Engineering - Reinforcement | 5000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | A lack of cover has been determined at the construction joint of a secondary wall (SW1) at -3 level adjacent to Truss 2 (GL D-B/7). Reinforcement continuity was provided using pull out bars, however when exposing the pull out bars 15mm cover has been determined (minimum) to the near face bars. The required amount of cover should be 30mm. The metal covering for the pull out bars also intrudes the cover zone.
| 02SL - Stations (LUL) | Cxxx-NCR-000394 | NCR | Bulge in escalator wall |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-02-25 | 2016-02-19 10:17 | -6 | 2016-01-20 10:02 | Civil - Civil Engineering General | 10000 |  | Workmanship | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Walls W5 & W6 on -3 were poured with a bulge in the timber shutter. This is on the external face (non escalator side) of the walls. Attached as-builts show the deviations.
| 02SL - Stations (LUL) | Cxxx-NCR-000395 | NCR | GYB - Gap behind pull out bar W6/W1 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-04-29 | 2016-02-29 15:59 | -60 | 2016-01-20 14:39 | Civil - Civil Engineering General | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Management Problem - Inadequate supervision | Completed |  | There is a gap (dimensions shown on attached sketch) behind the pull out bars. The reinforcement lacers are fully cast into the walls.
| 02SL - Stations (LUL) | Cxxx-NCR-000396 | NCR | Lift 11 halfen channel positioning. |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-12-15 | 2016-11-04 11:22 | -41 | 2016-01-20 17:50 | Civil - Civil Engineering General | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Supervision - Insufficient supervision | Completed |  | The halfen channels in lift 11 have been cast out of position as shown on the attached red-line drawings.
| 02SL - Stations (LUL) | Cxxx-NCR-000397 | NCR | W18 - reinforcement level +4 to +5 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-04-30 | 2016-02-18 16:14 | -72 | 2016-01-21 08:35 | Civil - Civil Engineering General | 10000 |  | Incorrect Installation | Use As-Is | 2 (6-60k) | Complete | Management Problem - Inadequate supervision | Completed |  | Reinforcement detail above doorway and box out was not installed as per the drawing - see attached drawing.
| 02SL - Stations (LUL) | Cxxx-NCR-000398 | NCR | Use of unapproved drawings in red line submittal |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-08-10 | 2016-08-18 08:08 | 8 | 2016-01-21 14:27 | Civil - Civil Engineering General | 1000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | The red line drawings used in the submittal of PES packages are currently only 'P' revisions.
| 02SL - Stations (LUL) | Cxxx-NCR-000400 | NCR | GYB +0 - A temporary pipe has been cast into permanent structural slab |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2017-07-28 | 2017-08-14 10:40 | 17 | 2016-01-21 16:55 | Civil - Civil Engineering General | 3000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Into the slab at +0 level in front of lift 11 (Phase2) a temporary power cable has been cast in the permanent slab and wall7. This cable feeds the hoist down to -5 level GYB. (See attached picture.)
| 02SL - Stations (LUL) | Cxxx-NCR-000401 | NCR | GYB +0 slab - concreting in frost conditions - loose blankets and no temperature reading |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2016-06-15 | 2016-05-27 14:01 | -19 | 2016-01-21 16:54 | Civil - Civil Engineering General | 4000 |  | Supervision/Management | Use As-Is | 3 (3-6k) | Complete | Procedure Problem - Not Defined | Completed |  | +0 level slab and wall 7 (in front of lift 11, phase 2) have been poured in frost conditions 0°C to -5°C over night. Pour date 19.01 to 20.01.. The concrete has been loose covered over night with partly full exposure to the air. Temperature readings from the concrete are not available too. The slab and wall have been struck the next morning. And works commenced in that area.
| 02SL - Stations (LUL) | Cxxx-NCR-000402 | NCR | -1 Slab infill out of level tolerance |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-02-22 | 2016-02-16 15:29 | -6 | 2016-01-21 17:31 | Civil - Civil Engineering General | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Previous Construction - Problems based on previous construction errors | Completed |  | The infill slab on level -1 was cast low by up to 23mm in localised areas. The reason for this was to match in with the -1 slab cast by others. See attached
| 02SL - Stations (LUL) | Cxxx-NCR-000403 | NCR | Core 4 level -1 to +0 level wall - over spil of concrete within boxed out section GL E/10 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-02-21 | 2016-02-22 15:40 | 1 | 2016-01-22 08:32 | Structural Engineering - Concrete Member | 5000 |  | Supervision/Management | Repair | 3 (3-6k) | Complete | Management Problem - Inadequate supervision | Completed |  | Concrete was accidently poured into a boxed out section of wall which was required to be left with no concrete. Location is in Core 4 at -1 to +0 level adjacent to GL E/10.
| 02SL - Stations (LUL) | Cxxx-NCR-000405 | NCR | Perimeter Blockwork Level -2 WTH - Completing Works without Assured Design or By Exception Form Completed |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-04-20 | 2016-05-25 11:55 | 35 | 2016-01-25 14:06 | Architectural - Brickworks/Blockworks | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | The Contractor has begun Blockwork Perimeter Walls at Level -2 without a Gate Approval or By Exception Form agreed.
| 02SL - Stations (LUL) | Cxxx-NCR-000408 | NCR | CMS Installation GYB Vent Shaft |  | Contr | SKC | TCR - Tottenham Court Road Station (West) |  | 2016-03-28 | 2016-03-30 12:44 | 2 | 2016-01-26 15:07 | Electrical - Cable Management | 50000 |  | Documentation and Records | Rework | 2 (6-60k) | Complete | Design Problem - Inadequate or defective design | Completed |  | In order to support the MOHS target programme & SLD dates the Contractor is aware that in commencing the installation of the CMS within the GYB Vent shaft they are not following the Crossrail assurance procedure set out within the Works Information, this is however to mitigate the delay the GYB vent shaft CMS.
| 02SL - Stations (LUL) | Cxxx-NCR-000410 | NCR | Delivery of WTH level -5 MEP Modules |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-11-30 | 2017-11-22 09:19 | -8 | 2016-01-28 14:56 | Mechanical - Mechanical Engineering General | 5000 |  | Documentation and Records | Use As-Is | 3 (3-6k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | The Contractor has commenced manufacture of modules to support the delivery dates agreed with CRL to assist in achieving the dates et in the MOHS programme. The Contractor is aware that he is required to demonstrate to the Project Manager, that he has comprehensive structural calculations.
| 02SL - Stations (LUL) | Cxxx-NCR-000412 | NCR | -2 level Buttress B4 position error GL A/8 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-02-12 | 2016-02-16 11:30 | 4 | 2016-01-29 15:38 | Structural Engineering - Concrete Member | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | The buttress at -2 level and upon GL A/8 is out of position by 20mm. Buttress is required, theoretically, to be positioned centrally upon GL 8. It was cast 20mm further north.
| 02SL - Stations (LUL) | Cxxx-NCR-000414 | NCR | Blockwork Mortar Testing |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-02-12 | 2016-02-26 15:34 | 14 | 2016-01-29 17:05 | Architectural - Brickworks/Blockworks | 500 |  | Incomplete Works | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | The Contractor informs the PM that four mortar tests were not completed on the following dates 18.09.15, 02.10.15, 16.10.15 and 30.10.15. The samples taken on the 13.11.15 were tested at 11 days rather than the specified 7 days. The sample taken on the 27.11.15 was tested on the 04.01.16 which is greater than the 28 days specified. The Contractor recognizes and highlights that this is the second NCR that relates to the management of mortar testing and the Contractor's Sub-contractor.
| 02SL - Stations (LUL) | Cxxx-NCR-000415 | NCR | Non-conformance to pull out testing requirement |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2016-02-15 | 2016-02-15 07:26 | 0 | 2016-02-01 09:22 | Structural Engineering - Testing | 20000 |  | Testing and Commissioning | Rework | 2 (6-60k) | Complete | Procedure Problem - Not Defined | Completed |  | The contractor is not complying with JY90 Fixing to Building Fabric Crossrail M&W Specification (CRL1-XRL-M-RSP-CR001-50089) which states all site fixings shall be subject to inspection and “pull out” tests in compliance with CFA guidelines. The contractor is proceeding with the installation of CMS and modules without doing this testing.
| 02SL - Stations (LUL) | Cxxx-NCR-000416 | NCR | GYB - W16 and W15 trimmer bars |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-06-30 | 2016-03-01 12:14 | -121 | 2016-02-01 10:36 | Civil - Civil Engineering General | 5000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Management Problem - Inadequate supervision | Completed |  | Couplers for the W16 and W15 trimmer bars were missed in the W7 pour. Wall 16 - BM 29 trimmers drilled and fixed. See drawing Cxxx-LAO-C-DWG-N105_W093_1-50019 attached Wall 15 - BM 34 B20 trimmers drilled and fixed. BM 33 diagonals drill and fixed. See drawing Cxxx-LAO-C-DWG-N105_W093_1-50018 attached The trimmer bars were drilled and fixed into W7 using V420+ resin to a depth of 180mm.
| 02SL - Stations (LUL) | Cxxx-NCR-000417 | NCR | GYB - Incorrect Setting Out of Plinth at Level +5 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-02-15 | 2016-03-10 11:03 | 24 | 2016-02-01 13:54 | Structural Engineering - Reinforcement | 10000 |  | Supervision/Management | Repair | 2 (6-60k) | Complete | Supervision - Insufficient supervision | Completed |  | The plinth shown in the attached sketch has been set out incorrectly (400mm out of position). The beam and the plinth have been casted and the issue was identified upon the As Built survey. This issue is currently under investigation and the proposed corrective action will be raised after discussion with the Structural Engineer.
| 02SL - Stations (LUL) | Cxxx-NCR-000418 | NCR | GYB - W8 level +5 connection |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-05-11 | 2016-03-01 12:25 | -71 | 2016-02-01 17:37 | Civil - Civil Engineering General | 5000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | The connection between beam A51 and wall 8 is not shown on the beam reinforcement drawing. W8 drawing Cxxx-LAO-C-DWG-N105_WS093_C-50004 shows a B25 L-bar coupler lapped onto a B12mm lacer. There were no B25 couplers on site (4no. required) so 4no. B20 couplers were installed instead.
| 02SL - Stations (LUL) | Cxxx-NCR-000419 | NCR | GYB - CON-103 finish level +4 to +5, W3 and W5 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-08-20 | 2016-03-31 15:54 | -142 | 2016-02-02 13:50 | Civil - Civil Engineering General | 5000 |  | Material | Repair | 3 (3-6k) | Complete | Management Problem - Inadequate supervision | Completed |  | There is a 5mm step in Wall 3 on the level +5 beams and a visible pour line on W5 along the beams at +5. See marked up drawings attached and photographs
| 02SL - Stations (LUL) | Cxxx-NCR-000420 | NCR | GYB - 28 day cube failure - windpost level -2 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-07-02 | 2016-06-01 15:39 | -31 | 2016-02-03 15:04 | Civil - Civil Engineering General | 0 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | 28 day results for cubes GYBMC87B &C have come in at 37.5N/mm2 and 39N/mm2 respectively. These are for a windpost on level -2. See attached pour history, cube sheet and result certificate.
| 02SL - Stations (LUL) | Cxxx-NCR-000421 | NCR | GYB - 28day cube failure - W2 level +3 to +4 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-07-02 | 2016-04-22 11:58 | -71 | 2016-02-03 17:07 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Training Deficiency - Not Defined | Completed |  | 28 days cubes for wall 2, GYBMC88 have been crushed at 35.1N/mm2 and 33.4N/mm2. Pour history and cube result certificate attached.
| 02SL - Stations (LUL) | Cxxx-NCR-000422 | NCR | GYB - External finish level +4 to +5, W1 and W5 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-07-02 | 2016-02-16 16:44 | -137 | 2016-02-03 18:04 | Civil - Civil Engineering General | 10000 |  | Workmanship | Repair | 2 (6-60k) | Complete | Supervision - Insufficient supervision | Completed |  | After inspection with Cxxx Architect (__) the following were picked up; 1. Dywidag tubes through soffit of openings that need making good 2. 8mm step in shutter joint to be made good See attached marked ups
| 02SL - Stations (LUL) | Cxxx-NCR-000423 | NCR | PES MCR - VCD JF-P 650W X 400H not accepted by Crossrail. Works already commenced |  | Contr | TWC | TCR - Tottenham Court Road Station (West) |  | 2016-03-18 | 2016-03-09 09:25 | -9 | 2016-02-04 08:46 | Mechanical - Heating Ventilation & Air Conditioning | 10000 |  | Documentation and Records | Use As-Is | 2 (6-60k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | MCR - VCD JF-P 650W X 400H has been given a Code 3 status and returned by Crossrail to be revised and resubmitted ahead of works commencing. Despite this, works have continued on site with a number of VCD's already installed.
| 02SL - Stations (LUL) | Cxxx-NCR-000424 | NCR | GYB +1 slab- drill and fix for missing couplers |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-07-04 | 2016-04-13 11:06 | -82 | 2016-02-05 07:14 | Civil - Construction Health & Safety | 4000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Management Problem - Inadequate supervision | Completed |  | 4no. (2x2) couplers were missed from W4 for the +1 slab. See attached marked drawing
| 02SL - Stations (LUL) | Cxxx-NCR-000425 | NCR | Internal block work walls misalignment with halfen channels |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-02-19 | 2016-02-26 13:48 | 7 | 2016-02-05 15:17 | Civil - Civil Engineering General | 5000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Management Problem - Inadequate supervision | Completed |  | There are instances where the internal block work walls do not align with the halfen channels cast into the wind posts. See attached photo
| 02SL - Stations (LUL) | Cxxx-NCR-000426 | NCR | -1 windpost out of position - WTH |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-05-20 | 2016-05-11 14:26 | -9 | 2016-02-12 17:47 | Structural Engineering - Concrete Member | 10000 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Management Problem - Inadequate supervision | Completed |  | The Contractor has set out and cast a wind post in the wrong position at -1 level. Windpost is located upon GL B and adjacent to GL 3. It has been set out two far south by 1m therefore in the doorway.
| 02SL - Stations (LUL) | Cxxx-NCR-000427 | NCR | Lightning Protection Works |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-03-06 | 2017-04-27 13:08 | 52 | 2016-02-08 10:09 | Electrical - Electrical Engineering General | 5000 |  | Documentation and Records | Rework | 3 (3-6k) | Complete | Management Problem - Inadequate administrative control | Completed |  | To support the SLD & Construction programme dates, the Contractor has had to commence installing Lightning Protection equipment, the equipment (Clamps/tapes/earth bonds) were under the MCR approval process when the works commenced onsite.
| 02SL - Stations (LUL) | Cxxx-NCR-000428 | NCR | Incorrect Installation of VCD's |  | Contr | TWC | TCR - Tottenham Court Road Station (West) |  | 2016-02-22 | 2016-03-29 12:11 | 36 | 2016-02-08 11:05 | Mechanical - Heating Ventilation & Air Conditioning | 10000 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Management Problem - Inadequate supervision | Completed |  | It has been identified that 1No. VCD has been installed incorrectly along the Westbound platform.
| 02SL - Stations (LUL) | Cxxx-NCR-000429 | NCR | Excessive Blemishing on Level -5 North Box Shear Walls |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-04-10 | 2016-04-11 14:48 | 1 | 2016-02-09 09:28 | Architectural - Walls | 3000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Finish to concrete walls on Level -5 North Box not in line with specification: JE20.1207 (d) (x) - The concrete shall be free of surface blemishing visible to the eye at 3m.
| 02SL - Stations (LUL) | Cxxx-NCR-000430 | NCR | GYB Inspection for closed up inaccessable wall without providing access to inspect. |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2016-02-23 | 2016-03-01 13:03 | 7 | 2016-02-09 16:11 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | The clients Field engineer and contractors Quality Engineer have been called in for inspection of wall 9 phase II second lift. The wall was closed up and no access possible. After asking for a ladder in order to do the inspection the Quality engineers got told by the contractors Site engineer that this wall has been inspected already?! Why has the client called in for inspection then? For giving a signature only?
| 02SL - Stations (LUL) | Cxxx-NCR-000431 | NCR | Spray Paint to Concrete surfaces under the Cross Passage slabs |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-02-23 | 2016-02-19 08:45 | -4 | 2016-02-09 17:19 | Structural Engineering - Concrete Member | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | The Contractor has become aware of a number of areas where spray paint is visible on finished concrete surfaces below the slabs (example in photos attached is from AP7). The concrete surfaces are all CON 104 as they are unseen areas that are uninhabited. The spray paint all appears to have been applied after the formwork has been struck so it has not been transferred from the shuttering. The Contractor proposes to leave the spray paint as is due to the program for installation of MEP due to start on 16/02/16 which would not allow sufficient time for rework and also the areas will not be seen by the public or service personnel. The Contractor requests that this NCR is completed at the earliest possible opportunity to allow the sign off to completed for these areas so the MEP works can progress.
| 02SL - Stations (LUL) | Cxxx-NCR-000432 | NCR | Lytag found in concrete pour |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-03-09 | 2016-03-10 14:42 | 1 | 2016-02-10 08:56 | Civil - Civil Engineering General | 5000 |  | Material | Use As-Is | 3 (3-6k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | Lytag was found in Mix 3D for pour 1 on wall W2, level -2GYB. The pour was on the 8/2/16.
| 02SL - Stations (LUL) | Cxxx-NCR-000433 | NCR | Movement joint gap in escalator wall. |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-02-24 | 2016-03-01 13:11 | 6 | 2016-02-10 16:00 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | The movement joint gap between the escalator wall and soffit has been poured with a gap of 60mm rather than 35mm. Please see mark-up on attached drawing
| 02SL - Stations (LUL) | Cxxx-NCR-000434 | NCR | Low cover on W3 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-05-11 | 2016-05-04 13:55 | -7 | 2016-02-11 10:37 | Civil - Civil Engineering General | 5000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | The lacers on W3 had low cover in three locations. At two locations the lacers were removed and replaced with drill and fix bars. These 5 no: 20mm lacers on the bottom of the wall and 5 no: at the top of the wall were drilled in 400mm (the amount specified by V420 + spec sheet) and fixed using the V420+ resin. The 6no: 12mm lacers that had 35mm cover on the other side of the wall have been cranked in and will remain as is.
| 02SL - Stations (LUL) | Cxxx-NCR-000435 | NCR | WTH Level -5 Module installation |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-03-07 | 2016-04-25 15:38 | 49 | 2016-02-11 14:26 | Mechanical - Mechanical Engineering General | 50000 |  | Documentation and Records | Use As-Is | 2 (6-60k) | Complete | Design Problem - Inadequate or defective design | Completed |  | In order to support the SLD/MOHS dates the Contractor has commenced installation of the WTH level -5 MEP modules prior to receipt of structural calculation reports. The Contractor advises that there is little risk in this works and will close out with the Project Manager by issuing calculations once received.
| 02SL - Stations (LUL) | Cxxx-NCR-000436 | NCR | Incorrect position of couplers and eazistrip for Wall 13 from Wall 8 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-05-12 | 2016-05-04 14:10 | -8 | 2016-02-12 14:37 | Civil - Civil Engineering General | 5000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | The Eazi-strip and couplers for wall 13 lacers have been cast into wall 8 leaving 15mm cover on one side of the wall and 80mm cover on the other side. Wall 8 has been cut back to reveal the front face of reinforcement and the couplers have been cranked across meaning they now have the minimum cover of 25mm.
| 02SL - Stations (LUL) | Cxxx-NCR-000437 | NCR | PES - Mid plenum baffle installed incorectly o both PTE and PTW |  | Contr | TWC | TCR - Tottenham Court Road Station (West) |  | 2016-12-20 | 2017-01-04 17:06 | 15 | 2016-02-12 15:35 | Architectural - General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The mid plenum baffle panels on both PTE and PTW have been not been installed in accordance with the design drawing. Each panel is secured in place by 1no. L bracket as opposed to the 3no. required. See attached drawing and photographs.
| 02SL - Stations (LUL) | Cxxx-NCR-000439 | NCR | PES MCR - __ Access Hatch not issued to Crossrail. Installation already commenced |  | Contr | TWC | TCR - Tottenham Court Road Station (West) |  | 2016-05-30 | 2016-05-18 14:24 | -12 | 2016-02-15 09:42 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Lack of procedure | Completed |  | MCR - __ Access Hatch has not been issued to Crossrail. Despite this, works have commenced on site with a number of hatches already installed. (4no. Eastbound, 6no. Westbound)
| 02SL - Stations (LUL) | Cxxx-NCR-000440 | NCR | Surface crack to -3 escalator wall |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-03-15 | 2016-04-20 15:15 | 36 | 2016-02-16 15:41 | Civil - Civil Engineering General | 5000 |  | Material | Repair | 3 (3-6k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | A surface crack has appeared on the escalator wall on -3.
| 02SL - Stations (LUL) | Cxxx-NCR-000442 | NCR | Platforms - Left open Boreholes in "handed over" structures by Crownhouse MEP works. |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2016-11-15 | 2016-11-04 11:28 | -11 | 2016-02-17 14:05 | Civil - Civil Engineering General | 1000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | At the Platform area (see attached picture) bore holes made for MEP installation have been drilled and left open.
| 02SL - Stations (LUL) | Cxxx-NCR-000443 | NCR | WTH, lvl -1, escalator starter bars cast to short |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-09-04 | 2016-03-31 16:21 | -157 | 2016-02-17 15:10 | Civil - Structural Engineering | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | __ installed to short B20 starter bars for escalator slab at level -1. Installed B20 900mm bottom mat starter bars and B20 1100mm top mat starter bars. Referring to drawing Cxxx-LAO-C-DWG-N105-WS089_5-50088 installed bars doesn't meet requirements of bond conditions for B20 bar. Please see attached drawings and photographs.
| 02SL - Stations (LUL) | Cxxx-NCR-000444 | NCR | WTH, lvl -3, Truss 2 and 3 chamfers not formed |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-09-04 | 2016-03-07 15:48 | -181 | 2016-02-17 17:17 | Civil - Structural Engineering | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | __ casted truss 2 & 3 at level -3 without forming chamfers right next to the soffit. Trusses have been cast as per marked red line. Please see attached sketches and photograph.
| 02SL - Stations (LUL) | Cxxx-NCR-000445 | NCR | Bolt FX20 missing from precast clamp |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-04-05 | 2017-04-18 12:22 | 13 | 2016-02-17 17:09 | Civil - Civil Engineering General | 1000 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Each precast panel is held in place by 2 FX20 bolts and a clamp. At each movement joint location one of these bolts cannot be fixed due to the steel box section below not allowing access to the nut.
| 02SL - Stations (LUL) | Cxxx-NCR-000446 | NCR | MEP Construction against 3D Model Snapshots, as oppose detailed construction drawings |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2017-02-15 | 2017-04-27 13:09 | 71 | 2016-02-17 18:07 | Electrical - Cable Management | 5000 |  | Design | Rework | 3 (3-6k) | Complete | Management Problem - Other management problem | Completed |  | The Contractor is currently undertaking and installing CMS associated works within The GYB Vent Shaft. The works are being installed against 3D Model Snapshots, as oppose detailed construction drawings , which provides no means of assurance or process and is not acceptable. The current Installation methodology runs the risk of future re-work, additional project cost and delays to the delivery of the project.
| 02SL - Stations (LUL) | Cxxx-NCR-000447 | NCR | Working to P status drawings |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-01-31 | 2016-07-14 17:28 | -201 | 2016-02-18 10:07 | Civil - Civil Engineering General | 500 |  | Planning | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | We have been working to P status drawings for the construction of escalator walls. drawings are attached.
| 02SL - Stations (LUL) | Cxxx-NCR-000448 | NCR | WTH, lvl -4, Core 2 doors |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-09-05 | 2016-03-23 08:55 | -166 | 2016-02-18 16:18 | Civil - Structural Engineering | 10000 |  | Incorrect Installation | Use As-Is | 2 (6-60k) | Complete | Management Problem - Inadequate supervision | Completed |  | __ installed incorrect size of door opening 1495x960mm instead of 2000x960mm. Please see attached sketches and photographs.
| 02SL - Stations (LUL) | Cxxx-NCR-000449 | NCR | Geothermal pipe loops blocked in diaphragm wall |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-03-04 | 2016-03-10 12:43 | 6 | 2016-02-19 08:28 | Civil - Civil Engineering General | 1000 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Previous Construction - Other | Completed |  | During the geothermal pipework installation works along cut off level of the diaphragm wall (123.335m ATD) along Gridline (A, 2-->10). __, the pipework subcontractor experienced 5 blocked loops. They have applied all the methods available to unblock them and have concluded they are irreversibly blocked. Please see attached drawing showing the location of the blocked loops. The Contractor notes that he has raised concerns about the long term protection of the geothermal pipes at ground level prior to taking site and cross references various previous communications. The Contractor also notes that he is using the same subcontractor that Cxxx used to design the system and C421 used to install the diaphragm wall loops. __ will make contact with __ to understand the impact of this but does not accept responsibility for this NCR.
| 02SL - Stations (LUL) | Cxxx-NCR-000450 | NCR | Step in escalator wall |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-03-18 | 2016-03-11 08:50 | -7 | 2016-02-19 15:04 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | There is a step of 20mm from the kicker to the main wall on -4 escalator wall. Outer face
| 02SL - Stations (LUL) | Cxxx-NCR-000451 | NCR | Crack in escalator wall on -4 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-05-05 | 2016-04-26 15:21 | -9 | 2016-02-19 15:13 | Civil - Civil Engineering General | 10000 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Management Problem - Inadequate supervision | Completed |  | There are cracks appearing in -4 escalator wall at the interface with the soffit. the cracks are up to 2mm
| 02SL - Stations (LUL) | Cxxx-NCR-000452 | NCR | Drill and fix for missing starter bars in Lift 11 slab |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-05-22 | 2016-05-05 10:20 | -17 | 2016-02-22 09:31 | Civil - Civil Engineering General | 10000 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Supervision - Insufficient supervision | Completed |  | 16mm __ Couplers for Lift 11 roof slab were not installed in W13 or W17. The contractor proposes to drill and fix the bars into position using V420+ resin.
| 02SL - Stations (LUL) | Cxxx-NCR-000453 | NCR | Reduced cover GYB +1 Wall 8 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-05-22 | 2016-05-03 12:02 | -19 | 2016-02-22 09:30 | Civil - Civil Engineering General | 10000 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Supervision - Insufficient supervision | Completed |  | At the wall 8 and wall 16 junction, these is minimal cover on the couplers (8No.) This is due to the chippies taking off a concrete spacer to allow for the stop end to be fitted. This issue was only discovered when the couplers where exposed. We propose to drill and fix 8No B12 bars.
| 02SL - Stations (LUL) | Cxxx-NCR-000454 | NCR | Lytag contamination in -2 escalator wall |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-03-07 | 2016-03-10 10:04 | 3 | 2016-02-22 09:46 | Civil - Civil Engineering General | 5000 |  | Material | Use As-Is | 3 (3-6k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | There is Lytag contamination on -2 W2
| 02SL - Stations (LUL) | Cxxx-NCR-000455 | NCR | PTE - Exposed duct within UPE wall |  | Contr | TWC | TCR - Tottenham Court Road Station (West) |  | 2016-03-07 | 2016-03-17 14:01 | 10 | 2016-02-22 16:20 | Civil - Civil Engineering General | 5000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Following the pre-pour inspection of the UTX concrete infill within the UPE zone, it was identified and raised with the relevant Engineer that 1no. redundant UTX duct was sat on the edge of the pour and would be left exposed following striking of the shutters. Despite this, the pour went ahead without the necessary remedial works having been carried out.
| 02SL - Stations (LUL) | Cxxx-NCR-000456 | NCR | GYB - wall 7 +0 to +1 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-06-15 | 2016-05-23 15:43 | -23 | 2016-02-23 12:37 | Civil - Civil Engineering General | 10000 |  | Workmanship | Repair | 2 (6-60k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | There are 5No areas where there are blow holes larger than allowed in the architectural specification, see attached photos.
| 02SL - Stations (LUL) | Cxxx-NCR-000457 | NCR | Fire System CMS |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2016-05-30 | 2016-06-24 13:15 | 25 | 2016-02-24 15:51 | Fire - Detection | 10 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | The Contractor is currently designing, constructing and installing works containing elements of Fire CMS (Tray) that are not in accordance with the Works Information and both historical and current works may be affected by this. The Contractor is to ensure all works are in accordance with the CRL1-XRL-M-RSP-CR001-50050_Technical Directorate - Material and Workmanship Specification: Mechanical, Electrical and Public Health JW50 Fire Detection and Alarms (clause JW50.1305 (i)), that clearly states the following. All “Cables shall generally be run in trunking or conduit” and any deviation from this detail is not in accordance with the Works Information. This issue may result in additional re-work, additional cost and delay to the final completion and delivery of the Project.
| 02SL - Stations (LUL) | Cxxx-NCR-000458 | NCR | WTH Cube No temperature control |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2016-03-04 | 2016-03-22 16:40 | 18 | 2016-02-26 12:27 | Civil - Civil Engineering General | 3000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Controlling the cube shed since at the 24/02 - 25/02 - 26/02 there is no concrete temperature control measure in place for the storage of concrete test cubes. Contractor is not prepared for cold weather conditions. Cube shed temp found to be very hot (sauna). Water tank temp at 10C with cubes in it. Grout test molds found outside the shed.
| 02SL - Stations (LUL) | Cxxx-NCR-000459 | NCR | WTH - CRL not invited for inspection for escalator slab first lift |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2016-03-11 | 2016-04-01 14:14 | 21 | 2016-02-26 12:37 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | CRL Field Engineer has not been called in for escalator pre pour inspection -3 level.
| 02SL - Stations (LUL) | Cxxx-NCR-000460 | NCR | WTH - Contractor not ready for inspection - several issues spotted (steel missing) |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2016-03-11 | 2016-03-22 16:43 | 11 | 2016-02-26 12:48 | Civil - Civil Engineering General | 2000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | At the slab pour +0 level the contractor has not been ready for inspection. - Steel missing for a whole structural beam 8 because of use of incomplete set of drawings - presented as complete - A whole beam coupler connection has been missing in the north east corner of the pour - Several cover issues have been detected as low as 10mm
| 02SL - Stations (LUL) | Cxxx-NCR-000462 | NCR | Wall 9 - Phase 2 out of position |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-01-25 | 2017-01-17 17:17 | -8 | 2016-03-01 17:43 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Wall 9 in Phase Two between level +1 and +2 is out of tolerance. Refer to attached As Built Survey.
| 02SL - Stations (LUL) | Cxxx-NCR-000463 | NCR | Radio cable cast into capping beam without FCD |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-12-30 | 2016-08-04 15:28 | -513 | 2016-03-02 10:18 | Civil - Structural Engineering | 10000 |  | Incorrect Installation | Use As-Is | 2 (6-60k) | Complete | Supervision - Insufficient supervision | Completed |  | A radio cable will be cast into the capping beam at GL A, 10+3m along the south elevation of the capping beam without prior FCD approval.
| 02SL - Stations (LUL) | Cxxx-NCR-000464 | NCR | Diaphragm wall starter bars low cover to construction joint |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-03-16 | 2016-03-11 09:57 | -5 | 2016-03-02 11:04 | Civil - Structural Engineering | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | At GL (A, 6-->7) a section of capping beam was cast integral with level -0 pour 1. The joint was formed with Hy-rib. Across an approximately 10m long section of this element, the diaphragm wall starter bars have reduced internal cover to the hy rib. Out for 28no. starter bars, 6no. have reduced cover in the lower 500mm of bar where the hy-rib has bulged tight to the diaphragm wall B40 starter bars.
| 02SL - Stations (LUL) | Cxxx-NCR-000466 | NCR | +0 Capping beam concrete segregation issues |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-06-15 | 2016-06-01 15:52 | -14 | 2016-03-03 14:22 | Structural Engineering - Concrete Member | 100000 |  | Material | Repair | 1 (>60k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | The Contractor has observed an issue with the quality of the concrete used in the WTH +0 capping beam between grids: 6-10/A and 10/A-D (southwest corner) poured on the night of 2/3/16. On inspection the top surface appears to have a lack of aggregate. The Contractor has investigated sections of the beam and dug down to the top layer of steel and has located aggregate (a depth of 50-60mm). The mix used was MIX 2 (Cxxx-LAO-O4-XDS-N105_WS089_Z-50009). As the mix has a F5 consistency, a flow test was carried out. Maximum flow measured was 660mm. This is on the limit allowed for a F5. Please see attached for records.
| 02SL - Stations (LUL) | Cxxx-NCR-000467 | NCR | Additional Movement Joints in Perimeter Blockwork Walling - GYB Level -4 & -3 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-03-17 | 2016-03-23 09:00 | 6 | 2016-03-03 14:42 | Architectural - Brickworks/Blockworks | 10000 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Management Problem - Inadequate supervision | Completed |  | Whilst building perimeter blockwork walling at GYB Level -4 and Level -3 the Contractor was incorrectly concerned with the spacing in certain locations of movement joints within the blockwork. The Supervisor introduced additional movement joints in long panels. Upon review with the Contractor's designer these were not necessary and as per drawings had been considered and designed correctly.
| 02SL - Stations (LUL) | Cxxx-NCR-000468 | NCR | Mass Concrete Poured at WTH Level -5 Inside Core 4 without Blockwork/Concrete Upstand Installed |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-08-26 | 2016-09-08 08:44 | 13 | 2016-03-03 16:28 | Architectural - Brickworks/Blockworks | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | Prior to completing the mass pour concrete the Contractor should have installed blockwork cut blocks to FFL within Core 4 WTH Level -5.
| 02SL - Stations (LUL) | Cxxx-NCR-000469 | NCR | Use of unapproved and outdated drawings on site (GYB, WTH) |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2016-06-02 | 2016-06-20 08:27 | 18 | 2016-03-04 16:05 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | On 16th of February a random audit was conducted to check whether the drawings used on site were the latest approved revision. It was found that 2 out of the 11 drawings checked were not the latest revisions (Cxxx-OVE-S-DDD-N105_2-34610 C01 was used, although X01 was available, Cxxx-LAO-A-DDD-N105_4-32012 P03 was used although P05 was available). In addition, three Cxxx drawings were not approved to be used on site (Cxxx-LAO-A-DDD-N105_4-32012, Cxxx-LAO-M1-DWG-N105_WS093_Z-50036, Cxxx-LAO-Z-DWG-N105_WS089_1-50001). There is also a concern about the labourers on site not having direct access to the drawings, currently the construction details are passed to them verbally by the __ project engineer.
| 02SL - Stations (LUL) | Cxxx-NCR-000470 | NCR | Setting Out Level of Perimeter Blockwork - GYB Level -3 and -4 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-03-18 | 2016-04-04 07:31 | 17 | 2016-03-04 17:55 | Architectural - Brickworks/Blockworks | 5000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Upon completing perimeter blockwork at GYB Level -4 the Contractor failed to check the as-built position of the upstand constructed to Others. The first course of blocks on the perimeter blockwork was a cut block to ensure that later in the programme of works when completing internal works the mortar joints were aligned. The Contractor assumed the as-built position was correct and installed 90mm (100mm joint) cut blocks without checking. Upon completing internal walls the mortar joints to do line up by 20/25mm. This error will affect 5 joint locations at Level -4 and 2 locations at Level -3. It affects both mortar joints and movement joints. The Contractor attaches example photos of these works.
| 02SL - Stations (LUL) | Cxxx-NCR-000471 | NCR | WTH Bending bars |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2016-03-21 | 2016-03-23 09:03 | 2 | 2016-03-07 16:20 | Civil - Civil Engineering General | 2000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Bars at the south beam of WTH capping beam have been bend in order to make space for labor to past through. It has been decided in the quality meeting 02/03/16 with __ to not bend bars.
| 02SL - Stations (LUL) | Cxxx-NCR-000474 | NCR | GYB - Precast stairs from __ |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-06-15 | 2016-04-28 13:40 | -48 | 2016-03-08 15:37 | Civil - Civil Engineering General | 500 |  | Manufacturing Defect | Reject | 4 (0.5-3k) | Complete | Subcontractor Problems - Insufficient surveillance of subcontractors | Completed |  | Precast stair set flight 24, MSN1 stairs was delivered to site with incorrect dimensions as per the approved drawing
| 02SL - Stations (LUL) | Cxxx-NCR-000475 | NCR | Installation of ductwork without assured design (Level -5, westbound platfrom, east, AP7A) |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2016-03-23 | 2016-04-04 14:19 | 12 | 2016-03-09 09:58 | Mechanical - Heating Ventilation & Air Conditioning | 10000 |  | Documentation and Records | Rework | 2 (6-60k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Per the drawing Cxxx-LAO-M-DDA-N105_6-26187 (attached) the Contractor was only to install the ductwork in the Maintenance Service Zone as part of the accepted SC1 Gate 3 design. However, the ductwork was installed beyond the agreed limit - into AP7A area (see photo attached). The Contractor is reminded that works cannot take place without an assured design in place.
| 02SL - Stations (LUL) | Cxxx-NCR-000476 | NCR | +0 level starter bars bent over excessively GL B/10 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-04-08 | 2016-04-18 07:56 | 10 | 2016-03-09 14:25 | Structural Engineering - Reinforcement | 5000 |  | Supervision/Management | Repair | 3 (3-6k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | To allow for a walkway, reinforcement starter bars have been bent over flat onto the +0 level. Minimum bar bending radius has been exceeded. No couplers in place therefore difficult to move around area. The engineering team was not consulted first.
| 02SL - Stations (LUL) | Cxxx-NCR-000477 | NCR | Set Out of Door at WTH Level -3 and Lintel Bearing (D2-4/008) |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-06-30 | 2016-05-12 11:04 | -49 | 2016-03-10 13:15 | Architectural - Brickworks/Blockworks | 3000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | The Contractor has incorrectly set out the blockwork at WTH Level -3 for the walling that forms the structural opening of door D2-4/008. This means that the lintel would be bearing on a half block and cause a straight joint between the block below and lintel.
| 02SL - Stations (LUL) | Cxxx-NCR-000478 | NCR | Blockwork and Secondary Concrete Internal Walls Started ahead of By Exception - GYB - Level -3 & -4 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-03-24 | 2016-03-18 13:24 | -6 | 2016-03-10 13:43 | Architectural - Brickworks/Blockworks | 2000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | The Contractor held a review of GYB Level -3 and GYB Level -4 internal walls with his designer, __, MEP team and the Project Manager (__) to release works via By Exception. Following communications the By Exception was submitted electronically to the Project Manager. The Contractor has progressed works at both GYB Level -3 (Blockwork to Concrete Walls) and at GYB Level -4 (Blockwork and Concrete) without approval of the By Exceptions.
| 02SL - Stations (LUL) | Cxxx-NCR-000479 | NCR | +0 Capping beam upstand reinforcement out of position GL 2.5-6/A |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-05-05 | 2016-05-11 14:12 | 6 | 2016-03-14 11:45 | Structural Engineering - Concrete Member | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | A setting out error has occurred with the positioning of reinforcement starter bars for an upstand upon the capping beam between grid lines 2.5-6 / A. This has lead to little or no cover to the reinforcement to the external face of the upstand.
| 02SL - Stations (LUL) | Cxxx-NCR-000480 | NCR | Wall reinforcement in incorrect position |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-05-05 | 2016-05-11 10:36 | 6 | 2016-03-14 12:58 | Structural Engineering - Concrete Member | 5000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Supervision - Insufficient supervision | Completed |  | The contractor has determined an error with the position of reinforcement starter bars required for a 250mm wall running west-east. The error means that both lines of reinforcement starter bars are offset by 100mm with 1 line out of the wall footprint entirely. See attached mark up for clarity. Starter bar sizes are B16 and B25 as per detailing drawing Cxxx-LAO-C-DWG-N105_WS089_1-50013.
| 02SL - Stations (LUL) | Cxxx-NCR-000482 | NCR | +0 Reinforcement bar position error - requiring starter bars to be cranked over |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-04-14 | 2016-03-24 10:34 | -21 | 2016-03-15 12:42 | Structural Engineering - Reinforcement | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Personnel Error - Inattention to detail | Completed |  | Due to a positioning error, reinforcement starter bars have needed to be cranked over to achieve cover (please see attached photos). This has lead to bars being bend and concrete spalling at step locations. Starter bars are shown on drawing: Cxxx-LAO-C-DWG-N105_WS089_1-50024.
| 02SL - Stations (LUL) | Cxxx-NCR-000483 | NCR | Plastic settlement latent defects on top of +0 beam B5 (GL 5/A-C) |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-10-28 | 2016-10-18 14:59 | -10 | 2016-03-15 15:15 | Structural Engineering - Concrete Member | 1000 |  | Material | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Upon observing the top of beam B5 at +0 level, located at GL 5/A-C, the Contractor has determined plastic settlement cracking has occurred on the surface. Settlement depths of up to 15mm have been observed. Location and photos can be found attached.
| 02SL - Stations (LUL) | Cxxx-NCR-000484 | NCR | GYB - Level +4 and +5 gullies |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-04-30 | 2017-04-20 14:20 | -10 | 2016-03-17 08:35 | Civil - Drainage | 1500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | Gullies have been installed on the roof level at GYB to achieve key date handover. At the time of installation, MCR for the gully was approved. Engineers installed the gully with a view that same product has been elsewhere.
| 02SL - Stations (LUL) | Cxxx-NCR-000485 | NCR | Concrete cover in -1 plinth area |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-05-05 | 2016-04-25 14:38 | -10 | 2016-03-17 10:16 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | The plinths in -1 vent area (as per FCD-000539) have been cast with 80mm of cover.
| 02SL - Stations (LUL) | Cxxx-NCR-000486 | NCR | Inspection request not sent |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-07-31 | 2016-04-01 13:20 | -121 | 2016-03-17 14:01 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | The inspection request form sent through to Crossrail did not capture every pour carried out on the day due to a late change in pour sequence.
| 02SL - Stations (LUL) | Cxxx-NCR-000487 | NCR | Debonding of fireproofing mastic within platform movement joints |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-07-31 | 2016-07-08 14:52 | -23 | 2016-03-18 10:59 | Civil - Civil Engineering General | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | It has been identified that in 5No locations within the maintenance zone of the platform tunnels (4No in PTW & 1No in PTE) the fire proofing mastic within the movement joints has debonded from the side of the concrete. In each location the mastic has debonded over an approx. length of 1m - see attached photo.
| 02SL - Stations (LUL) | Cxxx-NCR-000488 | NCR | __-Lightning Protection Contractor |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-10-31 | 2019-09-03 14:10 | -58 | 2017-10-17 06:36 | Electrical - General | 5000 |  | Planning | Use As-Is | 3 (3-6k) | Complete | Subcontractor Problems - Other | Completed |  | __ have been appointed to install/test and commission the lightning protection system. __ have documented QMS which is based on ISO but which is not externally audited and do not hold !SO 9001 certification.
| 02SL - Stations (LUL) | Cxxx-NCR-000489 | NCR | Core 4 temporary doorway mis-alignment at +0 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-01-31 | 2016-11-15 13:29 | -77 | 2016-03-22 18:04 | Structural Engineering - Concrete Member | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | Due to a setting out error with positioning a temporary opening within the Core 4 at +0 level, the Contractor has had to remove a portion of the wall through stitch drilling. The temporary opening has been positioned out of place by 150mm. In order for the temporary hoist to not snag the wall, a 1.5m long by 0.15m wide section will need to be removed.
| 02SL - Stations (LUL) | Cxxx-NCR-000490 | NCR | W4 External finish - blow holes that don't meet the spec Level +0 - +3 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-06-20 | 2016-06-15 13:37 | -5 | 2016-03-22 17:43 | Civil - Civil Engineering General | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Following an external finish inspection with the Architect it was noticed that W4 contains some blow holes that were larger than the specification allowed.
| 02SL - Stations (LUL) | Cxxx-NCR-000491 | NCR | Level -4 Mezzanine Slab cast to incorrect Buildersworks Drawing |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-08-30 | 2016-09-15 14:45 | 16 | 2016-03-23 17:50 | Structural Engineering - Concrete Member | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Level -4 Mezzanine Slabs have been cast to incorrect builderswork drawings, and in some instances General Arrangements only referred to. As a result a number of openings have been found to be inadequate for the latest buildersworks requirements. A summary of the openings that require extending or including has been attached. (Any openings without comment have been constructed to current buildersworks requirements).
| 02SL - Stations (LUL) | Cxxx-NCR-000492 | NCR | WTH Missing set of cubes -1 slab |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-10-21 | 2016-04-26 15:23 | -178 | 2016-04-04 13:37 | Civil - Civil Engineering General | 2000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | Cube results for WO124 A-D can not to be provided due set of cubes have gone missing in process. Four out of five sets of cubes ( WO122 A-D,WO123 A-DWO125 A-DWO126 A-D) taken for slab at level -1 have pass test for 28 days compressive cube strength. Also sixth set of cubes haven't been taken. 28 day cube results have been attached.
| 02SL - Stations (LUL) | Cxxx-NCR-000493 | NCR | Installation of firestopping prior to cover up inspection sign off |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-05-03 | 2016-04-12 14:17 | -21 | 2016-04-05 15:42 | Civil - Civil Engineering General | 5000 |  | Supervision/Management | Rework | 3 (3-6k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Movement joint firestopping works have been carried out in areas that haven't been signed off for cover up.
| 02SL - Stations (LUL) | Cxxx-NCR-000494 | NCR | TC1 crane erected without inviting Crossrail field engineers to witness points on ITP. |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-05-31 | 2016-04-11 10:58 | -50 | 2016-04-06 08:51 | Civil - Civil Engineering General | 500 |  | Planning | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | The crane was erected over the course of a weekend, the approved ITP (Cxxx-LAO-04-ITP-N105_WS089-50015) for this work required some activities to be witnessed by Crossrail field engineers. It was subsequently reported at Quality meeting that Crossrail were not invited to any of these witness points.
| 02SL - Stations (LUL) | Cxxx-NCR-000495 | NCR | Escalator slab excessive cover at -2 slab node |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-05-06 | 2016-04-22 09:49 | -14 | 2016-04-06 11:00 | Structural Engineering - Concrete Member | 3000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The excavator slab at the -2 slab interface has excessive cover measured to a maximum of 100mm (see attached for mark up of location). Cover should be 35mm, as indicated on Cxxx drawing: Cxxx-LAO-C-DWG-N105_WS089_5-50088.
| 02SL - Stations (LUL) | Cxxx-NCR-000496 | NCR | GYB -1.5 Walkway stair pour |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-04-20 | 2016-04-07 11:03 | -13 | 2016-04-06 15:39 | Civil - Civil Engineering General | 10000 |  | Planning | Rework | 2 (6-60k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | The stairs from -2 to -1.5 walkway were poured with the walkway slab mix. This mix was too wet for a stair pour. It was decided to stop the pour, remove the shuttering and clean out the wet concrete.
| 02SL - Stations (LUL) | Cxxx-NCR-000497 | NCR | Insufficient Cover in CW9 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-08-15 | 2016-07-19 15:04 | -27 | 2016-04-07 07:12 | Structural Engineering - Reinforcement | 2000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Above the stub walls in one of the columns in CW9 (refer to the attached drawing) the cover in a localized section along the side of the column is 27mm rather than 45mm which should be for the external wall. As this wall will be soon cladded I propose to accept the 27mm cover to this localized section as after the cladding the wall in this area will not be exposed to any weather effects (i.e. rain, sunshine etc.) and the standard internal cover (30mm) should suffice.
| 02SL - Stations (LUL) | Cxxx-NCR-000498 | NCR | Additional Access Panel Introduced at GYB Level -1 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-05-21 | 2016-06-15 13:41 | 25 | 2016-04-07 11:30 | Architectural - Brickworks/Blockworks | 0 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | The Project Manager instructed PMI 0411 which outlined the requirement to introduce access panels at re-injectable grout tube locations within the GYB. Upon construction of this perimeter walling it became apparent that introducing these access panels would not enable the desired access as the cladding system that sits in front of it wouldn't align and be designed to enable access. Through discussions between the Contractor (__) and the Project Manager (E Tibbitts) that in this location they would not be introduced. Unfortunately works on site had progressed and one of the access panels had been included already.
| 02SL - Stations (LUL) | Cxxx-NCR-000499 | NCR | OSD Pile 28 cut off lower than design |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-07-15 | 2016-04-22 12:17 | -84 | 2016-04-07 14:59 | Civil - Structural Engineering | 5000 |  | Damaged | Use As-Is | 3 (3-6k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Upon breaking down Pile 28 within the OSD basement of the western ticket hall, the Contractor had to overbrake the pile as uneven cracks were induced. The centre of pile remains as the design cut off level, however localized areas around the perimeter of the pile had to be broken down until sound concrete remained.
| 02SL - Stations (LUL) | Cxxx-NCR-000500 | NCR | GYB - Thermal Shrinkage Cracks - Level +3 beams |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-07-17 | 2016-07-19 10:53 | 2 | 2016-04-08 14:02 | Civil - Civil Engineering General | 10000 |  | Material | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Thermal shrinkage cracks have occurred in the top of the beams at level +3. Initial measurements show them to be 1mm wide
| 02SL - Stations (LUL) | Cxxx-NCR-000501 | NCR | Missing Concrete cube result for precast stair - Core 2 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-06-30 | 2016-05-23 15:55 | -38 | 2016-04-08 15:26 | Structural Engineering - Testing | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | BISON manufacturing limited have missed placed a __ concrete cube result record for one number precast concrete flight within Core 2 - WTH. The flight in question is denoted F3 and located between levels -4 and -3. Records from BISON's QR6 sheet state that the concrete cube was crushed at 65.66N/mm2.
| 02SL - Stations (LUL) | Cxxx-NCR-000502 | NCR | OSD basement pile 39 starter bars |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-05-02 | 2016-04-25 14:23 | -7 | 2016-04-08 14:55 | Civil - Structural Engineering | 0 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Previous Construction - Problems based on previous construction errors | Completed |  | Pile 39 on gridline 2-A the protruding starter bars were clamped to the above lifting cage. The starter bar lengths are in the attached sketch, please could you advise if acceptable of if any remediation needs to be done?
| 02SL - Stations (LUL) | Cxxx-NCR-000503 | NCR | Possibly Insufficient Cover around Box Outs CW8 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-08-15 | 2016-07-19 15:01 | -27 | 2016-04-11 11:15 | Structural Engineering - Reinforcement | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Before closing the external shutters in CW8 between Level +0 and Level +1 reinforcement appears that has insufficient cover around the openings. The operatives confirm that these were temporarily installed to support the boxes until the magnets were installed on the formwork. As there is an uncertainty on this I propose to use the cover-meter to confirm the cover and act accordingly.
| 02SL - Stations (LUL) | Cxxx-NCR-000504 | NCR | GYB GFL Blockwork and Concrete Walls Built without Approved Design |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2018-04-14 | 2018-03-02 13:36 | -43 | 2016-04-12 08:33 | Civil - Civil Engineering General | 1000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | The Contractor has begun constructing concrete and blockwork walls at GFL ahead of an approved design. Blockwork elevations have been produced and structurally checked however the door into the Mechanical Riser (1/767) changed position to enable suitable access to the ductwork within this riser. It then made part of these calculations void. These walls have begun construction to enable them to be completed ready for KD3.
| 02SL - Stations (LUL) | Cxxx-NCR-000506 | NCR | GYB - W3/Beam Connection |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-07-21 | 2016-04-28 10:12 | -84 | 2016-04-12 13:17 | Civil - Civil Engineering General | 2000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Couplers have not been cast into W3 to connect into the +3 upstand in phase 2. See attached drawing
| 02SL - Stations (LUL) | Cxxx-NCR-000507 | NCR | ITP not specific to task |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-05-10 | 2016-05-04 07:35 | -6 | 2016-04-13 08:55 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | The ITP Cxxx-LAO-04-ITP-N105_WS089_Z-50006 was quoted for the work of installing temporary slab supports shown on drawing Cxxx-OVE-S-DDD-N105_3-34403, which wasn't specific to the task.
| 02SL - Stations (LUL) | Cxxx-NCR-000508 | NCR | Additional Requirements for Level -5 and -4M WTH Risers and Basement |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-01-31 | 2016-12-16 16:18 | -46 | 2016-04-13 09:53 | Structural Engineering - Concrete Member | 0 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Openings within the WTH Core 04 risers have been constructed in line with Cxxx permanent works design (Stage F). As MEP design progresses the Stage F it has become apparent a number of openings need to be extended to facilitate MEP plant requirements. Additional openings through the Level -4 slab have also been requested based on MEP design.
| 02SL - Stations (LUL) | Cxxx-NCR-000510 | NCR | Level -2 Windpost repositioning |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-09-26 | 2016-10-14 14:08 | 18 | 2016-04-13 12:50 | Structural Engineering - Concrete Member | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Supervision - Insufficient supervision | Completed |  | Following a survey of Windposts on the Level -2 raft foundation, a number were found to be out of tolerance and adjoining blockwork cannot be installed. The attached drawing Cxxx-LAO-A-DDA-N105_3-20954 indicates 3 number windposts which need to be re-installed.
| 02SL - Stations (LUL) | Cxxx-NCR-000511 | NCR | Cracks to escalator wall on -2 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-06-10 | 2016-06-13 08:21 | 3 | 2016-04-14 14:34 | Civil - Civil Engineering General | 5000 |  | Material | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Cracks have appeared on level -2 escalator wall. The length and width varies from under 0.3mm up to 0.6mm. See attached mark-ups
| 02SL - Stations (LUL) | Cxxx-NCR-000512 | NCR | Beam B12 casted 100mm higher than design |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-07-14 | 2016-06-13 11:52 | -31 | 2016-04-15 11:41 | Structural Engineering - Reinforcement | 5000 |  | Supervision/Management | Repair | 3 (3-6k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | The beam B12 (at Level +1) was casted 100mm above the designed level due to setting out error. The soffit of the beam is at the correct level and the reinforcement was fixed to the correct level. I propose to break the excess 100mm concrete from the top and then make good to the correct level.
| 02SL - Stations (LUL) | Cxxx-NCR-000513 | NCR | Coring of -4 internal wall - Elevation 16 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-12-29 | 2016-05-26 15:12 | -217 | 2016-04-15 15:47 | Civil - Civil Engineering General | 5000 |  | Design | Repair | 3 (3-6k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | Elevation 16 on the attached document was cast with and opening shown in a previous revision of the mark-up.
| 02SL - Stations (LUL) | Cxxx-NCR-000514 | NCR | WTH Vent Tower - CW9 Drill and Fix 3No. B25 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-07-17 | 2016-04-26 15:31 | -82 | 2016-04-18 07:14 | Structural Engineering - Reinforcement | 5000 |  | Supervision/Management | Repair | 3 (3-6k) | Complete | Supervision - Insufficient supervision | Completed |  | Due to incorrect installation of 3No. B25 bars in CW9 there is not enough cover on the links (see attached sketch). I therefore propose to cut them and drill and fix them with resin.
| 02SL - Stations (LUL) | Cxxx-NCR-000515 | NCR | -1 OSD basement sump pour construction error |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-05-18 | 2016-05-26 15:00 | 8 | 2016-04-18 15:50 | Structural Engineering - Concrete Member | 5000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Supervision - Insufficient supervision | Completed |  | The Contractor has made a mistake with the pouring of a sump base within the OSD basement. Location of sumps are GL A-B/1. The base of the smaller sump (north of larger) is 90mm higher than the larger, as per the latest Cxxx drainage drawing Cxxx-LAO-P-DDA-N105_2-31143 P06, which has been transferred onto the Cxxx reinforcement detail drawings Cxxx-LAO-C-DWG-N105_WS089_2-50033 and 50034. The Cxxx structural drawings however indicate a different arrangement.
| 02SL - Stations (LUL) | Cxxx-NCR-000516 | NCR | Galvanised Pipe work – Galvanised Coating |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-06-30 | 2016-06-28 14:57 | -2 | 2016-04-19 10:11 | Materials - General | 5000 |  | Material | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The Contractor confirms that the following modules WTH-13/15&17 on the WTH level -5 have been delivered with 150mm galvanized tube (in total 5 lengths) which have the internal galve coating flaking internally where the groove was rolled.
| 02SL - Stations (LUL) | Cxxx-NCR-000517 | NCR | CW1 out of tollerance |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-07-19 | 2016-06-13 11:54 | -36 | 2016-04-20 06:36 | Structural Engineering - Concrete Member | 1000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | the stub wall in CW1/CW9 is out of tolerance between 15-20mm even though the cover to the reinforcement is as per design. (refer to attached cover meter reading)
| 02SL - Stations (LUL) | Cxxx-NCR-000518 | NCR | No IRF sent for OSD sump base and pile cap pre-pour inspection |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-05-04 | 2016-05-05 10:23 | 1 | 2016-04-20 08:39 | Human Factors - Human Factors General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | The Contractor failed to invite the CRL field engineer to attend a pre-pour inspection for a OSD basement sump base pour (see attached). Date of pours were: 13/04/16: Pile Caps 18/04/16: Small sump base pour
| 02SL - Stations (LUL) | Cxxx-NCR-000519 | NCR | Setting out error with back-blinding for capping beam - East side GL 9-10 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-05-04 | 2016-05-16 16:05 | 12 | 2016-04-20 09:42 | Structural Engineering - Concrete Member | 5000 |  | Incorrect Installation | Use As-Is | 3 (3-6k) | Complete | Supervision - Insufficient supervision | Completed |  | The Contractor has made a setting out error with the concrete back-blinding at +0 level GL 9-10/EE (East side). Blinding has been found to be 40mm out of position as shown attached. This has lead to the need to reduce the amount of cover to reinforcement on both the external and internal sides: 25mm internal (30mm design) and 40mm external (50mm design). The internal capping beam face shutter was moved by 15mm (working to within the structural tolerances) to assist with the reduced section size. One number B40 top bars has also be installed inbound of the upstand starter bars (see photos).
| 02SL - Stations (LUL) | Cxxx-NCR-000520 | NCR | Insufficient Cover in CW9 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-09-30 | 2016-09-14 11:04 | -16 | 2016-04-21 10:46 | Structural Engineering - Reinforcement | 2500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Cover of 30mm was observed in CW9 (Level - 130.500) for 900mm height and 5500mm long section. This was validated on the 19/05/2016 with the cover meter (see attached photo)
| 02SL - Stations (LUL) | Cxxx-NCR-000522 | NCR | WTH, +0 Capping beam Blocked Geothermal Loops |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-02-28 | 2017-02-01 15:18 | -27 | 2016-04-25 16:16 | Civil - Civil Engineering General | 5000 |  | Damaged | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | The geothermal contractor have encountered 1no blockages on each of panels: P42, P47, P49, P50, P54 and P55 such that they can not be extended and form part of the network. In accordance with __ procedure __ have attempted to flush and use Cobra system to clear blocked pipes.
| 02SL - Stations (LUL) | Cxxx-NCR-000523 | NCR | Reduced cover on -1 escalator wall |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-08-31 | 2016-07-25 12:16 | -37 | 2016-04-26 14:05 | Civil - Civil Engineering General | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Supervision - Insufficient supervision | Completed |  | The kicker for escalator wall on -1 was poured with reduced cover to the horizontal lacer. It is down to 15mm is some areas, however is, 30mm in most.
| 02SL - Stations (LUL) | Cxxx-NCR-000524 | NCR | Inadequate cover CW9 second lift |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-09-20 | 2016-09-14 11:13 | -6 | 2016-04-26 17:05 | Structural Engineering - Reinforcement | 0 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | Cover of 30-35mm has been observed at CW9 at level 134.200. Following the response from Cxxx for NCR 497, CW9 is classed with exposure class XD1 to BS 8500 table A5 for which a minimum cover of 30mm, excluding tolerance, is required to ensure durability. Therefore, even though the cover is not 45mm (which is stated as the nominal cover) is still above the minimum.
| 02SL - Stations (LUL) | Cxxx-NCR-000525 | NCR | Light Aggregate in CW9 at 2nd Lift |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-07-26 | 2016-06-06 09:00 | -50 | 2016-04-27 09:50 | Structural Engineering - Concrete Member | 0 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Lack or improper material identification and traceability | Completed |  | Minimum amount of light aggregate was identified at the top of the pour in CW9 at level 132.500.
| 02SL - Stations (LUL) | Cxxx-NCR-000526 | NCR | Bending bars in CW8 2nd Lift |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-07-26 | 2016-06-13 12:05 | -43 | 2016-04-27 09:59 | Structural Engineering - Reinforcement | 500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | 4No. B16 vertical bars were bend to allow access during construction.
| 02SL - Stations (LUL) | Cxxx-NCR-000527 | NCR | Cracked cocnrete in CW8 external face 2nd Lift |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-07-26 | 2016-07-15 14:33 | -11 | 2016-04-27 10:15 | Civil - Civil Engineering General | 5000 |  | Supervision/Management | Repair | 3 (3-6k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | The external face of CW8 has a visible crack due to a damaged cause by the shatter during lifting (refer to attached plan and elevation drawings). Permit to strike was authorized at 12N/mm2 (see attached) but the cracking occurs due to the shutter hitting the corner and not due to early strike. Striking of that wall occurs a day after the permit to strike was signed due to the sequence of lifting (therefore strength was more than 12N/mm2). Extend of cracking is shown in the second page of the attached drawing (NCR 527 - Cracked concrete in CW8_Latest)
| 02SL - Stations (LUL) | Cxxx-NCR-000528 | NCR | OSD basement - incorrect cover to sump walls |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-08-31 | 2016-08-18 07:59 | -13 | 2016-04-28 12:51 | Civil - Structural Engineering | 5000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Management Problem - Inadequate supervision | Completed |  | With reference to the attached markup and photos, during a post pour inspection it was found that 2no. walls of the OSD sumps have insufficient cover.
| 02SL - Stations (LUL) | Cxxx-NCR-000529 | NCR | GYB Level -1 - Making good of pilot/rig holes in soffit over escalator |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-07-28 | 2016-08-19 07:08 | 22 | 2016-04-29 14:24 | Civil - Civil Engineering General | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | In order to drill holes for the steel windposts at the level -1 escalator wall pilot/rig holes were drilled to hold the rig in position. These holes will need to be made good and matched to the existing soffit finish.
| 02SL - Stations (LUL) | Cxxx-NCR-000530 | NCR | Latent concrete defects to +0 propping slab adjacent to Core 4 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-10-31 | 2016-07-15 11:42 | -108 | 2016-05-03 13:02 | Structural Engineering - Concrete Member | 5000 |  | Material | Repair | 3 (3-6k) | Complete | Management Problem - Inadequate supervision | Completed |  | The Contractor has determined that there is some latent defects, 'de-lamination' with an area of the +0 slab adjacent to Core 4 (see attached for location). Latents are no more than 2mm thick therefore cover is not jeopardized.
| 02SL - Stations (LUL) | Cxxx-NCR-000531 | NCR | GYB Level -3 - Slab Opening Built out of Tolerance by Others - Movement of Blockwork Wall |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-11-16 | 2016-12-02 14:58 | 16 | 2016-05-03 13:13 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The majority of the primary structure within GYB was built by Others. As part of ongoing construction of Blockwork walling the Contractor would like to highlight that FAN 4/767 opening within the slab is 50mm larger than required. The architectural plan outlines that this opening has perimeter blockwork built around its edge.
| 02SL - Stations (LUL) | Cxxx-NCR-000532 | NCR | WTH Level -5 Fire Compartmentation Room for HV A and B Routes |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-11-18 | 2017-12-05 10:52 | 17 | 2016-05-03 13:59 | Architectural - Brickworks/Blockworks | 5000 |  | Design | Repair | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Following a site walk around with Systemwide Contractor Cxxx it was highlighted that the additional walling that forms a room at the end of the UPE in WTH Level -5 does not achieve the fire compartmentation required between the HV A and HV B route as per the design requirement. A meeting was organized between the Contractor's designer, the Contractor, and Cxxx to review the requirements and the correct solution required.
| 02SL - Stations (LUL) | Cxxx-NCR-000533 | NCR | WTH, lvl -1, escalator kicker shutter failure |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-01-30 | 2017-01-12 10:40 | -18 | 2016-05-09 08:20 | Civil - Civil Engineering General | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Due to escalator kicker shutter failure at level -1, __ obtain 10 to 35 mm excessive cover at a very top of 1.4m wide top section of kicker. Please see attached photos and sketch.
| 02SL - Stations (LUL) | Cxxx-NCR-000536 | NCR | Concrete pour short with cube up (GL 3-4/E) +0 level |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-06-08 | 2016-06-13 12:11 | 5 | 2016-05-09 16:05 | Structural Engineering - Concrete Member | 10000 |  | Incomplete Works | Repair | 2 (6-60k) | Complete | Personnel Error - Inattention to detail | Completed |  | Due to a quantity measurement error, the Contractor was short 1.5m3 of concrete required for pouring the +0 slab/ capping beam adjacent to GL 3/E on 28/4/16. As the pour was an over night pour, it was not possible to procure further concrete for that mis-cubed. This resulted in the need to place a 100mm deep stop end shutter across the pour as shown and pour the remaining section 100mm short of the SSL.
| 02SL - Stations (LUL) | Cxxx-NCR-000537 | NCR | Insufficient lap length and B20 rather than B25 bar in CW5 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-12-15 | 2016-06-13 12:12 | -185 | 2016-05-04 18:07 | Structural Engineering - Reinforcement | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | In the 3rd lift of the jump for in CW5 B20 bar was identified instead of B25 casted in the previous pour which has insufficient lap length for the 3rd lift (refer to the attached drawing).
| 02SL - Stations (LUL) | Cxxx-NCR-000538 | NCR | Tunnel AP7A - Ductwork Insulation Application Access |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-10-15 | 2016-09-15 14:26 | -30 | 2016-05-05 15:02 | Mechanical - Heating Ventilation & Air Conditioning | 5000 |  | Material | Repair | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | After reviewing fire rated ductwork in the under platform area the Contractor confirms that there are sections of ductwork which have limited access to enable the insulation due to services and structural restrictions. The Project Manger accepted insulation on the fire rated ductwork for thermal heat transfer purpose only (using 25mm duct wrap) As the areas identified being AP7a and under platform invert ductwork structure connections, the contractor deems access to be restricted are inaccessible by any occupants the Contractor therefore proposes that the need for insulation un-necessary. The contractor will raise an FCD with the agreed solution following review with the project manager.
| 02SL - Stations (LUL) | Cxxx-NCR-000539 | NCR | GYB - W13 builders work holes, level +1 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-08-13 | 2016-06-02 15:14 | -72 | 2016-05-05 16:08 | Civil - Civil Engineering General | 5000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | A builders work hole was missed in W13 of the GYB superstructure (see attached mark up drawing).
| 02SL - Stations (LUL) | Cxxx-NCR-000540 | NCR | WTH Vent Tower Cast-ins |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-02-05 | 2017-01-30 15:27 | -6 | 2016-05-11 11:57 | Structural Engineering - Inserts | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | During the construction of the vent tower, there is a requirement for cast in fixing to allow the precast panels to be secured on installation. We have proceeded with the installation without the formal sign off of the MCR; the item on concern is a M30 Het fixing which was missed off the MCR.
| 02SL - Stations (LUL) | Cxxx-NCR-000543 | NCR | OSD basement incorrect cover to sump gridline B/2 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-08-31 | 2016-08-18 13:47 | -13 | 2016-05-06 11:13 | Civil - Structural Engineering | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | The sump in level -1 of the OSD basement located at GL B/2 lacks cover to the North elevation.
| 02SL - Stations (LUL) | Cxxx-NCR-000544 | NCR | GYB - Level -4 - Cracked Block under Secondary Concrete Wall |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-05-20 | 2016-05-17 08:09 | -3 | 2016-05-06 16:48 | Architectural - Brickworks/Blockworks | 5000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | The Contractor reviewed and released blockwork risers for works to commence on Level -4 GYB whilst further structural checks were being completed to surrounding wall elevations. Two of the surrounding walls were later confirmed to be required as concrete due to the openings within them. Following a discussion with the structural engineer it was proposed to pour the concrete walls over the blockwork and the small nibs that formed the side of the doors remain in blockwork as it was toothed into the riser blockwork which had been built up to door height. In one location the block underneath the concrete was removed and thus the underside of the concrete shuttered. In the second wall the blockwork was used as a shutter to pour up to. Following review with the structural designer and the load checks this crack is believed to have been caused by early-age shrinkage. Please refer to the email attachment with __ Senior Structural Engineer __.
| 02SL - Stations (LUL) | Cxxx-NCR-000545 | NCR | CW5 Drill and Fix 2No. B32 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-08-06 | 2016-06-13 12:17 | -54 | 2016-05-08 20:40 | Structural Engineering - Reinforcement | 5000 |  | Supervision/Management | Repair | 3 (3-6k) | Complete | Supervision - Insufficient supervision | Completed |  | Due to incorrect setting out the 2No. B32 starter bars in CW5 are to close to the edge of the stub-wall providing no cover to the U-bars that will be installed (see attached sketch). I proposed to cut these two bars and drill and fix with resin in the designed position to allow enough cover to the u-bars. This is detailed in FCD 535.
| 02SL - Stations (LUL) | Cxxx-NCR-000546 | NCR | Dry shrinkage cracks in concrete - +0 level GL EE/8-10 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-11-30 | 2016-10-18 12:48 | -43 | 2016-05-10 06:55 | Structural Engineering - Concrete Member | 1000 |  | Material | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Several cracks have occurred within concrete structures located within the south/east corner of the WTH at +0 level. Cracks appear to have been caused by shrinkage, throughout the hydration process. Elements concerned are: - +0 propping slab (GL 8-10/EE): Poured 19/04/16. - +0 capping beam upstand (GL 9-10/EE): Poured 25/04/16. Temperatures at the time of pouring were: 19/04/16: 9degC 25/04/16: 10degC.
| 02SL - Stations (LUL) | Cxxx-NCR-000549 | NCR | GYB Substructure level -1: Slipped rockwall during concrete pour on movement joint |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-08-08 | 2016-07-20 12:10 | -19 | 2016-05-10 13:04 | Civil - Civil Engineering General | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The Rockwall placed at the edge of a concrete pour in level -1 between the escalator wall and the secondary wall slipped during the pouring of the concrete. This meant the movement joint was not consistent throughout the width of the wall.
| 02SL - Stations (LUL) | Cxxx-NCR-000550 | NCR | CON103 in 3rd Lift |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-08-08 | 2016-06-28 10:33 | -41 | 2016-05-10 12:55 | Architectural - Walls | 5000 |  | Supervision/Management | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | In the 3rd lift of the WTH Vent Tower the following localized issues have been identified in the CON 103 walls which do not conform with the specifications (refer to attached sketch): 1) Steps greater than 3mm 2) Scratch in wall from jump form
| 02SL - Stations (LUL) | Cxxx-NCR-000551 | NCR | Drill and fix B12 bars in stair core Level +1 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-08-08 | 2016-06-13 12:19 | -56 | 2016-05-10 17:27 | Structural Engineering - Reinforcement | 5000 |  | Supervision/Management | Repair | 3 (3-6k) | Complete | Supervision - Insufficient supervision | Completed |  | Couplers were not installed in the stair core in Level +1 for the landing slab (refer to the attached drawing).
| 02SL - Stations (LUL) | Cxxx-NCR-000552 | NCR | Missing trimmers in CW8 Level +2 to Level +3 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-08-08 | 2016-05-23 16:02 | -77 | 2016-05-10 17:45 | Structural Engineering - Reinforcement | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Wall between Level +2 to Level +3 was casted without the trimmer bars in the areas indicated in the attached drawing as they were not shown on the detailing drawing.
| 02SL - Stations (LUL) | Cxxx-NCR-000553 | NCR | GYB - +0 builders work holes for combined discharge main |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-01-31 | 2016-11-22 15:04 | -70 | 2016-05-11 14:30 | Civil - Civil Engineering General | 1000 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The builders work holes have been installed as per our builders work drawing at level +0 (Cxxx-LAO-Z-DWG-N105_WS093_1-50001) for the 225mm diameter combined discharge main. However the levels don’t work with the trap configuration in the pit behind W9 or the upstand on the outside.
| 02SL - Stations (LUL) | Cxxx-NCR-000554 | NCR | Phenolic Block - Supply Ductwork Level -5 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-01-25 | 2016-12-09 14:00 | -47 | 2016-05-11 14:40 | Mechanical - Heating Ventilation & Air Conditioning | 1500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | The contractor wishes to informs the project manager that phenolic foam blocks have been used to support the supply ductwork in level -5 (see photo attached). The material has been rejected for use under CRL-MCR-003171. The contractor has issued a RFI to the project manager requesting confirmation the wood blocks may be used to within brackets to support MEP services which require insulation.
| 02SL - Stations (LUL) | Cxxx-NCR-000555 | NCR | Incorrect Setting Out of a Blockwork Wall - WTH Level -4 Mezzanine |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-06-08 | 2016-06-13 12:21 | 5 | 2016-05-11 15:27 | Architectural - Brickworks/Blockworks | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | The Contractor has incorrectly set out a dividing wall on the WTH Level -4 Mezzanine. The blockwork nib that forms the door has been built 40mm to long.
| 02SL - Stations (LUL) | Cxxx-NCR-000556 | NCR | WTH Level -4 - Ductwork Installation within modules |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-06-25 | 2017-07-21 15:37 | 26 | 2016-05-11 15:08 | Mechanical - Heating Ventilation & Air Conditioning | 2000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The contractor wishes to inform the project manager that the ductwork installed in the MEP modules in WTH Level -4 is deemed to be non compliant with DW144, the contractor is to confirm compliance by close out of NCR.
| 02SL - Stations (LUL) | Cxxx-NCR-000557 | NCR | Concrete elements poured without CRL inspection +0 and Core 1 landings |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-06-11 | 2016-05-23 15:58 | -19 | 2016-05-12 09:05 | Structural Engineering - Concrete Member | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | The Contractor failed to invite CRL to inspect 3no. elements on ahead of them being poured on the backshift of 11/05/16. The elements concerned are: - Core 1 Landing - 121.475m - Core 1 Landing - 122.910m - Core 1 area 1m upstand +0 level GL The Contractor carried out their own pre-pour inspection ahead of formwork installed (6:30pm). Concrete ordered on the back shift was over ordered by 2m3 therefore the backshift manager decided to pour the landings and upstand in order to not waste the concrete.
| 02SL - Stations (LUL) | Cxxx-NCR-000559 | NCR | Cube Failure - WTH 10/03/2016 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-11-29 | 2016-10-04 08:58 | -56 | 2016-05-13 11:57 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | The strength of cubes W0219B and W0219C did not reach required 40N/mm2 in 28 days, see attached record sheet. This affect Capping beam 1 + 2 Upstand south beam top up. The consistence was within specification for used concrete mix.
| 02SL - Stations (LUL) | Cxxx-NCR-000560 | NCR | -4 plinth surface cracks |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-08-10 | 2016-08-18 13:34 | 8 | 2016-05-13 13:44 | Civil - Civil Engineering General | 5000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The plinth installed in room 5/686 has surface cracking of up to 0.5mm. The cracks will be scabbled back to good concrete, as well as this it has been discovered that the plinth was not cast to the correct height. Therefore once the scabbling has been completed reinforcement will be installed at 200mm centers and the plinth re cast to the correct height.
| 02SL - Stations (LUL) | Cxxx-NCR-000561 | NCR | Trunking Access |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-07-31 | 2016-06-04 08:03 | -57 | 2016-05-13 14:12 | Electrical - Cable Management | 10000 |  | Manufacturing Defect | Repair | 2 (6-60k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | WTH -5 Modules 13 & 15 Restricted /Limited Access due to services restricted within the module frame
| 02SL - Stations (LUL) | Cxxx-NCR-000562 | NCR | IRF not raised for infill panel pours Level -5 Escalator Pit Walls |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-08-02 | 2016-07-20 14:46 | -13 | 2016-05-18 07:30 | Civil - Civil Engineering General | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | In line with FCD-000566 and PMI-000359, 2# concrete infill panels are required to be concreted into the existing 350mm THK escalator pit walls at Level -5. Following agreement with CRL the work was planned outside the typical '6 Week Look Ahead' schedule. It was aimed to construct these iinfills in advance of any inclined hoist installation, to avoid any unsafe working at a later date. In the short time available for planning, the IRF issue to CRL was missed and panels cast without a CRL witness.
| 02SL - Stations (LUL) | Cxxx-NCR-000563 | NCR | Bending Bars on site - WTH Vent Tower |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-08-30 | 2016-07-01 09:46 | -60 | 2016-06-01 16:17 | Structural Engineering - Reinforcement | 5000 |  | Supervision/Management | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Worker not trained for the work being performed | Completed |  | In order to provide access over the top of the walls casted, bars were bend in two locations on WTH Vent Tower at the top of the 4th lift. According to the specifications KF10.3242 re-bending is not permitted before or after fixing into position. Also the bending of the bars in these locations was not done as per BS 8666 recommendations which leads to a non-conformance.
| 02SL - Stations (LUL) | Cxxx-NCR-000564 | NCR | External Wall CON103 Lift 4 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-08-16 | 2016-08-17 14:51 | 1 | 2016-05-18 16:37 | Architectural - Walls | 5000 |  | Supervision/Management | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following the inspection of the external wall Lift 4 the following items were identified to non conform with the specifications: 1) Number of blow holes larger than in the specifications 2) Concrete surface not smooth (possibly due to dirt on the shutters) 3) Step in a joint (CON 104 wall)
| 02SL - Stations (LUL) | Cxxx-NCR-000565 | NCR | Trimmer Bars Missing CW8 4th Lift |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-08-18 | 2016-06-13 12:23 | -66 | 2016-05-20 08:51 | Structural Engineering - Reinforcement | 1000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | The vertical trimmer bars were missed on the 4th lift in one side of the opening in CW8 (between CW & CW2) -refer to the attached drawing.
| 02SL - Stations (LUL) | Cxxx-NCR-000566 | NCR | GYB Superstructure +1 Chipped concrete from MEP fixing near pourline. |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-06-30 | 2016-07-08 09:14 | 8 | 2016-05-20 12:06 | Civil - Civil Engineering General | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | __ operatives were installing an angle bracket to support a cantilever arm holding pipes in the GYB Superstructure within the stair core at level +1 on Wall 13. The installation of the arm support when finished pulled out of the concrete. Following a discussion with __ it has been determined that this occurred due to the fixings being installed close to the top of a concrete pour, it is not best practice to install fixings near the top of a wall (or in this case near a construction joint). This is because it reduces the mass of concrete physically restraining the anchor.
| 02SL - Stations (LUL) | Cxxx-NCR-000567 | NCR | Blockwork - AP7a & CH1/AP2E Junction Infill without Design Assurance |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-01-31 | 2017-01-31 12:59 | 0 | 2016-05-23 13:54 | Architectural - Brickworks/Blockworks | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The Contractor has begun completing Blockwork walling within AP7a and CH1/AP2E junction. The elevations have been drawn and given to the Contractor's designer to complete the structural checks. The Structural Engineer has provided initial feedback outlining that 190mm walling in both locations is suitable and no wind posts are required.
| 02SL - Stations (LUL) | Cxxx-NCR-000568 | NCR | Bending Bars in 6th Lift |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-08-22 | 2016-06-14 09:43 | -69 | 2016-05-24 16:30 | Structural Engineering - Reinforcement | 5000 |  | Supervision/Management | Repair | 3 (3-6k) | Complete | Supervision - Insufficient supervision | Completed |  | In order to install the props to lift the shutters to the next lift at the top of the casted walls, bars were bend in two locations on WTH Vent Tower at the top of the 6th lift. According to the specifications KF10.3242 re-bending is not permitted before or after fixing into position. Also the bending of the bars in these locations was not done as per BS 8666 recommendations which leads to a non-conformance.
| 02SL - Stations (LUL) | Cxxx-NCR-000569 | NCR | Cracking Wall 9 at level +1 of the GYB |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2016-08-30 | 2016-07-21 09:19 | -40 | 2016-05-25 10:30 | Civil - Civil Engineering General | 500 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Cracking Wall 9 at level +1 of the GYB possibly wider than 0.5mm. Needs to be measured when access is available.
| 02SL - Stations (LUL) | Cxxx-NCR-000570 | NCR | OSD Basement total blocked geothermal loops |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-02-25 | 2017-02-01 15:20 | -24 | 2016-05-25 11:00 | Civil - Civil Engineering General | 5000 |  | Damaged | Repair | 3 (3-6k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | Further to Cxxx-NCR-000505 and Cxxx-EWN-00567, __ are raising an NCR for the total number of blocked geothermal loops as an action agreed in a Risk Reduction Meeting held on 10/5/16. Attended by: __ – __, __ GI – __ Cxxx – __ C135/OSD – __ CRL – __ __ confirm that out of the 60no. total loops, 27 are working. Please refer to attached markup drawing for the specific locations.
| 02SL - Stations (LUL) | Cxxx-NCR-000572 | NCR | Drill and fix bars in Slab Level +2 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-08-23 | 2016-06-14 09:45 | -70 | 2016-05-25 15:33 | Structural Engineering - Reinforcement | 5000 |  | Supervision/Management | Repair | 3 (3-6k) | Complete | Supervision - Insufficient supervision | Completed |  | Couplers missed at Level +2 in 2 different locations (see attached) - 12No. in total.
| 02SL - Stations (LUL) | Cxxx-NCR-000573 | NCR | Excessive blowholes on concrete in CW5 5th Lift |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-08-24 | 2016-08-01 13:53 | -23 | 2016-05-26 11:32 | Structural Engineering - Concrete Member | 5000 |  | Supervision/Management | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Excessive blowholes appear on the casted wall 5 in the 5th lift which does not comply with the CON 104 specifications.
| 02SL - Stations (LUL) | Cxxx-NCR-000574 | NCR | B12 Eazistrip casted in Level 3 & 4 rather than B16 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-08-24 | 2016-06-13 13:33 | -72 | 2016-05-26 17:15 | Structural Engineering - Reinforcement | 5000 |  | Design | Repair | 3 (3-6k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | B12 Eazistrip was casted in the primary walls for the fan room in Level +3 and Level +4 in the areas indicated in the attached document. This should be B16 bars.
| 02SL - Stations (LUL) | Cxxx-NCR-000575 | NCR | Design Approval - PPC for WTH Lightning Protection |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-09-30 | 2016-06-06 08:38 | -116 | 2016-06-02 12:05 | Over Head Line Electrification - Earthing & Bonding | 0 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | Works have been progressed without providing visibility to Crossrail of design submission PPC (Permission To Proceed With Construction) for WTH Lightning Protection is not listed in the PPC schedule available in the Collaboration Site.
| 02SL - Stations (LUL) | Cxxx-NCR-000576 | NCR | Inadequate cover in Beams Level +2 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-08-31 | 2016-08-22 13:35 | -9 | 2016-06-02 17:00 | Structural Engineering - Reinforcement | 5000 |  | Supervision/Management | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Inadequate cover was identified along Beams B21 and Beam B23 in Level +2 (from 15-18mm compare to 30mm which is the nominal cover). Refer to the attached drawing. Cover was checked with the cover meter.
| 02SL - Stations (LUL) | Cxxx-NCR-000577 | NCR | Shutters not properly prepared in CW5 6th Lift |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-09-14 | 2016-08-04 15:11 | -41 | 2016-06-06 12:15 | Structural Engineering - Concrete Member | 5000 |  | Supervision/Management | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Shutters were not properly prepared in CW5 6th Lift (refer to the attached drawing) before the pour. This caused the concrete to "stick" to the shutters and when we struck the shutters sections of the concrete were pulled from the surface of the wall. The concrete was tested and passed the flow test and cubes were taken as per specifications (see attached). Wall was struck with strength 15N/mm2.
| 02SL - Stations (LUL) | Cxxx-NCR-000578 | NCR | Module drawing details |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-04-30 | 2017-01-30 09:43 | -90 | 2016-06-23 14:58 | Electrical - Cable Management | 5000 |  | Supervision/Management | Repair | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Their appears to be a slight breakdown in QA at the __ factory. The drawing details an ISO view (which they have constructed) that differs with the section view, which illustrates CMS services on the lowest section, but the module has been constructed minus the supporting cross members and resulted in an on site retro fit, as per the attached photographs displaying the site added low level cross member supports
| 02SL - Stations (LUL) | Cxxx-NCR-000579 | NCR | Core 1 landing poured too high: Landing - 121.475m |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-08-02 | 2016-08-08 11:13 | 6 | 2016-06-07 12:12 | Structural Engineering - Concrete Member | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The Contractor has cast one of the southern core 1 landings (121.475m) 18mm too high resulting in a step occurring here. The landing soffit was positioned to the correct level, therefore the thickness was 268mm rather than 250mm.
| 02SL - Stations (LUL) | Cxxx-NCR-000580 | NCR | GYB GFRC - Nylon Washers |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-08-16 | 2016-08-16 10:36 | 0 | 2016-06-08 19:34 | Materials - Approval | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | The Contractor has used nylon washers as part of his GFRC GYB cladding installation. A Materials Compliance Record has not been submitted to the client. Please see the attached drawing for a typical detail.
| 02SL - Stations (LUL) | Cxxx-NCR-000581 | NCR | OSD basement - incorrect placement of sump reinforcement |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-07-04 | 2016-07-19 15:21 | 15 | 2016-06-20 07:40 | Civil - Structural Engineering | 5000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Management Problem - Inadequate supervision | Completed |  | Reinforcement for the sump in the southeast corner of the sump was fixed incorrectly. The north wall was fixed 500mm wide and the south wall was fixed 300mm wide adjacent to the diaphragm wall.
| 02SL - Stations (LUL) | Cxxx-NCR-000583 | NCR | MEP - Riser Framework |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-08-31 | 2016-09-14 14:56 | 14 | 2016-06-14 06:24 | Mechanical - Mechanical Engineering General | 5000 |  | Planning | Rework | 3 (3-6k) | Complete | Management Problem - Other | Completed |  | Riser framework for HC cable route was installed in WTH Level -4 and -5 rooms and then removed due to screed works were still to commence in these areas
| 02SL - Stations (LUL) | Cxxx-NCR-000584 | NCR | GYB GFRC Cladding Steelwork - Welding |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-10-28 | 2016-10-26 11:50 | -2 | 2016-06-14 08:05 | Architectural - General | 10000 |  | Workmanship | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Other | Completed |  | The following NCR was issued to the Contractor's supplier (__) against their fabricator (__). The Contractor has replicated this NCR on eB for the attention of the Project Manager to demonstrate that all future deliveries of the stainless steel carrier rails for the GYB GFRC cladding will have the correct welds as specified on the fabrication drawings. "A fixing plate became detached from a primary stainless steel fixing rail during installation of the Goslett Yard Box GFRC Cladding steelwork due to insufficient welding. Following this incident, a full inspection of the steel delivered to site (all of Face 3, 4 and 6) was carried out by __ (Lee Stones) on Wednesday 8th June 2016 with __ (__) present. A total number of 9 number stainless steel fixing rails were identified with welding issues and have been returned to __ on Thursday 9th June. Please refer to the attached document ‘GYB Steel Welding Issues’ for a list of the effected rails and the corresponding images."
| 02SL - Stations (LUL) | Cxxx-NCR-000586 | NCR | GYB - Level -1 - LCC (LEER Room) built without any design |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-05-18 | 2017-05-24 09:15 | 6 | 2016-06-15 16:29 | Architectural - Brickworks/Blockworks | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Following a review of programme requirements with regards to Lift 11 within the GYB and the Contract requirements within the Pan TfL contract with __ the Contractor is required to have the room prepared 1month prior to their start on site (Readiness Checklist). Lift 11 works are due to commence week commencing 15 August and thus the checklist items completed by week commencing 11 July. The MEP design for this floor is not fully coordinated and the blockwork elevations have not been produced to enable a structural check to be completed. With the time constraints in place the Contractor is progressing with the walling using current dimensioned model images for the builders work requirements. See attached.
| 02SL - Stations (LUL) | Cxxx-NCR-000587 | NCR | Chemical Fixings in Lieu of Mechanical Fixings |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-08-03 | 2016-07-14 12:56 | -20 | 2016-06-16 07:42 | Structural Engineering - Structural Engineering - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | The __ drawings for the windpost installation indicate use of HSC-IR fixings, these have not been used.
| 02SL - Stations (LUL) | Cxxx-NCR-000588 | NCR | Civils/MEP Co-ordination Of Works |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-07-29 | 2016-08-18 10:00 | 20 | 2016-06-16 14:27 | Mechanical - Mechanical Engineering General | 3000 |  | Planning | Rework | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | WTH Level -3, Pipework was installed where RC need to be built. Bars has been drilled awaiting further concrete work but the pipework installation went ahead before this. Works were not co-ordinated between MEP and Civils
| 02SL - Stations (LUL) | Cxxx-NCR-000589 | NCR | Coring of -1 slab GYB |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-07-14 | 2016-06-27 08:17 | -17 | 2016-06-16 14:31 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | -1 slab in Goslett Yard box was cored prior to the FCD submitted being approved. The void cored are 2 x 100mm x 800mm in size. Locations as shown in attached PDF
| 02SL - Stations (LUL) | Cxxx-NCR-000592 | NCR | PES structural steelwork specified traceability quality procedure and records not made available |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2016-12-19 | 2016-12-07 11:19 | -12 | 2016-06-21 09:50 | Structural Engineering - Structural Engineering - General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | The documentation provided by the Contractor regarding the PES structural steelwork on their own did not give confidence that the Contractor had implemented the requirements of specification clause KM10.1401. With reference BS EN 1090-2:2008+A1:2011 Table 1 for execution 2 structure it was expected to find, as a minimum a quality procedure in the form of a marked up tracking schedule which identified all the relevant items for the collation of statements of compliance and the results from specific inspections.
| 02SL - Stations (LUL) | Cxxx-NCR-000593 | NCR | Cube result below strength - W0217 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-08-31 | 2016-07-20 12:18 | -42 | 2016-06-20 09:05 | Structural Engineering - Concrete Member | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | The Contractor has determined a cube failure associated with the WTH capping beam/ +0 slab pour (GL 2-6/A)carried out on the 09/03/16. 28day cube results were: 35.3 and 36.7N/mm2, therefore below the 40N/mm2 characteristic strength.
| 02SL - Stations (LUL) | Cxxx-NCR-000594 | NCR | Fabrication & installation of PES structural steelwork undertaken without IFC drawings |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2016-08-29 | 2016-09-12 16:16 | 14 | 2016-06-21 09:51 | Structural Engineering - Structural Engineering - General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | With regards to the PES structural steelwork the black and white copies of a colour __ Progress & Performance Tracker together with a Truss Installation Westbound record were provided by the Contractor for post surveillance visit review. This demonstrated that the fabrication commenced before 18.07.15. However PM, acceptance was not obtained until 27.11.15 by which time according to the __ Progress & Performance Tracker documentation the PES structural steelwork was complete. This shows that the Contractor failed to meet the requirements of WIv2B part 7.7.8.2 i.e. to work from IFC drawings.
| 02SL - Stations (LUL) | Cxxx-NCR-000595 | NCR | PES structural steelwork delivery receipt inspect record did not provide clear evidence of conformance |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2016-10-22 | 2016-10-17 08:33 | -5 | 2016-06-21 09:52 | Structural Engineering - Structural Engineering - General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | The post surveillance document review for PES structural steelwork found the following: __ check sheet for; “3rd Call of PES” dated 12.08.15 was presented for this surveillance omitted detail of the Control Document which in this case would have been the relevant fabrication drawing numbers. In addition two of the check boxes, one for “Materials individual coding” and the other for “Dimensional checking against drawings” were blank. Due to the omissions the record does not provide clear evidence of conformance resulting in this NCR being raised
| 02SL - Stations (LUL) | Cxxx-NCR-000596 | NCR | PES structural steelwork NCR not in evidence for delivery rejected items |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2016-09-25 | 2016-09-14 13:33 | -11 | 2016-06-21 09:57 | Structural Engineering - Structural Engineering - General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | The post surveillance document review for PES structural steelwork found the following: With respect to the returned items documented on the __ check sheet ("3rd Call of PES" dated 12.08.15), the ITP (Cxxx-LAO-Y-ITP-N105_WS089_5_50006) under item 5.1 correctly identifies the necessity to close out all NCRs raised as a result of the inspection activity, no information was provided with respect to the non conformances recorded on the above check sheet with respect to the returned pallets with galvanizing damage. This NCR was raised to ensure re-verification to demonstrate conformity is documented to evidence the current status of the rejected items detailed on the above referenced __ check sheet.
| 02SL - Stations (LUL) | Cxxx-NCR-000597 | NCR | PES structural steelwork records to demonstrate personnel preforming inspection are competent not made available |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2016-08-31 | 2016-09-13 09:25 | 13 | 2016-06-21 09:57 | Structural Engineering - Structural Engineering - General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | As part of the PES structural steelwork surveillance, the requirements for ensuring the personnel performing inspection are competent and that their responsibilities are communicated to them were not demonstrated.
| 02SL - Stations (LUL) | Cxxx-NCR-000598 | NCR | PES structural steelwork supplier (__) Quality Management certification is not current |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2016-08-02 | 2016-08-01 15:58 | -1 | 2016-06-21 09:58 | Structural Engineering - Structural Engineering - General | 0 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Other | Completed |  | The Contractor provided a copy of __ ISO 9001 certification. This had an expiry date of 17.08.15, this is well before the installation works were complete.
| 02SL - Stations (LUL) | Cxxx-NCR-000599 | NCR | NSSS CE requirement for competent steelwork (for PES structural steelwork) contractor system acceptance not demonstrated |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2016-11-13 | 2016-12-06 10:54 | 23 | 2016-06-21 09:59 | Structural Engineering - Structural Engineering - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | The post surveillance document review for PES structural steelwork found the following: __ Ltd certification consisted of two parts, one for the Notifying Body ISOQAR required by CE Marking and the other for the quality management system issued by QMS. The QMS certification body is not accredited by UKAS. The requirement is that when there is no certification issued by a accredited certification body in place, it should be open to audit and approval by the Employer. As no audit reports or resulting approval were provided for this surveillance the potential exists that __ Ltd did not meet the requirement for a competent steelwork contractor.
| 02SL - Stations (LUL) | Cxxx-NCR-000600 | NCR | Incorrect Level GYB Level -4 (SR HVII) |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-06-25 | 2016-06-28 12:08 | 3 | 2016-06-24 15:29 | Architectural - Flooring | 500 |  | Supervision/Management | Reject | 4 (0.5-3k) | Complete | Personnel Error - Other human error | Completed |  | Incorrect levels were encountered to GYB Level -4 in the SR HV II room.
| 02SL - Stations (LUL) | Cxxx-NCR-000601 | NCR | WTH Capping beam upstand cast to the incorrect level - GL 3.5-4/E |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-12-16 | 2016-12-08 12:26 | -8 | 2016-06-21 15:18 | Structural Engineering - Concrete Member | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | A section of the capping beam upstand at +0 level has been cast 50mm too high. The area concerned is shown attached. The upstand should have been cast to 125.810, however was set at 125.860m.
| 02SL - Stations (LUL) | Cxxx-NCR-000602 | NCR | GYB Superstructure - No 28 day strength cubes for F22, F26 & F28 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-09-19 | 2016-07-21 08:45 | -60 | 2016-06-21 14:59 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | __ have informed me that the results for the 28 day concrete cube's manufactured for the GYB superstructure staircase (Flights F22, F26 & F28) are missing. __ have informed me that this is an administration error and will be raising an NCR that I have attached.
| 02SL - Stations (LUL) | Cxxx-NCR-000603 | NCR | WTH, Out of spec concrete used on site |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-01-08 | 2016-08-19 09:19 | -142 | 2016-06-22 10:55 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not trained for the work being performed | Completed |  | Concrete used for 1st lift of Secondary Wall 8 at level -3 WTH and CW2 at level -1 has been recorded out of specification. Concrete technician tested each wagon of MIX 1C, SCC and recorded 600 and 650 which are bellowed recommended range 660-750 however he made decision to use concrete. See attached pour history.
| 02SL - Stations (LUL) | Cxxx-NCR-000605 | NCR | Fabrication & installation of PES structural steelwork undertaken without IFC drawings |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-11-13 | 2017-11-02 12:01 | -11 | 2017-09-15 13:02 | Structural Engineering - Structural Engineering - General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Fabrication & installation of PES structural steelwork undertaken without IFC drawings
| 02SL - Stations (LUL) | Cxxx-NCR-000612 | NCR | Start of GFRC Ladder Frame Installation - PPC not signed |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-03-31 | 2017-03-13 13:03 | -18 | 2016-06-27 10:38 | Architectural - General | 5000 |  | Documentation and Records | Use As-Is | 3 (3-6k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | The Contractor has started installation of the ladder frame in the Westbound Platform without the respective PPC signed off. The Contractor (__) has held a meeting with the Project Manager (__) on the 27th June to demonstrate that all previous comments on the PPC form by the Project Manager have been addressed. It has been agreed that installation of the ladder frame can continue, including the __ fixings into the SCL. The Contractor will obtain the required signatures from his designers and then request the Project Manager to sign the PPC.
| 02SL - Stations (LUL) | Cxxx-NCR-000613 | NCR | Missing Couplers in Level +7 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-08-17 | 2016-07-19 10:49 | -29 | 2016-06-28 12:23 | Structural Engineering - Reinforcement | 5000 |  | Supervision/Management | Repair | 3 (3-6k) | Complete | Supervision - Insufficient supervision | Completed |  | B12 Couplers were missed in Level +7 over the stair core for the slab.
| 02SL - Stations (LUL) | Cxxx-NCR-000614 | NCR | OSD basement - concrete poured with no IRF |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-08-07 | 2016-07-20 14:18 | -18 | 2016-06-28 16:49 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Supervision - Supervisor does not have sufficient experience | Completed |  | On Monday 27/6/16 structural concrete to upstand beams at ground level was poured with no IRF raised to CRL/__ Field Engineer/Quality teams.
| 02SL - Stations (LUL) | Cxxx-NCR-000615 | NCR | OSD basement - GL2 wall cut/missing lacer bars |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-07-26 | 2016-07-19 15:30 | -7 | 2016-06-28 17:03 | Civil - Structural Engineering | 5000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Supervision - Insufficient supervision | Completed |  | The wall on gridline 2 linking to the beam on gridline A at ground level has horizontal lacer bars cut off/missing.
| 02SL - Stations (LUL) | Cxxx-NCR-000616 | NCR | OSD basement - incorrect coupler positioning in RW 2 buttress GL1-A |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-08-07 | 2016-08-17 15:58 | 10 | 2016-06-28 17:23 | Civil - Structural Engineering | 5000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Management Problem - Inadequate supervision | Completed |  | During a general check of the ground beam reinforcement along gridline A in the OSD basement, it was found that couplers for the 700x400 column near gridline A-1 have been positioned incorrectly such that 4no of the couplers are effectively missing from the column 'in plan' position.
| 02SL - Stations (LUL) | Cxxx-NCR-000617 | NCR | Additional Builderswork Holes proposed for WTH Level -4 North Box Suspended Slab |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-08-10 | 2016-08-19 08:24 | 9 | 2016-06-29 08:13 | Civil - Structural Engineering | 3000 |  | Design | Repair | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Following further MEP coordination, new revision drawings have been issued for Levels -4 and -4M in the WTH. The below list accounts for reasons leading to these additional requirements, and structural amendments site propose to carry out on site. The methodology for completing these works will be as for previous structural break out - coring followed by breaking using hand held breakers.
| 02SL - Stations (LUL) | Cxxx-NCR-000618 | NCR | Additional Core holes through Level -3 Slab for Recon Stone Installation |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-07-27 | 2016-08-18 07:50 | 22 | 2016-06-29 08:53 | Civil - Structural Engineering | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | The Level -3 slab has been constructed in the SW corner without any voids to facilitate installation of the Recon Stone underneath. It has been agreed that voids would be required for both installation and maintenance purposes. At the time of construction, setting out information was not available to allow these voids to be positioned within slab construction.
| 02SL - Stations (LUL) | Cxxx-NCR-000619 | NCR | WTH - Level -2 - Internal Blockwork & Concrete Walling Started without Design Assurance |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-01-13 | 2017-02-01 16:33 | 19 | 2016-06-29 09:31 | Architectural - Brickworks/Blockworks | 1000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | The Contractor is continuing with the internal partition walling (both Blockwork & Concrete) ahead of a fully assured design. A meeting was held between __ (__), __ (__) and CRL (__ & __) to outline the position of the design, the risks and plan to manage those risks and what works will be being progressed to what stage. The information and draft PPC was issued on email to all parties on the 13th June 2016.
| 02SL - Stations (LUL) | Cxxx-NCR-000620 | NCR | Installation of __ corner detail |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-06-20 | 2017-06-09 10:15 | -11 | 2016-06-30 09:19 | Architectural - Flooring | 5000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Incorrect installation of Yelfon to corner edge. Yelfon in some screed corners have curved, causing a void behind the __. There are seven areas which will require rectification and other areas have been identified as 'minor' which can be mitigated through the installation of the Vedafeu rope as per the screed perimeter edge detail.
| 02SL - Stations (LUL) | Cxxx-NCR-000621 | NCR | OSD basement - B18 to capping beam link bars missing |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-07-28 | 2016-08-17 15:48 | 20 | 2016-06-30 13:38 | Civil - Structural Engineering | 5000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | During an ongoing inspection by __ Senior engineer, it was discovered that tie reinforcement was missing from the preceeding capping beam B1 and B2 to the tie beam between GL2 and the capping beam (B18).
| 02SL - Stations (LUL) | Cxxx-NCR-000622 | NCR | GYB Level -5: Omission of Hydroduct |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-09-15 | 2016-07-21 16:23 | -56 | 2016-06-30 13:41 | Structural Engineering - Structural Engineering - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Due to services clearances at GYB Level -5, the PM instructed the Contractor under PMI-594 to omit the Hydroduct underslab drainage layer and topping slab. In doing so, the PM sought to reclassify the waterproofing performance level from Grade 3 to Grade 2. This is compliant with Crossrail CEDS (CR-STD-303), which states that the water resistance for 'base slabs to underground boxes in plant room areas' is required to be Grade B, ie. 'minor damp patches with no visible flow of water'. However it is not compliant with LU Standard S1064 Clause 3.6.1, in which all sub-surface structures are required to be designed and constructed to attain a performance level of Grade 3, as specified in Table 2 of BS 8102, ie.'no water penetration acceptable'. This NCR has been raised to provide justification for treating the space at GYB Level -5 as a Grade 3 environment even without the Hydroduct underslab drainage.
| 02SL - Stations (LUL) | Cxxx-NCR-000623 | NCR | OSD Basement - Excess Cover to Column C25 on GL 2-E |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-07-28 | 2016-07-15 14:41 | -13 | 2016-06-30 14:13 | Civil - Structural Engineering | 2000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | On setting out of the kicker for revised size of this column, it was discovered that the starter bars on the internal face had excess cover of approx. 125mm
| 02SL - Stations (LUL) | Cxxx-NCR-000624 | NCR | Delamination of Galve on Pipework WTH -5 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-07-29 | 2016-07-30 06:36 | 1 | 2016-07-01 07:14 | Mechanical - Mechanical Engineering General | 5000 |  | Manufacturing Defect | Rework | 3 (3-6k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | It has come to the Contractors attention that there are 2 sections of Galve hydrant pipe work where the galve delaminating following the grooving from the supplier. Note that the Contractor has had the onsite grooving methodology agreed and signed off, therefore the Contractor will remove, cut and re-groove these 2 sections and offer for sign off.
| 02SL - Stations (LUL) | Cxxx-NCR-000625 | NCR | Pre-cast stairs - MCR for __ Resin not approved |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-11-01 | 2016-10-24 21:38 | -8 | 2016-07-01 16:43 | Civil - Civil Engineering General | 10000 |  | Documentation and Records | Rework | 2 (6-60k) | Complete | Management Problem - Inadequate supervision | Completed |  | Further to FCD 661 the fixings connecting the pre cast stairs to the insitu landings changed from __ M16 FBN to __ v8.8 M16 threaded rod and __ HIT-HY-200a resin in order to combat progressive collapse. The MCR for __ HIT-HY-200a resin that was submitted in May 2015 was not approved due to an issue with the decal sheet, this meant was not picked up and reviewed by CRL. The resin has been used during the installation of the GYB superstructure stairs as well as the WTH Vent tower and substructure stairs.
| 02SL - Stations (LUL) | Cxxx-NCR-000626 | NCR | Additional __ within WTH vent shaft |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-08-01 | 2016-08-18 15:42 | 17 | 2016-07-04 07:58 | Civil - Structural Engineering | 5000 |  | Planning | Repair | 3 (3-6k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | Level -2: 2off 300mm x 300mm openings required within the header walls on GL 8. This was a design coordination error as they were not indicated on the BW drawings at the time of the pour. Level -1: Extend existing opening to accommodate 2 cable trays. On the original design these cable trays were intended to overlap and both fit through the opening. However this prevents maintenance access and as a result trays need to be installed side by side. Level +0: Continuation of cable trays from Level -1 need to extend through this level onto +0. For access purposes tray need to be installed side by side to facilitate access. Gully position has now changed at this level and 2 additional 200mm diameter will be required through the slab and wall (see attached drawing for location). Level +1: A __ was missed during construction of this level. Initially meant to be 260mm x 500mm however MEP have confirmed a 250mm diameter core hole will be enough to accommodate the 200mm dia pipe. Level +2 to +5: Drainage pipe opening does not align and pipework cannot be installed. Openings will need to be extended by 100mm. (Opening sizes typically 250mm x 500mm) Level +1 to +4: Existing 200mm x 200mm openings cannot accommodate vertical pipe stack from substructure. Propose to extend by up to 75mm to allow pipework maintain verticality. Level +6: 3off gully openings were missed during construction of this slab. 3 number 250mm core holes will be required to complete installation of MEP pipework.
| 02SL - Stations (LUL) | Cxxx-NCR-000627 | NCR | Lightning Protection WTH Roof Connection |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-09-30 | 2019-08-23 07:04 | -38 | 2016-07-04 14:07 | Electrical - General | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Management Problem - Inadequate supervision | Completed |  | The contractor has installed Lightning Protection connection at the WTH Vent Shaft roof level to the wrong cable CSA. The current design requirements as detailed in Cxxx-LAO-E-DDD-N105_Z-10501 are for two 95mm green yellow earth cables. The contractor has mistakenly installed two 70mm green yellow earth cables.
| 02SL - Stations (LUL) | Cxxx-NCR-000628 | NCR | Change of Material for PCC Stairs |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-10-10 | 2016-07-14 12:46 | -88 | 2016-07-04 15:20 | Structural Engineering - Structural Engineering - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | During the review of certification package for PCC stairs GYB, the material (Fisher Bolts) were found to be changed to __ bolts. Although overall MCR "Cxxx - Materials Compliance Record Precast Stair System - BISON (Cxxx-LAO-O4-XDS-N105_WS089_Z-50061)" was resubmitted and was Code 1 but the change was not formally captured by means of FCD. This change is applicable to sitewide precast stairs.
| 02SL - Stations (LUL) | Cxxx-NCR-000629 | NCR | Incorrect height of couplers for OSD in plinth in Block D |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-07-25 | 2017-03-15 16:45 | -132 | 2016-07-05 07:21 | Structural Engineering - Reinforcement | 1000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | The B32 couplers in the plinths of the Level +1 slab in Block D in WTH were installed at the wrong height (either lower or higher) - refer to the attached drawing.
| 02SL - Stations (LUL) | Cxxx-NCR-000630 | NCR | GYB L+1 and L+2 MEP without PPC |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2017-12-22 | 2017-12-19 16:27 | -3 | 2016-07-05 08:34 | Mechanical - Public Health Engineering | 1000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Elements of the MEP scope have been installed in GYB without an associated PPC as per the agreed prestart work procedure. There are pipes on L+1 and L+2 Vent tower phase 2 that were not included in the KD3 PPC.
| 02SL - Stations (LUL) | Cxxx-NCR-000631 | NCR | Fire Stopping Details Commenced Without PPC |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2017-05-28 | 2017-06-22 06:39 | 25 | 2016-07-05 08:47 | Fire - Compartmentation | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | The JP10.1205, k) 1:5 drawing for the top of concrete windpost fire stopping was not formally issued prior to commencement onsite. A PPC for these works is not in place as per the agreed prestart work procedure.
| 02SL - Stations (LUL) | Cxxx-NCR-000632 | NCR | OSD Basement - Column C10 Starter bars on GL 2-A |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-08-03 | 2016-08-15 14:47 | 12 | 2016-07-06 07:24 | Civil - Structural Engineering | 5000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | The preceeding B40 starter bars of the column C10 were sized for an 800x800 square column, however the column from ground level is 800x940. Therefore the external face of starter bars (chapel street side) are 140mm inbound of where they should be.
| 02SL - Stations (LUL) | Cxxx-NCR-000633 | NCR | OSD Basement - RW1 missing 1 bar at buttress between GL A and B |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-08-03 | 2016-07-20 11:30 | -14 | 2016-07-06 08:14 | Civil - Structural Engineering | 2000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | During a surveillance inspection it was found that a preceeding B40 female ended coupler bar was missing in the location shown in the attached marked up drawing. Attached are before and after photos showing how the snag was closed out.
| 02SL - Stations (LUL) | Cxxx-NCR-000634 | NCR | Access Panel Opening- WTH Level -5 North Box |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-09-04 | 2016-08-16 11:01 | -19 | 2016-07-06 15:21 | Architectural - Brickworks/Blockworks | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Access panel a2-6/002 should have been built to a structural opening of 685x685mm but was built to 710x710mm. Upon review of the as-builts some other openings have incorrect by 5mm or 10mm in singular direction.
| 02SL - Stations (LUL) | Cxxx-NCR-000635 | NCR | Pre-cast stairs in WTH Vent Tower 5mm wider |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-12-11 | 2016-11-28 15:48 | -13 | 2016-07-07 06:35 | Civil - Civil Engineering General | 1000 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | The precast stairs were delivered 5mm wider (within the BS tolerance). Trying to fit them through the landing slab openings there would be a risk of getting them damaged. Therefore I propose to scabble the landing slabs 10mm to get the stairs in and then repair them.
| 02SL - Stations (LUL) | Cxxx-NCR-000636 | NCR | Additional openings required on GYB -4 wall, elevation 9, 10 & 14 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-10-22 | 2016-10-11 13:51 | -11 | 2016-07-08 06:42 | Civil - Civil Engineering General | 2000 |  | Planning | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | 3 x openings have been missed from elevation 10 wall on -4 GYB.
| 02SL - Stations (LUL) | Cxxx-NCR-000637 | NCR | WTH Vent Tower - Door openings in Wall 8 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-09-20 | 2016-09-28 07:46 | 8 | 2016-07-11 13:55 | Civil - Civil Engineering General | 10000 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Supervision - Insufficient supervision | Completed |  | The opening in Wall 8 in the WTH Vent Tower has been cast out of position on levels 1, 2, 3 & 4. This means that the secondary walls, which have been cast correct, do not line in to the opening correctly. this has resulted in a step of between 20 and 25mm between the wall opening and the secondary walls.
| 02SL - Stations (LUL) | Cxxx-NCR-000639 | NCR | B12 couplers casted instead of B16 in +1 slab Block D |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-09-09 | 2016-08-04 15:22 | -36 | 2016-07-11 17:07 | Structural Engineering - Reinforcement | 5000 |  | Supervision/Management | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the construction of the Vent Tower wall B12 couplers were installed on the external slab rather than B16s which are specified in the design intent.
| 02SL - Stations (LUL) | Cxxx-NCR-000640 | NCR | GYB - Level -2 - Internal Blockwork Commenced without |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-11-05 | 2016-11-07 14:50 | 2 | 2016-07-14 16:16 | Architectural - Brickworks/Blockworks | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | The Contractor is progressing with Internal walling ahead of an assured design process sign-off
| 02SL - Stations (LUL) | Cxxx-NCR-000641 | NCR | CMS Installation GYB Level -1 behind Glass/Cladding |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-05-05 | 2017-04-28 08:08 | -7 | 2016-07-15 07:05 | Electrical - Cable Management | 5000 |  | Documentation and Records | Use As-Is | 3 (3-6k) | Complete | Management Problem - Inadequate supervision | Completed |  | The Contractor has commenced installation of CMS at GYB level -1 behind the glass prior to the PPC being signed off to support the programme. Co-ordination has been done with __/Cladding package manager
| 02SL - Stations (LUL) | Cxxx-NCR-000642 | NCR | MEP Services insallation within GYB HV swtich and Transformer rooms |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-08-12 | 2016-08-17 08:50 | 5 | 2016-07-15 07:09 | Mechanical - Mechanical Engineering General | 5000 |  | Documentation and Records | Use As-Is | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | To support the key room handover (MOSH/SLD) MEP services has been installed within the GYB HV transformer and switch rooms prior to the PPC official sign off. Note that co-ordination reviews have taken place and detailed drawings have been produced for these rooms showing dimensions and setting out. __ have reviewed and are signing off PPC prior to formal issue to CRL information.
| 02SL - Stations (LUL) | Cxxx-NCR-000643 | NCR | GYB - Level -4 - Incorrect Setting Out of Blockwork Walling - East Elevation |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-08-12 | 2016-08-16 10:40 | 4 | 2016-07-15 14:27 | Architectural - Brickworks/Blockworks | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Worker not trained for the work being performed | Completed |  | The blockwork walling along the East walling (as per attachment mark-up) was set out incorrectly. At the time the first lift of this walling was completed there were ongoing discussions around the access provision from access panels to doors. The setting out was not completed correctly and thus did not align to the cladding panels within the front face that are due to be removal for access.
| 02SL - Stations (LUL) | Cxxx-NCR-000644 | NCR | GYB Level -2 blockwork/ windposts out of position |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-08-13 | 2016-07-22 09:03 | -22 | 2016-07-16 09:07 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Previous Construction - Improper As Built | Completed |  | GYB level -2 blockwork and windposts are approximately 20mm out of position. This is due to the upstands being build out of position by the previous contractor.
| 02SL - Stations (LUL) | Cxxx-NCR-000645 | NCR | By Exception – GYB Escalator GFRC Cladding |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-04-28 | 2017-03-08 11:56 | -51 | 2016-07-18 06:19 | Architectural - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | The Contractor is proposing to commence manufacture/installation of the GFRC cladding system for Goslett Yard Box escalator decline, prior to Crossrail formal acceptance of the design at Assurance Gate 3. The design information was reviewed with Crossrail as per the above and documented in the report attached to this NCR [eB reference Cxxx-LAO-Z-MRC-N105_WS093-50144]. In order to maintain the Assurance process, this design must be finalised and aligned with the F1 design for Crossrail acceptance at Gate 3. Any fabrication drawings must be submitted for Crossrail acceptance.
| 02SL - Stations (LUL) | Cxxx-NCR-000646 | NCR | OSD basement - Insufficient cover to couplers in C11 for Wall-D |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-10-16 | 2016-10-20 10:57 | 4 | 2016-07-19 16:35 | Civil - Structural Engineering | 1000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | 1. 10mm cover to B20 couplers (bar mark 19) on south face of C11 for Wall-D at mezzanine level 2. 6no. B20 couplers (bar mark 19) not fixed
| 02SL - Stations (LUL) | Cxxx-NCR-000647 | NCR | WTH Level -5 - Standard Galvinized Ductwork Non Compliant Gasket Tape |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-08-17 | 2016-07-30 06:50 | -18 | 2016-07-20 09:27 | Mechanical - Heating Ventilation & Air Conditioning | 3000 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | The contractor wishes to inform the project manager of a non compliant installation of galvanized standard ductwork in WTH level -5. The there is approximately 40m of standard galvanized ductwork which has been installed using a gasket tape which was (MCR-001893) approved as F3 (minor use), the quantity which has been installed is greater than that of which is accepted for minor use, therefore the installation is non-compliant. The contract proposes rectifying this non-compliant installation by installing the galvanized standard ductwork using the F1 approved gasket tape which is being used for the installation of Flamesheild fire rated ductwork throughout the project. Please see attached mark up detailing the extent of the non compliant installation on Level -5 WTH.
| 02SL - Stations (LUL) | Cxxx-NCR-000648 | NCR | Additional Buildersworks Openings for WTH Vent Shaft |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-08-17 | 2016-08-18 15:45 | 1 | 2016-07-20 08:14 | Civil - Structural Engineering | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | MEP installation required additional coring through the WTH vent shaft in order to complete installation. Attached is a marked up set of drawings highlighting areas typically needing 150mm - 200mm diameter core holes. There are a number of larger opening requests, most notably through the +0 slab. 1200mm from the west capping beam is a proposed 700mm x 200mm slot connecting trays from the -1 level. This opening will replace the extended opening suggested in NCR-617 where a 1060mm x 730mm had been included on the east side of the vent shaft +0 slab. This opening will now remain as such and house 1 tray only.
| 02SL - Stations (LUL) | Cxxx-NCR-000649 | NCR | Riser 6 larger than opening in roof slab. |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-05-31 | 2017-05-10 14:55 | -21 | 2016-07-20 17:12 | Civil - Civil Engineering General | 10000 |  | Documentation and Records | Repair | 2 (6-60k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | Further to FCD 686 riser 6 (called riser 7 on FCD 686 as this was the original name) was built too large for the opening in the level +5 roof slab in GYB. The opening size was communicated to the Civils team when they constructed the roof and as-built information supplied to the MEP team, but this information was not correctly communicated to the team fabricating the riser off site. Opening size - 1520mm x 1150mm Riser size - 1760mm x 615mm
| 02SL - Stations (LUL) | Cxxx-NCR-000650 | NCR | Undersized opening for Riser 4 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-08-19 | 2016-08-18 08:02 | -1 | 2016-07-22 13:40 | Civil - Civil Engineering General | 10000 |  | Planning | Repair | 2 (6-60k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | The opening for riser 4 at level +3 is undersized for the module requirement
| 02SL - Stations (LUL) | Cxxx-NCR-000651 | NCR | WTH Vent Tower +1 Slab - Timber Chamfers |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-10-31 | 2016-09-23 13:54 | -38 | 2016-07-25 10:14 | Civil - Civil Engineering General | 5000 |  | Material | Repair | 3 (3-6k) | Complete | Management Problem - Inadequate supervision | Completed |  | Timber chamfers have been used on the +1 slab around the vent tower as opposed to the plastic ones as specified.
| 02SL - Stations (LUL) | Cxxx-NCR-000652 | NCR | WTH Vent Tower +1 slab internal cubes |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-10-31 | 2016-10-27 12:24 | -4 | 2016-07-25 10:54 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | Water was added to 3No loads of concrete for the +1 slab, date of pour was 24/05/2016, this was to bring the concrete back into spec and was done with the permission of s. No additional cubes where taken for the loads of concrete with additional water.
| 02SL - Stations (LUL) | Cxxx-NCR-000653 | NCR | PES pressure test proceeding without a Coded ITP available onsite |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2017-02-22 | 2016-12-23 09:49 | -61 | 2016-07-25 15:46 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Failure to follow status stamp | Completed |  | ITP ( Cxxx-LAO-Y-ITP-N105_WS089_5-50008) used on site was version 4 with no CRL acceptance code. document available on eB is Version 3 Code 1. Refer to CRL-OBS-11219 PES pressure test aborted due to inability to find leaks as smoke generating equipment non-functional. Method statement is silent on identifying leakage air paths using smoke generating equipment, and silent on remedial works to seal up plenum.
| 02SL - Stations (LUL) | Cxxx-NCR-000654 | NCR | WTH Vent Tower +1 slab corner chamfer |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-09-30 | 2016-09-30 09:02 | 0 | 2016-07-26 11:41 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The north west corner of the +1 slab around the vent tower has been cast without a corner chamfer. This is not compliant with the works information.
| 02SL - Stations (LUL) | Cxxx-NCR-000655 | NCR | Use of Link Studs using in Column 7A & 7B |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-02-15 | 2017-02-22 15:19 | 7 | 2016-07-26 12:38 | Structural Engineering - Reinforcement | 5000 |  | Design | Use As-Is | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Link Studs were installed in columns 7A & 7B based on the Link Stud Design without approval from Cxxx.
| 02SL - Stations (LUL) | Cxxx-NCR-000656 | NCR | Slump test in +1 slab out of tollerance |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-10-24 | 2016-08-01 14:28 | -84 | 2016-07-26 16:41 | Structural Engineering - Concrete Member | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Slump test on concrete for Level +1 slab identified to be out of spec - 250mm rather than 140-240mm which is the allowable range. This pour was on the 18th May 2016.
| 02SL - Stations (LUL) | Cxxx-NCR-000657 | NCR | Windpost out of position WTH Level -4 GL 10/A-B |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-09-20 | 2016-09-06 16:00 | -14 | 2016-08-23 10:49 | Civil - Structural Engineering | 2000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | On inspection for blockwork install, a windpost on Level -4 was found to be out of position. The windpost is marked up on the attached architectural floor finishes drawing. The windpost is 90m too far north in comparison to the blockwork wall alignment.
| 02SL - Stations (LUL) | Cxxx-NCR-000658 | NCR | WTH -2 escalator slab kicker cube failure |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-04-21 | 2016-10-04 11:01 | -199 | 2016-10-03 11:04 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | The strength of cubes W0239B and W0239C did not reach required 60N/mm2 in 28 days, see attached record sheet. Density of a cubes within required specification. However, __ used stronger SCC mix due to need of early striking of a shutter and appropriate compaction of sloping slab. In that case concrete meet required 40N/mm2 specified for slab (KF11 Appendix P.1.8. Concrete - ID.4) .
| 02SL - Stations (LUL) | Cxxx-NCR-000659 | NCR | Coring through main reinforcement in B21 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-10-25 | 2016-08-18 13:50 | -68 | 2016-07-27 17:47 | Structural Engineering - Reinforcement | 5000 |  | Supervision/Management | Repair | 3 (3-6k) | Complete | Management Problem - Inadequate supervision | Completed |  | The drilling contractor cored 50mm hole through B21 at 150mm from the soffit 500mm deep cutting through the second layer of B40 main reinforcement. The core drilled through 4No. Bars on the top half of each bar. The core was previously agreed with Cxxx to go through the middle of the beam where it will affect no reinforcement. The purpose of this core was to run a 50mm duct for MEP works.
| 02SL - Stations (LUL) | Cxxx-NCR-000660 | NCR | Daily Construction Report |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2016-08-25 | 2016-09-13 16:44 | 19 | 2016-07-28 08:53 | Civil - Civil Engineering General | 5000 |  | Documentation and Records | Use As-Is | 3 (3-6k) | Complete | Management Problem - Inadequate administrative control | Completed |  | The Project Manager is concerned with the quality of the current daily reports he is receiving. The reports are of very poor quality, lacking information and detail and require the immediate attention of the Contractor to ensure the current issues are corrected. The issues associated with the reports have been subject to a number of EWN's and subsequent follow on Risk Reduction meetings and the issues identified and discussed, have still not been addressed to date. The Contractor is requested to review the standard of the current reports and detail any applicable remedial actions required to ensure the reports are to a level of standard detailed within the Works Information. The Project Manager awaits the Contractors proposed action to rectify the issues identified, to enable closure of this NCR.
| 02SL - Stations (LUL) | Cxxx-NCR-000661 | NCR | WTH - Level -2 - 190mm blockwork wall built out of line and out of 140mm incorrectly |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-06-08 | 2017-05-19 14:05 | -20 | 2016-08-02 12:21 | Architectural - Brickworks/Blockworks | 2000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | The Contractor progressed with WTH Level -2 internal walls following on from initial design information from the Contractor's designer __. The end wall of the Core 2 stairs (West Face) was outlined as requiring to be built in 190mm blockwork. The first lift of blockwork was completed as 140mm and when correcting this to 190mm an error in setting out was highlighted that was present from the start. As per attached mark-up the dimension of 3.770m was set out to 3.882m from the wind post. This first lift of 190mm blockwork was removed and amended to the correct position as 190mm blockwork.
| 02SL - Stations (LUL) | Cxxx-NCR-000662 | NCR | Incorrect level of Builderswork hole |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-10-22 | 2016-10-20 11:03 | -2 | 2016-08-02 15:54 | Civil - Civil Engineering General | 2000 |  | Planning | Repair | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | The builders work void highlighted in the attached drawing has been cast to Rev 2. This has created a void that is approximately 600mm too low.
| 02SL - Stations (LUL) | Cxxx-NCR-000663 | NCR | WTH Capping beam waterproofing inspections |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-10-31 | 2016-09-14 10:53 | -47 | 2016-08-08 15:50 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | The waterproofing of the capping beam along Chapel Street and Diadem Court, alongside the vent tower has been undertaken with out Crossrail being invited to witness. The ITP states various witness points for the instillation of the waterproofing for which no invitation was sent. __ have taken numerous photos of the instillation of the waterproofing as well as this, a representative from GRACE has visited site during this section of works to check the instillation was correct. Note: eB wont let me upload attachments to provide details of the area not inspected. Contact myself for marked up drawing if required.
| 02SL - Stations (LUL) | Cxxx-NCR-000664 | NCR | Shrinkage Cracks in Slab Level +7 over stair-core |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-11-30 | 2016-09-02 09:16 | -89 | 2016-08-09 12:24 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Shrinkage cracks (max width 0.3mm) in the slab of Level +7 over the stair core (refer to the attached photo)
| 02SL - Stations (LUL) | Cxxx-NCR-000665 | NCR | WTH - Level -1 - LEER Room (LCC 2/135) Built without Approved Blockwork Design |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-06-08 | 2017-05-19 14:16 | -20 | 2016-08-10 14:19 | Architectural - Brickworks/Blockworks | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | In order to mitigate delays to the programme, in particular for the Lift sub-contractor __, and hand over the relevant areas on time the Contractor will be building the blockwork walling that forms the LEER Room to Lift 9 without approved blockwork design.
| 02SL - Stations (LUL) | Cxxx-NCR-000666 | NCR | WTH Vent Tower cubes crushed late |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-09-09 | 2016-08-16 11:47 | -24 | 2016-08-12 11:53 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | For the concrete pour in WTH Vent Tower on 9/6/16, the set of cubes taken where crushed at 29 days instead of the required 28 days. The mix was 3F which has a specified strength of 40N/mm2, the 2 cubes struck at 29 days had a average strength of 53N/mm2, this is well above the minimum strength required.
| 02SL - Stations (LUL) | Cxxx-NCR-000667 | NCR | Earthing From columns to Vent Tower Block D |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-03-15 | 2017-02-16 10:21 | -27 | 2016-08-12 13:30 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Earthing tape not installed across the first pour of the slab +1 in Block D from the columns to the vent tower in two locations (see attached).
| 02SL - Stations (LUL) | Cxxx-NCR-000668 | NCR | NCR - Change in opening sizes to elevations 17 and 18 GYB level -3 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-11-13 | 2016-12-01 15:22 | 18 | 2016-08-15 16:22 | Civil - Civil Engineering General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | Openings to elevation 17 and 18 level -3 were constructed to the correct drawings at the time of installation. However, since then the MEP design has changed and the size of the ducting units passing through the openings exceed the existing openings. Therefore, the contractor proposes to increase the sizes of the existing openings to suit. Elevation 17 - the contractor proposes to remove the wall to below the opening and rebuild with larger opening. Elevation 18 - the contractor proposes to core opening and make good to the correct opening size.
| 02SL - Stations (LUL) | Cxxx-NCR-000669 | NCR | additional core holes for recon stone install level -2 and -3 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-01-18 | 2017-01-24 15:44 | 6 | 2016-08-22 15:44 | Civil - Civil Engineering General | 2000 |  | Design | Repair | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Contractor has issued new builders work drawing for recon install which includes a additional core hole at level -3 adjacent GL 10. It is also necessary for an additional hole at -2 adj GL 8 as the core at -3 is not accessible or required.
| 02SL - Stations (LUL) | Cxxx-NCR-000670 | NCR | WTH Lift 8 Doorway out of position |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-09-20 | 2016-09-12 12:06 | -8 | 2016-08-23 08:49 | Civil - Civil Engineering General | 10000 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Supervision - Insufficient supervision | Completed |  | Following an as built survey of lift shaft 8, it was found that doorways across levels -4, -3 and -2 do not align. The doorway at Level -4 differs in comparison to the higher levels by 100mm.
| 02SL - Stations (LUL) | Cxxx-NCR-000671 | NCR | WTH - Level -1 - LCC Room for Lift 7 (2/133) - Blockwork being built ahead of Design Assurance sign-off |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-05-18 | 2017-05-19 14:19 | 1 | 2016-08-24 12:12 | Architectural - Brickworks/Blockworks | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | The Contractor is progressing with installing blockwork walling to form the LEER Room for Lift 7 (2/133) ahead of blockwork design assurance sign-off including structural checks. The Contractor needs to complete the blockwork to release the remaining MEP and finishing works to meet the programme dates for the Lift Sub-Contractor
| 02SL - Stations (LUL) | Cxxx-NCR-000673 | NCR | Precast Brick Panel potentially out of tolerance in manufacture |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-12-12 | 2016-11-16 12:59 | -26 | 2016-09-01 12:46 | Architectural - General | 500 |  | Manufacturing Defect | Reject | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The brick Precast panel to the corner of Dean Street and Diadem Court has been found to be 2mm outside the BS tolerances for manufacturing. Further inspections and surveys are being conducted to check compliance. if found to be outside the BS manufacture tolerances this panel will be remade.
| 02SL - Stations (LUL) | Cxxx-NCR-000674 | NCR | Implementation of PPC and Use of Unauthorised & Uncontrolled Drawings |  | Crossrail | PDP | TCR - Tottenham Court Road Station (West) |  | 2017-06-02 | 2017-06-23 16:10 | 21 | 2016-09-02 11:12 | Systems - Other | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | Further to EWN-00642 and the Risk Reduction Meetings held on 6-Jul-16 and 1-Sep-16 the Project Manager is concerned with the continued failure to comply with the controls set out within the Contractor's Permission to Progress Construction process, resulting in the release of uncontrolled and unauthorised drawings to eB and to site for construction. The following observations have been recorded as non-compliances with the PPC process: - A number of MEP packages have not been signed by CRL without agreement of relaxation to category C. - this is no longer an issue at all submissions badged as C have been reviewed by CRL as B categories. - Architectural Package tracker has not been uploaded to collaboration site weekly - this remains unaddressed. - PPC submissions have been uploaded to eB with incorrect stamps and without signature from __ Package Manager to evidence control of drawings - please provide evidence to demonstrate how this has been addressed. - Drawings associated with PPC submission have been uploaded to eB with incorrect stamps and without signature from __ Package Manager to evidence control of drawings - please provide evidence to demonstrate how this has been addressed. Please refer to the supporting files for additional information to assist in the resolution of this issue.
| 02SL - Stations (LUL) | Cxxx-NCR-000675 | NCR | OSD Mezzanine wall movement of fillet |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-12-18 | 2016-12-19 14:08 | 1 | 2016-11-11 13:52 | Civil - Civil Engineering General | 1000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Upon striking the shutter for the OSD mezzanine wall, it was noticed that the angle fillet moved during the pour. Refer attached photos
| 02SL - Stations (LUL) | Cxxx-NCR-000676 | NCR | Not Working to Con103 Specification |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-10-03 | 2016-09-28 10:00 | -5 | 2016-09-05 15:51 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Reject | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | Making good of joints to soffit without prior inspection from the project manager.
| 02SL - Stations (LUL) | Cxxx-NCR-000677 | NCR | Stainless Steel Welds to GFRC support frames: Corrosion prevention. |  | Crossrail | PDP | TCR - Tottenham Court Road Station (West) |  | 2016-10-28 | 2016-10-31 12:29 | 3 | 2016-09-02 15:32 | Architectural - General | 5000 |  | Manufacturing Defect | Use As-Is | 3 (3-6k) | Complete | Material/Preservation Problems - Other | Completed |  | Cxxx Architectural specs (Cxxx-ATK-N2-RSP-CR002-00001, Rev 11) requires “welded construction shall be finished to prevent corrosion. All welds shall be cleaned as necessary to ensure the durability…” NCR required to be raised because “welds are not finished to prevent corrosion” and “welds are not cleaned”
| 02SL - Stations (LUL) | Cxxx-NCR-000678 | NCR | Access Panels in Ductwork |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-06-30 | 2017-06-09 14:48 | -21 | 2016-09-06 10:38 | Mechanical - Heating Ventilation & Air Conditioning | 5000 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | The contractor wishes to inform the project manager that the current installation of ductwork in highly congested plant areas does not have access panels located on site. For maintenance practicality the contactor will be cutting some access panel in to ductwork in line with DW144 and the system access requirements at a later date when other MEP services are installed to ensure positioning of hatches are as practical as possible. The current ductwork installation ITP and method statement states that the access panels are to be cut prior to installation. The contractor will be updating the ITP and method statement in accordance with the points detailed above.
| 02SL - Stations (LUL) | Cxxx-NCR-000680 | NCR | GYB- Installed GRC Panels in Escalator Void |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-09-30 | 2019-08-20 09:38 | -41 | 2016-09-07 15:29 | Architectural - General | 500 |  | Manufacturing Defect | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | After installing the GRC cladding panels within escalator void area of GYB, it was noticed that about 15-20 panels have darker colour than the rest of panels.
| 02SL - Stations (LUL) | Cxxx-NCR-000681 | NCR | 3400 Installation of GFRC Cladding 'Tusks' Prior PPC Sign Off |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-04-14 | 2017-05-04 15:59 | 20 | 2016-09-08 12:45 | Architectural - Walls | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | The Contractor has proceeded to install the GFRC Cladding Type 4 tusks prior to PPC design approval. The PPC number is Cxxx-LAO-Z-MRC-N105_WS089-50232 which is currently with the Project Manager for review on the Collaboration site since 19th August 2016.
| 02SL - Stations (LUL) | Cxxx-NCR-000682 | NCR | CMS impending access |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2018-09-30 | 2018-10-10 09:38 | 10 | 2016-09-08 13:25 | Electrical - Cable Management | 1000 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | CMS has been installed, that is not synchronous with the agreed/modelled location and is currently impeding access and maintenance of the agreed general walkway
| 02SL - Stations (LUL) | Cxxx-NCR-000683 | NCR | Installed CMS route to facilitate the FOSC to FOSC fibre optic cable route |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-09-30 | 2017-06-02 12:35 | -120 | 2016-09-08 13:37 | Electrical - Cable Management | 5000 |  | Documentation and Records | Use As-Is | 3 (3-6k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | An additional CMS route has been installed to facilitate the FOSC to FOSC fibre optic cable route, as the originally installed route could not be utilised as it was not able to obtain the required bend radius of the installed cables. The New route was installed off a designers sketch and was retro fitted to the existing modular installation without following the agreed formal protocol of an FCD submittal, detailing the planned route deviation for review and acceptance prior to commencement of the amended CMS route
| 02SL - Stations (LUL) | Cxxx-NCR-000684 | NCR | CMS Trunking T sections |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2018-12-31 | 2019-01-07 15:06 | 7 | 2016-09-08 13:53 | Electrical - Cable Management | 3000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | Temporary CMS Trunking T sections have been fitted within the multi compartment trunking in lieu of delivery of the correct T sections.
| 02SL - Stations (LUL) | Cxxx-NCR-000685 | NCR | Pipework altered on as installed modules |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-01-31 | 2019-01-08 13:01 | -23 | 2016-09-08 14:16 | Mechanical - Piping | 1000 |  | Design | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Change in design has resulted in existing as installed pipework being altered on existing modules and not recorded on the FCD process.
| 02SL - Stations (LUL) | Cxxx-NCR-000686 | NCR | Installation of Trunking CMS routes not identified as a FCD. |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-11-30 | 2017-06-12 13:17 | -171 | 2016-09-08 14:31 | Electrical - Cable Management | 5000 |  | Design | Use As-Is | 3 (3-6k) | Complete | Management Problem - Inadequate supervision | Completed |  | Design changes has resulted in CMS routes being installed (trunkings) that are deviating away from the modelled route and not currently captured via the FCD/RLD process.
| 02SL - Stations (LUL) | Cxxx-NCR-000687 | NCR | CMS installation below head height limitations |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2018-09-30 | 2018-09-21 09:05 | -9 | 2016-09-08 14:47 | Electrical - Cable Management | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Linear runs of CMS currently being installed below agreed head height limitations.
| 02SL - Stations (LUL) | Cxxx-NCR-000689 | NCR | Change to pipework routes on the as installed modules |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-09-30 | 2018-09-05 17:18 | -390 | 2016-09-08 15:01 | Mechanical - Piping | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Change made to general pipework routes to under platform areas. This was witnessed within under platform areas Level -5, APE and APW.
| 02SL - Stations (LUL) | Cxxx-NCR-000691 | NCR | GYB - Level -5 - Blockwork Started Ahead of Design Assurance - Escalator Pit & Comms Risers (6/736 & 737) |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-05-28 | 2017-05-24 09:25 | -4 | 2016-09-13 10:11 | Architectural - Brickworks/Blockworks | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | In order to meet key contractual dates the blockwork walling at Level -5 around the escalator pit and the 2x Comms Riser (6/736 & 6/737) is been completed without approved design assurance in place. Both areas have been reviewed in the model and there is only one opening within the escalator pit and opening above the door for the Comms risers so are seen as low risk.
| 02SL - Stations (LUL) | Cxxx-NCR-000692 | NCR | Cavity Drain Installation in advance of approved PPC |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-05-25 | 2017-05-23 14:07 | -2 | 2016-09-13 09:13 | Civil - Civil Engineering General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | On review of Handover Certification for the WTH Cavity Drain Pack, it was observed that the Level -1 Public Health drawing (Cxxx-LAO-P-DWG-N105_WS089_2-50003) has not yet reached PPC status. All other Public Health drawings have been reviewed and approved under the PPC process, however Level -1 is a number of weeks from submission. The Level -1 cavity drainage was installed at risk in line with Preliminary Revision layout drawings.
| 02SL - Stations (LUL) | Cxxx-NCR-000693 | NCR | GYB - Level -1 Internal Blockwork/Concrete Walling started ahead of Assured Design |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-05-18 | 2017-05-24 09:27 | 6 | 2016-09-13 10:21 | Architectural - Brickworks/Blockworks | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | The blockwork/concrete internal walling on Level -1 is being built without a signed off assured design. The elevations have been built and are currently with the structural engineer for review. The Contractor is required to meet key dates as part of the SLD including key routes in this area. Elevations have been produced out of the co-ordinated PPC'd service information. Upon review the Contractor has deemed 3 walls to be too risky to build as blockwork due to the openings and therefore these are being completed as concrete. See mark-up for details.
| 02SL - Stations (LUL) | Cxxx-NCR-000694 | NCR | Installation of Luminares GYB Level -4 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-10-11 | 2016-09-13 17:34 | -28 | 2016-09-13 11:01 | Electrical - Lighting | 2500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | To fully supports the SLD/MOHS dates the Contractor has installed luminaires within the GYB level -4 HV rooms without an approved ITP. The Contractor has the light MCR approved along with a PPC coordinated/signed off layout.
| 02SL - Stations (LUL) | Cxxx-NCR-000695 | NCR | WTH Riser 3 Access blocked at level -1 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-12-12 | 2017-01-04 16:49 | 23 | 2016-09-13 11:20 | Mechanical - Mechanical Engineering General | 2000 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | There has been a welded SHS post onto the removable steel section that was required to strengthen the frame for the up-righting lift. (as per attached photo) The post will have to be cut to allow the bar to be removed and the section will be repaired in line with the agreed repair method.
| 02SL - Stations (LUL) | Cxxx-NCR-000696 | NCR | OSD Basement - bars missing from OSD +1 perimeter beams |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-10-13 | 2016-09-30 15:43 | -13 | 2016-09-15 13:45 | Civil - Civil Engineering General | 5000 |  | Incomplete Works | Repair | 3 (3-6k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | GL2 wall is missing 10no. L-bars that tie into the OSD +1 perimeter beam (BM31 in beam B2 and BM14 in beam B3, please refer to drawing no. Cxxx-LAO-C-DWG-N105_WS089_A-50063). As agreed with Cxxx, the missing L-bars will be drilled and fixed into the GL2 wall and the bottom layer of L-bars to beam B3 will be omitted (see attached sketch).
| 02SL - Stations (LUL) | Cxxx-NCR-000699 | NCR | __ pre cast records - Core 3 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-11-25 | 2016-10-05 15:07 | -51 | 2016-09-15 13:31 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | __ have incomplete records for the pre cast stairs installed in Core 3 WTH. We are currently missing the following information: F29 Cast 21/06/16 missing __ 28 day results F30 Cast 24/06/16 missing __ 28 day results F30 Cast 25/06/16 missing __ 28 day results and Hammer test F30 Cast 27/06/16 missing __ 28 day results Where __ results are missing, __ have provided us with there internal there internal cube records for the dates. These records will be placed in the Handover pack.
| 02SL - Stations (LUL) | Cxxx-NCR-000700 | NCR | CAT 2 checking for GRC Cladding System |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-03-31 | 2017-05-19 15:52 | 49 | 2016-09-16 10:05 | Architectural - General | 5000 |  | Design | Rework | 3 (3-6k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | Category 2 checking has been completed for the support structures for the GFRC cladding systems based on the __ design report and without reference to the TCR specific details. The certificates require update to reference the final details for TCR. the initial version of the certificate was unsuitable for assurance purposes and require rework to serve the purpose for which they were intended.
| 02SL - Stations (LUL) | Cxxx-NCR-000701 | NCR | Core 1 Pre Cast Stair Missing Cube Results |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-11-08 | 2016-10-14 10:45 | -25 | 2016-10-11 15:31 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | __ have incomplete records for the pre cast stairs installed in Core 1 WTH. We are currently missing the following information: F11 – Cast 9/5/16 – missing __ 28 day cube result & hammer test - __ internal cube taken only F13 – Cast 6/5/16 – missing __ 28 day cube result - __ internal cube taken only F18 – Cast 10/5/16 – missing __ 28 day cube result - __ internal cube taken only F19 – Cast 18/5/16 – missing __ 28 day cube result – no cube taken F20 – Cast 17/5/16 – missing __ 28 day cube result – no cube taken F21 – Cast 19/5/16 – missing hammer test result __ have provided their internal cube results for flights F11, F13 & F18 (attached), however there were no cubes taken for flights F19 & F21.
| 02SL - Stations (LUL) | Cxxx-NCR-000702 | NCR | WTH - Level -2 Riser 1 - Ductwork Access Hatch Clash with Module Frame |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-11-15 | 2016-12-07 17:14 | 22 | 2016-09-16 15:39 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The contractor wishes to inform the project manager of a NCR on WTH Riser 1. The cleaning access panel for the stair press ductwork currently clashes with the module frame and need to be relocated.
| 02SL - Stations (LUL) | Cxxx-NCR-000703 | NCR | Incorrect application of paint to WTH Level -4 North Box Room |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-10-17 | 2016-10-03 13:42 | -14 | 2016-09-19 15:38 | Architectural - Walls | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | A room in the WTH Level -4 north box has been painted instead of agreed FCD-423 which states a clear dustproofer shall be applied. The room is SR HV I, 5.685. marked up drawing Cxxx-LAO-A-DDD-N105_5-22017 is attached for reference.
| 02SL - Stations (LUL) | Cxxx-NCR-000706 | NCR | Fire door frame not insulated |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-12-18 | 2016-12-19 15:10 | 1 | 2016-09-19 16:35 | Architectural - Doors | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | __ fire doors in WTH north box level -4 have been placed in position without the frames filled with ceramic wool as specified on the manufacturers drawings. Door numbers are D2-5/004,D2-5/005,D2-5/006 and D2-5/007.
| 02SL - Stations (LUL) | Cxxx-NCR-000707 | NCR | TCR PES - Sealing of Smoke Extract air pathway |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-02-15 | 2016-12-23 09:57 | -54 | 2016-09-20 07:14 | Architectural - General | 25000 |  | Design | Rework | 2 (6-60k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | The Contractor raises this NCR to record that the PES Plenum air test carried out on site at TCR on 25-07-2016 failed to hold the required test pressure with reference to the current relevant technical sections of the WI, which requires the PES Plenum to be tested to air pressures of +/- 500pa. The air pressure test failed at a pressure of +130pa, approximately 25% of the required air pressure, due to excessive air leakage at the side corbel side of the plenum. The particular details of the air test and the mode of failure are covered in a separate document appended to Cxxx-EWN-00674.
| 02SL - Stations (LUL) | Cxxx-NCR-000708 | NCR | Under Platform Expansion Joints |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2019-01-31 | 2018-12-19 08:56 | -43 | 2016-09-20 08:42 | Electrical - Cable Management | 1000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | The Contractor has site manufactured expansion joints on the under platform multi compartment trunking, that has been installed to an unacceptable standard, which has multiple sharp edges and is at risk of damage to cable insulation, if cable installation was to commence prior to the units being replaced. The Contractor did procure a bespoke unit, but has made the decision to only utilise elements of it, which has resulted in the poor quality of the installation and is advised to replace them to an acceptable standard.
| 02SL - Stations (LUL) | Cxxx-NCR-000709 | NCR | additional Service cores required in -5 north Box |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-10-18 | 2016-11-09 13:34 | 22 | 2016-09-20 15:11 | Civil - Civil Engineering General | 1000 |  | Design | Repair | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | shear wall in -5 north box requires 5 no. holes as per attached at high level to receive trunking, cables. This information was not readily available at construction stage. We therefore propose coring through the wall to provide the required routes through the wall
| 02SL - Stations (LUL) | Cxxx-NCR-000710 | NCR | WTH Level -3 Installed CMS |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2018-05-01 | 2018-03-23 11:06 | -39 | 2016-09-21 10:51 | Electrical - General | 4000 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | CMS was installed within WTH Level -3 and then removed. The rework has been instigated by contractor to assist in reducing complexity of Fire rated ceiling
| 02SL - Stations (LUL) | Cxxx-NCR-000711 | NCR | WTH Capping Beam - Incorrect Waterproof Instillation |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-10-20 | 2016-10-27 11:19 | 7 | 2016-09-22 09:54 | Civil - Civil Engineering General | 2000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The capping beam on Dean Street grid line EE 7-9 and Diadem Court grid line 10 A-B, had issued picked up by GRACE during an inspection. The __ 300R was laid loose to the top of the capping beam, this would have happened when the capping beam was cast. We tried to bond the loose sections of __ 300R to the capping beam using LM, this didn't work so we had to cut off all the loose section of __ 300R off to expose the external face of the capping beam where it had bonded correctly. This allowed us to bring the __ 800PA over the __ 300R with a lap length of 150mm.
| 02SL - Stations (LUL) | Cxxx-NCR-000712 | NCR | Fire Hydrant Installation |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-09-14 | 2017-09-14 15:33 | 0 | 2016-09-22 13:56 | Mechanical - Mechanical Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other management problem | Completed |  | None of the ITP’s referenced contain the MCR for the landing valve / hydrant or any activity relating to a landing valve. CRL-MCR-003347 - JD Fire Valve is on eB awaiting CRL sign off. General pipe work installation ITP (doc ref Cxxx-LAO-O4-ITP-N105_WS089-50012) is been for installing the fire main system but no particular reference to landing valve has been made in ITP.
| 02SL - Stations (LUL) | Cxxx-NCR-000714 | NCR | GYB - Level -1 - WI System (Built By Others) 93mm out of position - Completing Remediation Works |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-11-08 | 2016-11-11 13:29 | 3 | 2016-09-29 12:10 | Architectural - Brickworks/Blockworks | 2000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Previous Construction - Interfacing issues | Completed |  | The Contractor raised EWN 580 outlining that the blockwork built by Others was out of tolerance by 93mm. Following meetings between the Contractor, Project Manager (__, __), LU and Others it has been agreed the wind post as part of the WI system built by Others can be cut back 100mm. The only compliance outlined as required is that the re-inforcement is not cut. The Contractor intends to cut back 100mm to enable 5-7mm worth of making good to the face of the blockwork/concrete/reinforcement in the face.
| 02SL - Stations (LUL) | Cxxx-NCR-000715 | NCR | GYB Substructure - Escalator support wall at level -4 height out of tolerance. |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-10-28 | 2016-10-12 15:45 | -16 | 2016-09-30 16:04 | Civil - Civil Engineering General | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The escalator support wall at level -4 was poured 14mm too high (103.923m ). This impedes the escalator installation and needs to be cut to the correct level (103.909m). __ (escalator contractor) have asked that we over cut the wall to 20mm so they have some flexibility with installation. This will not affect the reinforcement.
| 02SL - Stations (LUL) | Cxxx-NCR-000716 | NCR | Lighting Protection |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-09-30 | 2019-08-22 16:20 | -39 | 2016-10-04 07:23 | Electrical - General | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Management Problem - Inadequate supervision | Completed |  | the methodology deployed in linking the bars on the lower levels was not the same as the roof. This will require further works, these works will involve further exposure/break out of rebar (including works) that have now been covered and an alteration to the linkage of bars/clamps and cables
| 02SL - Stations (LUL) | Cxxx-NCR-000717 | NCR | Paint Spllater - FOSC 4 / Type 6a |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-05-30 | 2017-03-02 10:38 | -89 | 2016-10-05 09:13 | Architectural - General | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Contamination | Completed |  | protection has been removed and the stainless steel finish within FOSC 4 / Type 6a now has splattering’s of the anti – slip floor paint on the door.
| 02SL - Stations (LUL) | Cxxx-NCR-000718 | NCR | Inconsistent Black Recon Panels to -4 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-12-12 | 2017-02-03 09:53 | 53 | 2016-10-05 16:43 | Architectural - Walls | 0 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The contractor has installed black recon panels to -4 WTH. On close inspection the panels are a different shade to the surrounding panels. These panels are being investigated to the route cause, currently it is believed to be efflorescence. Further investigation is required to find the cause, on finding the route cause a remedial action can be applied if required or deemed necessary.
| 02SL - Stations (LUL) | Cxxx-NCR-000719 | NCR | GYB - Level -1 - Blockwork Walling Misalignment with Opening in Ground Floor Slab |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-05-31 | 2017-06-19 10:50 | 19 | 2016-10-05 17:40 | Architectural - Brickworks/Blockworks | 3000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Upon completing the blockwork at GYB Level -1 a discrepancy between the Architectural and Structural drawings has been identified. The walling surrounding the riser (FAN 2/916) behind door D3-2/009 does not align with the opening within the ground floor slab (see attached Mark-Up). The architectural drawing (Cxxx-LAO-A-DDD-N105_2-32007) sets out this wall from Gridline 3 as 4290mm. The structural drawing (ATK-N105-8742-STR-D-GAR-0-31600)shows the edge of the opening above set out at 4421mm from Gridline 3. See attached image showing this gap.
| 02SL - Stations (LUL) | Cxxx-NCR-000720 | NCR | Pier Damages WTH Level -3 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-01-25 | 2016-12-07 17:32 | -49 | 2016-10-10 09:22 | Civil - Civil Engineering General | 2000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Blockwork Pier Damaged/Struck (Corridor WTH -3) adjacent to the CER
| 02SL - Stations (LUL) | Cxxx-NCR-000722 | NCR | Water damage to screed WTH Level -4 northbox |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-03-15 | 2017-01-27 14:26 | -47 | 2016-10-26 10:44 | Architectural - Flooring | 5000 |  | Damaged | Repair | 3 (3-6k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | The Contractor has experienced water leaks within the WTH structure causing water damage to WTH Level -4 northbox screed. Water damage to the screed occurred via the void on WTH Level -3 northbox causing water to pool on top of the protection and penetrate into the screed.
| 02SL - Stations (LUL) | Cxxx-NCR-000723 | NCR | Damage to Finished MEP Works WTH -1 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-10-29 | 2017-06-02 12:31 | -149 | 2016-10-11 08:19 | Electrical - General | 5000 |  | Damaged | Use As-Is | 3 (3-6k) | Complete | Supervision - Insufficient supervision | Completed |  | Damage to Finished MEP Works WTH -1
| 02SL - Stations (LUL) | Cxxx-NCR-000724 | NCR | Level +0 Missing Couplers in column for mezzanine beam |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-12-06 | 2016-11-15 13:15 | -21 | 2016-10-11 13:53 | Civil - Civil Engineering General | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Couplers not installed in Column C21 to pick up beam.
| 02SL - Stations (LUL) | Cxxx-NCR-000725 | NCR | Ductwork Co-ordination |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-05-28 | 2017-06-09 14:42 | 12 | 2016-10-11 15:00 | Mechanical - Mechanical Engineering General | 7500 |  | Design | Rework | 2 (6-60k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Ductwork access hatches will need to be moved (rework) in GYB level -3 due to later installed CMS that obstructs them. Installed services are un-coordinated. Access hatches not shown on drawings at GYB level -2. Ductwork fitter does not want to fit access hatches before all the services are installed beneath due to ongoing services co-ordination issues and risk subsequent rework in lieu of a co-ordinated design / install
| 02SL - Stations (LUL) | Cxxx-NCR-000726 | NCR | Level -5 WTH - Escalator Pit Ductwork & Wall Seperation |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-02-28 | 2017-03-02 16:19 | 2 | 2016-10-11 15:45 | Mechanical - Heating Ventilation & Air Conditioning | 1000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | The contractor wishes to advise the project manager of a clash in level -5 WTH with the installed fire rated ductwork passing through the escalator pit. At present the ductwork passing through the area (see attached) limits the space available to build a conventional concrete wall. I have attached attached a detailed drawing of the wall as well as a layout marking up the location in question.
| 02SL - Stations (LUL) | Cxxx-NCR-000727 | NCR | GYB Substructure - Poor compaction of the Escalator slab concrete. |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-11-08 | 2016-10-24 12:05 | -15 | 2016-10-11 16:17 | Civil - Civil Engineering General | 3000 |  | Material | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In small areas of the escalator extension poor compaction has led to quilting or large voids on the top surface. These areas will be scabbled back to sound concrete and made good using Monomix HD as per a discussion with J Plant.
| 02SL - Stations (LUL) | Cxxx-NCR-000728 | NCR | Access hatches not accessible due to obstructions from other services. |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-05-28 | 2017-06-08 09:08 | 11 | 2016-10-13 16:11 | Mechanical - Heating Ventilation & Air Conditioning | 5000 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Hatch provisions not co-ordinated with other services within the 3D model.
| 02SL - Stations (LUL) | Cxxx-NCR-000729 | NCR | Installation of Bent Drop Rods |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-12-11 | 2016-11-09 09:00 | -32 | 2016-10-13 17:02 | Electrical - Cable Management | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | CMS installation supported by bent drop rods
| 02SL - Stations (LUL) | Cxxx-NCR-000730 | NCR | GL C/3 Truss Column & +1 Soffit Damage |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-07-30 | 2017-07-10 12:16 | -20 | 2016-10-18 09:55 | Civil - Civil Engineering General | 10000 |  | Workmanship | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Other | Completed |  | On striking of the WTH Block C +1 soffit falsework, it has become apparent that concrete from a section of the beam soffit around the truss column (GL C / 3) has spalled away (see attached Photo 1). Following a number of inspections and surveys, it has been determined that the +1 slab over the truss column has risen by around 15mm which would have occurred from the stressing process of the post tensioning (see attached Photo 2). It can be seen that the vertical threaded bars have been pulled out of the couplers which are welded to the truss column capping plate. The threaded bars have remained bonded with the cast concrete of the +1 slab/beams. It is therefore presumed that there is a 15mm void across the top of the truss column capping plate.
| 02SL - Stations (LUL) | Cxxx-NCR-000731 | NCR | Working outside of the PPC process |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-05-31 | 2017-03-13 17:07 | -79 | 2016-10-18 15:55 | Electrical - Cable Management | 5000 |  | Documentation and Records | Use As-Is | 3 (3-6k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | The drawings listed have been reviewed internally and have been issued for the formal PPC process (signed off by __ & __). To support SLD delivery we have progressed with the installation prior to CRL sign off which is due imminently. Cxxx-LAO-N-DWG-N105_WS093_2-50011 P01 Cxxx-LAO-N-DWG-N105_WS093_2-50012 P01 Cxxx-LAO-N-DWG-N105_WS093_3-50006 P01 Cxxx-LAO-E-DWG-N105_WS093_4-50008 P02
| 02SL - Stations (LUL) | Cxxx-NCR-000732 | NCR | Proceeding without a singed of PPC - WTH Level -2 ESR1 Room Services installation |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-11-16 | 2016-11-29 15:09 | 13 | 2016-10-19 07:36 | Electrical - Cable Management | 5000 |  | Documentation and Records | Rework | 3 (3-6k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | To support the SLD dates (10th Nov 16) the Contractor has progressed within installation of services within WTH Level -2 ESR1 (Room ref 3/675) drawing ref Cxxx-LAO-E-DWG-N105_WS089_3-50012 Rev P02. Both the Contractor and the Contractors designer has signed the PPC off and have deemed minimal risk in proceeding within this area. This PPC is currently sitting with CRL for formal sign off and approval
| 02SL - Stations (LUL) | Cxxx-NCR-000733 | NCR | service hole required in structure for OHLE services WTH -4 North box |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-01-05 | 2016-11-09 13:38 | -57 | 2016-10-19 11:35 | Civil - Civil Engineering General | 1000 |  | Design | Repair | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | A service route is required from trackside to the OHLE room in WTH -4 North Box. This requires a 550mm x550mm hole through 500mm thick shear wall (location attached).
| 02SL - Stations (LUL) | Cxxx-NCR-000734 | NCR | 3400 GFRC Cladding Manufacture and Installation Prior PPC & Gate III Certificate Sign Off |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2018-04-27 | 2018-04-27 10:43 | 0 | 2016-10-19 12:41 | Architectural - Walls | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The Contractor has proceeded with manufacture and installation of various areas of the 3400 GFRC Cladding in the Platforms and Tunnels out of sequence with the agreed review and approval process (i.e. out of the sequence with the Gate III and PPC processes).
| 02SL - Stations (LUL) | Cxxx-NCR-000735 | NCR | core holes for containment through slab in ESR3-5/679 and LBS 5/678 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-11-16 | 2016-11-09 13:36 | -7 | 2016-10-19 12:47 | Civil - Civil Engineering General | 1000 |  | Design | Repair | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | A service containment route is required from -4 to -5 WTH in rooms ESR3 -5/679 and LBS 5/678. To enable this we require to core 2 no. 250mm diameter holes through the -4 slab (700mm thick) in the locations as attached.
| 02SL - Stations (LUL) | Cxxx-NCR-000736 | NCR | Proceeding with installation of Conduit in PTW without accepted PPC |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-01-25 | 2016-12-07 17:27 | -49 | 2016-10-20 17:06 | Electrical - Electrical Engineering General | 2000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | In the area of PTW between AP2W and AP3W, the Contractor has progressed with the installation of the horizontal conduit prior to the acceptance of the relevant PPC (Number Cxxx-LAO-Z7-GMS-N105_WS089_Z-50012). The conduit installation was required prior to the installation of the cladding panels hence the need to progress these works ahead of the PPC being accepted. The Contractor had presented a benchmark for the installation which had been signed off by the Project Manager (see attached form) which is due to be uploaded onto the eB.
| 02SL - Stations (LUL) | Cxxx-NCR-000737 | NCR | Sub standard Square Washers to be replaced with approved unistrut type |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-03-26 | 2017-01-31 13:43 | -54 | 2016-10-21 08:01 | Electrical - General | 2000 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | On the inspection of module installation in WTH-3 it was noted that the square plate washers used are not substantial and are starting to buckle. Inspection also highlighted the issue with the square washers ( possibly buckling under load) and the visible differences in metal gauges, between the __ washers
| 02SL - Stations (LUL) | Cxxx-NCR-000738 | NCR | Installation of Electrical Wiring for Lighting |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-03-26 | 2017-02-01 09:24 | -53 | 2016-10-21 08:35 | Electrical - Lighting | 3000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Lighting Installation within the GYB -4 around the vicinity of the Cxxx HV Rooms works are covered under Cxxx-LAO-04-ITP-N105_WS089_Z-50063 (Rev 2), which is currently Code 3
| 02SL - Stations (LUL) | Cxxx-NCR-000739 | NCR | Galvanised Pipework Site Installed without MCR Approval |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-02-03 | 2016-12-23 10:53 | -42 | 2016-11-02 13:48 | Mechanical - Piping | 50000 |  | Material | Use As-Is | 2 (6-60k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Galvanised Pipework installed on site without MCR Approval
| 02SL - Stations (LUL) | Cxxx-NCR-000740 | NCR | On Site Use of PPC darwing without signature |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-11-30 | 2016-11-29 09:47 | -1 | 2016-10-26 09:25 | Mechanical - Mechanical Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Supervision - Supervisor does not have access to all pertinent information | Completed |  | During a site walk, it was identified that drawings under PPC Cxxx-LAO-Z-MRC-N105_WS093-50164 were used on site without signatures
| 02SL - Stations (LUL) | Cxxx-NCR-000741 | NCR | WTH __ Shear Bolt instillation |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-02-15 | 2017-02-22 14:44 | 7 | 2016-10-26 12:05 | Civil - Civil Engineering General | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Whilst installing the __ bolts in to the +1 slab, block D, we have had a large chunks of concrete break out of the soffit of the slab. This has happened when drilling through the concrete from the top of the slab to allow for the bolts to be inserted. We had some localized sprawling on the previous holes drilled, as expected, but on this occasion, we had it over a larger area.
| 02SL - Stations (LUL) | Cxxx-NCR-000743 | NCR | PES CMS installed with springs removed from spring nuts |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-02-28 | 2017-03-03 11:43 | 3 | 2016-10-27 12:47 | Electrical - Cable Management | 2000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | During an inspection of the CMS on the PES, the Contractor noted that sections of the CMS, tray and unistrut had been installed with the springs missing from the spring nuts. It was apparent they had been removed from the nuts prior to being placed (as opposed to coming off when torqued). The attached fixing schedule shows the correct parts (FX34 and FX35) and the drawing shows the location they were used. NOTE: CMS details accepted by the Project Manager on Fabrication Drawings Certificate Cxxx-LAO-X-CER-N105_WS089-50013 and Gate Impact Report Cxxx-LAO-C-RGN-N105_WS089_Z-50019
| 02SL - Stations (LUL) | Cxxx-NCR-000744 | NCR | Painting to GYB Props |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-03-31 | 2017-01-31 16:44 | -59 | 2016-10-31 14:40 | Architectural - General | 500 |  | Incomplete Works | Reject | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | The contractor has not completed the painting to GYB props. To comply with architectural requirements, contractor has to carryout the remainder of painting. This rework involves scaffolding installation, which may cause a disruption to other works in that area, therefore the contractor has to show also the required mitigation measures in the programme.
| 02SL - Stations (LUL) | Cxxx-NCR-000745 | NCR | __ Cabinet Installation |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-06-25 | 2017-07-19 13:11 | 24 | 2016-11-01 17:53 | Fire - Compartmentation | 1000 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | The contractor invited the Project Manager to inspect a benchmark that was constructed, the Project Manager did not attend this benchmark but the Contractor has chosen to move forward with the works. This is to allow the Contractor to maintain the programme and to ensure the works are completed inline with a critical date which is 10th November 2016.
| 02SL - Stations (LUL) | Cxxx-NCR-000746 | NCR | __ Cabinet - AP8 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-01-23 | 2017-01-10 14:03 | -13 | 2016-11-01 20:24 | Fire - Compartmentation | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | The Contractor will proceed to set-out and construct 1No. __ Cabinet located in AP8 even though no PPC has been signed. This is due to time constraints and the need to complete these works before 10th November.
| 02SL - Stations (LUL) | Cxxx-NCR-000747 | NCR | GYB - Level -5 - Blockwork Walling Started Ahead of Design Assurance |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-05-28 | 2017-05-24 09:33 | -4 | 2016-11-03 16:26 | Architectural - Brickworks/Blockworks | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | The Contractor has co-ordinated the MEP and produced Blockwork elevations. Upon review there are a number of walls with minimal openings within walls that have a low floor to soffit height that are low risk to progress with ahead of the structural check.
| 02SL - Stations (LUL) | Cxxx-NCR-000748 | NCR | Modified Ductwork Installation installed from site sketches |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-01-25 | 2017-01-30 14:03 | 5 | 2016-11-04 18:36 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Ductwork sub-contractor installing / modifying ductwork from site sketches. No PPC drawing on site.
| 02SL - Stations (LUL) | Cxxx-NCR-000749 | NCR | Lift 9 missed inspection. |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-12-06 | 2016-11-21 14:47 | -15 | 2016-11-08 10:53 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | On the 4/11/2016, an issue was raised during inspection of Lift 9 prior to pouring concrete. It was due to the application of bituthene (blackjack) on a wet surface caused by rain. The activity was suspended an no concrete was poured On 5/11/2016 __ carried out works to dry out the surface and once dry, applied bituthene to the concrete surface. On 7/11/2016 __ poured the concrete for the bottom of Lift 9 assuming that the actions carried on 5/11/2016 had been sufficient to pour. This occurred without a CRL re-inspection
| 02SL - Stations (LUL) | Cxxx-NCR-000750 | NCR | Level +1 PT Slab - rebar in cover zone soffit |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-12-18 | 2016-12-14 15:11 | -4 | 2016-11-09 15:39 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Upon striking the falsework for Level +1 PT Slab, it was noticed that a reinforcement bar is in the cover zone and slightly exposed through the concrete. Refer attached photo. It is believed that this is an isolated piece of rebar which has fallen onto the deck
| 02SL - Stations (LUL) | Cxxx-NCR-000753 | NCR | GYB Substructure - Increase in height of lift 10 doorway Level -3 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-12-22 | 2017-01-27 16:51 | 36 | 2016-11-10 09:40 | Civil - Civil Engineering General | 5000 |  | Design | Repair | 3 (3-6k) | Complete | Personnel Error - Not Defined | Completed |  | The height of doorway to lift 10 level -3 was cast as per drawing Cxxx-LAO-M1-DWG-N105_WS093_Z-50004. However, it did not account for the FFL in room 4/763 which was 75mm higher than the L&E engineer anticipated , who incorrectly informed the site team of the setting out. The doorway clear opening must be 1800mm from FFL, due to the error the existing clear opening is 1725mm. The bottom of the doorway needs to be filled in to match the new FFL level.
| 02SL - Stations (LUL) | Cxxx-NCR-000754 | NCR | WTH - Level -1 - SLD Rooms (FCR 2/762 & MCC 2/764) Blockwork Works Started Ahead of Design Assurance |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-02-08 | 2016-11-30 10:56 | -70 | 2016-11-10 14:16 | Architectural - Brickworks/Blockworks | 500 |  | Documentation and Records | Reject | 4 (0.5-3k) | Complete | Procedure Problem - Lack of procedure | Completed |  | In order to achieve SLD dates for the aforementioned rooms for December the Contractor intends to progress blockwork walling (as per mark-up) at WTH Level -1 ahead of a completed design assurance process. The Contractor has co-ordinated builders work holes on the attached elevations to align with the services.
| 02SL - Stations (LUL) | Cxxx-NCR-000755 | NCR | __ GYB Blast Check Evidence - 3400 GFRC Cladding |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-03-30 | 2017-02-23 09:16 | -35 | 2016-11-11 09:55 | Architectural - Walls | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Independent verifying evidence for the Goslett Yard Box escalator decline GFRC / GRC Cladding blast design has not yet been provided to the Contractor by their GFRC Cladding Designer and Supplier. As such, the Contractor is unable to provide the evidence to the Project Manager to confirm the cladding compliance with blast requirements.
| 02SL - Stations (LUL) | Cxxx-NCR-000756 | NCR | GYB Substructure - Level -1 Hole required for dry riser pipe |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-12-09 | 2016-11-21 13:23 | -18 | 2016-11-11 14:06 | Civil - Civil Engineering General | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The previous contractor built the wall at level -1 with out allowing for the dry riser (150mm) to penetrate through it. Therefore the current contractor needs to core through this wall to allow for the dry riser to be connected to Riser 4.
| 02SL - Stations (LUL) | Cxxx-NCR-000757 | NCR | Fire Alarm CMS Installation not installed to meet cable bending radius requirements |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-02-03 | 2017-01-31 13:30 | -3 | 2016-11-11 15:59 | Electrical - Cable Management | 2000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Fire alarm CMS in the HV switch rooms in the WTH North box -4 area has been installed such that it is not possible to achieve the minimum bending radius of the fire alarm cable.
| 02SL - Stations (LUL) | Cxxx-NCR-000758 | NCR | Block D External PPC Brickwork - Bow and Joint Alignment |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-06-30 | 2017-06-30 08:33 | 0 | 2016-11-14 11:56 | Architectural - General | 5000 |  | Design | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | The installation of the PPC Brickwork panels has been discussed and reviewed on site with CRL. The contractor has been using British Standard for the manufacture and installation as discussed at Tender report reviews. The British Standard is BS 8297:2000 the key table for the tolerances is Table 11 on page 26 (attached). It is the CRL believe that we have worked outside these tolerances, we can conduct site survey of the areas of concern and have found the bow to be within the tolerances stated within the BS of 12mm. The joints that have been stated as outside the required tolerance have been sight measured and found to be 27mm, which is acceptable, as 1 panel is 8mm small and the other being 3mm small resulting in the joint being oversized but within tolerance.
| 02SL - Stations (LUL) | Cxxx-NCR-000761 | NCR | WTH Level -5 Fibre Pull with out IRF |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-05-22 | 2017-05-10 16:10 | -12 | 2016-11-16 09:49 | Communications and Control Systems | 2000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | The Contractor has installed fiber cable within riser 3 WTH which has been signed of by CRL however have extended to FOSC 1 at level -5 which the IRF for the CMS has not been signed off.
| 02SL - Stations (LUL) | Cxxx-NCR-000762 | NCR | Cable retiaing clip installation within riser |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-09-30 | 2020-07-24 14:18 | 298 | 2016-11-16 09:56 | Communications and Control Systems | 5000 |  | Incomplete Works | Repair | 3 (3-6k) | Complete | Management Problem - Inadequate supervision | Completed |  | The Contractor has pulled Fiber cables within vertical trunking without the use of retaining clips, note that the cables pulled are protected, and have slack for future installation of clips.
| 02SL - Stations (LUL) | Cxxx-NCR-000763 | NCR | GYB Substructure - opening in DC cabinet roof level -2 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-12-14 | 2016-11-25 11:13 | -19 | 2016-11-16 12:28 | Civil - Civil Engineering General | 1000 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | A new opening is required at level -2 on the DC cabinet roof as the design has changed since the roof was cast. The opening is to be 400 x 400mm in the location stated on the attached drawing. The opening will be centrailsed around the stated setting out as much as practicable. The reinforcement detail is also attached.
| 02SL - Stations (LUL) | Cxxx-NCR-000764 | NCR | __working outside of the ITP process |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-03-31 | 2017-03-13 12:53 | -18 | 2016-11-16 14:37 | Fire - Detection | 2000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | __have pulled in fire alarm cables in the WTH -3 CER prior to final IRF sign off of the CMS by __ and sign off of the ITP which was at code 2 to allow install in the Cxxx rooms only.
| 02SL - Stations (LUL) | Cxxx-NCR-000765 | NCR | __ installing Dampers at WTH Level -2 using a blown up section of a drawing which had no PPC stamp and contained no drawing traceability |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2017-03-17 | 2017-03-21 09:16 | 4 | 2016-11-16 13:30 | Mechanical - Mechanical Engineering General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | A planned Crossrail surveillance was undertaken on 14th November 2016 to look at __’s adherence to their Proposal to Progress Construction (PPC) Works at Risk – Procedure Cxxx-LAO-O7-GPD-N105_WS089-50001. Five activities in progress were inspected during the site visit where the drawings were checked and traced back to the relevant PPC form. One of the activities witnessed was the installation of dampers at WTH Level -2 being undertaken by __. The operatives were requested to provide the drawing(s) they were using to install to enable a check for the PPC stamp. The detail that was presented was a blown up section of a drawing (see photo). The blown up section had no PPC stamp on, and no drawing attached with the section to enable traceability. As a result, traceability to the PPC could not be undertaken. The PPC procedure states “All drawings associated with the PPC will be stamped and signed by the __ Package Manager to provide traceability back to the PPC”. As a result of the PPC procedural failings for Damper installation this NCR was raised resulting from the surveillance.
| 02SL - Stations (LUL) | Cxxx-NCR-000766 | NCR | GFRC cladding was being installed, and drawings had been PPC stamped and signed without an accepted PPC form in place. |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2017-05-30 | 2017-05-25 10:37 | -5 | 2016-11-16 13:39 | Archaeology - General | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Procedure Problem - Not Defined | Completed |  | A planned Crossrail surveillance was undertaken on 14th November 2016 to look at __’s adherence to their Proposal to Progress Construction (PPC) Works at Risk – Procedure Cxxx-LAO-O7-GPD-N105_WS089-50001. Five activities in progress were inspected during the site visit where the drawings were checked and traced back to the relevant PPC form. One of the activities witnessed was the installation of GFRC cladding being undertaken by __ at Platform Level (EB and WB). Seven drawings were fixed to the timber hoarding relating to cladding steelwork and setting out. Each of the drawings contained a PPC stamp which had been signed and contained at least one PPC number reference (see attached photos). The two PPC numbers referenced on the drawings were Cxxx-LAO-Z-MRC-N105_WS089-50245 and 50229. On checking the PPC numbers back in the office, it was identified that both were Placeholders on eB. In addition, upon checking the collaboration site it was identified that both PPC submissions had not bee accepted by Crossrail, with only __ and __ signatures contained. As a result of this, the drawings referenced in the PPC had yet to be submitted onto eB. The fact that the drawings had been stamped and signed and were available on site demonstrates a breakdown of the PPC procedural requirements as the procedure process flow clearly states that drawings will only be stamped following PPC sign off and issue to eB. Based on this, __ have been installing GFRC cladding without acceptance to do so based on __’s PPC procedure, and drawings are being stamped and signed without any adherence to the procedure. In addition to the above, sketches concerning cable and conduit installation behind GFRC cladding panels had also been appended to the timber hoarding. These sketches had also been stamped and signed, and referenced PPC number Cxxx-LAO-Z-MRC-N105_WS089-50260 (see photo). On checking the PPC in the office, it was identified that the PPC was a Placeholder on eB and did not exist on the collaboration site. A hard copy was made available which showed __, __ and CRL sign off, however this had not processed via the correct systems. As a result of the PPC procedural failings for GFRC installation this NCR was raised resulting from the surveillance.
| 02SL - Stations (LUL) | Cxxx-NCR-000768 | NCR | To date, on 15 occasions works have proceeded without a PPC being in place. This is against the accepted PPC prcoedure |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2017-02-06 | 2017-01-30 12:19 | -7 | 2016-11-16 14:05 | Architectural - General | 500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | A planned Crossrail surveillance was undertaken on 14th November 2016 to look at __’s adherence to their Proposal to Progress Construction (PPC) Works at Risk – Procedure Cxxx-LAO-O7-GPD-N105_WS089-50001. During discussions it was identified that to date there have been 15 occasions where works have proceeded without adhering to the PPC procedure. In absence of a PPC, NCRs have been raised by __ personnel to either proceed with installation without a PPC, or document the fact that works had progressed without a PPC. The ability to raise an NCR in lieu of an accepted PPC is a process that has not been agreed by any party and should be stopped until such justification has been discussed, agreed and documented. In addition the procedure clearly states the requirements for PPC sign off before commencing any works. This is not being followed, bringing into question the implementation of the PPC procedure. A summary of the NCRs raised by __ are detailed below: Cxxx-NCR- *575, 612, 619, 630, 631, 640, 641, 642, 645, 671, 681, 732, 734, 736 and 754. As a result of these non procedural practices being undertaken, this NCR was raised. As part of the close out to this NCR the Contractor should undertake exercises to understand the root cause behind why the PPC process is not being followed to avoid continued recurrence.
| 02SL - Stations (LUL) | Cxxx-NCR-000770 | NCR | Use of Stainless Steel Cable Ties |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-01-31 | 2018-12-04 09:45 | -58 | 2017-11-02 15:30 | Electrical - Cable Management | 1000 |  | Incomplete Works | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Stainless Steel Cable Ties not being installed as part of the Cxxx cable installation (TEW +)
| 02SL - Stations (LUL) | Cxxx-NCR-000773 | NCR | Damaged As Installed Radio Cable |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-01-31 | 2019-01-08 11:52 | -23 | 2017-11-02 15:26 | Mechanical - Piping | 1500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Following the removal of electrical cable basket the as installed radio cable has been damaged within GYB Room CER 2 SID Number 4/734). Photos attached x 3.
| 02SL - Stations (LUL) | Cxxx-NCR-000774 | NCR | Installation of Hydroduct in Lift 9 Level -5 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2016-11-22 | 2016-11-21 14:02 | -1 | 2016-11-17 15:46 | Civil - Civil Engineering General | 5000 |  | Supervision/Management | Use As-Is | 3 (3-6k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | __ installed hydroduct in the base of Lift 9 at Level -5 believing it was required. However, the Cxxx drawings show it is not. Confusion occurred when reading the approved method statement which shows the area requiring hydroduct.
| 02SL - Stations (LUL) | Cxxx-NCR-000775 | NCR | GYB Level -3 - Dampers not to the level of the slab to be firestopped |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-02-15 | 2017-03-01 09:50 | 14 | 2016-11-21 10:26 | Mechanical - Heating Ventilation & Air Conditioning | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The Contractor has been progressing the ductwork installation. At GYB Level -3 there has been an error in the drawing and location of the damper as can be seen from the attached photo and drawing. The damper is sitting above the alignment of the slab. To enable fire compartmentation this damper should be fire stopped between it and the slab. With the damper being above this slab this is not possible.
| 02SL - Stations (LUL) | Cxxx-NCR-000776 | NCR | Damage to PTW/AP4 tusk arch |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-03-09 | 2017-03-10 14:20 | 1 | 2016-11-21 15:30 | Architectural - General | 5000 |  | Damaged | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The area highlighted on the attached image has been damaged during installation of the PTW/AP4 tusk arch and the plate that fixes between the tusk arch and plinth can not be installed at this location. Please refer to the attached image (IMG_2322) for the damage.
| 02SL - Stations (LUL) | Cxxx-NCR-000777 | NCR | Site Installed non manufactured trunkng T Section |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-02-28 | 2019-01-09 11:21 | -50 | 2019-01-07 14:15 | Electrical - Cable Management | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | Site Installed non manufactured trunkng T Section in lieu of factory manufactured unit
| 02SL - Stations (LUL) | Cxxx-NCR-000778 | NCR | PTW/AP3 and PTE/AP3 tusk arch installed out of tolerance |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-02-05 | 2017-02-22 15:31 | 17 | 2016-11-23 09:56 | Architectural - General | 2000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The tusk arch in PTW/AP3 and PTE/AP3 were installed out of tolerance. The Contractor has managed to install the tusk arch in PTW/AP4 and PTE/AP4 within tolerance and has therefore decided to re-visit PTW/AP3 and PTE/AP3 and adjust the position of the tusk arch and to ensure installation is within the acceptable tolerances.
| 02SL - Stations (LUL) | Cxxx-NCR-000779 | NCR | Fire Main Support Brackets |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-01-25 | 2017-02-02 14:02 | 8 | 2016-11-25 13:02 | Mechanical - Piping | 1300 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | Fire Main has been installed using brackets. The design on the drawings have not been applied
| 02SL - Stations (LUL) | Cxxx-NCR-000780 | NCR | Commencement __ Cabinet construction without MCR |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-03-23 | 2017-03-24 08:51 | 1 | 2016-11-28 16:28 | Fire - Compartmentation | 5000 |  | Documentation and Records | Use As-Is | 3 (3-6k) | Complete | Management Problem - Inadequate supervision | Completed |  | The main contractor proceeded with construction without an approved MCR for the __ cabinets along the Platforms and Tunnels. The main contractor had an ITP approved to Code 2 to based on the low risk due to a system wide MCR being approved on eB. The main contractor has provided and MCR to Project Manager to which the Project Manager has not responded within the period of replay (two weeks after submission).
| 02SL - Stations (LUL) | Cxxx-NCR-000781 | NCR | Unauthorised drilling of Lower cable tray on PES by Sub Contractor |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-04-30 | 2017-04-26 11:20 | -4 | 2016-11-29 13:31 | Electrical - Cable Management | 5000 |  | Documentation and Records | Use As-Is | 3 (3-6k) | Complete | Management Problem - Inadequate supervision | Completed |  | The Contractor has become aware that a sub contractor on site has drilled holes in the lower cable tray to the PES despite this activity not being detailed on their RAMS, Drawings or ITP. Additionally, there was no additional galvanising protection applied to the cable tray. The holes have been drilled at a frequency of one pair every 1.5m.
| 02SL - Stations (LUL) | Cxxx-NCR-000782 | NCR | Duct / CMS clash NCR to be raised – LVII WTH level -3 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-01-31 | 2017-02-01 13:39 | 1 | 2016-12-08 09:02 | Mechanical - Heating Ventilation & Air Conditioning | 1000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | CMS currently runs across were ductwork passes into room WTH level -3, SR LV 1 (4/681) . Co-ordination review required.
| 02SL - Stations (LUL) | Cxxx-NCR-000783 | NCR | Level +1 PT Slab. Understrength Cube |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-01-27 | 2016-12-05 09:39 | -53 | 2016-12-02 16:16 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | On Pour 2 top up section, the 56-day cube result reflects 58.5N/mm² which is a fraction lower than the required 60N/mm². This was poured on the slab section only along a small section of GL-6 (not near any PT sections). Refer attached
| 02SL - Stations (LUL) | Cxxx-NCR-000784 | NCR | Level +1 PT Slab. Flow test |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-01-27 | 2016-12-05 11:12 | -53 | 2016-12-02 16:20 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | While reviewing the handover documents for the Level +1 PT slab, it was observed that during the flow tests, the initial flow test at t0 shows flow time above 25 second and the subsequent tests at t30 with similar readings. While the t30 reading is acceptable, the initial tests are not. The attached grout cube reports show results above the required strength. During the operation it was observed all grout tubes were bled our correctly.
| 02SL - Stations (LUL) | Cxxx-NCR-000785 | NCR | Incorrectly interconnected 225mm communication trunkings |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-01-31 | 2019-01-28 17:13 | -3 | 2016-12-02 16:08 | Electrical - Cable Management | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Incorrectly interconnected 225mm communication trunkings - trunkings interconnected the wrong way round.
| 02SL - Stations (LUL) | Cxxx-NCR-000786 | NCR | Level +1 PT/Core 1 Wall Cracks |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-01-03 | 2016-12-09 17:08 | -25 | 2016-12-06 10:29 | Civil - Civil Engineering General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Cracks have been observed in the upper section of Core 1 walls where it is connected to Level +1 PT beams. Refer attached markup and photos.
| 02SL - Stations (LUL) | Cxxx-NCR-000787 | NCR | GYB - Coring to accommodate CHT traywork at Ground level |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-01-04 | 2016-12-15 09:28 | -20 | 2016-12-07 16:28 | Civil - Civil Engineering General | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | Two additional openings in room 1/243 at Ground Level Goslett Yard Box are required to accommodate CHT tray work.
| 02SL - Stations (LUL) | Cxxx-NCR-000788 | NCR | GYB Level +3 PFR Room - Install of Fan without ITP |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-05-26 | 2017-05-05 11:24 | -21 | 2016-12-08 09:15 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | The contractor wishes to inform the project manager that the work has progressed on the installation of stair press fans in GYB +3 without an approved ITP.
| 02SL - Stations (LUL) | Cxxx-NCR-000789 | NCR | Non Fire Rated Ductwork installed without an approved MCR |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2017-03-06 | 2017-03-13 09:28 | 7 | 2016-12-08 10:16 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | A planned Crossrail Surveillance on installation of Ductwork took place at Tottenham Court Road Crossrail Station on the 5th December 2016. After the site visit the contractor made available the MCR for non fire rated ductwork (CRL-MCR- 002715). On checking eB it was identified that the MCR had not been approved. This was last commented on the 28th January 2016 by Crossrail with no further action by the contractor; as such the Ductwork has been installed without any acceptance in place. Works Information Volume 2B – General Requirements - 13.3.8 Materials Compliance Record (MCR) states; “The Contractor shall utilise the template attached in Appendix 13J (MCR) for the purpose of recording material and product acceptances for the works and submit such records to the Project Manager for acceptance.” In addition the Demonstration of Materials Compliance Procedure under section 8.2 Materials Compliance Record states; “The Contractor will use the eB MCR system for MEP MCRs”.
| 02SL - Stations (LUL) | Cxxx-NCR-000790 | NCR | Room SID 5/669 signed off as completed however incorrect installation identified during surveillance |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2017-02-15 | 2017-02-13 08:19 | -2 | 2016-12-08 12:41 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | A planned Crossrail Surveillance on installation of Ductwork took place at Tottenham Court Road Crossrail Station on the 5th December 2016. Completed Ductwork installation within Room SID 5/669 (MPT-SC) Level -5 was visually inspected which had been signed off as complete by __ (Ductwork) and City Insulation (insulation). In addition the records had been signed off by the MEP Engineer. On inspection of Ductwork two defects were identified: 1 - A length of screwed rod had been encapsulated within the Ductwork insulation (see photos) which contravenes JY30 Air Ductlines and Ancillaries Crossrail M&W Specification, Section JY30.1402 - Ductwork Construction – (d) Hangers and Supports – iii) “Hangers for ductwork to be thermally insulated shall provide clearance for the insulation to be applied and finished”. 2 - The flange section of the ‘right’ Fire Damper(see photo) had only been fixed to the Block work wall via four screws (visually assessed from ground level), however the MAP BSK4 data sheet showed fixings through every hole via a general detail. In addition the ‘left’ damper has more fixings than that of the ‘right’ damper. The contractor could not clarify which was the correct fixing arrangement. As Room SID 5/669 (MPT-SC) Level -5 had gone through the room review process and been signed off as complete and defect free by all parties this non conformance was raised to highlight the breakdown in the checking process.
| 02SL - Stations (LUL) | Cxxx-NCR-000791 | NCR | GYB - Level -3 - Contractor's Missing Cavity Benching & Drainage Pipework Records |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-02-15 | 2017-03-01 16:14 | 14 | 2016-12-09 12:22 | Civil - Civil Engineering General | 1000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | The Contractor completed the benching and cavity drain pipe installation at GYB Level -3. The Contractor was regularly engaging with inspections with the Client to sign these works off as they are a pre-start requirement for Blockwork. These inspections were undertaken by __, __ _, __ with __. The records and as-builts for these works have not been kept suitably and cannot be located anymore.
| 02SL - Stations (LUL) | Cxxx-NCR-000792 | NCR | GYB - Level -1 - Missing Cavity Drainage and Benching Documentation |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-02-15 | 2017-03-01 15:28 | 14 | 2016-12-09 13:44 | Architectural - Brickworks/Blockworks | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | The Contractor completed the benching and cavity drain pipe installation at GYB Level -1. The Contractor was regularly engaging with inspections with the Client to sign these works off as they are a pre-start requirement for Blockwork. These inspections were undertaken by __, __ _, __ with __. The records and as-builts for these works have not been kept suitably and cannot be located anymore.
| 02SL - Stations (LUL) | Cxxx-NCR-000794 | NCR | level -5 breaking of concrete topping for hoist relocation |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-05-20 | 2017-01-24 15:56 | -116 | 2016-12-21 17:25 | Civil - Civil Engineering General | 500 |  | Planning | Rework | 4 (0.5-3k) | Complete | Training Deficiency - Inadequate content | Completed |  | The temporary works requirement for the re-location of the WTH goods hoist in Core 4, was to fix direct to raft slab. Therefore we had to break out the 100mm concrete topping and the hydroduct.
| 02SL - Stations (LUL) | Cxxx-NCR-000795 | NCR | enlarging lifting hole for reconstone erection -2 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-03-03 | 2017-01-24 15:59 | -38 | 2016-12-13 15:42 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | The 150mm square hole on level -2 utilized for lifting reconstituted panels is incorrectly set out and needs to be extended by 150mm making the hole 300 long by 150 wide.
| 02SL - Stations (LUL) | Cxxx-NCR-000796 | NCR | Recon Corner Panel Oxford Street/Great Chapel Street |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-07-03 | 2017-04-10 15:55 | -84 | 2016-12-15 12:39 | Architectural - General | 500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The recon corner panel on Great Chapel street to Oxford Street, has an area where the aggregate has not be come to the front of the panel. This areas is approximately 150mm long by 50mm wide and is the grey matrix showing through. On completion of the panel installation a specialist will come to site and conduct a repair to bring the panel to the required finish
| 02SL - Stations (LUL) | Cxxx-NCR-000797 | NCR | Gas suppression pipework fixing detail |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-07-06 | 2017-07-20 10:53 | 14 | 2016-12-15 17:53 | Fire - Suppression | 3000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | The pipe support detail for the gas suppression pipework in the 4 no respective transformer rooms has been installed with a different fixing detail compared to the PPC drawing. Additionally the munsen ring that has been installed is not covered under the MCR noted on the ITP.
| 02SL - Stations (LUL) | Cxxx-NCR-000798 | NCR | Installation of Electrical Wiring without approved ITP |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-01-13 | 2017-01-23 12:34 | 10 | 2016-12-16 10:22 | Electrical - General | 2000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | The Contractor commenced the installation of Electrical prior to the approval of Cxxx-LAO-O4-ITP-N105_WS089_Z-50063 ITP.
| 02SL - Stations (LUL) | Cxxx-NCR-000799 | NCR | Installation of Distribution Boards without approved ITP |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-01-13 | 2017-01-20 12:38 | 7 | 2016-12-16 11:56 | Electrical - General | 2000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | The Contractor commenced the installation of Distribution Boards prior to the approval of Cxxx-LAO-O4-ITP-N105_WS089_Z-50063 ITP.
| 02SL - Stations (LUL) | Cxxx-NCR-000800 | NCR | EWS-416A Reconstituted stone cladding |  | Contr | OVE | TCR - Tottenham Court Road Station (West) |  | 2017-07-25 | 2017-06-28 10:00 | -27 | 2016-12-21 09:32 | Architectural - Walls | 500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | non compliance with Architectural specification also shown on attached comments sheet 1. omitted.ca 2. omitted.ca 3. omitted.ca 4. Specification Non compliances JH42.1207 c) top member of opening surround on dean street not polished .ca 5. Specification Non compliances JH42.1206h)i)4th para ie visible exposed core material on corner panels. ca 6. Specification Non compliances JH42.2202.confirm or not that this will be done ca 7. Specification Non compliances .ca JH42.3106 a) 8. b)where are the accepted samples for the corners? ca 9. c)ii) various panels, 10. iii)see 4 above , 11. vi) corner panel 12. vii) corner panel 13. ix) gaps in aggregate corner panel 14. Specification Non compliances .ca JH42.3107 a) each type has not been offered for inspection 15. b) its not clear what is defective and what is repaired. Have there been any factory repairs and have they been accepted by the PM?.ca 16. Specification Non compliances .ca JH42.3108. Corner panels appear to have not been inspected. Please clarify if they were inspected by the manufacturer or not and if so why so many unexplained defects?. 17. Specification Non compliances .ca JH42.3109b) Manufacturers check sheets have not been provided, when will they be available? 18. Specification Non compliances.ca JH42.3213a) 19. Specification Non compliances.ca JH42.3205a) 20. 15mm corner radius or equivalent detail not provided.ca 21. JH42.3205g) Please provide evidence that the remediation of the corners and other chipped edges and faces where required can be rectified on site. Please provide this before starting work. PM s view is that the corner panel(s) need(s) to be remade. This is due to concerns about quality and durability. Any necessary alterations in the design must be fully clarified by Cxxx and accepted by the PM before remediation.ca
| 02SL - Stations (LUL) | Cxxx-NCR-000801 | NCR | Alterations required to secondary structure on -4 DC1 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-03-11 | 2017-01-25 11:03 | -45 | 2016-12-21 16:58 | Civil - Civil Engineering General | 1000 |  | Design | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Adjustments were required to door opening height to accommodate cabinets, cabinets cabinets are only permitted to tilt by 30 degrees maximum. At 30 degrees the cabinet would not fit into DC1 without adjusting the head height of the door. In addition the cabinet is top fed so CMS needed to enter the room via the top slab directly over the cabinet, hence a 400x 400m hole was required to be cored through the top slab.
| 02SL - Stations (LUL) | Cxxx-NCR-000802 | NCR | Re-work of ductwork required - GYB level -3 (4/683) |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2017-03-15 | 2017-03-21 16:02 | 6 | 2016-12-22 14:45 | Mechanical - Heating Ventilation & Air Conditioning | 5000 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Owing to a lack of coordination between services in GYB SR LV1 (4/683), the ventilation ductwork that has been installed and insulated in this room needs to be removed and re-installed.
| 02SL - Stations (LUL) | Cxxx-NCR-000803 | NCR | Motorised fire damper mounting plate fixings not installed |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2018-12-31 | 2019-04-25 09:06 | 115 | 2016-12-22 16:15 | Mechanical - Heating Ventilation & Air Conditioning | 2500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | Technical literature for the MAP BSK4 motorised fire dampers shows that the "__" mounting plates and rear closing angles are to be fixed to the fire rated structure. A number of the __ mounting plates and closing angles across the site are not fixed to the structure and are therefore not installed in compliance with the manufacturers requirements.
| 02SL - Stations (LUL) | Cxxx-NCR-000804 | NCR | Inaccessible ductwork maintenance hatches - GYB level -3 (4/736) |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2018-05-31 | 2018-05-29 08:35 | -2 | 2016-12-22 15:28 | Mechanical - Heating Ventilation & Air Conditioning | 1500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Access and maintenance hatches in the high level ventilation ductwork within GYB COM-R room 4/736 are not accessible as they are located above a significant quantity of CMS and Cxxx equipment. This will prevent routine maintenance from being undertaken on this ductwork.
| 02SL - Stations (LUL) | Cxxx-NCR-000805 | NCR | heater battery sizes to AHU W1 & W2 |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2017-04-28 | 2017-05-22 13:42 | 24 | 2016-12-23 11:09 | Mechanical - Heating Ventilation & Air Conditioning | 2000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | Following on from a risk reduction meeting on Friday 16th December, the contractors designer has acknowledged the heater battery have been sized utilising a different battery sizing strategy from both the WI and GYB shaft, in error. This represents a departure from WI, and necessitates an NCR against the design. The consequence of the error is the heater battery provision is in excess by at least 460 kW (ie 230kW +230kW), with knock on impact on electrical infrastructure.
| 02SL - Stations (LUL) | Cxxx-NCR-000806 | NCR | __ Cabinets: Incorrect Design and Installation. Damage to installed work. |  | Crossrail | PDP | TCR - Tottenham Court Road Station (West) |  | 2017-03-28 | 2017-03-20 16:08 | -8 | 2016-12-23 11:23 | Archaeology - General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The design for the installed __ cabinets at -4 level does not reflect the details as issued post design meeting. The exposed edges do not have the protective angle on the design drawings, and have not been installed. There are instances of the exposed cut edges starting to delaminate already.
| 02SL - Stations (LUL) | Cxxx-NCR-000807 | NCR | GYB - Failure of quality system |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-02-01 | 2017-01-18 12:41 | -14 | 2017-01-04 15:12 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Failure to record additional concrete test for Goslett Yard Box escalator support walls, escalator ramp pours 1 & 3 and escalator slab on pour history sheet.
| 02SL - Stations (LUL) | Cxxx-NCR-000808 | NCR | Blockwork Structural Ties - Not Installed Correctly |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-05-05 | 2017-04-24 11:56 | -11 | 2017-01-04 17:43 | Architectural - Brickworks/Blockworks | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The Contractor has incorrectly installed ties into walls at WTH Level -2. The 225mm long ties have not been positioned to enable 105mm embedment into each wall length.
| 02SL - Stations (LUL) | Cxxx-NCR-000809 | NCR | Bowing of metal trunking IP4X cover clips to 225mm and 300mm trunking (__) |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-01-31 | 2018-12-19 15:49 | -43 | 2017-01-09 10:01 | Electrical - Cable Management | 3000 |  | Manufacturing Defect | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Bowing of as installed metal trunking IP4X cover clips to 225mm and 300mm trunking (__)
| 02SL - Stations (LUL) | Cxxx-NCR-000810 | NCR | GFRC Panels - Platform Benchmark Manufacture Check-sheets |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-02-08 | 2017-03-31 13:31 | 51 | 2017-01-11 16:58 | Architectural - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | The manufacture check-sheets of the GFRC panels in the platform benchmark were not available on site at the time of the benchmark inspection. The Contractor has confirmed to the Project Manager that these are available at the Contractor's GFRC Supplier's (__) factory and these will be shown to the Project Manager when the benchmark panels are re-inspected (w/c 16/01/17).
| 02SL - Stations (LUL) | Cxxx-NCR-000811 | NCR | Hydrant low point drains incorrect size |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-02-09 | 2017-02-07 16:59 | -2 | 2017-01-12 07:53 | Fire - Suppression | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | 25mm drains have been installed on the hydrant low points in GYB -5 where they are required to be 50mm.
| 02SL - Stations (LUL) | Cxxx-NCR-000812 | NCR | Non-acceptance of GFRC panels in platform benchmark |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-03-29 | 2017-03-23 09:05 | -6 | 2017-02-15 16:12 | Architectural - General | 500 |  | Manufacturing Defect | Reject | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | The Project Manager has not accepted 5no. GFRC panels within the platform benchmark. Please refer to the attached photo produced by the Project Manager highlighting the panels that have not been accepted - please note, following a review of the benchmark panels on site with the Project Manager (__) on the the 11th January 2016 the mark up of the panels that have not been accepted has been revised. - The 2no. panels marked in red will be removed and replaced. The flange of one panel is broken at the top and the other panel is of a poor quality finish. - The 1no. panel marked in purple has not been accepted in the benchmark because of the finish to the top edge of the panel. The Contractor believes this panel should be included in the works and will discuss this further with the Project Manager. - The 2no. panels marked in yellow has not been accepted because they have a shiny finish. The Project Manager has not accepted them in the benchmark, however, confirmation from the Project Manager is expected if the panels can be included in the works.
| 02SL - Stations (LUL) | Cxxx-NCR-000813 | NCR | Location of hydrant isolation valve - WTH -5 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-02-14 | 2017-01-19 08:32 | -26 | 2017-01-17 08:29 | Fire - Suppression | 250 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | An isolation valve on the station hydrant system had been located within the platform inverts which is considered a confined space. There is a requirement for equipment to not be located within confined spaces where reasonably practicable. The valve needs to be moved.
| 02SL - Stations (LUL) | Cxxx-NCR-000814 | NCR | level -1 soffit finish |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-04-30 | 2017-02-28 11:04 | -61 | 2017-01-17 17:25 | Civil - Civil Engineering General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The perimeter of the WTH -1 soffit is different in colour to the approved benchmark for exposed concrete soffit. Extent of works is as per attachment.
| 02SL - Stations (LUL) | Cxxx-NCR-000815 | NCR | GYB CER Cxxx Cabinet Connections |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-05-12 | 2017-05-15 11:40 | 3 | 2017-01-19 10:36 | Electrical - Electrical Engineering General | 10000 |  | Supervision/Management | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Contamination | Completed |  | The Contractor has site drilled 25mm cable entry holes in the top of the Cxxx (GYB CER) equipment racks, despite the panels being supplied with pre-drilled cable entries. This has now introduced a risk of metallic fragments (swarf) entering sensitive electrical equipment and resulted in the associated commissioning lots being excluded from the planned IRN of the 18/01/2017, as __ Cxxx deem it a risk to energise the racks in their current state, until demonstrated as safe to be energised.
| 02SL - Stations (LUL) | Cxxx-NCR-000816 | NCR | OHLE WTH Power Connection |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-05-22 | 2017-05-18 09:02 | -4 | 2017-01-19 10:41 | Electrical - Electrical Engineering General | 5000 |  | Supervision/Management | Rework | 3 (3-6k) | Complete | Management Problem - Inadequate supervision | Completed |  | The Contractor has site drilled 25mm cable entry holes in the side of the Cxxx (OHLE WTH) MS146 Mini RTU, despite the panels being supplied with pre-drilled cable entries. This has now introduced a risk of damage to internal PCB’s and metallic fragments (swarf) entering sensitive electrical equipment
| 02SL - Stations (LUL) | Cxxx-NCR-000817 | NCR | Equipotential bonding conductors to CER Equipment |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-03-31 | 2017-03-13 12:17 | -18 | 2017-01-19 10:45 | Electrical - Electrical Engineering General | 5000 |  | Supervision/Management | Use As-Is | 3 (3-6k) | Complete | Management Problem - Inadequate supervision | Completed |  | The Contractor has installed 10mm Equipotential bonding conductors to CER Equipment racks, which have been cut short and not terminated correctly to the main internal earth bar, requiring rewiring to the correct destination earth bar.
| 02SL - Stations (LUL) | Cxxx-NCR-000818 | NCR | Cable Management: Lifts |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2018-07-20 | 2018-07-17 10:20 | -3 | 2017-01-19 17:05 | Electrical - Cable Management | 1500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | On inspection of readiness for power to motors, it was confirmed that __ and __ had worked exactly to the approved Quality plan, Method Statement and ITP, however, the CMS running between the Lift shaft and LEER room is subject to the CTH assurance processes, and this had not been done.
| 02SL - Stations (LUL) | Cxxx-NCR-000819 | NCR | GYB - Door fabrication error |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-02-17 | 2017-01-27 09:24 | -21 | 2017-01-20 09:13 | Civil - Civil Engineering General | 2000 |  | Supervision/Management | Reject | 4 (0.5-3k) | Complete | Personnel Error - Other human error | Completed |  | Doors D3-1/016 and D3-1/018 have been fabricated to an incorrect length. This is due to the screed not being accounted for whilst measuring the required door heights.
| 02SL - Stations (LUL) | Cxxx-NCR-000820 | NCR | Testing of __ Mechanical Anchors WTH |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2017-07-07 | 2017-07-20 13:20 | 13 | 2017-01-27 15:20 | Architectural - Walls | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | On 25th January 2016, the PM witnessed the testing of 3 No. __ mechanical anchors on the reconstituted stone cladding at the top of WTH escalator incline (Note: each post is supported by two mechanical and two resin anchors, however the test was offered for the mechanical anchors only). The anchors were tested to a load of 24kN and all failed (load started to drop when held for more than just a few seconds). The sub-contractor (__) then stated that the test load should have been 10kN, but was unable to provide any documentation to substantiate this. This NCR is raised for the following reasons: 1) Failed tests on reconstituted cladding fixings at WTH escalator incline 2) Lack of clarity over what the test load should be and how long this should be held for 3) Uncertainty over integrity of other fixings site wide which may have been tested to a load in excess of their capacity The Contractor is to provide an action plan to address the above concerns.
| 02SL - Stations (LUL) | Cxxx-NCR-000821 | NCR | Insulation Pins - Installation Conditions |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-04-01 | 2017-02-03 15:52 | -57 | 2017-01-31 18:51 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | The contractor wishes to inform the project manager of that the insulation pins which have been used to hang the 50mm thick __ thermal insulation to ductwork have been installed outside of the manufacturers recommendations during the last month since the ambient temperature of on the project has decreased. The manufacturers recommendation is that the insulation pins are installed between ambient temperatures of 15-24c.
| 02SL - Stations (LUL) | Cxxx-NCR-000822 | NCR | GYB - Drill and fix reinforcement for half landing level -1 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-03-02 | 2017-02-06 09:20 | -24 | 2017-02-02 09:27 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | On the previous landings, in the section highlighted on the attached drawing, there has been a polystyrene block within the riser enabling us to break this out and tie the half landing reinforcement to the riser reinforcement. On level -1 there is no polystyrene block.
| 02SL - Stations (LUL) | Cxxx-NCR-000823 | NCR | GYB Substructure - level -2 Elevation 37, 38, openings for ducting to be increased |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-06-06 | 2017-06-09 09:52 | 3 | 2017-02-03 09:54 | Civil - Civil Engineering General | 1000 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Due to a new EU directive the ducting dampers have increased in size. This directive was passed after the concrete walls were cast, therefore the openings need to be increased to accommodate the new dampers. The openings must increase by 55mm vertically.
| 02SL - Stations (LUL) | Cxxx-NCR-000824 | NCR | GFRC acoustic panel delivered to site with cracks around Big Head fixing. Failure in __ checking process |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2017-09-29 | 2017-10-04 10:13 | 5 | 2017-02-07 11:17 | Architectural - General | 500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | A planned Crossrail surveillance was undertaken on 2nd February 2017 to look at GFRC installation being carried out by __. During the site visit an inspection of the GFRC panels stored in Goslet Yard level minus one was undertaken. On checking a crate (limited availability due to stacking) of acoustic panels, it was identified that one of the panels showed cracking on the outer edge around one of the big head fixings. The panel was removed; this showed significant structural cracking on the inner side around the same fixing (see photo). A similar issue was identified during a planned Crossrail surveillance to __ on 27th January 2017 (see photo), however the panel had yet to go through its final quality checking where it was stated issues like this was a one off and would be rejected. As the panel had been delivered to site, there appears to have been a breakdown in __'s quality checking procedure, which has allowed a non compliant cladding panel to be delivered to site for installation. In addition, this panel was produced before the batch checked during the off-site visit. __ manufacture ITP Cxxx-LAO-O4-ITP-N105_WS089_Z-50015 section 7 details the checks required prior to loading and delivery, which in this instance have failed.
| 02SL - Stations (LUL) | Cxxx-NCR-000825 | NCR | No MCR in place for Thixotropic Grout being used as part of GFRC system installation |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2017-03-07 | 2017-03-13 11:22 | 6 | 2017-02-07 11:20 | Architectural - General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | A planned Crossrail surveillance was undertaken on 2nd February 2017 to look at GFRC installation being carried out by __. A review of the MCR’s for the materials in use for the installation of the GFRC cladding panel system was carried out. On review, it was identified that no MCR existed for the ‘Thixotropic Joint Filling Grout’ being used for the packing beneath the stainless steel base plates; and in the construction of the evaporation channels.
| 02SL - Stations (LUL) | Cxxx-NCR-000826 | NCR | No PPC stamp on GFRC drawing being used at AP3W; and drawing obsolete on eB |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2017-05-12 | 2017-05-12 10:53 | 0 | 2017-02-07 11:24 | Architectural - General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | A planned Crossrail surveillance was undertaken on 2nd February 2017 to look at GFRC installation being carried out by __. During the site visit it was noted that the Contractor was using installation Drawing Cxxx-LAO-Y-DWG-N105_WS089_6-50072 which had no PPC stamp on (see photo). In addition, on reviewing the drawing on eB it was found that the drawing is marked as ‘obsolete’. The PPC procedure Cxxx-LAO-O7-GPD-N105_WS089-50001 states; “All drawings associated with the PPC will be stamped and signed by the __ Package Manager to provide traceability back to the PPC”. In addition it states; “These drawings will be submitted to eB for information under a decal signed by the __ Design Manager..”.
| 02SL - Stations (LUL) | Cxxx-NCR-000827 | NCR | 3400 GFRC Cladding - BigHead GFRC Pull-out failure |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-09-29 | 2017-10-04 10:12 | 5 | 2017-02-07 12:30 | Architectural - Walls | 5000 |  | Workmanship | Rework | 3 (3-6k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | During installation of the double curved passenger zone panel on PTE/AP3E (Eastbound Platform to Cross-Passage AP3E RHS) w/c 30th January 2017 the Contractor and his installer __ UK Ltd became aware of an issue with some of the BigHead sockets cast into the GFRC panel and the supporting GFRC ‘tusk’. The BigHead sockets are cast into GFRC to form connection points in the GFRC to attach stainless steel rails/brackets. It was observed that the GFRC material appeared to fail as a result of the BigHead socket being pulled out.
| 02SL - Stations (LUL) | Cxxx-NCR-000828 | NCR | __ undertaking repairs (inc face coat cracks) to panels without acceptance (or agreed procedure) as part of manufacturing process |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2017-06-02 | 2017-06-07 11:33 | 5 | 2017-02-08 09:07 | Architectural - General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Lack of procedure | Completed |  | A planned Crossrail surveillance was undertaken on 27th January 2017 to look at GFRC manufacture being undertaken by __ at their factory in Doncaster. During the visit, __ stated that patching and repairing is being completed as part of the manufacturing process, including repairs to face coat cracking. This process was witnessed being undertaken within Unit 3. During the visit, and as part of the Exit Note, __ were requested to provide evidence of __ and CRL acceptance for undertaking such patching and repairing as required by Cxxx Architectural Specification Sections; JH40.1702 b) i) “‘Units receiving minor local damage to the surface or edges may be patched if acceptance is given by the Project Manager. The patching may be carried out by the Sub Contractor in the fabrication plant …” and JH40.1702 b) ii) “cracks and fractures in GFRC elements are unacceptable and affected elements will be rejected” A repair procedure with acceptance from __ and CRL could not be provided; which should define and differentiate between the types of repairs (aesthetic or major) being completed, and the methods and materials used. This should also include information of what types require discussion and agreement with CRL and __ prior to proceeding; i.e. major types such as crack repairs. Following an Exit Note request, no verifiable evidence could be provided showing Project Managers acceptance of such patching and repairing (or procedure defining such) which is being completed as part of the manufacture process. This contravenes JH40.1702 b) i). In addition, as part of the manufacturing process, face coat cracking is being remediated without formal acceptance to do so, which contravenes JH40.1702 b) ii). Furthermore, quality records are not recording any repairs being completed, such as major types. This should also be discussed and agreed to ensure alignment and agreement between all parties.
| 02SL - Stations (LUL) | Cxxx-NCR-000829 | NCR | Non compliant fixings embedment depths and/or base plate protrusions |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2017-08-23 | 2017-08-18 15:48 | -5 | 2017-02-08 11:39 | Architectural - Finishes | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | A planned Crossrail surveillance was undertaken on 7th February 2017 to look at Reconstituted Stone Cladding installation being carried out by __. During the site visit an inspection of the wall cladding support framework on level -4 found that two number __ HAS-F Stud Anchor fixings had been embedded to deep; resulting in nuts, once tightened, showing no visible thread pitch above the nut, see attached photo’s. Industry standards state a minimum of two threads should be exposed above the nut to ensure adequate nut engagement. As the surveillance was based on a sample a review should be undertaken on all installed base plate fixings to ensure compliance with the design details and industry standards.
| 02SL - Stations (LUL) | Cxxx-NCR-000830 | NCR | GYB Level -1 access plate angle |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-07-28 | 2017-07-25 09:27 | -3 | 2017-06-09 11:12 | Architectural - Balustrade | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Closer angles to GYB Level -1 access plates were not installed.
| 02SL - Stations (LUL) | Cxxx-NCR-000831 | NCR | GYB - Openings for busbar on level -3 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-06-30 | 2017-06-30 13:02 | 0 | 2017-02-13 17:13 | Civil - Civil Engineering General | 5000 |  | Design | Repair | 3 (3-6k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | Additional openings are required for the installation of busbar on level -3. A 600mm x 340mm opening is required in elevation 17 above doorway D3-4/018 and a 500mm x 300mm opening in the slab in room 4/787.
| 02SL - Stations (LUL) | Cxxx-NCR-000832 | NCR | WTH - Level -1 - Internal Blockwork Walling Incorrect As-built |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-05-26 | 2017-05-19 14:25 | -7 | 2017-02-14 12:05 | Architectural - Brickworks/Blockworks | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Upon setting out follow on internal walling it has become clear that the setting out for the LEER Room (LCC 2/133) blockwork walling is incorrect and out of position. See attached mark-up. To summarise the front wall is between 170 to 217mm into the Circulation space (CIR-S 2/241) and the dividing wall between the aforementioned LEER room and SCR (2/761) is 140mm into the LEER room.
| 02SL - Stations (LUL) | Cxxx-NCR-000833 | NCR | WTH - Level -2 - Blockwork Opening Incorrectly Set-Out (Elevation 33) |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-03-14 | 2017-03-31 09:08 | 17 | 2017-02-14 16:47 | Architectural - Brickworks/Blockworks | 1000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | An opening within Elevation 33 has been incorrectly set-out and installed within the blockwork. The opening clashes with the perpendicular wall that comes off it.
| 02SL - Stations (LUL) | Cxxx-NCR-000834 | NCR | GYB Level -5 - Air Release Duct Serving Room 5/100 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-03-15 | 2017-03-30 12:52 | 15 | 2017-02-15 13:51 | Mechanical - Heating Ventilation & Air Conditioning | 7500 |  | Design | Rework | 2 (6-60k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | With reference to EWN-00853 the contractor highlights that the air release ductwork serving Room 5/100 (level -4) is no longer required due to a design change from F1 design. The contractor confirms that the ductwork and associated dampers serving this area is manufactured, on site and is approximately 60% installed. Re-work/removal will be required.
| 02SL - Stations (LUL) | Cxxx-NCR-000835 | NCR | GYB - Doorways on level -4 built to wrong revision of drawing |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-04-30 | 2017-05-17 12:40 | 17 | 2017-02-17 12:37 | Civil - Civil Engineering General | 2000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Doorways D3-5/008 and D3-5/009 on level -4 have been built to an earlier revision of the drawing. This means the doorways are both 70mm out of position.
| 02SL - Stations (LUL) | Cxxx-NCR-000837 | NCR | CMS Re-work Level WTH Level -3 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-05-28 | 2017-05-15 12:24 | -13 | 2017-02-21 10:30 | Electrical - General | 1000 |  | Planning | Rework | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | CMS re-work is required due to a small element being removed in order to accommodate the installation of the ductwork outside the LV Room on WTH level -3.
| 02SL - Stations (LUL) | Cxxx-NCR-000838 | NCR | Use of a Hiliti HUS 3 Screw Anchor into concrete block without MCR approval |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-09-29 | 2017-10-13 09:19 | 14 | 2017-02-22 13:58 | Electrical - General | 5000 |  | Documentation and Records | Rework | 3 (3-6k) | Complete | Management Problem - Inadequate supervision | Completed |  | We have stopped using the __ HUS 3 HF Screw Anchor for fixing into concrete block, and only using in conjunction with the current MCR into cracked and non-cracked concrete.
| 02SL - Stations (LUL) | Cxxx-NCR-000839 | NCR | Lift Landing Door: Glass Shattered |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-04-14 | 2017-04-21 13:07 | 7 | 2017-02-23 11:46 | Mechanical - Lifts | 1000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Lift Landing Door on Lift 7 at Level -1: Glass panel has shattered
| 02SL - Stations (LUL) | Cxxx-NCR-000840 | NCR | Damaged lighting within main corridor outside CER2 GYB |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2017-06-08 | 2017-06-06 14:20 | -2 | 2017-02-23 17:25 | Electrical - Lighting | 2000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Management Problem - Other management problem | Completed |  | The Contractor has installed light fittings within the corridor outside the GYB CER2 at -3 and failed to protect finished works, which have been subject to damage on the external paint finish. This was pointed out to the local operatives at the time of observing who implemented temporary protection. Furthermore the positioning of the fittings was also questions as some of them (at the time of observation) were impeding access and maintenance to the high level CMS
| 02SL - Stations (LUL) | Cxxx-NCR-000841 | NCR | WTH - Level -2 - Secondary Concrete Walls - Installed Incorrectly and Out of Line |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-04-28 | 2017-04-21 13:18 | -7 | 2017-02-23 17:14 | Civil - Civil Engineering General | 3000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | The Contractor has set out and poured a number of concrete walls out of line, one has a missed opening and there is concrete walling been missed from the approved PPC design. See attached the photos and mark-ups for details on all 3 walls.
| 02SL - Stations (LUL) | Cxxx-NCR-000842 | NCR | Damage to concrete wall WTH -2 Vent tower by Cxxx Systemwide Contractor |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-03-27 | 2017-04-04 09:43 | 8 | 2017-02-27 07:46 | Architectural - General | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Damage caused by __ Cxxx to attached concrete wall. Caused by drilling for steelwork.
| 02SL - Stations (LUL) | Cxxx-NCR-000843 | NCR | Incorrectly Installed Duct Lining Panels in West end of Westbound Tunnel PES |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-05-01 | 2017-04-10 14:57 | -21 | 2017-02-27 16:36 | Mechanical - Mechanical Engineering General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | The Contractor has become aware that his Sub-Contractor has incorrectly installed the duct lining panels in the back of house area at the West End of the Westbound tunnel. The drawing (attached) shows that the access hatch should be nearest to the concrete tunnel end wall, with the duct off-take panels as the next 2 panels towards the plenum end baffle. However as shown in the photo shows that the duct off-take panels are installed nearer the concrete end wall (with one opening partially obscured by the duct). In the as installed arrangement, the duct connections can't be made and the access panel is too far from the previous one. As such the panels will need to be removed and re-installed in their correct position.
| 02SL - Stations (LUL) | Cxxx-NCR-000844 | NCR | GYB - Reinforcement protruding from topping layer pour level +4 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-09-04 | 2017-07-11 13:43 | -55 | 2017-07-10 11:38 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | A bar of reinforcement is protruding from the protective topping layer of the level +4 waterproofing.
| 02SL - Stations (LUL) | Cxxx-NCR-000846 | NCR | Consolidated NCR's(14) for non compliance to design at Assurance Gate 3 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-05-31 | 2017-06-09 11:11 | 9 | 2017-03-08 11:47 | Architectural - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The Contractor commenced construction of a number of design packages prior to Crossrail formal acceptance of the design at Assurance Gate 3. This NCR consolidates 14 separate NCR's relation to By Exception. The design information was reviewed with Crossrail as per 'By Exception Construction Prior to Gate Acceptance' procedure for Stations Portals and Shafts [eB reference CRL1-XRL-O7-GPD-CR001-50023 version 1.0] The design information was reviewed and documented in the following reports and NCRs: Cxxx-LAO-Z-MRC-N105_WS089-50136 Cxxx-NCR-000315 Cxxx-XRL-O7-RGN-N105_WS093-50001 Cxxx-NCR-000383 Cxxx-LAO-Z-MRC-N105_WS089-50143 Cxxx-NCR-000521 Cxxx-LAO-Z-MRC-N105_WS089-50145 Cxxx-NCR-000413 Cxxx-XRL-O-RGN-N105-50001 Cxxx-NCR-000404 Cxxx-LAO-Z-MRC-N105_WS089-50149 Cxxx-NCR-000542 Cxxx-LAO-Z-MRC-N105_WS093-50144 Cxxx-NCR-000645 Cxxx-LAO-Z-MRC-N105_WS089-50153 Cxxx-NCR-000441 Cxxx-LAO-Z-MRC-N105_WS089-50146 Cxxx-NCR-000465 Cxxx-LAO-Z-MRC-N105_WS089-50151 Cxxx-NCR-000541 Cxxx-LAO-Z-MRC-N105_WS089-50159 Cxxx-NCR-000548 Cxxx-LAO-Z-MRC-N105_WS089-50160 Cxxx-NCR-000547 Cxxx-LAO-Z-MRC-N105_WS089-50163 Cxxx-NCR-000472 Cxxx-NCR-000481 In order to maintain the Assurance process, this design should have been finalised and aligned with the F1 design for Crossrail acceptance at Gate 3. In addition, NCR's 534,535 and 542 were raised by CRL but these were cancelled and then raised by Contractor under different numbers and are included above.
| 02SL - Stations (LUL) | Cxxx-NCR-000847 | NCR | Removal of Access Hatch within ductwork Riser Level +3 GYB |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-06-30 | 2017-06-08 10:32 | -22 | 2017-03-16 08:35 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | A access panel which was located within E1/E2 exhaust riser on level +3 has been removed. This section of ductwork was signed off by the contractor and CRL.
| 02SL - Stations (LUL) | Cxxx-NCR-000848 | NCR | WTH - Level -1 - Incorrect height of Door D2-2/026 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-04-07 | 2017-03-13 09:23 | -25 | 2017-03-10 17:46 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | The Contractor has incorrectly built the opening for a door on WTH Level -1 - D2-2/026. The door and ironmongery schedule outlines that this door should be 2500mm high from SSL however this has been installed to 2260mm. This error has occurred as the elevation for this wall indicates a 2260mm wall within PPC Cxxx-LAO-Z-MRC-N105_WS089-50296 for SLD rooms (Elevation 40) and as such has been built to this. This error was not picked up as part of the PPC review process.
| 02SL - Stations (LUL) | Cxxx-NCR-000849 | NCR | WTH Block C level 0 Visible Joints to EWS-416 recon mullions and transoms |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2017-06-29 | 2017-06-30 10:53 | 1 | 2017-03-13 14:54 | Architectural - Masonary | 500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Information not detailed | Completed |  | As built Notched joints at Mullion transom connection at head of openings are visible see attachment 1. Design and manufacturing drawings (see attachment 2) show these joints are intended to be not visible and concealed behind the external face of the Precast Cladding.
| 02SL - Stations (LUL) | Cxxx-NCR-000850 | NCR | Fixing of Cable Tray to structural soffit: __ |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-04-27 | 2017-05-23 15:12 | 26 | 2017-03-14 12:42 | Electrical - Cable Management | 5000 |  | Supervision/Management | Rework | 3 (3-6k) | Complete | Subcontractor Problems - Insufficient surveillance of subcontractors | Completed |  | During an inspection prior to proving temporary power to __ such that complete their installation, the following NCR was identified on __' incomplete works. __ have not complied with the following specification clauses in the method with which they have secured CMS to the structural soffit: CRL1-XRL-RSP-CR001-50089 JY90 JY90.3208 Fixings to Concrete a) Fixings to conceret will generally be made using one of the following: i) Mechanical Expansion Anchors ii) Chemical Anchors iii) Resin Anchors iv) Concrete Screws v) Under Cut Anchors d) Use of 'hammer in' wedge anchors is not permitted as their installation can not be quality assured. Pan TfL Specification SPC-LAE-301941170 Part 1 10.20 Fixings. 10.20.6 When fixing into concrete, brickwork or block work, chemical resin anchors shall be used. 10.20.9 No fixings other than those specified within this document shall be used without the prior written agreement of the employer. __ have however Code 1 for all MCR's submissions, however the generic MCR's and project specific MCR's did not include fixings to the structure for CMS.
| 02SL - Stations (LUL) | Cxxx-NCR-000852 | NCR | GYB - Air Release System Changes |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-05-08 | 2017-05-19 13:41 | 11 | 2017-03-16 08:55 | Mechanical - Heating Ventilation & Air Conditioning | 15000 |  | Design | Rework | 2 (6-60k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The contractor wishes to advise the project manager of the element of re-work required in removing a redundant section of the air release system in GYB.
| 02SL - Stations (LUL) | Cxxx-NCR-000853 | NCR | Non compliance with the works information vol 2B part 20. |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2017-06-19 | 2017-06-12 11:33 | -7 | 2017-03-16 15:52 | Architectural - Masonary | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | During the installation of the Western Ticket Hall Block C Type EWS-416 Architectural Precast Concrete Cladding at level 0 Cxxx failed to issue a schedule of or invitations to the witness points described in the installation ITP and as required by the WI. Cxxx are to propose the remedy that will enable CRL to confirm compliance of items that are now covered up.
| 02SL - Stations (LUL) | Cxxx-NCR-000855 | NCR | Missing PPIR Records for Secondary walls A+B Level -3 WTH |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-04-13 | 2017-03-16 16:52 | -28 | 2017-03-16 15:53 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Misplaced PPIR Records on site for Secondary walls A+B Level -3 WTH
| 02SL - Stations (LUL) | Cxxx-NCR-000856 | NCR | Non compliance with the works information vol 2B |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2017-05-05 | 2017-05-11 14:48 | 6 | 2017-03-17 08:04 | Architectural - Glazing | 500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | During the installation of the Western Ticket Hall Block C EWS-155 Glazed Cladding / Curtain Wall System at level 0, Cxxx failed to issue a schedule of or invitations to the witness points described in the installation ITP and as required by the WI. .
| 02SL - Stations (LUL) | Cxxx-NCR-000857 | NCR | WTH reconstituted stone corner pieces non compliant with specification |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2017-09-18 | 2017-10-12 08:25 | 24 | 2017-03-17 15:50 | Architectural - Masonary | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The horizontal alignment of the preformed south west corner piece of Block D cornice /Light grey polished reconstituted stone banding type EWS-416D spec clause JH42.1207D is non compliant with spec clause JH42.3301c). see attached. Cxxx must propose remediation for crossrail acceptance. further to this Cxxx must confirm the horizontal off set of the other block D as built cornice sections so as to enable CRL to determine compliance of alignment.
| 02SL - Stations (LUL) | Cxxx-NCR-000858 | NCR | GFRC cladding panel gaskets not correctly jointed and continuous |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2017-05-15 | 2017-05-15 12:31 | 0 | 2017-03-20 10:19 | Architectural - General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | A planned Crossrail surveillance was undertaken on 2nd February 2017 to look at GFRC installation being carried out by __. During the site visit the gasket detail was checked for panels stored at platform level. It was found that the gaskets on multiple panels checked had not been fully jointed with a gap appearing between the strips at the corner edge (see photo attached). Clarification was provided in GRCUK/BWT Report 14014_AI No.575 for the gasket jointing requirements following an Exit Note request. The response referred to Cxxx Specification Section JZ23 ‘Gaskets’ noting that a butt joint is required. On further investigation of this section, clause 1101 (g) states, “All gasket to gasket joints shall be butt jointed and heat sealed. The bonding of gaskets using other materials shall not be acceptable. The gaskets shall perform and appear as a single continuous material”. As identified during the surveillance, there was a gap between the gaskets at the corner edge joint which contravenes this Cxxx requirement. As the surveillance was based on a check at that given time, it is unclear how many panels have been jointed like this.
| 02SL - Stations (LUL) | Cxxx-NCR-000859 | NCR | No grout testing completed for grouting of GFRC cladding ladder frame base plates |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2017-05-30 | 2017-05-15 13:28 | -15 | 2017-03-20 10:24 | Architectural - General | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Supervision - Other | Completed |  | A planned Crossrail surveillance was undertaken on 2nd February 2017 to look at GFRC installation being carried out by __. During the site visit the ladder frame base plate connection detail was checked, where it was identified that grouting had been completed in the void between the base plate and platform. In addition, grouting of the evaporation channel had been completed. During discussion, it was identified that no grout testing had been carried out. It was not clear from the response in GRCUK/BWT Report 14014_AI No.575 whether grout testing was required following an Exit Note request. On review of KM10.1407 ‘Grouting’, clause (i) states “Contractor to maintain full site records of grout strength, and pour volumes”. As no site testing has been completed to date, no site records exist confirming grout strength which contravenes the Cxxx requirement.
| 02SL - Stations (LUL) | Cxxx-NCR-000860 | NCR | GFRC Water Absorption test results non compliant with GRCA Specification; __ not notifying |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2017-05-30 | 2017-05-25 12:01 | -5 | 2017-03-20 10:33 | Architectural - General | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | A planned Crossrail surveillance was undertaken on 27th January 2017 to look at GFRC Manufacture at __ __. __ made available Water Absorption test reports (dated 31st January 2017) for samples T1, T2, T3 and T4. The ITP (Cxxx-LAO-O4-ITP-N105_WS089_Z-50015) states the parameters for water absorption as ‘difference between two weights 24hrs apart is less than 1%’. On review, it was identified that the test report showed a value at 24hrs and a value at 7 days for each sample. In addition, it was noted that a water absorption range of between 5-11% was included on the report; both not aligning with the parameter defined in the ITP. Clarification for water absorption performance requirements was provided in __/__ Report 14014_AI No.575 following a post request. __ confirmed that the results should be between 5-11% as required in the ‘Specification for the Manufacture, Curing & Testing of Glassfibre Reinforced Concrete (GRC) Products’ Part 3 for Grade 18 mix designs; as such the ITP parameters were incorrect and need rectifying. Moreover, on review of the results based on these requirements, it was identified that the mean at both 24hrs (11.18%) and 7 days (12.00%) exceeded the 5-11% range. __ pointed to the following text within the Specification; ‘the mix designs in Table 3a, 3b and 3c are intended as a guide indicating typical figures; designs falling outside these guidelines may be acceptable but should be scrutinised before use’, stating that they had internally assessed these non-conformances and deemed the mix acceptable. However, these had not been captured on the Crossrail Project Technical Request (PTR) system as a NCR, meaning Crossrail and __ have not had visibility of the rationale and justification for the acceptance of these samples/ panels outside of the Specification range. As the surveillance was based on a sample, it is unclear how many samples fall outside of the Specification requirements; this should be investigated as part of the closure to this NCR.
| 02SL - Stations (LUL) | Cxxx-NCR-000861 | NCR | Internal/External Reconstone/Precast Brick on-site Installation Benchmark |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2018-01-31 | 2018-02-02 14:50 | 2 | 2017-03-21 14:30 | Architectural - General | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | (i) Internal Recon stone (Benchmark not approved) (ii) External recon (Benchmark Code 3) (iii) precast brick(Benchmark not approved) all of the systems have been installed or in progress with a code 3 benchmark (External recon stone) and not approved benchmarks for internal recon stone and precast brick
| 02SL - Stations (LUL) | Cxxx-NCR-000862 | NCR | Coordination of tunnel fire main in GYB-5 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2018-01-01 | 2017-12-13 11:57 | -19 | 2017-03-22 10:01 | Fire - Suppression | 3000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | At present the 200mm diameter tunnel fire main pipe runs at high level and consequently blocks access for the ductwork that needs to run from the riser in to the GYB -5 area. The probable solution (__/__ to confirm) will be to locally set the pipe down to low level to avoid the ductwork. If this is the solution a new/relocated drain valve will be required as the system low point would then be at this location.
| 02SL - Stations (LUL) | Cxxx-NCR-000863 | NCR | GYB -5 Containment Drawing Rev 4 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-04-20 | 2017-04-05 10:57 | -15 | 2017-03-23 15:38 | Electrical - Cable Management | 5000 |  | Documentation and Records | Use As-Is | 3 (3-6k) | Complete | Management Problem - Inadequate supervision | Completed |  | __ working to drawing Cxxx-LAO-E-CWG-N105_WS093_6-50004 Revision 04, with showed updates from the version of the drawing that was PPC’ed.
| 02SL - Stations (LUL) | Cxxx-NCR-000864 | NCR | WTH - Level -2 - Incorrect position of wall to FWC/SSR (3/420) |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-10-14 | 2017-04-21 13:22 | -176 | 2017-03-28 14:59 | Architectural - Brickworks/Blockworks | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | As per attached mark-ups the end of the concrete wall constructed on Level -2 to the front face to the toilet was cast 160-170mm short of its correct position on the drawing. By changing the arrangement for how the perpendicular blockwork wall connects to this concrete wall it means that it is actually only out of position by 20-30mm. This has created a small step between the blockwork and the concrete walling roughly hallway down the wall.
| 02SL - Stations (LUL) | Cxxx-NCR-000865 | NCR | Damage to waterproofing |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-04-25 | 2017-04-21 13:05 | -4 | 2017-03-28 12:53 | Civil - Civil Engineering General | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | During excavation there appears to be damage to the D-Wall waterproofing. It is unknown at the moment if this has been caused by Cxxx or by the previous contractor during initial installation.
| 02SL - Stations (LUL) | Cxxx-NCR-000866 | NCR | WTH __ Manifold and Gas Pipe Interface |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-09-17 | 2017-09-15 11:56 | -2 | 2017-03-30 14:42 | Civil - Civil Engineering General | 3000 |  | Planning | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The interface between the __ trench and the existing gas pipe has made it as such that we haven't got the space to install the manifold. It is a __ requirement to have steel ducts running through the capping beam into there trench and for this to be water tight.
| 02SL - Stations (LUL) | Cxxx-NCR-000867 | NCR | WTH - Level -2 - AHU Delivery is unable to fit through door D2-3/001 - Removal of Blockwork and Re-instate |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-08-31 | 2019-06-05 07:40 | -87 | 2017-03-30 15:02 | Architectural - Brickworks/Blockworks | 2000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | The Contractor is delivering the AHU's for the WTH Level -2 on Tuesday. Upon review of the drawings of the assembled items it is clear that the current door into the AHU Room (3/767) does not enable enough space for the delivery. Refer to drawing for W4 AHU and the largest single central piece is 2302mm high, 2m wide and 2m deep and this does not allow for a pallet truck underneath. The current door opening is 2260mm high by 1980mm wide. The Contractor proposes installing a reversed cleat under the lintel above the door lintel that forms part of the builderswork hole. With this supporting the walling above to then remove the pier to the left and the lintel itself. The small nib to the right hand side of the door will be stitch drilled down enabling a width of 2030 wide. Once the delivery is complete these works will then be re-instated as per design including stitching out the blockwork to the right to re-instate the nib.
| 02SL - Stations (LUL) | Cxxx-NCR-000868 | NCR | GYB - Level -4 change in opening size of doorway D3-5/009 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-05-26 | 2017-05-17 13:00 | -9 | 2017-03-31 08:47 | Civil - Civil Engineering General | 1000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | The opening size of doorway D3-5/009 on level -4 was changed after the construction of the wall. Therefore the doorway is 240mm shorter than is necessary.
| 02SL - Stations (LUL) | Cxxx-NCR-000869 | NCR | Level -1 wall movement during pour |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-05-02 | 2017-04-10 12:39 | -22 | 2017-04-04 09:31 | Civil - Civil Engineering General | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the pour of Level -1 walls (adjacent to Core 1), it was noticed that there was movement during the pour which resulted in a shutter moving out 10mm in the middle creating a belly effect.
| 02SL - Stations (LUL) | Cxxx-NCR-000870 | NCR | Lightning Protection |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-10-31 | 2017-09-05 10:47 | -56 | 2017-04-04 17:31 | Electrical - General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | The Contractor has submitted the below MCRs on the 04/04/17 in relation to the Lightning Protection System. CRL-MCR-004809 CRL-MCR-004810 CRL-MCR-004811 CRL-MCR-004812 CRL-MCR-004813 CRL-MCR-004818 CRL-MCR-004819 The Contractor intends to carry out the works on 10/04/17 in order to achieve the PMs handover date in relation to SC3 handover. The Contractor specialist Lighting Protection Sub Contractor has proposed the materials submitted. All the MCRs submitted have been related to already code 1 MCRs and have been installed at other Crossrail stations.
| 02SL - Stations (LUL) | Cxxx-NCR-000871 | NCR | Diverse Routing of Fibre Optic Cables |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2017-07-06 | 2017-07-14 08:18 | 8 | 2017-04-05 15:51 | Communications and Control Systems - Fibre Optic Network | 5000 |  | Supervision/Management | Rework | 3 (3-6k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | The Contractors Specialist Communication Contractor (__) has failed to ensure they have applied a diverse routing philosophy associated with Fibre Optics from the GYB CER2, to the -5 basement of GYB. The Contractors Communication Contractor (__) has opted to route all vertical rising fibre optic cables within a single Communication Trunking, within a single side of what is a partitioned riser, despite their being separate Communication CMS in either side of the riser and should have opted to segregate the cables accordingly. This oversight has demonstrated the Contractor and its specialist have worked on a “free hand basis” and decided locally what CMS to use, as oppose following the __ design detail. This error will now result in additional re-work, associated re-testing, additional costs and risk of delay in completing the project and is currently holding up __ Cxxx’s works until the issue is resolved. Furthermore it demonstrates a lack of Site Management/Supervision on the behalf of the Contractor, as despite this issue being raised in December to the Contractor under Cxxx-EWN-00796 , it has now taken the Project Manager to intervene and assist the Contractor in directing him to the errors, having undertaken his own survey in the absence of the Contractor to ascertain the extent and resolve the issue. The Project Manager will provide the details of the associated Fibres to be re-routed, but requests the Contractor and his Specialist (__), demonstrate they are now working to the specific design detail provided by __ and notes, while assisting the Contractor with this information provision, it is the Contractors responsibility to undertake his own survey to satisfy himself that the Installation is in accordance with the __ detail.
| 02SL - Stations (LUL) | Cxxx-NCR-000873 | NCR | Missing Cube Results - Column C23 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-05-31 | 2017-05-16 13:56 | -15 | 2017-04-06 09:56 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | During the handover of Level +0 verts package, it was noticed that there was a missing cube result for column C23
| 02SL - Stations (LUL) | Cxxx-NCR-000874 | NCR | 200mm tunnel fire main - deflection of brackets |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-12-31 | 2017-12-08 15:40 | -23 | 2017-04-05 15:41 | Fire - Suppression | 2000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Supports for the 200mm tunnel fire main in GYB at -5 show signs of deflection.
| 02SL - Stations (LUL) | Cxxx-NCR-000875 | NCR | The Contractor did not comply with the Cxxx Protection of Works Strategy |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2017-05-30 | 2017-06-13 15:59 | 14 | 2017-04-06 11:26 | Architectural - General | 500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | A planned Crossrail surveillance was undertaken on 4th April 2017 to look at the Protection of Completed and Ongoing Work, during the site visit it was identified that the Contractor had failed to protect the __ Communication cabinets as Referenced in the Contractors Protection of Works Strategy.
| 02SL - Stations (LUL) | Cxxx-NCR-000876 | NCR | The Contractor has not complied with the MEP Materials Workmanship Specification |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2017-08-31 | 2017-09-15 11:36 | 15 | 2017-04-06 12:37 | Electrical - General | 500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | A planned Crossrail surveillance was undertaken on 4th April 2017 to look at the Protection of Completed and Ongoing Work, during the site visit it was witnessed that there were light fittings that had not been protected, there were also light fittings the had been protected with a mixture of materials i.e. Cardboard, plastic bubble wrap and Corex. On inspection of the Method Statement ‘Installation of Luminaries' Cxxx-LAO-O4-GMS-N105_WS089_Z-50012 (Rev 1). It was found that no reference has been made to the protection of light fittings, which is a requirement in the MEP Materials and Workmanship Specification CRL1-XRL-M-RSP-CR001-50016 Version 2.0.
| 02SL - Stations (LUL) | Cxxx-NCR-000877 | NCR | Tunnel - OHLE - Front Face Blockwork Wall - Incorrect Setting Out Information by Designer |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-05-04 | 2017-05-24 11:17 | 20 | 2017-04-06 12:39 | Architectural - Brickworks/Blockworks | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | The Contractor has built the Blockwork walling to the Setting out sketch provided by the Contractor's designer (see attached 1399-SK-164) as per PPC for walling in this location (Cxxx-LAO-Z-MRC-N105_WS089-50191). The Contractor has as-built this information against the sketch and the walling is within 14mm however the as-built co-ordinates were passed onto __ (GRC Designers) who highlighted that this wall was 300mm to far forward into AP7a. The Contractors designer has reviewed the as-built and setting out information and has confirmed that the wall is in the correct position and the setting out information is wrong.
| 02SL - Stations (LUL) | Cxxx-NCR-000879 | NCR | GYB Chiller Panel Damage |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-10-27 | 2017-09-29 10:00 | -28 | 2017-04-12 14:32 | Mechanical - Heating Ventilation & Air Conditioning | 6000 |  | Damaged | Repair | 3 (3-6k) | Complete | Material/Preservation Problems - Improper handling of material | Completed |  | Upon receipt of the GYB chillers, there has bee damage caused onsite to a number of panels (3No.)
| 02SL - Stations (LUL) | Cxxx-NCR-000880 | NCR | Control of Access |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-05-17 | 2017-05-09 16:09 | -8 | 2017-04-19 07:27 | Electrical - General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Unauthorized access into an SLD room, together with periodic testing isolating critical equipment. Note the Contractor confirms that Cxxx confirmed no effect to equipment.
| 02SL - Stations (LUL) | Cxxx-NCR-000881 | NCR | GYB 4/676 - Access Panels to be cut into Ductwork |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-06-25 | 2017-06-21 10:22 | -4 | 2017-04-21 14:56 | Mechanical - Heating Ventilation & Air Conditioning | 1500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Re-work is required to cut in the access panel within the ductwork services within room 4/676, the ductwork has also been lagged and will need to be cut to allow the panels to be cut into the ductwork.
| 02SL - Stations (LUL) | Cxxx-NCR-000882 | NCR | GYB -4 lobby 5/244: inaccessible MFD motor |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-11-30 | 2017-11-30 09:08 | 0 | 2017-04-21 15:20 | Mechanical - Heating Ventilation & Air Conditioning | 4000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | The client has identified that the MFD actuators which are serving room 5/244 are inaccessible due to cms below restricting access for wiring.
| 02SL - Stations (LUL) | Cxxx-NCR-000884 | NCR | Works commenced prior to pre-construction deliverable documentation acceptance |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-07-03 | 2017-06-19 11:14 | -14 | 2017-04-24 16:53 | Mechanical - Piping | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | The installation of the ground source heat pump buried pipework commenced prior to acceptance of the pre-construction deliverable documentation. Both ITP (Cxxx-LAO-O4-ITP-N105_WS089_1-50008) and MCR (Cxxx-LAO-O4-XDS-N105_WS089_1-50002) had been reviewed off-line by CRL and issued on eB, however these had mistakenly been uploaded 'for information' so no comment sheet or work order was produced for CRL action.
| 02SL - Stations (LUL) | Cxxx-NCR-000885 | NCR | AHU W4 - AHU on site unable to meet design duty |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2017-09-12 | 2017-08-18 09:57 | -25 | 2017-04-25 09:17 | Mechanical - Heating Ventilation & Air Conditioning | 5000 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | AHU-W4 requires a minimum air flow rate 2.5 m3/s for the heater batteries to function. The design schematics only require a flow of 1.8 m3/s. The unit onsite is therefore unable to operate at the design duty. Note: Cxxx have been requested several times to raise this as an NCR but have not done so or provided an explanation why.
| 02SL - Stations (LUL) | Cxxx-NCR-000886 | NCR | AHU-E1 & E2 - Fliter Position |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-06-30 | 2017-07-21 15:35 | 21 | 2017-04-25 17:09 | Mechanical - Heating Ventilation & Air Conditioning | 4000 |  | Design | Repair | 3 (3-6k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | The contractor wishes to highlight the incorrect configuration of the filter on AHU-E1&E2, a gate 3 comment was highlighted buy CEG requesting the position of the filters on these units to be before both the cooling coil and the heater battery, the configuration of the filter in the units on site is between the cooling coil and the heater battery. This comment was not picked up by the designer during the PPC process.
| 02SL - Stations (LUL) | Cxxx-NCR-000888 | NCR | MNS4 staircase handrail |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-09-17 | 2017-10-12 08:22 | 25 | 2017-04-28 07:51 | Architectural - Handrail | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | As per JZ30.1203 the galvanizing finish of the handrails within MNS4 does not comply with clause JZ30.1203 (c) as visible scratches and imperfections to the 'off the shelf' interclamp tubes are unsatisfactory. The countersunk fixings installed in the MNS4 wall mounted brackets are installed using the wrong size screws. The Contractor has also raised FCD-000883 in clarification of previously agreed FCD-000678 to the galvanized versus black polyester powder coating (PPC) to back of house staircases. Pending the response of this FCD, this item shall be added / removed from this NCR.
| 02SL - Stations (LUL) | Cxxx-NCR-000889 | NCR | Level -2 Lintel Removal (__ Doors) |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-06-30 | 2017-05-16 13:58 | -45 | 2017-05-02 15:12 | Civil - Civil Engineering General | 1000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | __ __ had surveyed door opening, __ determined that door height was 40mm low and required 40mm taken off to achieve installation. __ had removed RC door lintel and recast to achieve concrete cover. However __ __ drawing does not tie in with __ drawing, __ __ door drawing shows height of 2305m where __ drawing shows door height to be 2260m high. Lintel was then recast to __ original height. Later discussed lintel would have to be changed and cast a third time to 2305m high.
| 02SL - Stations (LUL) | Cxxx-NCR-000890 | NCR | Level -2 Secondary wall missed voids |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-05-31 | 2017-05-26 08:15 | -5 | 2017-05-03 17:32 | Civil - Civil Engineering General | 2000 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | It appears voids in a secondary wall on Level -2 has missing voids above the door (Riser wall on the north side of Core 1). Refer attached
| 02SL - Stations (LUL) | Cxxx-NCR-000891 | NCR | Delivery of Chillers without an approved ITP |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-06-30 | 2017-07-20 07:48 | 20 | 2017-05-05 13:32 | Mechanical - Heating Ventilation & Air Conditioning | 2000 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | The Contractor has delivered and dropped the chillers into position onsite without an approved ITP Note - Lift plan added to __ genera lift plan document
| 02SL - Stations (LUL) | Cxxx-NCR-000892 | NCR | Damage to AHU W2 top section |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-07-13 | 2017-07-17 16:03 | 4 | 2017-05-10 11:37 | Mechanical - Mechanical Engineering General | 5500 |  | Damaged | Repair | 3 (3-6k) | Complete | Supervision - Other | Completed |  | Whilst lifting the last top section of AHU W2 the section, The section center of gravity was eccentric when lifting and slipped/dropped 150mm damaging the damper housing and blades. We confirm that No persons were at risk
| 02SL - Stations (LUL) | Cxxx-NCR-000893 | NCR | Glazing - colour of the installed glasspanels |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-07-31 | 2021-05-12 09:34 | 1381 | 2021-05-07 08:52 | Architectural - General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | The colour of the installed panels was questioned by CRL during inspection due to perceived colour. difference. Signed off Reference sample presented on site is labelled pure white and spec requires RAL 9010 Pure White. However Contractor has stated that Polar white has superseded the previously agreed RAL 9010 Pure White colour. Contractor has been requested by CRL to evidence this , provide and retain appropriate samples and amend the specification.
| 02SL - Stations (LUL) | Cxxx-NCR-000894 | NCR | Loose Trims to PES Lightboxes, PTE and PTW |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2018-07-31 | 2018-08-20 10:53 | 20 | 2017-05-17 11:08 | Architectural - General | 3000 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The Contractor has been made aware that a number of trims to the DesignPlan lightboxes on the PES are loose. Attached marked up elevation shows locations of the lightboxes with loose trims. The Contractor has made his Sub-Contractor aware and has raise formal communication requesting that the supplier provide a remedial detail to correct this defect. All instances of loose trims will be raised as snags of the Field View system until they are addressed.
| 02SL - Stations (LUL) | Cxxx-NCR-000895 | NCR | Locking Pins to PES Lower Grille Pentagram Hinge |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-06-28 | 2017-07-14 11:30 | 16 | 2017-05-17 11:49 | Architectural - General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | The Contractor has been made aware that one of the pins required to lock the pentagram hinge to the lower PES grille could not be inserted into the pair of holes, suggesting the hinges were misaligned. This issue appears to have been cause by the alignment between units 6 and 7 which have slightly affected the hinge operation, preventing the locking pin from being inserted easily. The Sub-Contractor has been notified and is expected to correct the defect by 19/05/2017.
| 02SL - Stations (LUL) | Cxxx-NCR-000896 | NCR | WTH Ground Level - Door not installed D2-1/049 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-07-13 | 2017-07-10 14:53 | -3 | 2017-05-18 14:05 | Civil - Civil Engineering General | 3000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | Door opening not installed on WTH vent shaft wall as it was missed on the structural drawings
| 02SL - Stations (LUL) | Cxxx-NCR-000897 | NCR | Damaged Materials |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-09-30 | 2017-10-12 10:30 | 12 | 2017-05-22 09:45 | Mechanical - Escalators | 2000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper handling of material | Completed |  | 4 No. Escalator Steps identified as damaged by __ Lead Engineer prior to install in GYB Escalators.
| 02SL - Stations (LUL) | Cxxx-NCR-000898 | NCR | Onsite recon cladding repairs completed without Crossrail acceptance |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2018-07-30 | 2018-12-05 16:06 | 128 | 2017-05-31 10:16 | Architectural - General | 2000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A planned Crossrail surveillance was undertaken on 26th May 2017 to look at onsite installation of the Reconstituted Stone Cladding at TCR Station. During the site visit it was noted that a number of onsite repairs had been made to recon cladding panels where defects had been identified. It was further stated that these repairs had been made by __ per their in-house procedure. A request was made for Crossrail acceptance of such repairs per Architectural Specification Cxxx-OVE-A-XDS-N105-50009 JH42.3205 which states “do not repair damaged units without acceptance. Such acceptance shall not be given where the units are badly damaged or where the proposed repair would impair appearance or performance”. No verifiable evidence could be provided. Furthermore, it was identified that the __ repair procedure to which the repairs are being completed, had not been approved/accepted by __ via Asite or by CRL via eB. As a result, no evidence exists that the onsite repairs to the recon units are acceptable in terms of integrity (will meet the required design life) and finish (visual), including the level at which a panel is repaired/rejected in terms of damage encountered.
| 02SL - Stations (LUL) | Cxxx-NCR-000899 | NCR | Lift 10 LEER Room Blockwork |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-12-22 | 2018-01-04 13:54 | 13 | 2017-06-01 10:35 | Architectural - Brickworks/Blockworks | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Block work has spalled locally on the external face of the LEER block work for Lift 10: GYB Level -2. The spalling is in the location of lift control panels fitted inside the LEER.
| 02SL - Stations (LUL) | Cxxx-NCR-000900 | NCR | Tunnel S4 - Ductwork Corrosion |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-11-30 | 2017-12-01 15:55 | 1 | 2017-06-09 10:19 | Mechanical - Heating Ventilation & Air Conditioning | 2000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | With reference to the Smoke extract ductwork on level -5 (tunnel S4) the contractor highlights the requirement for a section of ductwork to be replaced, due to water leaking through the structure onto the ductwork causing corrosion. The duct insulation on this section will need to be removed to allow the duct section to be replaced.
| 02SL - Stations (LUL) | Cxxx-NCR-000901 | NCR | PTE east end ductwork clash with door |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-09-01 | 2017-07-04 09:18 | -59 | 2017-06-13 16:04 | Mechanical - Heating Ventilation & Air Conditioning | 5000 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The PTE GYB PES connection requires re-work as the current design clashes with the cupboard door opposite were the ductwork rises from below the platform.
| 02SL - Stations (LUL) | Cxxx-NCR-000902 | NCR | Re-work on ductwork in WTH -2 accommodation areas for coordination with ceiling |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2018-12-31 | 2019-11-01 14:32 | 305 | 2017-06-13 16:10 | Mechanical - Heating Ventilation & Air Conditioning | 5000 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The following rooms will require re-work on the duct installation due to the interface/coordination with the false ceiling: DRR-3/485 __F-3/481 SLR-3/318 SLR-3/320 SMK-3/333 MWC/SSR - 3/421 FWC/SSR - 3/420
| 02SL - Stations (LUL) | Cxxx-NCR-000903 | NCR | Application of Anti Graffiti and Waterproof Coatings to Recon Cladding removed from Specification scope without formal acceptance |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2018-04-27 | 2018-04-27 14:19 | 0 | 2017-06-14 11:27 | Architectural - General | 0 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | A planned Crossrail surveillance was undertaken on 26th May 2017 to look at onsite installation of the Reconstituted Stone Cladding at TCR Station. During the surveillance questions were asked regarding Anti Graffiti and Waterproof Coatings based on the Cxxx Architectural Specification (Cxxx-LAO-A-RSP-N105_WS089-50001) requirements below (also Cxxx requirements); - Section JH42.1207 ‘Precast Concrete Cladding f) A factory applied anti-graffiti coating as recommended by the reconstituted stone supplier and to the acceptance of the Project Manager. - Section JH42.1207 ‘Precast Concrete Cladding g) A factory applied bitumen based waterproof coating applied to the faces of the panel below ground level. Offsite Manufacture check sheets were provided which included a tick box for AG/Waterproof Coatings; however these were marked as N/A. In a meeting held on 9th June to follow up on the surveillance items, it was stated by __ that Anti Graffiti and Waterproof coatings had been ‘omitted from the scope’ early on. __ were requested to provide the formal acceptance for the removal of the Specification requirements. On 13th June, it was confirmed by both __ and CRL that no formal acceptance existed for the scope removal. It is not clear what the reason is for this relaxation and the impact on the installed works.
| 02SL - Stations (LUL) | Cxxx-NCR-000904 | NCR | GYB - Openings for doors D3-1/016 and D3-1/018 at ground level |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-10-20 | 2017-10-18 11:28 | -2 | 2017-06-15 15:54 | Civil - Civil Engineering General | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Doors D3-1/016 and D3-1/018 highlighted in the attached drawing have been fabricated to an incorrect length. This is due to the screed not being accounted for whilst measuring the required door heights.
| 02SL - Stations (LUL) | Cxxx-NCR-000906 | NCR | Glass (Light) Panels at GYB Level -1 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2018-08-15 | 2019-01-11 12:08 | 149 | 2017-06-20 10:10 | Architectural - Glazing | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | This NCR is being raised against glass panels associated with light fixtures at Level -1. __ has recently erected some additional panels in this area. This installation was a continuation of installed as per original layout and is not as per PMI 1041.
| 02SL - Stations (LUL) | Cxxx-NCR-000907 | NCR | No evidence of Pull Testing by __ on manufactured Recon and Brick panel fixings as required by the Specification |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2018-05-25 | 2018-05-22 14:57 | -3 | 2017-06-20 14:53 | Architectural - General | 1000 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Insufficient surveillance of subcontractors | Completed |  | A planned Crossrail surveillance was undertaken on 26th May 2017 to look at onsite installation of the Reconstituted Stone Cladding at TCR Station. In the Exit Meeting the Contractor was requested to provide evidence of Pull Testing from __ completed on the manufactured panels cast in fixings as required by the Architectural Specification (Cxxx-LAO-A-RSP-N105_WS089-500001) requirements in Section JH42.2210 (also Cxxx requirements). Following requests from __ and __, __ failed to provide evidence to assure that the JH42.2210 testing requirements had been followed with compliant results. Furthermore, on checking the __ offsite manufacture ITP (Cxxx-LAO-O4-ITP-N105_WS089_Z-50022) it was identified that this did not contain any activity for pull testing validation against the design requirements. As no evidence has been provided following requests to __, it can not be confirmed that the cast in fixings installed in the manufactured panels to date are compliant.
| 02SL - Stations (LUL) | Cxxx-NCR-000908 | NCR | PTW PES Posts installed out of tolerance |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-10-27 | 2017-08-25 10:10 | -63 | 2017-06-21 15:35 | Structural Engineering - Steel Member | 3000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following the installation of the isolator remedial details in PTW, the PES posts have been surveyed and several have been found to be out of tolerance either in terms of verticality or in chainage. All PES posts are in tolerance relative to the track centreline so no items foul the train gauge. Maximum out of verticality is 6mm (3mm out of tolerance). Maximum out of chainage position is 21mm (11mm out of tolerance). The results of the survey are attached to NCR.
| 02SL - Stations (LUL) | Cxxx-NCR-000909 | NCR | __ not UKAS accredited for undertaking concrete sampling and testing activities |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2017-10-16 | 2017-09-25 12:06 | -21 | 2017-06-27 07:33 | Architectural - General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | A planned Crossrail surveillance was undertaken on 26th May 2017 to look at onsite installation of the Reconstituted Stone Cladding at TCR Station. The Contractor was requested to provide evidence of UKAS accreditation for __ who have undertaken sampling and testing activities throughout the offsite manufacture of the pre-cast cladding panels; this being concrete sampling, consistency testing, cube manufacture and compressive strength testing. During a post meeting it was stated that __ were not UKAS accredited. Calibration records, training records and ISO 9001 certification were presented as justification for their testing, however no formal acceptance existed from Crossrail accepting this in lieu of UKAS accreditation. Based on this, it can not be confirmed that the testing completed is compliant with the relevant British Standards, including the validity of outputted results (compressive strength).
| 02SL - Stations (LUL) | Cxxx-NCR-000910 | NCR | Small Power & Lighting Wiring Progression |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2018-02-09 | 2018-01-05 16:11 | -35 | 2017-06-27 15:36 | Electrical - Lighting | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other management problem | Completed |  | The Contractor has progressed the following areas with small power and Emergency Lighting wiring without an approved circuit layout PPC. WTH -5 ref Cxxx-LAO-E-DWG-N105_WS089-650017 Rev P06 WTH -4 FOH ref Cxxx-OVE-A-DDF-N105_5-20754-4-4 Rev C02 WTH -4 BOH ref Cxxx-LAO-E-DDA-N105_5-11213 Rev P07 WTH -3 ref Cxxx-LAO-E-DWG-N105_WS089-6-50017 Rev P06 GYB -5 ref Cxxx-LAO-E-DDA-N105-6-12215 Rev P06 GYB -4 ref Cxxx-LAO-E-DDA-N105-5-12213 Rev P06 GYB -3 ref Cxxx-LAO-E-DDA-N105-4-12211 Rev P06 GYB -2 ref Cxxx-LAO-E-DDA-N105-3-12209 Rev P07 1 of 2 GYB -2 ref Cxxx-LAO-E-DDA-N105-3-12210 Rev P07 2 of 2
| 02SL - Stations (LUL) | Cxxx-NCR-000911 | NCR | Installation bracketry and secondary containment preventing equipment access |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-08-19 | 2017-08-18 14:34 | -1 | 2017-06-28 16:14 | Electrical - Cable Management | 3000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | Sewage Pump Room 3/772 Installation bracketry and secondary containment preventing access to Damper Actuator at high level.
| 02SL - Stations (LUL) | Cxxx-NCR-000912 | NCR | JY53 Control Components |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-07-27 | 2017-08-11 10:26 | 15 | 2017-06-29 13:54 | Mechanical - Mechanical Engineering General | 1000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | The Contractors MEP specifications do not contain the Employer's Materials & Workmanship Specification clause JY53, issued under PMI 121.
| 02SL - Stations (LUL) | Cxxx-NCR-000913 | NCR | Concrete screws protuding and packed with additonal washers |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2018-12-31 | 2020-07-03 12:42 | 550 | 2017-06-30 13:24 | Mechanical - Heating Ventilation & Air Conditioning | 10000 |  | Workmanship | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Insufficient information made available to the worker. | Completed |  | The contractor wishes to highlight the issue of a number of concrete fixings supporting MEP services which are protruding around 5-10mm from the unistrut which its is supporting. These fixings have been packed out with additional washers to make the support make up flush with the fixing and support the services.
| 02SL - Stations (LUL) | Cxxx-NCR-000915 | NCR | IRF 0301 - LV A/B/E Cablig on CMS without CMS IRF sign off |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-08-03 | 2017-07-14 10:37 | -20 | 2017-07-06 11:17 | Electrical - Cable Management | 2000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | LV A/B & E cabling has been installed on CMS without a signed IRF for the associated CMS
| 02SL - Stations (LUL) | Cxxx-NCR-000916 | NCR | Fold/damage to GFRC acousitc insulation |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-08-31 | 2017-10-13 07:22 | 43 | 2017-07-07 11:29 | Architectural - General | 5000 |  | Manufacturing Defect | Rework | 3 (3-6k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | During recent inspections of the GFRC cladding installation, the Project Manager raised comments in regards to the acoustic insulation on the perforated platform panels. The main comments were in relation to noticeable folds and/or damage to the insulation. The Project Manager and Contractor carried out a joint review on the 14th June to agree what is and is not accepted. A benchmark area in the Westbound Platform between Bay 42-44 was agreed. The general principles that were agreed are listed below: - Any panels with very noticeable folds/damage to the acoustic insulation are to be replaced. If there are minor folds, especially vertical folds, the Project Manager and Contractor will review and look to accept these panels. - Folds in the top two acoustic perforated panels are to be more forgiving than the lower two. - For panels where the acoustic insulation is rejected, the insulation is to be replaced on site as per the attached task sheet. All materials are to supplied by __ with all products approved.
| 02SL - Stations (LUL) | Cxxx-NCR-000917 | NCR | GYB - Openings cored to incorrect size to allow firestopping around pipework |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-09-01 | 2017-07-26 14:21 | -37 | 2017-07-07 12:40 | Civil - Civil Engineering General | 1000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Two openings for pipework on level -5 ( shown on the highlight drawing attached ) have been cored to the incorrect size. This means there is not enough room to sleeve and firestop the pipework.
| 02SL - Stations (LUL) | Cxxx-NCR-000919 | NCR | Ductwork subcontractor cutting and installed HILTI HUS3 fixings |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2018-07-31 | 2018-08-13 08:10 | 13 | 2017-07-17 13:05 | Mechanical - Heating Ventilation & Air Conditioning | 50000 |  | Workmanship | Rework | 2 (6-60k) | Complete | Management Problem - Inadequate supervision | Completed |  | The contractor highlights the issue of a number of cut down __ HUS-3 cut ends of fixings which have been located within level -2 WTH where the contractors ductwork sub-contractor has been installing ventilation services.
| 02SL - Stations (LUL) | Cxxx-NCR-000920 | NCR | PES lower cable tray fixing protruding below design level |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-10-14 | 2017-10-12 12:48 | -2 | 2017-07-17 12:34 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | After inspecting the PES lower cable tray coupler fixings, the Contractor has identified several locations where the bolt on the underside protrudes below the level of the inverted T. As per Cxxx-LAO-Y-DWG-N105_WS089_5-50156, a nominal 8mm gap is given to prevent components of the CMS falling below the inverted T level.
| 02SL - Stations (LUL) | Cxxx-NCR-000921 | NCR | materials installed with a Code 3 MCR- lifting beams in lifts 7 and 8 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2018-01-31 | 2017-12-11 11:04 | -51 | 2017-07-18 13:40 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | We have installed bolts to install lifting beams for lift shaft 7 and 8 which have not been signed off on MCR Cxxx-LAO-04-XDS-N105_WS089_z-50171
| 02SL - Stations (LUL) | Cxxx-NCR-000922 | NCR | Glazed Cladding materials used in the works at a Code 3 Decal |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2018-05-04 | 2018-05-23 12:19 | 19 | 2017-07-18 15:18 | Architectural - Glazing | 3000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | A planned Surveillance was carried on the Glass Cladding Installation on the 7th July 2017. During the surveillance it was witnessed that 10mm and 12mm Versapanel cement bonded board has been installed in areas of the works by Design Rational Limited (E6 and E7). On checking eB; ‘Versapanel - Cement bonded particle board’ MCR Cxxx-LAO-Y-XDS-N105_WS089_Z-50026 (Rev 3) is at a Code 3 Decal with comments associated concerning LU 1-085 compliance. It was also found that the fixings & sundry items in use for the installation; MCR Cxxx-LAO-Y-XDS-N105_WS089_Z-50024 (Rev 3) was also at Decal Code 3.
| 02SL - Stations (LUL) | Cxxx-NCR-000923 | NCR | WTH Secondary Walls 9, 11 & 12 - Missing Cube Results |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-09-21 | 2017-07-20 08:25 | -63 | 2017-07-19 10:35 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | There are missing cube results for WTH -1 Secondary Walls 9, 11 & 12 poured 04/05/17 using Mix 1C.
| 02SL - Stations (LUL) | Cxxx-NCR-000924 | NCR | Rodding access points - CEG Comments June 2017 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-12-31 | 2017-12-01 13:55 | -30 | 2017-07-19 14:49 | Mechanical - Public Health Engineering | 2000 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | 1)CEG observation - Rodding access points required within installation as per marked up drawings issued by I.Ford. 2) Pipe sleeve required at locations identified on drawings detailed above
| 02SL - Stations (LUL) | Cxxx-NCR-000925 | NCR | GFRC Design Assurance - Non Compliance to PPC Process |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2018-07-27 | 2019-12-12 13:50 | 503 | 2017-09-08 13:01 | Architectural - General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | This NCR is raised to record that the GFRC cladding works have progressed without correct use of the PPC process. Only a number of drawings were made available to the Project Manager for acceptance, instead of all, as is required for category A type activities and was previously followed for earlier phases within the GFRC cladding works. The affected GFRC panels will remain installed at risk until such time as the required assurance deliverables are accepted by the Project Manager. These include checking certificates, drawings and Post Gate Impact Report.
| 02SL - Stations (LUL) | Cxxx-NCR-000926 | NCR | Damaged optical fibre cables x 2 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-01-31 | 2018-12-18 11:35 | -44 | 2017-08-24 13:58 | Communications and Control Systems - Fibre Optic Network | 2000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Two number as installed fibre optic cables have been identified as damaged by __, the cables have been identified as damaged following their testing of the installation. The cabling has been previously handed over to __ undercover of an IRN.
| 02SL - Stations (LUL) | Cxxx-NCR-000927 | NCR | LV Switchboard Location |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-12-31 | 2017-11-15 11:59 | -46 | 2017-08-09 06:57 | Electrical - LV Equipment | 2000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Lack of procedure | Completed |  | The contractor completed the PPC signed MEP design for WTH LV switchroom 2 as identified in the attached Cxxx-LAO-Z-MRC-N105_WS093-50253 PPC reference and drawing Cxxx-LAO-N-DWG-N105_WS089_4-50036 P04. The builders works hole identified in the attached marked (YELLOW Provided by others) was requested to be moved by the contractor to the corner of the room identified (GREEN). The builders work hole was cast (By Others) to allow the transition of the LV busbar system to pass from the transformer room below to the respective LV switchboard. Relocating the builders work hole would have allowed adequate space around the entire panel. The proposal was later rejected by Cxxx due to the importance of the structural steel support beam in the newly proposed location. For this reason the LV switchboard was relocated further away from the wall as identified in red to increase the access and maintenance space around the LV switchboard from roughly 600mm to 1 meter. Access to the high level CMS and SWA cabling will be from the rear of the LV switchboard via approved working at height methods if required in maintenance or new/remedial works.
| 02SL - Stations (LUL) | Cxxx-NCR-000928 | NCR | __ External Louvre Screen Installation |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2018-09-28 | 2018-11-20 16:23 | 53 | 2018-08-14 08:19 | Architectural - Walls | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The external louvre screen installation at the __ room at Block D WTH the extent and the setting out is not as per works information
| 02SL - Stations (LUL) | Cxxx-NCR-000929 | NCR | __’s production process for the manufacture of Granazzo Terrazzo Flooring |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2018-02-23 | 2018-01-18 10:22 | -36 | 2017-11-16 15:59 | Architectural - Flooring | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | It has been identified that no evidence of calibration is in place for the following as part of __’s production process for the manufacture of Granazzo Terrazzo Flooring on Crossrail: • Volumetric measuring of constituent materials for batching • Dimensional measuring tools • SRV testing equipment Calibration should be carried out as part of an ISO 9001 Quality Control System where calibration of equipment will have an affect on the end product. ISO 9001 clause 7.1.5.2 states: “When measurement traceability is a requirement, or is considered by the organization to be an essential part of providing confidence in the validity of measurement results, measuring equipment shall be: a) calibrated or verified, or both, at specified intervals, or prior to use, against measurement standards traceable to international or national measurement standards; when no such standards exist, the basis used for calibration or verification shall be retained as documented information” Furthermore the Works Information requires this under Part 20.8: “The Contractor shall maintain a schedule of all inspection, measuring and test Equipment used for the works that includes records of the calibration of such Equipment to nationally recognised standards.” In addition, __ does not hold accreditation (UKAS equivalent) for the Slip Resistance testing being completed and reported from the factory. Works Information 20.8 further requires: “All on-site and off-site testing shall be carried out by laboratories accredited by UKAS or similar, acceptable national body or by persons accredited to a similar standard.” With this lack of evidence, the composition of the Crossrail manufactured tiles cannot be confirmed as in alignment with that which formed part of the ‘Declared Performance’ testing as part of the CE Marking process to EN 13748-1 which was completed/declared by __ in 2014. Furthermore, the testing and dimensional analysis being conducted throughout production batching cannot be confirmed as acceptable based on the lack of calibration evidence for the equipment used. No Crossrail acceptance currently exists for __s’ reduced Quality systems/checking processes.
| 02SL - Stations (LUL) | Cxxx-NCR-000930 | NCR | Torqueing activity and associated parameters omitted from ITP and Checksheet for Internal Glass Steelwork Installation. Torque values used not supplied by __. |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2018-07-31 | 2019-04-26 07:13 | 269 | 2017-08-24 14:37 | Architectural - Glazing | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | A planned Crossrail surveillance was undertaken on 07th July 2017 to look at onsite installation of the Internal Glass Steel Support System at TCR Station. During the site visit torqueing of the fixings was discussed. It was stated by __ that the fixings (size dependant) had been/are tightened in accordance with the relevant technical data sheet requirements (was stated __ at time of surveillance however __ now noted that __ anchors used). Two areas were sampled, WTH Level -2 and GYB Level -4, to enable a check of the records associated with this activity to show evidence that it had been completed/checked. On checking the Installation ITP (Cxxx-LAO-Y-ITP-N105_WS093_Z-50001) it was identified that it did not include torqueing as an activity, including the parameters as defined. Furthermore, on checking the __ checksheets, it was also identified that they did not include a check item for torqueing of the fixings into the concrete structure. Based on this, no evidence exists assuring that torqueing has been completed, and to the correct values stipulated by the manufacturer for each type fixing, for all installed sections to date. Works Information Vol 2B Part 20.8 states; “The Contractor … shall maintain ITPs for the services they provide” … “These ITPs shall stipulate the necessary level and frequency of tests and inspection for each aspect of the works” … “The Contractor shall conduct inspections and tests in accordance with his details ITPs … which shall include activities of structural or operations, significance, and inspections which are of a subjective nature or release work that is to be covered up.” In addition to this, following multiple post surveillance requests to both __ and __ for the torque value used for the M8, M12 and M16 anchors, nothing was provided. As such it is not actually known what torque values have been applied and whether this torque application is in fact compliant with the manufacturer’s data. As no records exist, this information is not documented. This lack of evidence and supply of information puts at risk the installation of the support steelwork.
| 02SL - Stations (LUL) | Cxxx-NCR-000931 | NCR | __ Internal Glass Steelwork structural calculations completed using __ software/data where __ resin anchor system used; also contradictions from __ as to what fixings have been used in the works |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2018-06-25 | 2019-04-17 09:50 | 296 | 2017-08-24 14:40 | Architectural - Glazing | 5000 |  | Design | Use As-Is | 3 (3-6k) | Complete | Management Problem - Inadequate supervision | Completed |  | A planned Crossrail surveillance was undertaken on 07th July 2017 to look at onsite installation of the Internal Glass Steel Support System at TCR Station. During the surveillance, the fixing details were discussed. It was noted by __ at the time that __ anchors had been used with a __ resin. Based on this arrangement, post surveillance __ was contacted to discuss the use of their fixings with another non __ resin product. It was confirmed that __ could not assure nor guarantee any arrangement that uses a mix of __ and non __ products. Based on this, as part of the Exit Note, the Structural Calculations were requested for the steelwork. Nothing was provided. Following this, it was then noted by __ and __ that __ fixings had in fact not been used with __ anchors and __ resin used. Based on this, and the inconsistencies regarding the fixing products used, the Structural Calculations were again requested to provide clarification on what product information had been used to assure the support system. On 23/08 it a response was received from __ and __ which stated: a) that the structural calculations had been made using __ software and data b) that the evidence of calculations could not be provided due to confidentiality It is unsure why the calculations could not be provided to assure that the steelwork system can support the loads being parted on it by the Glass Cladding panels. However, as (based on the statement from __) the calculations have been carried out based on __ data and not __ it can not be confirmed that the calculations are correct. It should be confirmed what fixing system has been used in the works, and calculations submitted reflecting the system installed.
| 02SL - Stations (LUL) | Cxxx-NCR-000932 | NCR | No MCR for __ Anchors and __ V420 Resin forming part of __ Internal Glazing |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2017-11-17 | 2017-11-21 17:12 | 4 | 2017-08-24 14:43 | Architectural - Glazing | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | A planned Crossrail surveillance was undertaken on 07th July 2017 to look at onsite installation of the Internal Glass Steel Support System at TCR Station. Referring to Cxxx-NCR-000931, __ stated that they had used __ Anchors and __ Resin installed into the concrete structure to support the steelwork. An MCR was requested for this system. Following multiple requests, no MCR was provided for the __ Anchors. An MCR was provided for the __ Resin, Cxxx-LAO-O4-LRC-N105_WS089_Z-50053 refers. However on review, this had been submitted in 2014 and covered ‘post fixing reinforcement and temporary works anchorage’. This was not submitted for __ works, and as such has not been assessed based on this use.
| 02SL - Stations (LUL) | Cxxx-NCR-000933 | NCR | Damage to Door D2-4/012 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-12-03 | 2017-12-07 13:18 | 4 | 2017-08-25 08:14 | Architectural - Doors | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Damage has occurred to the top of the door frame to Door D2-4/012 - see attached photos. The faces of the door and ironmongery are protected but as the door requires to be closed when not required for access, the door frame is unable to be protected. The damage has occurred when the door has been open and materials carried through.
| 02SL - Stations (LUL) | Cxxx-NCR-000934 | NCR | EWS 416a recon stone cladding out of tolerance |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2018-05-18 | 2018-04-17 14:20 | -31 | 2017-09-05 07:14 | Architectural - Walls | 500 |  | Manufacturing Defect | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Pointed panel adjacent to floor slab out of tolerance and non compliant with Cxxx-LAO-A-RSP-N105_WS089-50001 JH42.3301. Located on internal east facing elevation of WTH escalator drop at level-1
| 02SL - Stations (LUL) | Cxxx-NCR-000935 | NCR | 200 dia pipe rerouted WTH L-5 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-11-24 | 2017-12-05 15:38 | 11 | 2017-09-08 08:07 | Materials - General | 2000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | There appears to be rework on level -5 WTH. An additional hole has been drilled and the 200 dia pipe has been rerouted through the new hole.
| 02SL - Stations (LUL) | Cxxx-NCR-000936 | NCR | Escalator Floor Plates Level interface with Terrazzo |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2018-08-06 | 2018-12-10 14:14 | 126 | 2017-09-11 11:27 | Mechanical - Escalators | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | NCR: Level Tolerance of East Ticket hall Escalator Floor plates relative to existing floor finished. __ have cast the escalator support plinths exactly as shown on the __ builderswork drawings. (Reference __ pre-start survey for evidence if requierd) __, however were unable to install the escalators to achieve the correct FFL at the top landing, and as a result, the top landing plates are within 2mm of each other, as requried in the Pan TfL specification, but are not within 2mm of the designed adjacent floor levels. Specification references: Pan TfL Specification Part 2 SPC-LAE-301941170 Part 2 Clause 19.14: Floor plates shall be accurately levelled to within 2mm of each other and adjacent flooring. Cxxx Architectural Specification: Cxxx-LAO-A-RSP-N105_WS089-50001 JC20.1102, JM41.1213 BS 5385-5: 3mm local variation under a 2mm straight edge.
| 02SL - Stations (LUL) | Cxxx-NCR-000937 | NCR | Louvred __ Doors MCR |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2018-11-16 | 2018-12-04 09:44 | 18 | 2017-09-13 06:04 | Architectural - General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | __ louvred doors have been installed ay __ sub station. MCR was not in place at time of installation
| 02SL - Stations (LUL) | Cxxx-NCR-000938 | NCR | Installation of Incorrectly sized CMS |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-09-30 | 2019-07-15 15:48 | -77 | 2017-09-15 14:40 | Electrical - Cable Management | 1200 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | GYB AP8 Level -4 corridor, installation of incorrectly sized CMS. The CMS has been installed against a sketch showing 75mm tray when site inspected against the newly issued PPC CMS tray is identified as 100mm. Submains cabling and associated earth are installed on the tray.
| 02SL - Stations (LUL) | Cxxx-NCR-000939 | NCR | Inconsistent Outer Radii of External Curtain Wall Mullions by __ |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-01-31 | 2019-01-24 11:29 | -7 | 2018-12-13 09:39 | Architectural - Glazing | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Other | Completed |  | The contractor reports an inconsistent outer radius on the curtain wall mullions installed by __ on the Block D curtain walling.
| 02SL - Stations (LUL) | Cxxx-NCR-000941 | NCR | Construction PPC drawings found on site without PPC signature. |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-12-24 | 2017-11-07 18:53 | -47 | 2017-09-25 14:30 | Electrical - Cable Management | 2000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Unauthorised drawings i.e. no signature on PPC found on site in GYB vent tower L+0 and WTH CIR-s 2/241 L-1.
| 02SL - Stations (LUL) | Cxxx-NCR-000942 | NCR | __ & __ ATS |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2018-06-30 | 2018-07-24 12:51 | 24 | 2017-09-29 08:51 | Electrical - Switchgear | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | __ (Lifts ) ATS should be dual output which is shown within the spec requirement, what has been installed onsite was a single output ATS. __ ( Escalator ) ATS required sub boards are missing. Correct installation has been PPC'd, PPC number is Cxxx-LAO-Z-MRC-N105_WS089-50509.
| 02SL - Stations (LUL) | Cxxx-NCR-000943 | NCR | AP1 & AP2 Radial GFRC Panels Manufactured Incorrectly |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2018-05-31 | 2018-05-24 14:16 | -7 | 2017-09-29 17:16 | Architectural - General | 0 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Sixteen panels in AP2W and AP1W have been made incorrectly and will need to be re-cast. This occurred due to a problem with the moulds. Twelve of the panels are in AP2W and four of the panels are in AP1W. The panels in AP1W will actually be installed, however, due to an unacceptable step will need to be replaced at a later date. See the screenshots of the affected panels attached.
| 02SL - Stations (LUL) | Cxxx-NCR-000944 | NCR | Rectilinear GFRC Panels Manufactured Incorrectly |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2018-05-31 | 2018-05-24 14:14 | -7 | 2017-10-06 15:49 | Architectural - General | 0 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | 18no. panels in AP8 have been manufactured incorrectly which prevent the panels from being installed. 6no. are missing face fixings and the other 12no. have been manufactured too small.
| 02SL - Stations (LUL) | Cxxx-NCR-000946 | NCR | Scratch to chiller paint GYB |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2018-03-31 | 2019-09-24 12:27 | 542 | 2017-10-05 14:01 | Mechanical - Heating Ventilation & Air Conditioning | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Personnel Error - Not Defined | Completed |  | scratch to side panel of chiller was witnessed within GYB site Level 2 chiller plant room.
| 02SL - Stations (LUL) | Cxxx-NCR-000947 | NCR | Failed Drop Hammer Test |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-11-30 | 2017-12-01 15:19 | 1 | 2017-10-09 09:48 | Civil - Base Course | 1000 |  | Material | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Screed drop hammer testing has been carried out progressively. On the drop hammer witness test within PTE (Between AP4 and AP3), one area failed the drop hammer test
| 02SL - Stations (LUL) | Cxxx-NCR-000948 | NCR | Lighting system wired without CMS IRF sign off |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-04-30 | 2019-04-25 17:12 | -5 | 2017-10-09 14:17 | Electrical - Lighting | 2500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Lighting wired without CMS being inspected and IRF sign off.
| 02SL - Stations (LUL) | Cxxx-NCR-000949 | NCR | CMS installed for General Lighting and Emergency Lighting CCT routes merging within Junction Box transitions, which would result in cross contamination of Norm/Emergency CCTS |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-02-14 | 2019-02-07 17:41 | -7 | 2017-10-09 14:25 | Electrical - Cable Management | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | CMS installed for General Lighting and Emergency Lighting CCT routes merging within Junction Box transitions.
| 02SL - Stations (LUL) | Cxxx-NCR-000950 | NCR | Tunnel Fire main pipework |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2018-01-07 | 2017-12-08 15:40 | -30 | 2017-10-09 14:42 | Mechanical - Hot & Cold Water Supplies | 2000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | 3 flexible couplings (model GR8LOK 8000) installed at GYB -5 without MCR.
| 02SL - Stations (LUL) | Cxxx-NCR-000951 | NCR | Working without a PPC drawing |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-03-31 | 2019-01-09 12:37 | -81 | 2017-10-09 16:57 | Electrical - Cable Management | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Site CMS installation proceeding on site without a signed PPC drawing.
| 02SL - Stations (LUL) | Cxxx-NCR-000953 | NCR | Riser 4 Modifications to CMS |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2018-12-21 | 2018-12-12 09:41 | -9 | 2017-10-10 07:09 | Electrical - Cable Management | 1000 |  | Design | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | CMS Cable Tray Modified within Riser 4
| 02SL - Stations (LUL) | Cxxx-NCR-000954 | NCR | Potential inaccessible MFD |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2018-10-28 | 2018-08-16 08:59 | -73 | 2017-10-10 07:19 | Mechanical - Heating Ventilation & Air Conditioning | 5000 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Potential inaccessible MFD level -1 into AER Room number 2/766
| 02SL - Stations (LUL) | Cxxx-NCR-000955 | NCR | Potentially inaccessible MFD |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2018-01-08 | 2017-12-08 15:51 | -31 | 2017-10-10 07:24 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Potentially inaccessible MFD at WTH Level -1 ductwork into Riser 2/907
| 02SL - Stations (LUL) | Cxxx-NCR-000956 | NCR | Potential inaccessible MFD |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2018-09-28 | 2018-09-24 07:45 | -4 | 2017-10-10 07:33 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Potential inaccessible MFD
| 02SL - Stations (LUL) | Cxxx-NCR-000957 | NCR | Potentially inaccessible MFD |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2018-03-25 | 2018-01-31 10:50 | -53 | 2017-10-10 07:38 | Mechanical - Heating Ventilation & Air Conditioning | 3000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Potentially inaccessible MFD
| 02SL - Stations (LUL) | Cxxx-NCR-000960 | NCR | WTH Vent Shaft Level +1 to +5 - 225mm core through slab for fire hydrant |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-11-13 | 2017-11-06 16:47 | -7 | 2017-10-10 16:09 | Civil - Civil Engineering General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | __ have cored a 225mm core through the vent shaft slab in the main stairwell.
| 02SL - Stations (LUL) | Cxxx-NCR-000961 | NCR | Metal fillings located within ATS |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2018-12-31 | 2018-12-19 15:51 | -12 | 2017-10-11 10:57 | Electrical - Power Distribution | 1500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Metal fillings located within ATS Ref SW/P E01
| 02SL - Stations (LUL) | Cxxx-NCR-000962 | NCR | Relocation of Smoke Extract Ductwork |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2018-06-29 | 2018-05-29 08:53 | -31 | 2017-11-02 15:06 | Mechanical - Heating Ventilation & Air Conditioning | 0 |  | Design | Rework | 4 (0.5-3k) | Complete | External Phenomenon - External fire or explosion | Completed |  | Rework required to relocate the 1700 x 700 smoke extract duct that is shown in the attached photograph (although somewhat hidden by a number of pipes and other ducts that have been installed beneath it). The duct needs to be removed and repositioned to allow the fire stopping to be installed, as at present the duct is tight to the side of the builders-work opening.
| 02SL - Stations (LUL) | Cxxx-NCR-000963 | NCR | PES bump stop thread protrusion |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2018-10-31 | 2018-10-19 13:20 | -12 | 2017-10-13 15:01 | Architectural - General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | While inspecting the PES architectural works, CRL raised issue with the lower grille bump stops, which are fixed to the grille posts by a threaded rod in an 8mm deep insert. The bump stops are adjusted to the appropriate distance from the steelwork in order to line the grilles. Because of this adjustment, there are some instances where the threaded rod does not protrude through the other side of the 8mm insert. The post drawing (Cxxx-LAO-Y-DWG-N105_WS089_5-50152) shows a slight protrusion.
| 02SL - Stations (LUL) | Cxxx-NCR-000965 | NCR | Non compliant finish of BAL112 WTH +0 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-11-17 | 2017-11-20 16:20 | 3 | 2017-10-16 11:06 | Architectural - Balustrade | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | The polished finish of the WTH S/S glass track does not meet the standard of the benchmark in GYB -1.
| 02SL - Stations (LUL) | Cxxx-NCR-000966 | NCR | WTH -4 Failed Drop Hammer Test |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-11-15 | 2017-12-04 14:28 | 19 | 2017-10-18 13:01 | Architectural - Flooring | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Screed in WTH -4 failed drop hammer test. See mark-up area attached. Screed is to be borken out, re-laid and re-inspected.
| 02SL - Stations (LUL) | Cxxx-NCR-000967 | NCR | PAVA wiring commenced in CMS within IRF Sign Off |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2018-02-15 | 2018-02-06 16:25 | -9 | 2017-10-17 12:28 | Electrical - Cable Management | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other management problem | Completed |  | PAVA wiring commenced in CMS within IRF Sign Off GYB -2 Corridor CIR-S 3/243 & 3/244
| 02SL - Stations (LUL) | Cxxx-NCR-000968 | NCR | BMS - Panels (Non-life safety) delivered to site with MCRs still to be submitted |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2018-11-30 | 2018-08-09 14:50 | -113 | 2017-10-23 14:20 | Communications and Control Systems - General | 1000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | It was identified at the BMS panel FAT test that certain materials used in the MCCs had not yet been covered by an MCR. The situation and materials were highlighted by the Subcontractor at the FAT test to flag the issue. The materials were discussed with CRL (__) and following review it was agreed this was a low risk as materials were from reputable suppliers, were low smoke/ zero halogen and & CE marked where applicable. It was agreed that the panels should be delivered to site and MCRs would be submitted as soon as possible.
| 02SL - Stations (LUL) | Cxxx-NCR-000969 | NCR | Pipework requiring rerouting for access |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2018-01-31 | 2018-01-29 17:30 | -2 | 2017-10-27 14:13 | Mechanical - Piping | 3100 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | WTH AHU connection chilled water pipework to be reworked to enable access to the Cooling Coil
| 02SL - Stations (LUL) | Cxxx-NCR-000970 | NCR | Chilled water pipework not installed in accordance with __ schematic |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-12-26 | 2017-12-05 15:57 | -21 | 2017-10-27 14:19 | Mechanical - Piping | 2000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | GYB Chilled water Low Loss header not installed in accordance with __ schematic and installation has minor differences with the installation drawings.
| 02SL - Stations (LUL) | Cxxx-NCR-000971 | NCR | Incorrect hydrant valves installed in station risers. |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-12-26 | 2017-12-19 16:22 | -7 | 2017-10-27 14:36 | Fire - Fire Systems & General | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | Incorrect hydrant valves installed in station risers.
| 02SL - Stations (LUL) | Cxxx-NCR-000972 | NCR | Fire partion not maintained around hydrant box. |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2018-07-31 | 2018-10-17 15:24 | 78 | 2017-10-27 14:42 | Fire - Fire Systems & General | 10000 |  | Material | Rework | 2 (6-60k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | Fire partion not maintained around hydrant box.
| 02SL - Stations (LUL) | Cxxx-NCR-000973 | NCR | Draindown valves and isolation valves in station fire main |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-12-26 | 2017-12-05 15:43 | -21 | 2017-10-27 14:55 | Fire - Fire Systems & General | 2000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Draindown valves and isolation valves in station fire main -4 need to be swapped round .
| 02SL - Stations (LUL) | Cxxx-NCR-000975 | NCR | Damage to a cladding panel of AHU W4 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-06-30 | 2019-01-28 11:27 | -153 | 2017-10-27 15:25 | Mechanical - Heating Ventilation & Air Conditioning | 2000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Damage to a cladding panel of AHU W4.
| 02SL - Stations (LUL) | Cxxx-NCR-000976 | NCR | Damaged MFD |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2018-10-26 | 2018-10-30 12:10 | 4 | 2017-10-27 15:30 | Mechanical - Heating Ventilation & Air Conditioning | 1500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | Lobby 5/100 MFD. Damper previously installed in a non-compliant orientation and to achieve this drilled a pair of holes in the damper case for a support fixing.
| 02SL - Stations (LUL) | Cxxx-NCR-000978 | NCR | Ductwork installation proceeding without PPC |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-12-26 | 2017-12-19 10:23 | -7 | 2017-10-27 15:43 | Mechanical - Heating Ventilation & Air Conditioning | 3000 |  | Design | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Ductwork installation proceeding without PPC within north end of ticket hall outside of water mist room
| 02SL - Stations (LUL) | Cxxx-NCR-000979 | NCR | GYB Substructure - -1 cladding line (NOT SITE MEASURED) |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-11-30 | 2017-12-05 16:45 | 5 | 2017-10-27 15:58 | Architectural - Glazing | 0 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Previous Construction - Interfacing issues | Completed |  | __ have installed wall cladding on E2 and E3 up to the Crossrail/LU demarcation line. The final panel should have been a site measure to align with the TCRSU designed bulkhead. Due to the panel already having been installed the bulkhead has been matched to this line and therefore leaving a larger gap between the builkhead glazing and the acoustic baffles.
| 02SL - Stations (LUL) | Cxxx-NCR-000980 | NCR | Management of CTU process for lift 11 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2018-01-31 | 2018-02-01 17:46 | 1 | 2017-10-30 07:02 | Mechanical - Lifts | 2500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Call Out; 13/10/2017 Attending __ staff; C. Power Grade; Infrastructure Technician Fault identified; Attended following Entrapment event 12/10/2017. Witnessed damage to Exit Door mechanism at Top Level 9/Ground. Root cause of damage is misuse with the Lift car being misaligned by overloading with point loads. Established that Two Tonne cable drums are being transported in lift car. Rated load for lift use is with even distribution of load/passengers throughout car. Movement of materials is routinely permissible at a maximum of 25% lift rated load to prevent point loading discrepancy/misalignment of lift car. The movement of materials /overloading is causing misalignment of the lift car in travel with damage resulting to Lift Car Door Operator and landing lock assemblies. Made temporary repairs. Parts on order and requires additional attendance to repair with new parts and undertake full lift car and shaft survey/check for any resulting damage to the installation.
| 02SL - Stations (LUL) | Cxxx-NCR-000981 | NCR | Utilising HUS fixings within the concrete block in the WTH EER |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2018-07-31 | 2018-12-04 09:48 | 126 | 2017-10-30 07:19 | Materials - General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | HUS fixings have been utilized by __ within the concrete block in the WTH EER
| 02SL - Stations (LUL) | Cxxx-NCR-000982 | NCR | Blockwork - Incorrect Installation WTH -1 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-11-29 | 2017-12-08 09:36 | 9 | 2017-11-01 07:44 | Architectural - Masonary | 2000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | On 28/10/2017 the door reveal around door D2-2/035 was installed to an incorrect height. The reveal on attached drawing (Cxxx-LAO-DDD-N105_2-22006) was built up to the soffit. Upon review it is aparant that the returns are to be built up to door height (2.260m) with a concrete slab as a lid.
| 02SL - Stations (LUL) | Cxxx-NCR-000983 | NCR | Blockwork - Removal of 3No. Lintels and blocwork WTH -4 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-11-28 | 2017-12-08 09:37 | 10 | 2017-11-01 07:53 | Architectural - Masonary | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The main contractor took the decision to remove the lintels and blockwork above doors D2-5/025, D2-5/024 & D2-5/022. This decision was made due the doors not fitting in the structural opening. At this point in time (01/11/2017) the main contractor is undecided on the detail above the permement doors in this area.
| 02SL - Stations (LUL) | Cxxx-NCR-000984 | NCR | Blockwork - Incomplete Quality Packs - No Mortar Results |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-11-29 | 2017-12-04 14:30 | 5 | 2017-11-01 08:03 | Architectural - Masonary | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Construction Quality Packs for WTH -1 and GYB -5 were submitted the Project Manager with insufiienct mortar test evidence. Both packs have out dated mortar results and were not rectified as per the project managers request.
| 02SL - Stations (LUL) | Cxxx-NCR-000985 | NCR | LV System Identification |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-10-31 | 2021-03-31 08:09 | 517 | 2017-11-06 10:46 | Electrical - Power Distribution | 2500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Non compliance with Works Information JY82.1309 and response to RFI 001289 and 001622.
| 02SL - Stations (LUL) | Cxxx-NCR-000986 | NCR | WTH Level -2 Tiling Layout |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2018-02-08 | 2017-12-20 05:55 | -50 | 2017-11-10 12:09 | Architectural - Flooring | 0 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | The WTH Level -2 tiling along the PRM corridor has been laid between gridlines 4 to 6 offset from design by 200mm in a northerly direction.
| 02SL - Stations (LUL) | Cxxx-NCR-000987 | NCR | Speaker Housing Sign Font |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2018-10-24 | 2018-12-03 11:17 | 40 | 2017-11-10 14:49 | Systems - Signage | 2000 |  | Material | Rework | 4 (0.5-3k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | Speaker Housing; The ‘Please Stand on the Right’ font is incorrect and inconsistent across all speaker housings. First identified at site inspection with __ Quality Manager 25/9/17. __ are required to identify how the error occurred, how and when it will be resolved.
| 02SL - Stations (LUL) | Cxxx-NCR-000988 | NCR | Recess for Escalator Light Fitting |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2018-06-15 | 2018-08-07 08:21 | 53 | 2017-11-10 14:55 | Electrical - Lighting | 2000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | The recess provided for the escalator deck light has a stainless steel shelf for the light carcass to sit on. This angle should be between 25 and 27mm as confirmed on site 7/11/17 by CEG (__, __) and Future Designs (__). The as built angle is between 25mm and 35mm, therefore where the stainless steel protrudes more than 27mm, the stainless steel needs to be cut back. These works need to be carried out by a specialist subcontractor taking as the top decking sheet cannot be damaged and the flatness of the decking needs to be maintained.
| 02SL - Stations (LUL) | Cxxx-NCR-000989 | NCR | Crossover of electrical secondary CMS from primary trunking |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-04-30 | 2019-01-09 11:25 | -111 | 2017-11-13 15:42 | Electrical - Cable Management | 1000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Electrical secondary CMS (conduit) installed from incorrect compartment of primary trunking CMS crossing over general and emergency lighting within the Vent Shaft levels +3, +2 & +1.
| 02SL - Stations (LUL) | Cxxx-NCR-000990 | NCR | Lift DMI's |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2018-09-21 | 2018-12-03 11:09 | 73 | 2017-11-16 12:40 | Mechanical - Lifts | 2000 |  | Material | Rework | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | The DMI's installed on the Lift Fronts on PRM Lift 7 are he standard __ DMI's, not glass as required by the Pan TfL Specification. Therefore need to be replaced.
| 02SL - Stations (LUL) | Cxxx-NCR-000991 | NCR | WTH - Core 4. -5 precast stair upstand location |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2018-02-13 | 2017-11-23 15:02 | -82 | 2017-11-15 18:24 | Civil - Civil Engineering General | 3000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | The structural up stand on -5 (north side of) Core 4 has been constructed as per Cxxx-OVE-S-DDC-N105_Z-22152 Rev C01. __ has produced the precast stairs as per Cxxx-OVE-A-DDD-N105_Z-20909 Rev C01. As a result of the discrepancy between the two Cxxx drawings the up stand location does not correspond with the required location to land the precast stair unit.
| 02SL - Stations (LUL) | Cxxx-NCR-000992 | NCR | Incorrect installation of six compartment in situ floor trunking |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-04-18 | 2019-04-12 08:50 | -6 | 2017-11-17 14:40 | Electrical - Cable Management | 0 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | In situ 6 compartment metal trunking fixed directly to the exposed slab without a supporting bed of compound.
| 02SL - Stations (LUL) | Cxxx-NCR-000993 | NCR | WTH -4 Missing Movement Joint within Screed & Tiling |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2018-10-31 | 2018-11-09 10:20 | 9 | 2017-11-21 11:18 | Architectural - Flooring | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | A movement joint has been missed within the screed and tiling on WTH Level -4 as shown on the attached marked up sketch.
| 02SL - Stations (LUL) | Cxxx-NCR-000994 | NCR | PTE East End Movement Joint Misalignment within Tiling |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2018-09-30 | 2018-11-23 15:39 | 54 | 2017-11-21 11:28 | Architectural - Flooring | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | As can be seen within the attached photo, the transverse movement joint across PTE platform abuts the access hatch frame instead of running along its edge, as detailed on the design drawings.
| 02SL - Stations (LUL) | Cxxx-NCR-000995 | NCR | WTH Level +1 Edge Beam and Column Coring |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2018-03-29 | 2017-12-19 10:37 | -100 | 2017-11-29 12:41 | Civil - Civil Engineering General | 5000 |  | Incorrect Installation | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | It has been identified that coring into the WTH Block C +1 edge beam and WTH station entrance +0 to +1 columns has occurred for fixing of cladding elements. A presentation is attached identifying the areas of coring and potential clashes with reinforcement. The areas identified where coring has occurred are as follows: WTH station entrance +1 edge beam soffit for the downstand glazing screen and cladding windposts: - 19No 30mm diameter, 203mm long cores, 250mm from inside face of GL E edge beam into soffit for downstand glazing screen. - 6No 24mm diameter, 200mm long cores into each column either side of the station entrance for downstand glazing screen. - 8No 14mm diameter, 110mm long cores, in a 150mm 2x2 grid 85mm from inside face of GL E edge beam into soffit for cladding windposts. WTH GL A & 6 +1 edge beam (outside face) for rainscreen cladding: - Max 40No 18mm diameter cores, 130mm long, 100mm from bottom of edge beam into outside face of GL 6 & A edge beam. - Max 32No 24mm diameter cores, 180mm long, in a 100 x 250mm 2x2 grid 100mm from bottom of edge beam into outside face of GL A edge beam. For the rainscreen cladding both drilling and coring was carried out, however the total number of fixings has been assumed to be cored.
| 02SL - Stations (LUL) | Cxxx-NCR-000997 | NCR | WTH - Core 4 - Spine wall and landing making good |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2018-02-27 | 2018-02-01 12:16 | -26 | 2017-11-29 13:51 | Civil - Civil Engineering General | 3000 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Due to an error that wasn't spotted on the BOD for the pre-cast spine walls, they have been manufactories to the same dimension as the distance between the landings. Taking into account tolerances for the pre-cast and in situ works, a number of the walls and 3No. landings required breaking to allow them to be installed. Please see attached marked up drawings detailing spine walls and landings for repair.
| 02SL - Stations (LUL) | Cxxx-NCR-000998 | NCR | Addition VCD's to be cut into Ventilation systems site wide, missed at design stage |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-02-28 | 2019-03-13 09:20 | 13 | 2017-11-30 10:50 | Mechanical - Heating Ventilation & Air Conditioning | 5000 |  | Supervision/Management | Rework | 3 (3-6k) | Complete | Management Problem - Inadequate supervision | Completed |  | There are multiple volume control dampers (VCDs) shown on the updated/current schematic drawings but are missing from the installation in the WTH and GYB. Refer to the attached marked-up plant ventilation schematics for details. In addition to the VCDs shown on the attached plant vent schematics, there are two further VCDs missing from the AHU W4 installation as recorded in IRF-299 (corridor 3/241) and IRF 280 (store room 3/413).
| 02SL - Stations (LUL) | Cxxx-NCR-000999 | NCR | __ Terrazzo Flooring - 'P' Status Drawings |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2018-12-31 | 2018-12-18 11:34 | -13 | 2017-11-30 10:55 | Architectural - Flooring | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | The Main Contractor is laying flooring to P Status Drawings. Drawings should be at C Status for construction and handover.
| 02SL - Stations (LUL) | Cxxx-NCR-001000 | NCR | VCD's - Air Release Systems |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2018-07-31 | 2018-10-10 12:08 | 71 | 2017-11-30 10:56 | Mechanical - Heating Ventilation & Air Conditioning | 6000 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | On the latest schematic for the air release system in WTH, the designer has incorporated VCD's to be installed on each branch. These are required and need to be installed. Designer to update GYB in line with requirements. VCD's are also required in GYB.
| 02SL - Stations (LUL) | Cxxx-NCR-001001 | NCR | VCD's on Smoke Extract System Site wide |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2017-12-28 | 2017-12-14 16:15 | -14 | 2017-11-30 11:00 | Mechanical - Heating Ventilation & Air Conditioning | 3000 |  | Design | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | VCD's are installed on site on the smoke extract systems, these are not required and need to be removed from the design drawings and install on site. Please refer to RFI-1871.
| 02SL - Stations (LUL) | Cxxx-NCR-001002 | NCR | WTH GL A Waling Beams and Capping Beam Coring for Recon Stone Support Steelwork Fixings |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2018-04-06 | 2017-12-19 10:41 | -108 | 2017-12-07 17:03 | Civil - Civil Engineering General | 5000 |  | Incorrect Installation | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | It has been identified that coring into the WTH GL A waling beams and capping beam has occurred for fixing of recon stone steelwork fixings. The majority of holes were drilled, however a number of drilled holes did not reach the required depth due to clashing with reinforcement. In these instances a request was put in for coring to achieve a required depth of 150mm. A presentation is attached identifying the areas of coring and potential clashes with reinforcement. The areas identified where coring has occurred are as follows: - Level -2 Waling Beam: Total 14No 16mm diameter cores, 150mm long. 8No into the soffit and 6No into the top of the waling beam. - Level -1 Waling Beam: Total 13No 16mm diameter cores, 150mm long. 9No into the soffit and 4No into the top of the waling beam. - Level +0 Capping Beam: Total 28No 16mm diameter cores, 150mm long. 15No into the soffit and 13No into the top of the capping beam. The location of each core is still to be determined, however it is clear from photos taken at the time that the cored holes are in both the inside and outside line of holes. Potential reinforcement cored through is: B32 side bar NF4 B25 bottom bar B2 B25 top bar T2 B20 link bar (waling beam) / B12 link bar (capping beam)
| 02SL - Stations (LUL) | Cxxx-NCR-001003 | NCR | Lack of approved PPC for Urban Realm Paving |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2018-02-12 | 2018-02-27 19:44 | 15 | 2017-12-18 12:04 | Civil - Landscaping | 500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | Paving works to Dean Street South Western footway commenced without an agreed and signed off PPC in place.
| 02SL - Stations (LUL) | Cxxx-NCR-001004 | NCR | Bracket deflection on fire mains |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2018-09-28 | 2018-12-04 10:08 | 67 | 2017-12-20 13:09 | Fire - Fire Systems & General | 50000 |  | Incorrect Installation | Rework | 2 (6-60k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Deflection of fire main pipe work brackets due to thrust from pressure testing to the requied test pressure. Several type A brackets on droprods have had minimal deflection, the submitted calculations have identified a type A bracket as not suitable for thrust from 90 degree bends. This has happened in the following areas: WTH 200 dia level -5 near Westbound entrance WTH 200 dia level -5 near S4 tunnel GYB 150 dia West tunnel east end GYB 150 dia near AP8
| 02SL - Stations (LUL) | Cxxx-NCR-001007 | NCR | Faulty LED boards in PES lightboxes |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2018-06-28 | 2018-05-29 15:14 | -30 | 2018-01-04 14:12 | Electrical - Lighting | 5000 |  | Manufacturing Defect | Repair | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | When the Contractor tested the PES lightboxes, several defects were noticed. The defects were: some LED boards not working, a chessboard effect, and differences in brightness between LED boards.
| 02SL - Stations (LUL) | Cxxx-NCR-001008 | NCR | Gas suppression design Argonite / Inergen |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-04-30 | 2019-02-21 10:21 | -68 | 2018-01-05 14:19 | Mechanical - Mechanical Engineering General | 5000 |  | Design | Reject | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | __ Design drawings Cxxx-LAO-O9-DWG-N105_WS093_5-50006 / Cxxx-LAO-O9-DWG-N105_WS089_5-50008 Identify IG-55 Argonite as the suppressant. PMI-199 (CRL1-XRL-E1-RGN-CR001-50007 ) requires Inergen IG-541 suppressant. Non-compliance with PMI-199 will now result in rework and possible delay.
| 02SL - Stations (LUL) | Cxxx-NCR-001009 | NCR | AP8 - non metalic Tunnel fire main section -not co-ordinated with Cxxx |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-09-01 | 2019-08-30 15:20 | -2 | 2018-01-05 14:23 | Electrical - General | 2000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | Detailed arrangement and co-ordination of non-metallic tunnel fire main section in AP8 was agreed with __ (TCR Lead Electrical FAE), __ (EM for Cxxx) and __(Cxxx design co-ordinator). The pipework fitters installed to an alternate detail that will now require re-work to correct. The pipework cannot be left as is.
| 02SL - Stations (LUL) | Cxxx-NCR-001010 | NCR | Foam Concrete - Density results from pour 1, CL1 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2018-03-14 | 2018-01-19 12:29 | -54 | 2018-01-17 08:16 | Structural Engineering - Concrete Member | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Due to an issue with the batching plant at Kings Cross, foam concrete supplied to Tottenham Court Road was higher than the required density of 1850kg/m3 on pour 1. Later loads in the pour showed lower density but a number of loads were above the required figure. Pour History record attached refers.
| 02SL - Stations (LUL) | Cxxx-NCR-001011 | NCR | Foam Concrete - Pour History Records for CL1 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2018-03-14 | 2018-01-18 12:44 | -55 | 2018-01-17 11:30 | Structural Engineering - Concrete Member | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | The Contractor does not have a full records available for the foam concrete pours in CL1 and the first stage of the headwalls. As these work items were never completed, paperwork had not been submitted to Crossrail for review at the time the work was completed Cube results for all pours are available, as well as the pour history for foam concrete pour 1.
| 02SL - Stations (LUL) | Cxxx-NCR-001012 | NCR | Lack of protruding thread in AP9d walling system |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2018-06-18 | 2018-05-25 07:23 | -24 | 2018-01-12 09:11 | Architectural - Walls | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | During inspection of the walling system within AP9d it became apparent that there was a lack of threads protruding from the attached nut. Speaking to the __ operative they confirmed they installed the bolts too deep.
| 02SL - Stations (LUL) | Cxxx-NCR-001013 | NCR | Flooring - WTH -2 - Failed Screed Drop Hammer Test |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2018-02-13 | 2018-01-23 11:50 | -21 | 2018-01-16 13:26 | Architectural - Flooring | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Screed in floor on WTH -2 failed the drop hammer test in multiple areas on WTH -2 (see attached mark-up) Screed has been repaired and re-tested before the Terrazzo tile was laid.
| 02SL - Stations (LUL) | Cxxx-NCR-001014 | NCR | WTH - Ticket hall - Floating slab - Missing Cube Results |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2018-03-15 | 2018-01-18 11:46 | -56 | 2018-01-18 11:22 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Unfortunately 1 set of cubes taken for the WTH – GF – Ticket Hall – Floating slab – Pour 1&2 (please see attached marked up drawing) have been miss placed or lost. The concrete mix used to pour these slabs was: MIX 1B, this is a C50/60 mix (MCR: Cxxx-LAO-O4-XDS-N105_WS089_Z-50008) and is greater than specified in the specification (C32/40). Please find attached the Pour history record and concrete tickets. Please find attached __ records for Mix 1B for 3No. pours before and 3No. pours after the missing results.
| 02SL - Stations (LUL) | Cxxx-NCR-001016 | NCR | WTH Block C Earthing / Lightning Tail As-built |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2018-07-02 | 2018-07-06 14:49 | 4 | 2018-01-25 12:02 | Electrical - Earthing & Bonding | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Supervision - Other | Completed |  | PMI 614 was issued which detailed the earthing and lightning requirements for both WTH Block C & D. Noted on the drawing was a requirement for a 'minimum 3m of cable left above the First Floor Slab for conncection with OSD lightning protection system'. The attached as-built provides the length of earthing cables exposed above the 100mm protection concrete on WTH Block C. As noted on the as-built, there are a number of exposed earthing cables which are less than 3m in length. It should be noted that, from GL 2 north, the first floor slab is 500mm higher then south of GL 2. The exposed lengths of earthing tail which will be left exposed above OSD FFL of both Block C and D are noted in blue. It has been noted by David __ that a minimum 0.5m of earthing tail is to be exposed above FFL to allow for future connection. There is 1No earthing tail which is 0.6m in length above FFL on the SE corner of Block C. All other tails required by OSD are over 1m in length above FFL. There are however additional earthing tails to which OSD require which are above 1m in length above FFL which can be used if required.
| 02SL - Stations (LUL) | Cxxx-NCR-001017 | NCR | Damage to doors D2-2/028 & D3-3/022 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2018-06-04 | 2018-08-17 15:05 | 74 | 2018-01-29 10:40 | Architectural - Doors | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Doors D2-2/028 & D3-3/022 have been damaged during transportation. D3-3/022 door has a scratch on the door skin. D2-2/028 door has a dent on the door skin. For both doors to be repaired the scratch and dent are to be filled. A wet coat paint system will then need to be applied so that there are no visual imperfections. The wet coat paint colour will match the rest of the door. Please see attached for description of the wet coat paint system. Repairs to be carried out within __ factory under factory conditions.
| 02SL - Stations (LUL) | Cxxx-NCR-001018 | NCR | Damaged submain cable within DB E0503 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-08-31 | 2019-06-04 16:51 | -88 | 2018-11-19 10:44 | Electrical - Power Distribution | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following a __/CRL site inspection on the 16th January to GYB level -5 (benchmark Inspection) it was noticed that the adjacent Distribution Board reference E0503 within room ESR3 6/681 had Insulation/conductor damage with the cores buckled/stressed, the core in question was also noted to have insulation tape (phase coloured) covering part of the core.
| 02SL - Stations (LUL) | Cxxx-NCR-001019 | NCR | GYB Substructure - -1 cladding line (NOT SITE MEASURED) |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2018-08-31 | 2019-01-14 11:45 | 136 | 2018-02-02 06:58 | Architectural - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | __ have installed wall cladding on E2 and E3 up to the Crossrail/LU demarcation line. The final panel should have been a site measure to align with the TCRSU designed bulkhead. Due to the panel already having been installed the bulkhead has been matched to this line and therefore leaving a larger gap between the builkhead glazing and the acoustic baffles.
| 02SL - Stations (LUL) | Cxxx-NCR-001020 | NCR | Fire Main - Fire Stopping |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2018-12-31 | 2019-01-21 11:28 | 21 | 2018-02-02 10:02 | Fire - Fire Systems & General | 5999 |  | System Defect | Repair | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Fire stopping around pipework is damaged and will need to be made good (rework) in various locations.
| 02SL - Stations (LUL) | Cxxx-NCR-001021 | NCR | WTH -2 maintenance stair lobby. Mech e re-work to the ductwork system |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2018-12-31 | 2018-12-04 10:08 | -27 | 2018-02-02 16:04 | Mechanical - Heating Ventilation & Air Conditioning | 20000 |  | Design | Rework | 2 (6-60k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Ductwork associated with the stair pressurisation system, along with numerous runs of CMS, has been installed to a superseded design in the new lobby connecting WTH maintenance stairs MNS2 and MNS4 at level -2, and consequently need to be removed. New ductwork and CMS shall be installed to the current approved PPC design. FCDs shall be produced for additional builders-work openings that are required in the new RC and blockwork walls to provide routes for ductwork and CMS.
| 02SL - Stations (LUL) | Cxxx-NCR-001022 | NCR | WTH -2 - Shower Gully |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2018-11-30 | 2018-12-03 15:02 | 3 | 2018-02-21 17:54 | Architectural - Flooring | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | The Shower gulley in the male shower room on WTH -2 (2/421) does not align with the wall skirting. This means the interface detail does not work. (See attached Photo)
| 02SL - Stations (LUL) | Cxxx-NCR-001023 | NCR | Material on site without prior MCR Approval |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2018-11-30 | 2018-10-17 15:44 | -44 | 2018-02-22 12:44 | Mechanical - Public Health Engineering | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | During a site inspection at Cxxx Tottenham Court Road Station as part of the CRAF (Completion Readiness Assessment Framework) it was found that Sump Pump Control Panels were on site without prior MCR approval. CRL-MCR-000296 covers the Sump Pump Control Panels, this has unaddressed electrical comments associated with it from CEG dated 12/6/2017. The comments included in CRL-MCR-000296-008 state the following: "References made to LU documentation, but these are not included. Please resubmit including LUL documentation. If this product has an LU APR number, please also include that. Please also review and confirm you are compliant with M&W specification JY53, JY72, JY71, BSEN61439. The primary attachment is padded out to 321 pages by including the __ catalogue twice. Please include a materials schedule/list as provided for the switchboards. Submission currently rejected. "
| 02SL - Stations (LUL) | Cxxx-NCR-001024 | NCR | GYB Level -1 Rebate Around Void MNS50 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2018-06-04 | 2018-06-13 11:28 | 9 | 2018-02-23 15:50 | Civil - Civil Engineering General | 2000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | A 80mm dp x 125mm wide rebate has been formed around the GYB Level -1 void MNS 50 as highlighted in the attached sketch to allow the access hatch to be installed. This work had been requested through FCD 1055, however the answer to this FCD was that it was unacceptable to form the rebate due to a concern with damaging the punching shear links within the slab. On inspecting the rebate formed, 16mm U bars and 25mm top horizontal bars have been cut. There is no evidence that the shear links have been cut. All exposed cut ends of reinforcement bars have been identified as U bars or horizontal top mat bars.
| 02SL - Stations (LUL) | Cxxx-NCR-001025 | NCR | Incorrectly pullled cables |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2018-09-30 | 2018-09-20 15:42 | -10 | 2018-02-28 09:15 | Electrical - Cable Management | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Management Problem - Inadequate supervision | Completed |  | Cables were pulled during the weekend on 17th Feb for LU connects and pulled in non diverse routes
| 02SL - Stations (LUL) | Cxxx-NCR-001026 | NCR | potential short cables in West CER for __ |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2018-09-30 | 2018-09-20 15:48 | -10 | 2018-02-28 09:20 | Electrical - General | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Management Problem - Inadequate supervision | Completed |  | potential short cables in West CER for __
| 02SL - Stations (LUL) | Cxxx-NCR-001027 | NCR | Wiring cabling installed within cable trunkings not free of swarf or debris. |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2020-06-30 | 2020-07-16 08:38 | 16 | 2018-02-28 13:50 | Electrical - Cable Management | 100000 |  | Supervision/Management | Use As-Is | 1 (>60k) | Complete | Management Problem - Inadequate supervision | Completed |  | General wiring of cabling within as installed trunkings found with debris and swarf within and not IRF accepted.
| 02SL - Stations (LUL) | Cxxx-NCR-001028 | NCR | Tiling - AP1 Discoloured Tiles |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-03-01 | 2019-09-18 14:52 | 201 | 2018-03-01 16:33 | Architectural - Flooring | 500 |  | System Defect | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | 4 no. discoloured tiles witnessed during inspection of Ap1 tiles on 01.03.2018
| 02SL - Stations (LUL) | Cxxx-NCR-001029 | NCR | GYB - Capping beam damage (__'s) |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2018-06-07 | 2018-05-31 11:52 | -7 | 2018-03-09 17:17 | Civil - Civil Engineering General | 3000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | During excavations for drainage in Goslett Yard Box JMS encountered reinforced concrete that was assumed to be a buried retaining structure as discovered previously in same location of the site. The capping beam protection slab was broken away and the southern corner of the capping beam has been damaged, exposing reinforcement and removing part of the waterproofing membrane.
| 02SL - Stations (LUL) | Cxxx-NCR-001030 | NCR | Damaged Submain Cable |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-01-31 | 2019-01-11 11:13 | -20 | 2018-03-13 14:37 | Electrical - Power Distribution | 1500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Damaged core to installed and terminated submain cable Sump Pump Supply (IRN 573)
| 02SL - Stations (LUL) | Cxxx-NCR-001031 | NCR | Use of un approved cable lubricant |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-06-30 | 2019-03-06 10:02 | -116 | 2018-03-14 10:52 | Fire - Detection | 1500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | __Fire Detection installation of cabling using an unapproved cable lubricant on GYB levels +1 to +4 inclusive. MCR not issued / approved.
| 02SL - Stations (LUL) | Cxxx-NCR-001032 | NCR | Missing DOO Camera, Housing, and Lens |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2018-05-25 | 2018-05-23 11:17 | -2 | 2018-03-14 10:44 | Communications and Control Systems - Driver only Operation CCTV | 3000 |  | Material | Rework | 4 (0.5-3k) | Complete | Personnel Error - Other human error | Completed |  | In EWN -1161 the Contractor requested the following Cxxx free issued material: - 1 x 1/3’’ Analogue Colour Camera (LVF-400C-D0550); - 1 x 1/3’’ Vari-Focal 5-50mm F1.4 DC Controlled Lenses (VBN-5085/11); - 1 x Weatherproof Camera Housing Complete with built in heater (UHOO-HGS-50). However, as per PMC-3524, the Contractor was already in receipt of all required DOO camera items. NCR-1032 records the failure of the Contractors quality process to effectively manage the storage of the above Pant and Materials.
| 02SL - Stations (LUL) | Cxxx-NCR-001033 | NCR | Platform Ends CMS Gapping |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-01-31 | 2018-12-12 16:41 | -50 | 2018-03-14 11:33 | Electrical - Cable Management | 2500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Works proceeded on site under verbal CRL instruction not to install gapping CMS, subsequently works had to be removed due to installation not as drawing intent.
| 02SL - Stations (LUL) | Cxxx-NCR-001034 | NCR | ATS Blockwork Cupboard WTH -5 Basement |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-12-31 | 2019-11-16 14:32 | -45 | 2018-03-19 08:30 | Electrical - General | 1500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Reference to ATS cupboard next to the TEB room in the WTH -5 Basement, ATS is central to the door opening, so you can’t get to the access hatch unless your on your hands and knees, hence the additional hatch. Also the slab drainage pipe is sitting directly above and running parallel with the Blockwork fascia which will hinder any lintel installation reducing the door height ?
| 02SL - Stations (LUL) | Cxxx-NCR-001035 | NCR | WTH Substructure -2 - Broken glass cladding panel |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2018-06-26 | 2018-07-19 11:50 | 23 | 2018-03-28 08:04 | Architectural - Glazing | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Other | Completed |  | A glass cladding panel in the PRM corridor was broken during the adjacent panel install. The subcontractor responsible has left the panel in position until the replacement panel arrives.
| 02SL - Stations (LUL) | Cxxx-NCR-001037 | NCR | Incorrectly installed cabling within 3 compartment CMS |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-10-01 | 2019-08-23 07:11 | -39 | 2018-03-28 12:15 | Electrical - General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Single core general wiring cabling installed in incorrect compartments of 3 compartment trunking.
| 02SL - Stations (LUL) | Cxxx-NCR-001040 | NCR | non compliance with Cxxx-LAO-A-RSP-N105_WS089-50001 Tottenham Court Road Architectural Specification JK40.2104 Prototype Requirements |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2018-07-30 | 2019-01-23 10:11 | 177 | 2018-03-29 13:55 | Architectural - Ceilings & Soffits | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | There will be no prototype of CLG 716 Stainless Steel ceilings provided as per the architectural specification. Crossrail have accepted that a benchmark will be installed on site which will include light to light straight / corner abutment details, perimeter /border panel to panel details including Cxxx designers comments contained in the PPC pack.
| 02SL - Stations (LUL) | Cxxx-NCR-001041 | NCR | Portable Appliance Test Certificate out of date |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2018-12-31 | 2018-12-04 10:01 | -27 | 2018-03-29 14:55 | Mechanical - Public Health Engineering | 500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Lack or improper material identification and traceability | Completed |  | Pipe cutting machine located on site found to have PAT certificate out of date.
| 02SL - Stations (LUL) | Cxxx-NCR-001042 | NCR | Fire Hydrant Bracket Design Drawings Not Followed |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2018-09-28 | 2018-12-17 16:11 | 80 | 2018-04-12 13:45 | Mechanical - Piping | 4000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Management Problem - Other | Completed |  | __F2 drawings identify bracket types at specific locations. Installation has used different bracket types and in general not followed the bracket types. Please refer to attached markups and __drawings.
| 02SL - Stations (LUL) | Cxxx-NCR-001043 | NCR | WTH Level -2 Chilled Water Pipe deviation from design |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2018-07-30 | 2018-08-20 14:44 | 21 | 2018-04-12 13:52 | Mechanical - Piping | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | WTH Level -2, chilled water pipework in main AHU plantroom at high level near wall by escalator has been installed differently to drawings possibly for good reasons. FCD has not been raised. Pipework is not co-ordinated with other services. CMS installed below making legging installation difficult. Additional scaffolding may be required for rework
| 02SL - Stations (LUL) | Cxxx-NCR-001044 | NCR | ATS cable terminations installed with incorrect bias (duty standby). |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-10-17 | 2019-09-18 13:39 | -29 | 2018-04-13 17:22 | Electrical - Switchgear | 1500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | ATS cable terminations installed with incorrect bias (duty standby).
| 02SL - Stations (LUL) | Cxxx-NCR-001045 | NCR | GFRC panels: Striped colouring in AP4W and AP4E |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2018-07-31 | 2019-01-24 17:02 | 177 | 2018-04-19 13:48 | Archaeology - General | 500 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The Contractor has identified distinct differences in colour of GFRC panels in alternate bays in sections of AP4W and AP4E. The locations of these bays are highlighted in the attachment "AP4 zebra stripes".
| 02SL - Stations (LUL) | Cxxx-NCR-001046 | NCR | WTH +6 Incomplete waterproofing |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2018-07-22 | 2018-10-29 16:44 | 99 | 2018-04-23 09:01 | Civil - Civil Engineering General | 3000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | The EPDM waterproofing was installed to +6 WTH on the 20/10/16. In the time since install, only minimal protection had been installed and to date the outstanding permanent works had not been completed. Due to this the Contractor is aware remedial works will be required prior to completion.
| 02SL - Stations (LUL) | Cxxx-NCR-001047 | NCR | The Contractor has not installed Platform Edge Screen (PES) light boxes in line with the Specification. |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2018-09-14 | 2018-10-09 12:22 | 25 | 2018-04-26 13:07 | Architectural - General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | A planned Crossrail surveillance was undertaken on 11th April 2018 to look at platform Edge Screen (PES) installation, including MEP installation works being carried out by __. During the site visit it was noted that the Contractor had installed a light box .that appeared to be non compliant on the Westbound platform. The gap at the bottom of the light box appeared to be similar to adjacent joints but the joint at the top was very tight (see attached photograph). On checking the drawing and specification the joint between two vertical faces are to be 8mm as shown on Cxxx-LAO-Y-DWG-N105_WS089_5-50147 (Rev C01) with a specified tolerance of +2, -2mm, Specification Cxxx-ATK-N2-RSP-CR002-00001 -JH11.1208 Framing that states; “Joints/ framing shall align with interfacing systems. Gaps within joints shall be uniform”.
| 02SL - Stations (LUL) | Cxxx-NCR-001048 | NCR | Cxxx- Live Cables |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-01-27 | 2019-01-23 12:00 | -4 | 2018-04-27 07:33 | Electrical - General | 1000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Cxxx have IRNd and terminated cables within CMS at present, if these fibres go down due to the work being carried out the whole CDN network would crash. riser in the WTH side +1
| 02SL - Stations (LUL) | Cxxx-NCR-001049 | NCR | Damaged Curtain Wall Glazed Panel |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-02-28 | 2018-12-18 09:58 | -72 | 2018-04-27 07:47 | Architectural - Glazing | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Contamination | Completed |  | Panel has been found smashed on the curtain wall section on Great Chapel Street
| 02SL - Stations (LUL) | Cxxx-NCR-001050 | NCR | __ Ltd - CAT II Check Certificate |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-10-31 | 2019-11-15 12:00 | 15 | 2018-04-27 13:38 | Architectural - Glazing | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | __ Ltd carrying on the glazing/curtain walling/louvre installation works on site whereas CAT II check certificate has not been approved. Some of the installed works assurance documentation has also been submitted but missing CAT II cert
| 02SL - Stations (LUL) | Cxxx-NCR-001051 | NCR | GYB - Access panel clash with tile curbs |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2018-06-14 | 2018-06-08 06:39 | -6 | 2018-05-04 08:30 | Architectural - Finishes | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | Access panels A3-5/009 and 5/011 on level -4 GYB clashed with the tile curbs. This impeded the access panels from fully opening. To resolve this issue, the access panels will be removed and the lintel above the doorway will be scabbled back 10mm. This will not affect the reinforcement and the lintel will be made good with cementitious coating. The panels with then be reinstalled with packers positioned below to lift this above the curb.
| 02SL - Stations (LUL) | Cxxx-NCR-001052 | NCR | Precast Cladding CAT III Certificate |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-07-19 | 2019-10-08 14:08 | 81 | 2018-05-10 08:55 | Architectural - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | CAT III checks were carried out by __ for Precast Cladding but the certificate has not been issued to CRL for acceptance
| 02SL - Stations (LUL) | Cxxx-NCR-001053 | NCR | Vent Shaft Accoustic Cladding CAT II Certificate |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-08-16 | 2019-08-16 15:24 | 0 | 2018-05-10 09:00 | Architectural - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | CAT II check certificate for the vent shaft acoustic cladding “including acoustic performance specification” has not been submitted for CRL acceptance and is required for assurance certification
| 02SL - Stations (LUL) | Cxxx-NCR-001054 | NCR | Use of __ Acoustic Pad |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2018-10-30 | 2018-12-04 10:25 | 35 | 2018-05-10 09:10 | Architectural - General | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | __ Acoustic Pad – Mineral Wool in a Foil Tissue Backing used with cladding/glazing panels and Mechanically fixed is non compliant with LU-1085 standard and need to be removed and replaced with compliant material
| 02SL - Stations (LUL) | Cxxx-NCR-001055 | NCR | - Installation of Luminaries and Associated Accessories’ Method Statement has been at Code 3 since October 2016 |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2018-06-27 | 2018-06-29 13:28 | 2 | 2018-05-16 10:05 | Electrical - Lighting | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | A planned Crossrail surveillance was undertaken on 15th May 2018 to look at the installation of Light Drums and associated MEP work. During the documentation review it was identified that the ‘Installation of Luminaries and Associated Accessories’ Cxxx-LAO-O4-GMS-N105_WS089_Z-50002 (Rev 2) had been at Decal Code 3 since first review 07/09/2016.
| 02SL - Stations (LUL) | Cxxx-NCR-001057 | NCR | Flooring - AP3E Structural Movement Joint |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2018-10-30 | 2018-11-21 10:55 | 22 | 2018-05-21 14:45 | Architectural - Flooring | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The structural movement joint in AP3E had lifted on side putting this zone out of level. Terrazzo quality pack no. Cxxx-LAO-O7-LRC-N105_WS089_Z-50233.
| 02SL - Stations (LUL) | Cxxx-NCR-001059 | NCR | Defective installation – GYB PFR-E1 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2018-12-31 | 2018-12-21 10:09 | -10 | 2018-05-29 12:04 | Mechanical - Mechanical Engineering General | 15000 |  | Workmanship | Rework | 2 (6-60k) | Complete | Supervision - Insufficient supervision | Completed |  | The GYB stair pressurisation fan PFR-E1 installation is defective as the fans are not aligned with the adjacent square to round transient pieces. The offsets are clearly visible to the naked eye.
| 02SL - Stations (LUL) | Cxxx-NCR-001060 | NCR | Defective installation – GYB PFR-E3 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2018-09-30 | 2018-09-20 14:30 | -10 | 2018-05-29 12:08 | Mechanical - Mechanical Engineering General | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The GYB stair pressurisation air release fan PFR-E3 installation is defective for a number of reasons including the following: 1) the fans are not aligned with the adjacent square to round transient pieces. The offsets are clearly visible to the naked eye. 2) the flexible connection gap widths are non-compliant with Cxxx specifications (and industry standard guide DW/144) as the spaces between fan and transitions are less than 50mm.
| 02SL - Stations (LUL) | Cxxx-NCR-001061 | NCR | Defective installation – WTH PFR-W1 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2018-12-31 | 2018-12-21 10:20 | -10 | 2018-05-29 12:12 | Mechanical - Mechanical Engineering General | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The WTH stair pressurisation fan PFR-W1 installation is defective for a number of reasons including the following: 1) the fans are not aligned with the adjacent square to round transient pieces. The offsets are clearly visible to the naked eye. 2) the flexible connection gap widths are non-compliant with Cxxx specifications (and industry standard guide DW/144) as the spaces between fan and transitions are less than 50mm.
| 02SL - Stations (LUL) | Cxxx-NCR-001062 | NCR | Defective installation – WTH PFR-W4 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2018-12-31 | 2018-12-21 10:29 | -10 | 2018-05-29 12:16 | Mechanical - Mechanical Engineering General | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The WTH stair pressurisation fan PFR-W4 installation is defective as the fans are not aligned with the adjacent square to round transient pieces. The offsets are clearly visible to the naked eye.
| 02SL - Stations (LUL) | Cxxx-NCR-001063 | NCR | Defective installation – WTH PFR-W3 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2018-10-23 | 2018-10-15 08:25 | -8 | 2018-05-29 12:19 | Mechanical - Mechanical Engineering General | 2500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | NCR details: The WTH stair pressurisation air release fan PFR-W3 installation is defective for a number of reasons including the following: 1) the fans are not aligned with the adjacent square to round transient pieces. The offsets are clearly visible to the naked eye. 2) the flexible connection gap widths are non-compliant with Cxxx specifications (and industry standard guide DW/144) as the spaces between fan and transitions are less than 50mm.
| 02SL - Stations (LUL) | Cxxx-NCR-001064 | NCR | Defective installation - GYB SEF E1 and E2. |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2018-09-30 | 2018-09-21 14:52 | -9 | 2018-05-29 12:23 | Mechanical - Mechanical Engineering General | 2000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The GYB SEF-E1 and E2 platform smoke extract fan installation is defective for a number of reasons including the following: 1) the fans are not aligned with the adjacent square to round transient pieces. The offsets are clearly visible to the naked eye. 2) the flexible connection gap widths are non-compliant with Cxxx specifications (and industry standard guide DW/144) as the spaces between fan and transitions are less than 50mm. 3) the AV mount installation is not compliant with the manufacturer’s requirements for a maximum baseplate overhang of 20% (14mm for the 70mm base plates on SEF W1 and W2).
| 02SL - Stations (LUL) | Cxxx-NCR-001065 | NCR | Defective installation - WTH SEF W1 and W2. |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2018-09-30 | 2019-02-08 10:18 | 131 | 2018-05-29 12:28 | Mechanical - Mechanical Engineering General | 3500 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The WTH SEF-W1 and W2 platform smoke extract fan installation is defective for a number of reasons including the following: 1) the fans are not aligned with the adjacent square to round transient pieces. The offsets are clearly visible to the naked eye. 2) the flexible connection gap widths are non-compliant with Cxxx specifications (and industry standard guide DW/144) as the spaces between fan and transitions are less than 50mm. 3) the AV mount installation is not compliant with the manufacturer’s requirements for a maximum baseplate overhang of 20% (14mm for the 70mm base plates on SEF W1 and W2).
| 02SL - Stations (LUL) | Cxxx-NCR-001066 | NCR | Ductwork and CMS removal - WTH |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2018-12-25 | 2018-12-21 10:06 | -4 | 2018-06-01 12:45 | Mechanical - Mechanical Engineering General | 10000 |  | Design | Rework | 2 (6-60k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The contractor highlights the re-work associated with the design changes to the ductwork serving GLR 1/410 on the ground floor, as a result of services co-ordination and design changes/development the installed standard galvanised ductwork is to be stripped out and be re-installed in fire rated.
| 02SL - Stations (LUL) | Cxxx-NCR-001067 | NCR | Wiring commenced without CRL IRF Sign off |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-10-31 | 2019-08-23 08:58 | -69 | 2018-06-04 11:09 | Electrical - Lighting | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Not Defined | Completed |  | Lighting wiring commencement within the lighting boom in AP8 without CRL IRF Sign off.
| 02SL - Stations (LUL) | Cxxx-NCR-001068 | NCR | __ - Defective welds on stair threads MNS66 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2018-07-02 | 2018-07-23 08:01 | 21 | 2018-06-04 14:05 | Architectural - Finishes | 500 |  | Manufacturing Defect | Reject | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Some of the welds on MNS66 stair threads at level +6 WTH are defective. The grillage welds have separated from the trim as seen in the attached photo.
| 02SL - Stations (LUL) | Cxxx-NCR-001069 | NCR | PTP - Terrazzo installed to incorrect levels |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-06-30 | 2019-04-12 08:30 | -79 | 2018-06-06 13:04 | Architectural - Flooring | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | The contractor has installed the terrazzo tiles to an incorrect level at PTE eastend and PTW westend. The tiles require a level change to be flat where they interface with the head wall. The tiles were subsequently removed and reinstalled to the correct levels
| 02SL - Stations (LUL) | Cxxx-NCR-001070 | NCR | VSD Cable terminations installed to the wrong locations. |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-01-31 | 2019-01-08 13:49 | -23 | 2018-06-11 11:06 | Electrical - Power Distribution | 2000 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | The VSD cables x3 (AS INSTALLED) have been run to the wrong locations and do not reflect the design and associated assurance documentation. All associated documentation needs to be amended to reflect the actual installation, noting amtech calculations/test results and the cable installation schedule.
| 02SL - Stations (LUL) | Cxxx-NCR-001071 | NCR | PTE and PTW emergency DBs |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-04-30 | 2019-02-05 15:48 | -84 | 2018-06-15 11:57 | Electrical - General | 2000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | 1. All 8 No doors have been removed 2. The __ box facia has been damaged 3. These are 1 No hour fire rated enclosures that have been signed off by CRL fire engineer. 4. Normally once a Tek screw has gone into __ it cannot be reused 5. State of recently signed off board covered in zinger.
| 02SL - Stations (LUL) | Cxxx-NCR-001072 | NCR | WTH - GF - Late floating slab concrete cube results |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2018-08-15 | 2018-08-22 20:49 | 7 | 2018-06-19 09:54 | Civil - Civil Engineering General | 0 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | __ failed to collect the cubes for the GF floating slab Block D pour. When the Contractor noticed the missing results the cubes were sent ASAP and crushed shortly after. The cubes were crushed at 35 days not 28.
| 02SL - Stations (LUL) | Cxxx-NCR-001073 | NCR | WTH - GF - Secondary walls failed cubes |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2018-08-15 | 2018-08-22 20:54 | 7 | 2018-06-19 16:20 | Civil - Civil Engineering General | 0 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | The strength of cubes TCR62B (58.1N/mm2) and TCR62C (58.8N/mm2) (Secondary wall 3) & TCR61B (54.5N/mm2) and TCR61C (56N/mm2) (Secondary wall 4) did not reach the required 60N/mm2 in 28 days, see attached cube result sheets. The concrete strength required for these elements was 40N/mm2, however 60N/mm2 concrete was used. The 56 day results gave strengths of TCR61D (65.8N/mm2) (Secondary wall 4) & TCR62D (68.9N/mm2) (Secondary wall 3). The cube test reports are attached.
| 02SL - Stations (LUL) | Cxxx-NCR-001074 | NCR | Incorrectly positioned floor gulley |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-04-30 | 2019-04-08 10:39 | -22 | 2018-06-20 12:53 | Civil - Drainage | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | Floor gulley appears to be cast in mid-slope in the screed, not at a low point.
| 02SL - Stations (LUL) | Cxxx-NCR-001075 | NCR | Damage to as Installed Radio Cable |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-01-31 | 2019-01-09 12:44 | -22 | 2018-06-27 10:00 | Communications and Control Systems - Radio | 1500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following the removal of electrical cable basket the as installed radio cable has been damaged within GYB Room CER 2 SID Number 4/734). Photos attached x 3.
| 02SL - Stations (LUL) | Cxxx-NCR-001076 | NCR | 32A 400V TPN Power supplies to temporary sumps |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-01-31 | 2019-06-05 11:13 | 125 | 2018-06-29 05:52 | Electrical - General | 5000 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Baseline standard LUL 1-069 A2 3.6.2 requires 32A 400V TPN sockets for use with a temporary sump pump in the event of sump pump failure. These sockets and power supplies are required but are not in the Cxxx design or installation. Refer to RFI-1953 for more details.
| 02SL - Stations (LUL) | Cxxx-NCR-001077 | NCR | anti-vibration mounts on pumps |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2018-10-01 | 2018-09-18 10:08 | -13 | 2018-06-29 05:55 | Materials - General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Skid mounted dry well pumps supplied by __ do not have anti-vibration mounts as required by CRL M&W specification JY20.1301 (CRL1-XRL-M-RSP-CR001-50060). One possible route to close out would be to demonstrate the pumps comply with JY52 Vibration Isolation CRL1-XRL-M-RSP-CR001-50074 without the mounts. Note: this NCR does not apply to the wet well pumps.
| 02SL - Stations (LUL) | Cxxx-NCR-001078 | NCR | RCD protection on Trace Heating circuits |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-11-30 | 2020-02-25 14:48 | 87 | 2018-06-29 06:14 | Materials - General | 7000 |  | Design | Rework | 2 (6-60k) | Complete | Design Problem - Inadequate or defective design | Completed |  | CRL M&W specification JY24.3101 j (CRL1-XRL-M-RSP-CR001-50062) requires RCD protection of all trace heating circuits. Following on from a site survey the contractor has advised that no RCD protection is present in the design or installation.
| 02SL - Stations (LUL) | Cxxx-NCR-001079 | NCR | High temperature fans non-compliant with BS EN 12101-3:2015 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2018-09-26 | 2018-08-20 10:13 | -37 | 2018-06-29 06:17 | Mechanical - Mechanical Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Following on from EWN-1029, no evidence of compliance with BS EN 12101-3:2015 has been provided. Without certification of compliance for the fan and inverter pairing, the installation is deemed non-compliant with the BS EN.
| 02SL - Stations (LUL) | Cxxx-NCR-001080 | NCR | Pipework welds on platform hydrants |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-01-31 | 2018-12-06 14:47 | -56 | 2018-06-29 06:28 | Mechanical - Mechanical Engineering General | 1000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Other | Completed |  | No assurance evidence exists for the welded pipe sections supplied by __and installed at every platform hydrant. The installation in not in compliance with CRL M&W specification clauses JA.6520 & JA.6521 of General Requirements for MEP Crossrail M&W Specification CRL1-XRL-M-RSP-CR001-50016. Independent N__ testing of the welds is now required by a UKAS accredited tester in accordance with the specification. It is understood that ultrasonic testing can be done on site.
| 02SL - Stations (LUL) | Cxxx-NCR-001081 | NCR | BMS - Fibre tap boxes installed without approved MCR |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2018-08-24 | 2018-08-24 12:52 | 0 | 2018-06-29 15:39 | Communications and Control Systems - General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | BMS fibre tap boxes installed without approved MCR. MCR approved tap boxes not available in order to meet programme and may not have been suitable for purpose.
| 02SL - Stations (LUL) | Cxxx-NCR-001083 | NCR | Fabrication and installtion of GFRC panels out of tolerance |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2018-10-05 | 2019-05-16 14:35 | 223 | 2018-06-30 13:23 | Architectural - General | 500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | GFRC panels have been fabricated and installed outside of tolerances specified in the Cxxx specification (Cxxx-ATK-N2-RSP-CR002-00001). This has lead to steps between panels and uneven joints.
| 02SL - Stations (LUL) | Cxxx-NCR-001084 | NCR | Interface between GFRC and cross passage service boom. |  | Crossrail | PDP | TCR - Tottenham Court Road Station (West) |  | 2018-11-01 | 2018-11-20 17:25 | 19 | 2018-07-04 11:42 | Architectural - Ceilings & Soffits | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | This interface detail is not compliant with the Works Information design intent as demonstrated on drawing Cxxx-ATK-A-DDD-CR001_Z-73101 where the outer hinged access panel overlaps the adjacent GFRC infill strip which hides the gap between the two elements. The interface detail is also not compliant with the drawing referred to in PMI 1034 (CCM2333). The interface detail as installed is not consistent with your fabrication drawing Cxxx-LAO-Y-DWG-N105_WS098_5-50192. These drawings indicate an over lap of the service boom edges with the adjacent GFRC infill strip to cover the gap between elements. The exposed gap is not acceptable to CRL and is required to be rectified, to be made compliant with the works information.
| 02SL - Stations (LUL) | Cxxx-NCR-001085 | NCR | BMS - PLC Panels (life safety) delivered to site with MCRs still to be submitted |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2018-08-30 | 2018-08-09 15:00 | -21 | 2018-07-05 14:46 | Communications and Control Systems - General | 1000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | It was identified at the BMS PLC panel FAT tests that certain materials used in the MCCs had not yet been covered by an MCR. The situation and materials were highlighted by the Subcontractor at the FAT test to flag the issue. The materials were discussed with CRL (__) and following review it was agreed this was a low risk as materials were from reputable suppliers, were low smoke/ zero halogen and & CE marked where applicable. It was agreed that the panels should be delivered to site and MCRs would be submitted as soon as possible.
| 02SL - Stations (LUL) | Cxxx-NCR-001086 | NCR | BMS - Secondary chilled water pump inverters |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2018-08-30 | 2018-08-29 10:09 | -1 | 2018-07-05 14:55 | Communications and Control Systems - General | 4500 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | __ design not aligned to Cxxx procured __ inverters and vice versa. IO not available to meet requirements of BMS design.
| 02SL - Stations (LUL) | Cxxx-NCR-001088 | NCR | Chiller coil damage |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2018-12-31 | 2018-12-11 17:02 | -20 | 2018-07-17 14:57 | Mechanical - Heating Ventilation & Air Conditioning | 2500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | There is damege to the chiller coil on chiller unit CH-E1 in GYB +2 plantroom rusulting in the coil leaking.
| 02SL - Stations (LUL) | Cxxx-NCR-001089 | NCR | Platform Cavity Drainage |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2019-01-31 | 2019-09-09 13:07 | 221 | 2018-07-18 14:56 | Civil - Drainage | 10000 |  | Supervision/Management | Rework | 2 (6-60k) | Complete | Management Problem - Other management problem | Completed |  | This NCR has been reluctantly raised by CRL as the contractor has not raised an NCR covering the core issues despite constant requests over a sustained period of time. Core issues are: 1) Failure to manage the works in terms of co-ordination and sequencing such that rework and removal of finishes is now a necessity to complete the works. 2) Failure to provide the min 2m long pipe on all discharges 3) Failure to test and prove the works prior to covering up This NCR supersedes reworked NCR-1082. This NCR supersedes sections d & e of the proposed answer to NCR-959.
| 02SL - Stations (LUL) | Cxxx-NCR-001090 | NCR | BMS - minor damage to fibre connector on network switch in MCC/E/2/1 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2018-08-23 | 2018-07-27 09:48 | -27 | 2018-07-26 08:35 | Communications and Control Systems - General | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | There is minor damage to one of the two network switches to be installed in MCC/E/2/1 - see attached photo. Proposal is to use as is. The damage does not affect operation of the switch - this has been tested, the connector still works and even if it was decided not to use this connector, there is still 25% spare capacity in the panel. Highlighted on the attached photo in green are 3 undamaged ports. 2 will be used, 1 will be spare.
| 02SL - Stations (LUL) | Cxxx-NCR-001092 | NCR | Specification and Location of Unique Sign 309 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-02-28 | 2019-02-21 17:05 | -7 | 2018-07-30 12:24 | Architectural - Signage | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | The Project Manager has advised that unique sign number 309 has the following non-conformances: 1. Installed in incorrect location as this should be in alignment with unique sign 308 2. The sign has an LED and must not have an LED
| 02SL - Stations (LUL) | Cxxx-NCR-001093 | NCR | Welding documentation could not be provided. |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2018-11-16 | 2018-12-21 10:53 | 35 | 2018-08-03 13:29 | Architectural - General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | 1) A planned Surveillance was carried on __ Architectural Steelwork Installation and Assurance on the 25th June 2018. The following documentation was requested for __; WPS, WPQR, WPQC, FPC and RWC Certificate. No Weld Documentation had been received, as such could not be provided, and CRL acceptance could be demonstrated.
| 02SL - Stations (LUL) | Cxxx-NCR-001094 | NCR | Evidence of galvanising thickness to installed steel work could not be provided by the Contractor. |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2018-11-16 | 2019-01-09 12:49 | 54 | 2018-08-03 13:35 | Architectural - General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Not Defined | Completed |  | 2) A planned Surveillance was carried on __ Architectural Steelwork Installation and Assurance on the 25th June 2018. The following documentation was requested for __; Evidence that the installed Architectural Steelwork had been galvanised to the specified thickness. No Documentation had been received, as such could not be provided, and CRL acceptance could be demonstrated.
| 02SL - Stations (LUL) | Cxxx-NCR-001095 | NCR | Chiller UV Degradation of factory applied Insulation |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-07-31 | 2020-06-30 13:37 | 335 | 2018-08-03 13:51 | Mechanical - Heating Ventilation & Air Conditioning | 8000 |  | Damaged | Repair | 2 (6-60k) | Complete | Material/Preservation Problems - Improper storage of material | Completed |  | Factory applied insulation on WTH chillers is showing signs of UV degradation and needs to be replaced. Chillers have been installed for over a year. The acoustic panels that would have provided shielding from sunlight have not yet been installed.
| 02SL - Stations (LUL) | Cxxx-NCR-001096 | NCR | Polyester Powder Coating (PPC) Records could not be provided |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2018-11-16 | 2018-12-07 13:03 | 21 | 2018-08-03 13:40 | Architectural - General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | A planned Surveillance was carried on __ Architectural Steelwork Installation and Assurance on the 25th June 2018. The following documentation was requested for __; records for the Polyester Powder Coating (PPC) applied to the handrails including; thickness applied, testing, who carried out the testing and coating grantees. No Documentation had been received, as such could not be provided, and CRL acceptance could be demonstrated.
| 02SL - Stations (LUL) | Cxxx-NCR-001097 | NCR | The design/specification showing the galvanised finish requirements for the key clamp and tube could not be provided. |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2019-06-21 | 2019-08-30 09:53 | 70 | 2018-08-03 13:50 | Architectural - General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | A planned Surveillance was carried on __ Architectural Steelwork Installation and Assurance on the 25th June 2018. The Contractor was asked to provide the design/specification showing the galvanised finish requirements for the key clamp and tube. Key clamp has been hot dipped whilst the tube is electroplated. Finish differences observed. See attached photo.
| 02SL - Stations (LUL) | Cxxx-NCR-001098 | NCR | Metalwork Package - Non Compliant Ladder |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2018-10-01 | 2019-02-26 15:52 | 148 | 2018-08-06 14:07 | Architectural - General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On Plan FF attached clear space on the drawing appears to be 155mm. Upon inspection the dimension on site confirms this see photo. BS 5395-3: clause 6.3 requires a minimum clear space of 230 mm behind each rung to allow foot room,
| 02SL - Stations (LUL) | Cxxx-NCR-001099 | NCR | WTH - Damaged __ chamber |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2018-09-10 | 2018-11-08 17:24 | 59 | 2018-08-13 14:29 | Civil - Civil Engineering General | 5000 |  | Damaged | Use As-Is | 3 (3-6k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | The Contractor is raising an NCR for the damaged __ (service provider) chamber. The chamber was partially collapsed and was filled with concrete and soil, it is not clear how or when this damage took place. The chamber has been re-built by __’s contractor __.
| 02SL - Stations (LUL) | Cxxx-NCR-001100 | NCR | WTH +6 Pipe work support - Incorrect fixing galv coating |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-02-15 | 2019-07-10 12:59 | 145 | 2018-08-13 14:55 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | The contractor has been made aware that the fixings used to secure the +6 steelwork posts were not the ones stated on the MCR. The MCR states that __ HIT-V-F rod should be used. Instead due to a delivery mix up HAS-E rod has been used.
| 02SL - Stations (LUL) | Cxxx-NCR-001101 | NCR | Ventilation Materials Not Required |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2018-10-16 | 2019-03-05 08:40 | 140 | 2018-08-17 12:45 | Mechanical - Heating Ventilation & Air Conditioning | 120000 |  | Design | Rework | 1 (>60k) | Complete | Management Problem - Inadequate resources | Completed |  | Following email correspondence on 16/08/18, the contractor acknowledges that there is redundant material on including MFD's, MD's VCD's & Fan's of which some will not be required and subsequently be discarded off. The contractor will close this NCR by summarizing the root cause/source of each of the item's of equipment which are discarded of.
| 02SL - Stations (LUL) | Cxxx-NCR-001103 | NCR | Damage to Cxxx Telephone Assets (label) and Cable Installation |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2018-12-14 | 2018-12-18 11:30 | 4 | 2018-08-20 15:30 | Communications and Control Systems | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Damage to Cxxx Telephone Assets (label) and Cable Installation.
| 02SL - Stations (LUL) | Cxxx-NCR-001104 | NCR | Cut __ Cable |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-02-28 | 2018-12-18 11:28 | -72 | 2018-08-20 15:53 | Communications and Control Systems | 2000 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | 50M Coiled __ Cable cut from coil to reduced length as photo attached.
| 02SL - Stations (LUL) | Cxxx-NCR-001105 | NCR | EFR-E1 - Fan Replacement |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2018-11-02 | 2018-11-28 09:32 | 26 | 2018-08-20 15:45 | Mechanical - Heating Ventilation & Air Conditioning | 10000 |  | Design | Rework | 2 (6-60k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The contractor highlight's the requirement to replace EFR-E1 from a 315 dia __s twin box unit to a 450 dia unit, due to the being unable to achieve the required duty. The consequence of replacing the fan is; a new plinth to be built, new square to round connections to the fan, power supply revised from single phase to 3 phase, replace breakers within MCC panel, modify wiring within MCC panel, revise cable calcs & re-testing/commissioning.
| 02SL - Stations (LUL) | Cxxx-NCR-001106 | NCR | Cxxx PSD/CMS Alterations |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-10-31 | 2019-08-23 09:06 | -69 | 2018-08-23 12:58 | Electrical - Cable Management | 1000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | 1c 75mm x 75mm trunking installed to the side of 300mm header, trunking stopped before right angle bend, trunking installation continued by third party in 50mm x 50mm trunking from before the bend and horizontally across the header trunking. 50mm x 50mm Trunking installed insufficiently sized to accommodate cable bending radius. Trunking to be removed and reinstalled in 75mm x 75mm.
| 02SL - Stations (LUL) | Cxxx-NCR-001107 | NCR | __ Test - Lack of Inspection and Snagging by Protec |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-06-30 | 2019-04-08 10:41 | -83 | 2018-09-04 06:13 | Electrical - General | 1000 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Not Defined | Completed |  | Following __ test inspection, it was noted by CRL FE that; • __have not inspected and snagged their own installation. • the comment on the IRF sheet required Cxxx Fire Engineer and CEG fire engineers comments to be incorporated. The witness test was the first time __ fire engineer and CEG fire engineer had inspected the system as a whole. • The system was offered for witnessing before it had been commissioned.
| 02SL - Stations (LUL) | Cxxx-NCR-001108 | NCR | Incorrect __ Enclosure |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-06-30 | 2019-04-11 14:47 | -80 | 2018-09-04 06:18 | Electrical - General | 1000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | It was noted by CRL FE that incorrect __ enclosure door has been installed. The vision panel is in the wrong place for the __ lights. discuss suitable mitigation with the fire engineers
| 02SL - Stations (LUL) | Cxxx-NCR-001109 | NCR | Damaged __ Cabling |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-08-31 | 2019-09-03 13:54 | 3 | 2018-09-04 17:34 | Communications and Control Systems - Fibre Optic Network | 1500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Prior to commencement of Cxxx works it is noted that __ cabling has been damaged within the modified CMS cable trunking. Cxxx email attached dated 31/08/18 refers.
| 02SL - Stations (LUL) | Cxxx-NCR-001110 | NCR | RFS-108 Roof finish and membrane to WTH Block D |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2018-11-01 | 2019-01-11 11:35 | 71 | 2018-09-04 14:33 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | RFS-108 Roof finish and membrane to WTH Block D installation is in progress. Existing waterproofing test plan covers __ system but does not cover the specific waterproofing finish (RFS-108). The draft test plan is available and require sign off
| 02SL - Stations (LUL) | Cxxx-NCR-001111 | NCR | No bi-metallic isolation has not been installed between galvanised bracket and Stainless steel connection. |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2018-10-29 | 2018-11-21 08:11 | 23 | 2018-09-13 08:56 | Architectural - Signage | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Information not detailed | Completed |  | A planned Crossrail surveillance was undertaken on 22nd August 2018 at Cxxx Tottenham Court Road Station to look at the installation of Signage. On checking the Totem installation, it was found that no bi-metallic isolation has been installed between the between the Totem galvanised base box and the Stainless Steel M20 nuts and bolts. It could also not be verified that the isolation has been installed between the baseplate and Stainless Steel M16 HILTI HST-R anchor bolts as this section of the installation is within the surrounding screed and tiles.
| 02SL - Stations (LUL) | Cxxx-NCR-001112 | NCR | Pull Testing is being completed without evidence of competence. |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2019-03-31 | 2019-03-21 00:11 | -10 | 2018-09-13 09:02 | Architectural - Signage | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Supervision - Supervisor does not have sufficient experience | Completed |  | A planned Crossrail surveillance was undertaken on 22nd August 2018 at Cxxx Tottenham Court Road Station to look at the installation of Signage. The Contractor was requested to provide evidence of the competency of the operatives that have carried out pull testing on signage connections. The Contractor has been able to provide this evidence, therefor it can not be verified that the testing has been carried out correctly.
| 02SL - Stations (LUL) | Cxxx-NCR-001113 | NCR | Contractor is carrying the signage installation using ‘P’ status drawings with no Proposal to Progress Construction (PPC) in place. |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2018-10-11 | 2018-12-04 10:16 | 54 | 2018-09-13 09:10 | Architectural - Signage | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | A planned Crossrail surveillance was undertaken on 22nd August 2018 at Cxxx Tottenham Court Road Station to look at the installation of Signage. On checking it was found that the Contractor is carrying the signage installation using ‘P’ status drawings. On request the Contractor was unable to provide Proposal to Progress Construction (PPC) number that allows the Contractor to construct to the P status drawings.
| 02SL - Stations (LUL) | Cxxx-NCR-001114 | NCR | GYB prop plate covers not manufactured to the design drawings |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2018-10-15 | 2019-07-15 13:35 | 273 | 2018-09-17 15:56 | Architectural - General | 500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Error by manufacturer in shipping or marking | Completed |  | The Contractor raises the issue that 2no upper prop end plates in GYB do not align with the adjacent GFRC panels.
| 02SL - Stations (LUL) | Cxxx-NCR-001116 | NCR | No PPC and stamped drawings in place for hand rail installation. |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2019-02-28 | 2019-09-26 14:25 | 210 | 2018-09-21 07:56 | Architectural - Handrail | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | A planned Surveillance was carried on __ Architectural Steelwork Installation and Assurance on the 25th June 2018. On request the Contractor submitted PPC ref number Cxxx-LAO-Z-MRC-N105_WS089-50438 for the use ‘P’ revision drawings in the installation of Hand Rails. On checking eB it was found to be a place holder. It was also found that the drawings are not on eB. The PPC Procedure Cxxx-LAO-O7-GPD-N105_WS089-50001 (Rev 1) states; “Reissue drawings to eB for information. All Associated drawings to be stamped approved for construction by PPC process.
| 02SL - Stations (LUL) | Cxxx-NCR-001117 | NCR | No impact testing in place as required in Architectural Specification. |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2020-12-04 | 2020-12-03 15:55 | -1 | 2018-09-21 08:28 | Architectural - Handrail | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | The Contractor was requested to submit evidence of testing as required in the Architectural specification JL32.2202 ‘Impact Testing’; a) “A hard body impact test shall be carried out in accordance with BS 8200, conforming to the category requirements specified”. “b) A test for resistance to impacts from hand held objects shall be carried out in accordance with BS EN 356, conforming to the category requirements specified”. “c) A test for resistance to impacts from hand held objects shall be carried out in accordance with BS EN 356, conforming to the category requirements specified. The Contractor could not provide the specified testing.
| 02SL - Stations (LUL) | Cxxx-NCR-001118 | NCR | No evidence of proof loading of hand rail fixings (M6x50 screws) supplied. |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2018-10-19 | 2019-03-18 16:05 | 150 | 2018-09-21 08:38 | Architectural - Handrail | 500 |  | Material | Reject | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | The Contractor was requested to supply evidence of proof loading of hand rail fixings (M6x50 screws).. Architectural Specification JL32.2203 Testing of Fixings states; “as the work proceeds, allow for the fixings to be proof load tested as required and witnessed by the Project Manager”. The Contractor was unable to supply the evidence.
| 02SL - Stations (LUL) | Cxxx-NCR-001119 | NCR | WTH - +6 - Concrete support pads |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2018-10-23 | 2019-01-17 10:23 | 86 | 2018-09-25 11:57 | Civil - Civil Engineering General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | A number of concrete plinths on +6 WTH have been chipped or sustained surface cracking during MEP steel work install.
| 02SL - Stations (LUL) | Cxxx-NCR-001120 | NCR | MFD Transfer Grille - WTH level -5 sump room 6/772 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2018-11-24 | 2019-01-09 08:45 | 46 | 2018-09-25 15:37 | Mechanical - Heating Ventilation & Air Conditioning | 2000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | The contractor highlights the re-work associated with re-positioning the MFD providing make up air into Sump room 6/772.
| 02SL - Stations (LUL) | Cxxx-NCR-001121 | NCR | MFD-W208 & W209 - Removal |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2018-12-04 | 2018-10-26 10:20 | -39 | 2018-09-25 15:47 | Mechanical - Heating Ventilation & Air Conditioning | 6000 |  | Design | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | The contractor highlights the requirement to remove MFD-W208 & W209.
| 02SL - Stations (LUL) | Cxxx-NCR-001122 | NCR | SCADA - Cat 6 cable __ RailSafe Category 6A S/FTP LSC Cable |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2018-10-01 | 2018-10-02 13:32 | 1 | 2018-09-26 14:37 | Communications and Control Systems | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | The Contractor has used __ RailSafe Category 6A S/FTP LSC Cable for use in SCADA Cabling installations which differs from the free issued cabling by __ Cxxx. i.e BMS/PSD/Signaling SCADA The Contractor has MCR'd this cable for use in the comms discipline and has an approved F1 MCR ref CRL-MCR-006975. The NCR is to record the deviation in cable use however it has been agreed with the Project Manager (Kevin Ten) that there is nothing technically wrong with this cable, and that the NCR is due to using an alternative material prior to an FCD approval. The Contractor will red-line the schedule to highlight all cables which were __ Cat6 to the __ RailSafe Category 6A S/FTP LSC Cable
| 02SL - Stations (LUL) | Cxxx-NCR-001123 | NCR | Stainless Steel Door Sample |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-10-31 | 2019-06-19 12:43 | -134 | 2018-10-02 09:22 | Architectural - Doors | 500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | Although the stainless steel door sample has been found stored in the site sample room but the formal acceptance form cannot be located as hard copy or on eB
| 02SL - Stations (LUL) | Cxxx-NCR-001124 | NCR | Incorrect specification of ductwork installed - WTH EFR-W3 |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2018-10-26 | 2018-10-25 11:43 | -1 | 2018-10-03 13:20 | Mechanical - Heating Ventilation & Air Conditioning | 1500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Ventilation ductwork of incorrect specification has been installed in WTH riser 3/738 between levels -2 and -1. The ductwork is part of the battery extract system EFR-W3. Fire rated ductwork should have been installed, but non-fire rated 'DW144' ductwork has been installed instead. The Contractor had been given a deadline to raise this NCR, which has now passed.
| 02SL - Stations (LUL) | Cxxx-NCR-001125 | NCR | Re-design of WTH battery room extract system EFR-W3 |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2019-01-31 | 2019-02-13 17:30 | 13 | 2018-10-04 13:59 | Mechanical - Heating Ventilation & Air Conditioning | 2500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The Contractor has commissioned his EFR-W3 battery room extract fan system in the WTH and found that it unable to satisfy the volume flow rate design requirements. The Contractor has identified potential causes for the shortfall in performance, such as the configuration and sizes of sections of the installed ductwork. Rather than re-work the installation to achieve the gated design flow rate the Contractor has revisited the calculations and concluded that the design duty for the fan system can instead be greatly reduced to a level that is achieved by the current installation. The PM has given the Contractor over a week to raise this NCR, with the final deadline having now passed.
| 02SL - Stations (LUL) | Cxxx-NCR-001126 | NCR | Damaged motorised fire damper to be replaced - EFR-W3 |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2018-11-30 | 2018-11-26 11:02 | -4 | 2018-10-05 14:55 | Mechanical - Heating Ventilation & Air Conditioning | 6000 |  | Workmanship | Rework | 3 (3-6k) | Complete | Management Problem - Inadequate supervision | Completed |  | The Contractor has damaged a motorised damper (MFD W181) on the WTH battery extract fan system. The Contractor has confirmed that a replacement damper is required and that this has already been procured. The MFD was also the incorrect type. The replacement damper procured by the Contractor shall be an 'off-the-wall' type of MFD.
| 02SL - Stations (LUL) | Cxxx-NCR-001127 | NCR | Removal of ductwork in riser 3/745 to facilitate completion of lagging and installation of damper plates |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2019-01-31 | 2018-12-21 10:26 | -41 | 2018-10-09 14:46 | Mechanical - Heating Ventilation & Air Conditioning | 1000 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | The Contractor has failed to correctly sequence his installation works in WTH riser 3/745, and consequently must now remove segments of installed supply and extract ductwork in order to safely complete the installation of damper plates and thermal insulation at high level in the riser. The Contractor's deadline for raising this NCR has passed.
| 02SL - Stations (LUL) | Cxxx-NCR-001128 | NCR | WTH Ground Floor - Relocation of speaker |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2018-12-21 | 2018-12-11 10:36 | -10 | 2018-10-10 12:36 | Electrical - General | 1000 |  | Design | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Relocation of speaker and conduit in WTH ground floor cleaners room
| 02SL - Stations (LUL) | Cxxx-NCR-001129 | NCR | WTH Level -1 water pipework co-ordination |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-01-31 | 2018-12-21 11:48 | -41 | 2018-10-11 09:55 | Mechanical - Piping | 1000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | The pipework shown in the picture will obstruct the access to damper access hatch, cms and damper interface box. This needs to be co-ordinated See attached email communication
| 02SL - Stations (LUL) | Cxxx-NCR-001130 | NCR | GYB level -5 Non Compliant Floor SRV |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-01-31 | 2019-08-12 13:26 | 193 | 2018-10-11 10:35 | Architectural - Flooring | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | __ carried our SRV testing to 2 locations at GYB level -5 Non Compliant Floor SRV on 10/10/18. THis was done due to concerns on few shine areas of painted floor. THe 2 location failed the test when wet achieving average SRV of 33.25
| 02SL - Stations (LUL) | Cxxx-NCR-001131 | NCR | WTH Block D roof waterproofing co-ordination |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2018-12-31 | 2019-01-17 10:29 | 17 | 2018-10-19 08:43 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | 1. As built +6 roof membrane extensively damaged since installation 2. As built +6 RFS 108 was not protected after installation 3. +7 roof membrane damaged 4. details not full co-ordinated with RFS 108 5. +6 Defective concrete Damage and surface cracking
| 02SL - Stations (LUL) | Cxxx-NCR-001132 | NCR | Cash counting desk - WTH Room 1/23 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2018-11-26 | 2019-01-18 11:08 | 53 | 2018-10-29 16:38 | Architectural - General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | During a meeting with __, CRL, __ and LU, it was recommended the cash counting desk in WTH Room 1/23 was ordered from supplier __. However, after ordering two options of desk from __, LU stated the desk must comply with a new standard - LU Cat 1 Standard S1375 – Design for Ticket Issuing Facilities. Neither of the desks ordered comply with this standard.
| 02SL - Stations (LUL) | Cxxx-NCR-001133 | NCR | GYB Level -3 - MFD-E34 (ESR Room Extract Ductwork) Replacement |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2018-11-27 | 2018-11-29 14:02 | 2 | 2018-10-30 13:17 | Mechanical - Heating Ventilation & Air Conditioning | 10000 |  | Incorrect Installation | Rework | 2 (6-60k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The contractor highlights the re-work associated with MFD-E34 serving ESR room GYB -3. The contractor was required to replace the MFD in order to achieve an installation compliant with the manufactures requirements to fit the closing angle plates on the referenced MFD.
| 02SL - Stations (LUL) | Cxxx-NCR-001134 | NCR | __ - Pull test of PAEE cabinet fixings - adajacent to cabinet |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2018-11-27 | 2018-11-29 16:54 | 2 | 2018-10-30 14:43 | Archaeology - General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | Due to inaccessibility of the PAEE cabinet floor fixings sacrificial anchors were placed adjacent to cabinet 7 to ensure the 10% test requirement was met. Attached is an email from __ quoting the CFA guidelines and stating that they see no issue with this.
| 02SL - Stations (LUL) | Cxxx-NCR-001135 | NCR | __ - Public seating bench pan - visible welds |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2018-11-28 | 2018-11-20 18:05 | -8 | 2018-10-31 12:11 | Architectural - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Upon inspection it was noted that there were visible deformations in the seat pan finish, this was due to plates being welded to the underside of the pans that did not comply with the Cxxx intent.
| 02SL - Stations (LUL) | Cxxx-NCR-001136 | NCR | Re-work - MFD-E37 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-01-31 | 2019-01-30 08:53 | -1 | 2018-11-05 16:51 | Mechanical - Heating Ventilation & Air Conditioning | 1000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The contractor highlight the re-work associated with correcting alteration for the ductwork serving PFR-E1 GYB -3, MFD-E37 requires alterations in order to move the damper over approx. 10mm in order to fit the damper plates, note that there may be CMS, cable & fire stopping alterations associated with this. 2 of the damper plates are to be replaced as they have been cut down.
| 02SL - Stations (LUL) | Cxxx-NCR-001137 | NCR | Urban Realm - Drainage ITP |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-06-03 | 2019-07-16 12:58 | 43 | 2018-11-07 10:13 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | The Urban Realm drainage ITP Rev 1.0 was accepted as code 1, Rev 2.0 made two changes and was given issued code 3. At the time work continued as a code 1 ITP had been in place, while the issues with the Rev 2.0 to dealt with. The ITP remains code 3.
| 02SL - Stations (LUL) | Cxxx-NCR-001138 | NCR | GYB - Urban Realm - Drainage run bedding |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-06-30 | 2019-05-22 17:04 | -39 | 2018-11-07 11:43 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | CRL requested an NCR be raised for a section of drainage run on the south elevation of GYB. CRL did not witness pipe bedding material being installed or being in place. The Contractor is able to provide evidence in the form of check sheets, photos and concrete tickets to prove the required bedding material was placed around the pipe prior to backfill.
| 02SL - Stations (LUL) | Cxxx-NCR-001139 | NCR | Westbound Platform CIS screen installation |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2018-12-06 | 2018-12-18 10:46 | 12 | 2018-11-08 11:48 | Communications and Control Systems | 2000 |  | Design | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | The westbound platform CIS screen has been installed/tested and IRN signed off however it has been installed inline with the Cxxx cable schedule and not inline with GA layout, therefore it has to be re-located and re-offered for acceptance.
| 02SL - Stations (LUL) | Cxxx-NCR-001140 | NCR | PFR-W1 - Ductwork re-work required to acheive design duty |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2018-12-09 | 2019-08-02 12:24 | 236 | 2018-11-11 15:22 | Mechanical - Heating Ventilation & Air Conditioning | 150000 |  | Design | Rework | 1 (>60k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The contractor highlights the ductwork alterations associated with PFR-W1 as a result of excessive system pressure losses on the ventilation system as a result of; poor design flow conditions due to limited space & construction restraints as well as excessive pressure loss due to manufacturing details. The manufacturing of the ductwork system intake plenum's on this system has multiple internal flanges which the shoes/connections are cut out in between (see attached photos) causing excessive pressure loss, the contractor has had confirmation from the sub-contractor that the referenced 'blockages' which are increasing the pressure loss on the system can be removed and internally butt strapped to reduce the losses and improve flow conditions of the system. There is also a VCD installed on each of the fans on the intake/suction side of PFR-W1a/b which has been installed in line with the specification requirements in order to isolate the stand-by fan in the even of maintaining it, the contractor will be proposing to remove the mentioned VCD's in order to reduce the system loss and try to achieve the required duty. Although the vcd's form part of the specification requirements the contractor see's no purpose for the mentioned VCD's as they are not for balancing purposes they are for isolation of which could be achieved with a cap end. The contractor also highlights that the removal of the VCD's will prevent unwanted tampering of the life safety system. VCD's are to be replaced with make up sections of fire rated ductwork.
| 02SL - Stations (LUL) | Cxxx-NCR-001141 | NCR | GYB_Intervention Stairs Landing Level -2 Screed |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-06-30 | 2019-07-11 13:38 | 11 | 2018-11-14 08:46 | Architectural - Flooring | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Area of screed has been damaged due to material transport at GYB stairs landing Level -2.
| 02SL - Stations (LUL) | Cxxx-NCR-001142 | NCR | Electrical items in front of PFR 1 WTH -1 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-01-31 | 2019-11-18 12:14 | 291 | 2018-11-23 14:03 | Electrical - General | 1500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Within PFR1 WTH -1 the luminaire conduit installation is such that should the removal of the fan be required, unreasonable electrical strip-out would be required.
| 02SL - Stations (LUL) | Cxxx-NCR-001143 | NCR | Radio antenna in front of PFR 3 fan WTH -1 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-01-14 | 2019-05-13 14:10 | 119 | 2018-11-23 14:24 | Electrical - General | 1000 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Within PFR3 WTH -1 the radio antenna installation is such that should the removal of the fan be required, the antenna would be in the way.
| 02SL - Stations (LUL) | Cxxx-NCR-001144 | NCR | Electrical items installed in front of PFR 4 WTH -1 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-01-31 | 2021-04-27 09:54 | 817 | 2018-11-23 14:46 | Electrical - General | 30000 |  | Supervision/Management | Rework | 2 (6-60k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Within PFR4 WTH -1 the electrical trunking, conduits, and radio antenna is such that should the removal of the fan be required, unreasonable electrical strip-out would be required.
| 02SL - Stations (LUL) | Cxxx-NCR-001145 | NCR | Urban Realm - Witness Point Inspection Requests |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-10-31 | 2019-06-03 07:56 | -150 | 2018-11-28 09:43 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Not Defined | Completed |  | Urban Realm works are in progress and it was noted that IRF's ( Inspection Requests) have not been formally submitted progressively for required ITP witness points inspection
| 02SL - Stations (LUL) | Cxxx-NCR-001146 | NCR | Smoke downstand and GFRC interface not as per the design drawings |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2018-12-27 | 2019-02-22 12:19 | 57 | 2018-11-29 15:22 | Architectural - General | 500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Error by manufacturer in shipping or marking | Completed |  | The interface between the GFRC and the smoke downstands are not as per the design drawing (see Cxxx-LAO-Y-DWG-N105_WS089_5-50189). The gap between the surrounding GFRC panels is greater than the specified 70mm on the design drawing, resulting in visibility of the smoke downstand bracketry (see attached photos).
| 02SL - Stations (LUL) | Cxxx-NCR-001147 | NCR | Broken PSD glass on Westbound platform |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2018-12-27 | 2019-03-05 16:36 | 68 | 2018-11-29 15:39 | Architectural - General | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | It was reported to the Contractor that, during works on the temporary door, a PSD glass panel broke.
| 02SL - Stations (LUL) | Cxxx-NCR-001149 | NCR | Urban Realm - __ Assurance |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2019-06-30 | 2019-05-22 17:09 | -39 | 2018-12-05 14:38 | Civil - Drainage | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | Under the Works Information Part 13 Clause 13.2 Assurance the Contractor has failed to provide progress assurance that the constructed works comply with the requirements set out in the contract. __ assurance means that there will be continual confirmation of compliance by the generation of contemporaneous records. This is demonstrated by the following chronological events set out below. 2/11/2018 (refer Att 01 and Att 02) Goslett Yard drainage installation was in progress, given the stage of works observed at that time the following ITP inspection activities must have taken place previously:- Drainage Installation -5A.1 Setting out -5A.2 Check pipe diameter -5A.3 Excavation -5A.5 Check for obstructions -5A.6 Inspect formation -5A.7 Place pipe bedding -5A.8 Install pipework 5/11/2018 (refer Att.03) Goslett Yard drainage installation complete, given the stage of works observed at that time the following ITP inspection activities had taken place prior to that:- Drainage Installation -5A.1 Setting out -5A.2 Check pipe diameter -5A.3 Excavation -5A.5 Check for obstructions -5A.6 Inspect formation -5A.7 Place pipe bedding -5A.8 Install pipework -5A.9 CCTV survey -5A.10 Carry out as-built survey -5A.11 Place pipe surround -5A.12 Backfill to formation level 5/11/2018 (refer Att.04) Drainage installation checksheet dated 5/11/2018 was presented
| 02SL - Stations (LUL) | Cxxx-NCR-001150 | NCR | WTH CER Room - MFD Re-work |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-02-27 | 2019-02-11 16:09 | -16 | 2018-12-10 17:21 | Mechanical - Heating Ventilation & Air Conditioning | 30000 |  | Design | Rework | 2 (6-60k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The contractor highlights the re-work required in WTH -3 CER room to MFD-W46 & MFD-W194/W195. The current installation & design does not provide the required spacing in order to install the damper plates. Re-work will include disconnecting the fire alarm and altering any CMS currently clashing with the required location for damper plates. MFD-W194/W195 are to moved over to increase the spacing between them (fire stopping to be cut out, damper to be re-positioned, fire alarm cable to be reconnected, fire stopping to be re-dressed & ductwork to be re connected, ). MFD-W46 - damper to be removed and a smaller damper to be installed in its place (500 x 500)to suit requirements for plates, note the design check has been carried out for the reduction. (fire stopping to be cut out, damper to be re-positioned, fire alarm cable to be reconnected, fire stopping to be re-dressed & ductwork to be re connected.
| 02SL - Stations (LUL) | Cxxx-NCR-001151 | NCR | __ Cladding Fixing Bracket |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-01-31 | 2019-01-21 16:15 | -10 | 2018-12-11 09:07 | Architectural - Glazing | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | the fixing of the panels as has currently taken place is not supported by the sub-contractors specialist engineer. As a consequence __ are working with DR to develop a solution which will require the panels to have the fixings amended, the details are awaited.
| 02SL - Stations (LUL) | Cxxx-NCR-001152 | NCR | WTH - Urban Realm - Dean St - Pavement bedding |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-02-12 | 2019-06-04 14:31 | 112 | 2018-12-14 16:20 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | WTH – Dean St North An area of concrete sub base was laid deeper than design (200mm). Please see attached photos of slab depth. As a result the bedding mortar in this area was lowered (below the 50mm design depth) to ensure the designed FFL was achieved. Mortar bedding depths of between 70mm & 35mm were found in multiple locations, in one location a depth of 25mm was identified.
| 02SL - Stations (LUL) | Cxxx-NCR-001153 | NCR | VWW Sprayed Concrete - Missing Slump Test Result |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-03-29 | 2019-03-07 12:37 | -22 | 2019-01-07 11:49 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | The slump test result for the spray lined concrete for VWW opening works was not recorded as specified under item 3.5 of ITP Cxxx-LAO-O4-ITP-N105_WS089_Z-50075.
| 02SL - Stations (LUL) | Cxxx-NCR-001154 | NCR | GYB AP9A- Making good to LUL link wall |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-08-29 | 2019-09-06 12:29 | 8 | 2019-01-07 21:50 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The sub-contractor working under __ were instructed to install structural steel work in AP9A to accommodate a door leading into LEER room 10 and to support grillage. During the install a section of concrete was damaged and broke away. Area has been broken out, cleared and made good with Monomix HD. CRL were not invited for a pre inspection by __ prior to making good.
| 02SL - Stations (LUL) | Cxxx-NCR-001155 | NCR | Unique Sign 312 Not Visible From CH1 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-06-28 | 2019-06-19 08:37 | -9 | 2019-01-17 17:15 | Architectural - Signage | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The installation of sign USN 312 is not compliant with section 7.3 of the TfL signage standard - LU Signs Manual. The standard requires ‘way out/emergency exit’ signs to be repeated every 15m. The emergency exit sign USN 312 is not visible from within Ch1, or 15m away. In addition where the ‘way out/emergency exit’ routes divide at the junction of Ch1 and WTH -4 level the placement of sign USN 312 is not compliant with section 6.3 of the LU Signs Manual, the standard requires that: “ At each decision point within sub-surface Underground stations, there must be an illuminated ‘Way Out’ sign (or emergency exit where applicable) clearly visible in case of an emergency evacuation”.
| 02SL - Stations (LUL) | Cxxx-NCR-001156 | NCR | Gaps Between Recon Stone and WTH -4 Soffit |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-02-14 | 2019-04-17 15:21 | 62 | 2019-01-17 17:20 | Architectural - Walls | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | The works information - Cxxx-LAO-A-DDC-N105_Z-20216 – indicates that the joint between the black recon cladding panels in WTH with the concrete soffit and downstand beams is to be 10mm. The installation has a joint in excess of this, at least 50mm. This is particularly noticeable at the junction of the cross beams – ref photo attached.
| 02SL - Stations (LUL) | Cxxx-NCR-001157 | NCR | Rusty Damper plates |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-02-21 | 2020-04-07 14:38 | 411 | 2019-01-24 09:02 | Mechanical - Heating Ventilation & Air Conditioning | 1500 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper handling of material | Completed |  | WTH -2 accommodation area - Minor rusting of the damper plates as per attached photo
| 02SL - Stations (LUL) | Cxxx-NCR-001158 | NCR | Sump Pump Panels delivered on site without adequate FAT docs |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-04-30 | 2019-04-11 15:07 | -19 | 2019-01-31 11:30 | Mechanical - Pumps | 2000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | the SCADA Sump Pump FAT held in June was extremely disorganised. The panels installed on site, while the FAT documentation / certification is outstanding Works have progressed with gaps in the ITP. Standard factory delivered items (eg factory fitted cables on submersible pumps) which have been subjected to on site modifications such as jointing and adding SWA for mechanical protection are not reflected in the current ITP for the required electrical testing.
| 02SL - Stations (LUL) | Cxxx-NCR-001159 | NCR | TCR Entrance Fascia Signage |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-02-22 | 2019-07-19 09:48 | 147 | 2019-02-05 09:12 | Architectural - Signage | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The currently installed Tottenham Court Road entrance fascia unique sign number 002 is not in line with the Elizabeth Line Standards. Although the sign is in line with the Cxxx signage schedule Cxxx-ATK-A-RGN-CRG02-50042 and Cxxx signage schedule Cxxx-LAO-A-XDS-N105_WS089-50002 this is not in line with Elizabeth Line Standard CRL1-XRL-A-STD-CRG03_Z-50001.
| 02SL - Stations (LUL) | Cxxx-NCR-001160 | NCR | Automatic Transfer Switches |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-08-30 | 2019-09-18 13:11 | 19 | 2019-02-06 07:49 | Electrical - LV Equipment | 1500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | Following recent site surveys / investigations the following faults have been identified on the ATS:- • Incorrect ATS Bias - During the installation of the submains cabling the ATS supplies feeding 12 number ATS have been installed to suit the CMS installation and not as the Schematics. • Incorrect Source Button Colour - Source button lens cap colour not in accordance with BS 60204 10.2.1 • Duty and Standby LED Indication Lamps both Illuminated - Induced voltage found (0.8v to 2.0v) across lamp not in use, (other Burnell supplied projects have the same issue). • Investigate the lack of illumination on the Duty Supply Available/Standby Supply Available lamp indicators and upon resolution of this issue undertake a further test to demonstrate that the indicators are not illuminated via any form of back feed when the supplies are isolated (Investigation results TBC).
| 02SL - Stations (LUL) | Cxxx-NCR-001161 | NCR | GYB -West Elevation Asphalt Dips |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-04-06 | 2019-06-04 14:33 | 59 | 2019-02-05 13:33 | Civil - Streets & Highways | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Supervision - Other | Completed |  | Asphalt dips below minimum required
| 02SL - Stations (LUL) | Cxxx-NCR-001163 | NCR | __anks - overflow beneath high level alarm |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-05-31 | 2019-05-13 09:09 | -18 | 2019-02-06 15:31 | Fire - Suppression | 5000 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | The overflow pipes for the __supplied mist tank and hydrant tanks are at a lower level than the high level float alarms. This will now require on site modifications to correct.
| 02SL - Stations (LUL) | Cxxx-NCR-001164 | NCR | Geothermal Cooling Test report |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-10-31 | 2019-09-10 14:37 | -51 | 2019-02-06 15:37 | Mechanical - Mechanical Engineering General | 2000 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Following a review of the GSHP report Cxxx-LAO-Y-XCL-N105_WS089_Z-50137 by __ (GI), 1) Test methodology does not align with specification. See comment sheet Cxxx-LAO-Y-XCS-N105_WS089_Z-50277. 2) Application of Straight Line Theory is identified as unsuitable for installation of large piles, yet the test has proceeded. The specialist contractor has written “the results produced are of low quality therefore limiting interpretation and confidence in determination.” The conclusion is therefore meaningless.
| 02SL - Stations (LUL) | Cxxx-NCR-001165 | NCR | __ Manufacturing Deliverables |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-03-11 | 2019-03-13 12:13 | 2 | 2019-02-11 09:15 | Architectural - Glazing | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | Upon the review of the __ manufacturing packs it has become evident that a number of the manufacturers of the glazing and stainless steel system components are unable to provide the verifying documents identified as deliverables within the accepted Code 1 manufacturing ITPs. These missing deliverables are job sheets, cutting lists, work orders etc. To mitigate against the above and to provide assurance for the installations mentioned above, the various manufacturers have provided certificates of conformity/compliance as proof that the relevant QA checks to the relevant standards have been undertaken during manufacturing processes. The Specialist Contractor DR and The Contractor __ therefore propose to provide the following items to The Project Manager for the assurance of the above items: • Certificates of conformity / compliance from the various manufacturers • The attached statement from __ to support the manufacturer compliance • Amended ITPs to cover the above proposed change The three items above are attached for review by The Project Manager.
| 02SL - Stations (LUL) | Cxxx-NCR-001166 | NCR | PFR W4 A&B IRN 376 Pull Tests |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-03-12 | 2019-10-11 13:57 | 213 | 2019-02-12 14:30 | Mechanical - Heating Ventilation & Air Conditioning | 1000 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | The Contractor wishes to confirm his discussion with the Project Manager in relation to __ not working in accordance with the ITP by not carrying out 100% pull tests on this system. The Contractor confirms approx. 65-70% of the fixings on this system have been pull tested and relevant test results form part of the IRN. The Contractor will identify the brackets/supports that cannot be tested and will issue with reasons to the PM (__) as a record which will ultimately accompany the IRN/PCC
| 02SL - Stations (LUL) | Cxxx-NCR-001167 | NCR | WTH - Block D Level +5 Smoke Extract Riser Leak |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-06-28 | 2019-06-04 14:57 | -24 | 2019-02-12 16:03 | Civil - Civil Engineering General | 5000 |  | Material | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | An ingress of water into the +5 Smoke Extract Riser room E780 has been identified WC the 4th of Feb. The leak was identified in the NW corner of the room.
| 02SL - Stations (LUL) | Cxxx-NCR-001168 | NCR | Damage to floor tiles in AP4 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-03-19 | 2019-02-26 15:53 | -21 | 2019-02-19 08:56 | Architectural - General | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Approximately 25 floor tiles in AP4 are damaged and the surface cannot be cleaned.
| 02SL - Stations (LUL) | Cxxx-NCR-001169 | NCR | Cxxx - FOH Asset labeling not line with CRL labeling guidelines |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-04-30 | 2019-09-13 13:04 | 136 | 2019-02-20 13:09 | Communications and Control Systems | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Insufficient information made available to the worker. | Completed |  | __ have installed the FOH labeling on the PES and FOH areas not inline with CRL asset identification standard – CRL1-XRL-O6-STD-CR001-00031 Therefore we will need to carry out some remedial works. One the installed labels are removed they will no longer be able re-used (self adhesive). Can we request the following PAVA/RADIO asset labels to be re-printed and issued to __
| 02SL - Stations (LUL) | Cxxx-NCR-001170 | NCR | Broken GFRC panels |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-03-21 | 2019-04-15 13:52 | 25 | 2019-02-21 17:20 | Architectural - General | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | Several GRFC panels have been damaged on site, requiring panels to be remade
| 02SL - Stations (LUL) | Cxxx-NCR-001171 | NCR | Interface between GFRC panels and platform cabinets not to design |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-04-03 | 2019-10-11 10:50 | 191 | 2019-03-06 11:28 | Architectural - General | 500 |  | Incorrect Installation | Reject | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The gap between the GFRC panels and the top of the platform cabinets is not compliant with the works information Cxxx-ATK-A-DDD-CR001_Z-43701 detail 2.
| 02SL - Stations (LUL) | Cxxx-NCR-001172 | NCR | Protected 230V Maintainer socket |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-04-03 | 2019-08-29 08:17 | 148 | 2019-03-06 15:12 | Electrical - Power Distribution | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Protected 230V Maintainer socket absent in sump pump MCC’s - Requirement of Cxxx __ electrical specification JV22.1302. No 230V sockets present in __ MCC’s
| 02SL - Stations (LUL) | Cxxx-NCR-001173 | NCR | __ Sump Pumps - FAT certs |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-04-03 | 2019-03-20 13:25 | -14 | 2019-03-06 15:22 | Mechanical - Public Health Engineering | 10000 |  | Documentation and Records | Rework | 2 (6-60k) | Complete | Management Problem - Inadequate supervision | Completed |  | WI specification requirement JR20.1402: “All PLC software, pumps and panels shall be witness tested in the factory and a Factory Acceptance Test (FAT) certificate shall be provided.” Cxxx had not issued prior to delivery Requirements of WI Vol 2B requirements Section 28.2.2.1 “Factory acceptance tests (FATs) shall be satisfactorily completed by the Contractor before shipment to Site”.
| 02SL - Stations (LUL) | Cxxx-NCR-001174 | NCR | Public Health Equipment - Fly Lead MCR |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-04-03 | 2020-10-20 12:26 | 566 | 2019-03-06 15:29 | Mechanical - Public Health Engineering | 2500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | unarmored cable and PVC cable on small PH items - Supplied as part of the approved (LU approved) equipment such as water heaters
| 02SL - Stations (LUL) | Cxxx-NCR-001175 | NCR | AP7b GFRC soffit not compliant |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-04-08 | 2019-06-14 14:01 | 67 | 2019-03-11 15:08 | Architectural - General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | AP7b GFRC soffit panel joints are misaligned.
| 02SL - Stations (LUL) | Cxxx-NCR-001176 | NCR | Use of wedge anchors to support electrical services (lighting trough system) within stainless steel suspended ceiling system |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-11-30 | 2019-11-13 13:57 | -17 | 2019-04-05 11:22 | Electrical - Cable Management | 5000 |  | Incorrect Installation | Use As-Is | 3 (3-6k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | Use of wedge anchors to support electrical services (lighting trough system) within stainless steel suspended ceiling system.
| 02SL - Stations (LUL) | Cxxx-NCR-001177 | NCR | WTH -4 smoke downstand alignment |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-08-31 | 2019-10-23 16:01 | 53 | 2019-04-12 06:31 | Architectural - General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | “During an inspection of the WTH -4 smoke down stand screen over the escalator it was noted that the glass is 30mm out of plumb which exceeds the architectural install tolerances. The Contractor proposes to leave this item as is because it’s location means the non conformity will be extremely difficult to spot by passengers when the station opens (because it is located at the bottom of the steps so passengers will be concentrating on alighting) and the misalignment has no impact on the performance requirements of the screen.”
| 02SL - Stations (LUL) | Cxxx-NCR-001178 | NCR | Air release system pressure sensor replacement |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2019-08-29 | 2019-09-25 13:19 | 27 | 2019-04-12 10:55 | Mechanical - Mechanical Engineering General | 5000 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Phase 2.2 testing of the air release and stair pressurisation systems has concluded that the pressure sensors measuring the pressure differential between each lobby and accommodation area need to be replaced with sensors rated for a greater pressure range. This is due to a spike in pressure that exceeds the range of the existing sensor each time a lobby to accommodation door closes whilst the air release fan is operating at full speed. The existing sensor is rated to read pressures up to 100Pa. Air release schematics Cxxx-M-DDE-21800 (rev X01) and 22800 (rev X01) show that there are 19 DPS switches requiring pressure sensor replacement.
| 02SL - Stations (LUL) | Cxxx-NCR-001179 | NCR | M4 Natural Mortar - Prism Test Sample 28/04/2017 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-08-31 | 2019-09-18 16:51 | 18 | 2019-06-10 09:07 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | Prism mortar testing did not achieve it's required strength of 4N/mm^2.
| 02SL - Stations (LUL) | Cxxx-NCR-001180 | NCR | Sump fixings & Sump Brackets |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2019-08-30 | 2019-07-11 12:28 | -50 | 2019-04-24 10:08 | Mechanical - Public Health Engineering | 8000 |  | Incorrect Installation | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | Non-stainless HUS-3 fixings have been used in all the wet well sumps and have already started to rust. These fixings are not suitable for a submerged environment. No MCR submitted for cable support bracket. This bracket is required to be made of stainless steel with stainless fixings, refer to electrical specification JV20.1309. Bracket material is not verified, fixings are non-stainless.
| 02SL - Stations (LUL) | Cxxx-NCR-001181 | NCR | PES Lighting Control |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-08-30 | 2019-09-04 18:08 | 5 | 2019-05-08 13:42 | Electrical - Lighting | 1500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | It appears that the wiring to the PES lighting has not been correctly installed and has omitted 2 of 3 of each of the drivers to the light units. This will require to be reinstalled and amended in order to achieve the required control functionality
| 02SL - Stations (LUL) | Cxxx-NCR-001182 | NCR | Level -4 Telepphone Cable over length |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-08-30 | 2019-09-03 10:50 | 4 | 2019-05-09 10:55 | Communications and Control Systems | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Information not detailed | Completed |  | On handover of the Level -4 the contractor confirms there are 3 cables that ''failed'' due to be over length These are N105-TEL-00741 N105-TEL-00609 N105-TEL-00744 The T&C of these has been completed and the system ''works'' so Cxxx Design needs to confirm by return acceptance.
| 02SL - Stations (LUL) | Cxxx-NCR-001183 | NCR | Corroding ventialtion ductwork supports |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-08-31 | 2020-02-25 15:36 | 178 | 2019-05-16 13:26 | Mechanical - Heating Ventilation & Air Conditioning | 1500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | ductwork support bracketry provided by ventilation ductwork subcontractor __ is corroding. Photographs are attached showing corrosion identified during the past fortnight.
| 02SL - Stations (LUL) | Cxxx-NCR-001184 | NCR | Incorrect installation of E__ motorised control dampers on PFR-E4 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-08-31 | 2019-07-11 15:26 | -51 | 2019-05-16 13:59 | Mechanical - Heating Ventilation & Air Conditioning | 6000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | the motorized control dampers have been installed with the actuator on the top and the blades in a vertical position. The manufacturer has confirmed this is not acceptable and the blades need to be in a horizontal orientation.
| 02SL - Stations (LUL) | Cxxx-NCR-001185 | NCR | Platform Cabinets - Fire Stopping Corrosion |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-08-31 | 2020-07-31 08:19 | 335 | 2019-05-16 14:23 | Fire - Compartmentation | 1500 |  | Material | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | material corrosion post installation of fire compartmentation compound has been observed specifically within the platform cabinets.
| 02SL - Stations (LUL) | Cxxx-NCR-001187 | NCR | __ __ - Incorrect Thumb Turn Cylinder |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-08-13 | 2019-09-30 12:55 | 48 | 2019-05-30 12:08 | Architectural - Doors | 500 |  | Material | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Error by manufacturer in shipping or marking | Completed |  | When inspecting door D3-4/010, it was highlighted that the incorrect thumb turn cylinder has been installed on __ __ door set.
| 02SL - Stations (LUL) | Cxxx-NCR-001188 | NCR | __ __ - Security Screws in Ironmongery |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-10-31 | 2019-09-30 14:24 | -31 | 2019-05-30 12:15 | Architectural - Doors | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | On site inspection of __ __ doors, __ have inspected a number of __ __ doors with missing security screws within handles and handle plates.
| 02SL - Stations (LUL) | Cxxx-NCR-001189 | NCR | __ Doors |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-10-31 | 2019-11-05 08:38 | 5 | 2019-05-30 12:21 | Architectural - Doors | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | On inspection of __ doors, it has been highlighted that there are several security screws missing from ironmongery handle plates site wide. Vision panels for all northern line link doors consist of normal cross head screws.
| 02SL - Stations (LUL) | Cxxx-NCR-001191 | NCR | Fixings in SCL for service boom not as per MCR |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-07-02 | 2019-07-10 11:54 | 8 | 2019-06-04 10:00 | Architectural - General | 0 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | The fixings used to support the tunnel service boom are not as per the MCR issued on Eb (Cxxx-LAO-Y-XDS-N105_WS089_Z-500720) this MCR stated that stainless steel fixings were to be used. The fixings used are __ HSC (I) undercutting anchors which are electroplated. BZP fixings are generally not permitted on Crossrail due to technical alerts that have been raised due to failures of this type related to Hydrogen Embrittlement. Generally accepted fixings on Crossrail are either Hot Dip Galvanised, Stainless Steel or Mechanically applied zinc finish (e.g. __ Plus bolt). In this particular application of these anchors, there are several mitigating factors which reduce the risk of a potential failure and must be considered: • The __ HSC I fixings used in this application are grade 8.8 steel. Primarily, hydrogen embrittlement is observed in bolts of grade 10.9 or above. This is due to the manufacturing process which leaves bolts of this strength grading prone to failures of this type in certain conditions. It is very rare for such failures to occur on bolts graded 8.8 or lower. Please find attached technical notes from __ industry experts corroborating this. • In addition to the grading of the steel, it is also worth noting that the most common failure mechanism attributed to Hydrogen embrittlement is failure around or underneath the bolt head (again a result of the manufacturing process). It is less likely to occur in a threaded bar than a bolt. • The fixings being used in this application are being utilised in tension rather than in a shear capacity. • For information, the Sub-Contractor’s design Consultant has carried out a structural analysis of the largest service boom module and the calculation and report are attached. • There is sufficient redundancy within each service boom module as they have 8 fixings per element. In the unlikely event that 25% of the fixings were to be subject to Hydrogen embrittlement failure there would be no observable deleterious effect on the remainder of the structure. A new MCR has been drafted and sent across to Eb for CRL approval (Cxxx-LAO-Y-XDS-N105_WS089_Z-50089). This has also been attached.
| 02SL - Stations (LUL) | Cxxx-NCR-001192 | NCR | Disabled shower non compliance |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-08-06 | 2019-07-26 10:10 | -11 | 2019-06-04 09:53 | Mechanical - Public Health Engineering | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | The installed disabled shower mixing valve in WTH accommodation area is not compliant with building regulations part M and is awaiting approval from WRAS. Measured water temperature of 57 degrees C at outlet.
| 02SL - Stations (LUL) | Cxxx-NCR-001193 | NCR | Shower room ceiling access hatches not co-ordinated |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-08-06 | 2019-08-23 09:18 | 17 | 2019-06-04 10:08 | Mechanical - Public Health Engineering | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Insufficient work planning by the subcontractors | Completed |  | Shower room ceiling access hatches are not coordinated with shower isolation valve locations. Incomplete pipe insulation now obstructed by ceiling with no safe access.
| 02SL - Stations (LUL) | Cxxx-NCR-001194 | NCR | AHU cooling coil pipework re configuration |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-07-04 | 2019-07-08 15:49 | 4 | 2019-06-04 10:26 | Mechanical - Heating Ventilation & Air Conditioning | 3000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Insufficient information made available to the worker. | Completed |  | AHU cooling coils incorrectly connected to chilled water system.
| 02SL - Stations (LUL) | Cxxx-NCR-001195 | NCR | Incorrect pipe ID bandings installed on CAT5 pipework. Incorrect pipe ID bandings purchased for damp fire mains (station and tunnel) |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-08-06 | 2019-08-09 14:00 | 3 | 2019-06-04 11:14 | Mechanical - Mechanical Engineering General | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Information not detailed | Completed |  | Incorrect pipe banding installed on CAT5 pipework. The pipework banding installed is for potable water where CAT5
| 02SL - Stations (LUL) | Cxxx-NCR-001196 | NCR | Dean Street Louvre removal, installation of ductwork blanking plates and pipework surround |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-07-03 | 2019-08-02 12:30 | 30 | 2019-06-05 15:46 | Mechanical - Heating Ventilation & Air Conditioning | 10000 |  | Supervision/Management | Rework | 2 (6-60k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Louvre backing plates and vent pipework surround are required to prevent recirculation of exhaust air (toilet and sump) back into the station.
| 02SL - Stations (LUL) | Cxxx-NCR-001197 | NCR | Northern Line Link Doors - Opening Force |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2020-04-24 | 2020-04-24 14:45 | 0 | 2019-06-07 07:16 | Architectural - Doors | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | During inspection with CRL, it was noted that the Norther Line Link doors opening force was excessive. __ to further investigate the issue
| 02SL - Stations (LUL) | Cxxx-NCR-001198 | NCR | Prism Results Missing (28 day) 28/04/17 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-08-31 | 2019-09-18 16:54 | 18 | 2019-06-10 09:16 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | 28-day results for Prism sample taken 28th April 2017 are unable to be located for the inclusion of quality assurance package
| 02SL - Stations (LUL) | Cxxx-NCR-001199 | NCR | Damage to as installed Refuge Help Points |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-08-12 | 2019-07-18 11:44 | -25 | 2019-06-11 11:53 | Communications and Control Systems | 2000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Damage to as installed Refuge Help Points in GYB and WTH - Total quantity 2 together with 3 number Induction Loops.
| 02SL - Stations (LUL) | Cxxx-NCR-001200 | NCR | Signage Destinations on Totems and CH1 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-09-30 | 2019-09-18 14:08 | -12 | 2019-06-12 12:33 | Architectural - Signage | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | The Project Manager architectural team has raised a concern regarding the destination names shown on 4 signs (2 suspended in CH1 and 2 projecting totem signs). The Contractor advises that the destination names on the installed signs match those on the Cxxx signage schedule and those on Rev 4.0 Cxxx signage and wayfinding schedule. Whilst the Project Manager highlighted differences between that Revisions 4 and 5 of the Schedule the signs are compliant with the Works Information. Due to programme constraints the signs had been released for manufacture on the basis of information included in Revision 4.0 of this schedule. The Contractor will evaluate the expedient and cost effective way of changing the information on the sign to that now required by the Project Manager. As the change in information on the sign represents a change to the information with the Works Information a PMI will be required form the Project Manager to confirm this change.
| 02SL - Stations (LUL) | Cxxx-NCR-001201 | NCR | WTH Level -5 Sump and Catch Pit covers rusting |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-11-15 | 2019-11-07 16:53 | -8 | 2019-06-12 17:23 | Civil - Drainage | 1000 |  | Material | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | The access hatch to sump SW-W02 is showing advanced signs of corrosion. Other sump access and catchpits being investigated. The MCR are not readily available and suspected absent.
| 02SL - Stations (LUL) | Cxxx-NCR-001202 | NCR | PTW East - Insufficient manhole aperture to facilitate removal of 2 out of 4 sump pumps in SW-E02 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-10-31 | 2019-08-02 11:38 | -90 | 2019-06-12 17:31 | Civil - Civil Engineering General | 8000 |  | Design | Rework | 2 (6-60k) | Complete | Design Problem - Other | Completed |  | Insufficient manhole aperture to facilitate removal of 2 out of 4 sump pumps in SW-E02.
| 02SL - Stations (LUL) | Cxxx-NCR-001205 | NCR | Cooker Hood - Staff Mess Room WTH L-2 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-10-31 | 2019-10-11 11:04 | -20 | 2019-06-18 11:58 | Architectural - Finishes | 500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | The cooker hood has been installed to low for operation of the cooker hot plates. The instructions state that the cooker hood should be 800mm above the cooking surface – ie the hot plates. The cooker hood has been installed 1650mm off the floor, 800mm above the worktop, 450mm above the cooking surface. Cxxx-LAO-A-DDC-N105_3-20254 shows that the cooker hood should be 800mm above the worktop which is not consistent with the requirements of the hood. Unfortunately it appears that the hood is located to suit the plug which will require moving to get the hood up to a compliant level.
| 02SL - Stations (LUL) | Cxxx-NCR-001206 | NCR | Services blocking MFD's GYB L-5 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-11-30 | 2020-02-12 16:48 | 74 | 2019-06-19 05:45 | Electrical - General | 2500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During inspection, issues were identified for MFD access at GYB -5 . Summary below: Lobby 5/100 · PAVA, Comms, and Radio trays need to be re-routed. They block access to three number MFDs, preventing routine maintenance and inspection. See photo 1. · Power conduit is installed over the body of the MFD on the RHS of photo 9. This is to be relocated. __R Fire conduits installed over plates on both low level MFDs. These need to be re-routed. See photos 3 and 4.
| 02SL - Stations (LUL) | Cxxx-NCR-001209 | NCR | Installation of radio antenna |  | Crossrail | PDP | TCR - Tottenham Court Road Station (West) |  | 2019-07-26 | 2019-07-19 13:43 | -7 | 2019-06-28 09:41 | Communications and Control Systems - Radio | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | The square radio antenna are incorrectly installed into the brackets and housing and are required to be straightened up prior handover..
| 02SL - Stations (LUL) | Cxxx-NCR-001210 | NCR | Cracks in granazzo joints |  | Crossrail | PDP | TCR - Tottenham Court Road Station (West) |  | 2019-07-26 | 2019-10-18 12:51 | 84 | 2019-06-28 10:12 | Architectural - Flooring | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | External Phenomenon - Not Defined | Completed |  | Cracks are appearing in the joints to the granazzo flooring on the platforms. The cracks are generally located adjacent to the movement joints. Cracks joints need to be rectified and root cause established.
| 02SL - Stations (LUL) | Cxxx-NCR-001211 | NCR | Incomplete skirting |  | Crossrail | PDP | TCR - Tottenham Court Road Station (West) |  | 2019-07-26 | 2019-12-16 15:11 | 143 | 2019-06-28 16:09 | Architectural - Flooring | 500 |  | Incomplete Works | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Please be advised that there are areas of the skirting that are incomplete, where grout/mastic is missing or the skirting itself is missing.
| 02SL - Stations (LUL) | Cxxx-NCR-001212 | NCR | Quality of terrazzo skirting installation |  | Crossrail | PDP | TCR - Tottenham Court Road Station (West) |  | 2019-07-26 | 2019-12-16 15:15 | 143 | 2019-06-28 16:35 | Architectural - Flooring | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Please be advised that the quality of the installation of the terrazzo skirting is not consistent with the works information in that the edges are irregular an have been infilled with grout rather than effecting a proper repair of the skirting block. In addition at the interface of the tunnels with the boxes where the corner radii of the skirting differs to that of the GFRC the skirting has been backfilled with grout
| 02SL - Stations (LUL) | Cxxx-NCR-001213 | NCR | Gaskets between skirting and wall cladding |  | Crossrail | PDP | TCR - Tottenham Court Road Station (West) |  | 2019-07-26 | 2020-09-29 16:47 | 431 | 2019-06-28 16:44 | Architectural - Flooring | 500 |  | Incomplete Works | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During a general walk about I could not find any location where a gasket had been installed to fill the gap behind the terrazzo skirting.
| 02SL - Stations (LUL) | Cxxx-NCR-001214 | NCR | __ Flooring - Cracked movement joints in Terrazzo |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2021-12-07 | 2021-11-10 18:43 | -27 | 2021-11-09 08:04 | Architectural - Flooring | 500 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Other | Completed |  | In multiple tile movement joints across the platforms and passageways have cracked both within the movement joint and within the adjacent grout joint.
| 02SL - Stations (LUL) | Cxxx-NCR-001215 | NCR | Distribution Board spare capacity for future expansion not achieved. |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-11-30 | 2020-02-07 15:28 | 69 | 2019-07-01 15:58 | Electrical - Switchgear | 5000 |  | Design | Use As-Is | 3 (3-6k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Distribution Boards installed without the required 25% spare capacity.
| 02SL - Stations (LUL) | Cxxx-NCR-001216 | NCR | External Cills On Dean & Fareham Street |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-08-21 | 2019-10-23 15:57 | 63 | 2019-07-24 08:06 | Architectural - Walls | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The Project Manager TCR Station Architect has advised that the cills installed at the base of the louvre and fin installations on Dean and Fareham Street externally do not satisfy the Crossrail Security Standard. The Project Manager TCR Station Architect has advised that the Crossrail Security Advisor has advised that the cills need to be angled rather than flat to satisfy the Crossrail Security Standard. The Contractor requests clarification as to the required angle of the cill to allow The Contractor to develop a compliant and cost effective solution.
| 02SL - Stations (LUL) | Cxxx-NCR-001217 | NCR | Unidentified quantum of Electrical DB calculated results |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-08-23 | 2020-02-21 15:28 | 182 | 2019-07-26 10:01 | Electrical - General | 2500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Inspection points not adequate | Completed |  | In conjunction with RFI numbered Cxxx-RFI-002094, the contractor has requested confirmation from CRL on the quantum of measured electrical test results for both Distribution Boards and MCC Panels. This NCR is raised for the following two number Distribution Boards which have been issued at PCC Stage with 100% calculated results:- IRN 227 DB-B-2002 IRN 1120 DB-E-U0441.
| 02SL - Stations (LUL) | Cxxx-NCR-001218 | NCR | Damage to Block D concrete sill by external lighting installation |  | Crossrail | PDP | TCR - Tottenham Court Road Station (West) |  | 2020-08-09 | 2020-12-22 12:32 | 135 | 2019-07-26 14:54 | Architectural - Finishes | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The junction box feeding the external light on Block D, Great Chapel Street, north west corner has been installed by cutting out a section of the pre-cast concrete sill, creating significant permanent damage to the sill. This does not comply with the works information. Refer to attached photo.
| 02SL - Stations (LUL) | Cxxx-NCR-001219 | NCR | OSD Residential Water Connection Block D |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-09-20 | 2019-11-15 15:43 | 56 | 2019-07-26 15:57 | Civil - Utilities Engineering | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | After installing the water pipe that runs from the Dean Street water main to the connection point into the OSD Block D residential unit (Fareham Street), the areas at each end of the run where the connections were to be made were paved over. This was because it was believed to be no longer required although this is not the case.
| 02SL - Stations (LUL) | Cxxx-NCR-001220 | NCR | PES grille interface with GFRC/concrete beam and concrete soffit - WTH/PTE |  | Crossrail | PDP | TCR - Tottenham Court Road Station (West) |  | 2019-10-04 | 2019-10-11 11:01 | 7 | 2019-07-26 15:59 | Architectural - Finishes | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | There are 3 areas of stainless steel trim installed on the PES that are not compliant with the Works information: 1 - Interface of the PES grille and the concrete beam - non compliance; 2 - Interface of the PES grille with the concrete soffit - unacceptable quality; 3 - Interface of the PES grille with the GFRC at the WTH box/tunnel junction - non compliance with the Works Information.
| 02SL - Stations (LUL) | Cxxx-NCR-001221 | NCR | Unidentified quantum of Electrical DB calculated test results |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-08-27 | 2020-02-21 15:33 | 178 | 2019-07-30 15:53 | Electrical - General | 2500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Inspection points not adequate | Completed |  | In conjunction with RFI numbered Cxxx-RFI-002094, the contractor has requested confirmation from CRL on the quantum of measured electrical test results for both Distribution Boards and MCC Panels. This NCR is raised for the following five number Distribution Boards which have been issued at PCC Stage with 100% calculated results:- IRN 290 DB-E-1413 IRN 261 DB-E-2006 IRN 946 DB-U-2306 IRN 256 DB-E-2406 IRN 272 DB-E-2403.
| 02SL - Stations (LUL) | Cxxx-NCR-001222 | NCR | Door subcontractors not snagging the install; inconsistencies between schedule, fabrication drawings and install. |  | Crossrail | PDP | TCR - Tottenham Court Road Station (West) |  | 2019-10-31 | 2020-07-02 17:44 | 245 | 2019-08-01 09:38 | Architectural - Doors | 500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Door subcontractors __ __ and __e are not snagging the installation of their works. This is apparent from the excessive list of snags - see attached IRF -. The lack of inspection and snagging by the subcontractors results in the __ package manager and the CRL FA inspections and remedial actions taking much longer than anticipated. If this continues it will put the programme for SC3 at risk; There is no valid up to date schedule for __ and CRL to inspect to, the fabrication drawings offered are regularly inconsistent with the install, it is not known which is correct or what performance the door is supposed to meet. Without a valid schedule it is not known how __ are able to manage the installation package properly; CRL have concerns over the stress and pressures being placed on the current package manager to meet a programme that is unrealistic with the information available and sub-contractor behaviour that is currently being observed. It is believed that to prevent the package from becoming out of control __ should employ a competent experienced person on a short term basis to assist the package manager in taking control of the installation and handover process.
| 02SL - Stations (LUL) | Cxxx-NCR-001223 | NCR | Damage to column casings GYB -4 & WTH -4 |  | Crossrail | PDP | TCR - Tottenham Court Road Station (West) |  | 2019-08-29 | 2019-09-06 12:17 | 8 | 2019-08-01 16:46 | Architectural - Finishes | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The middle casing to GYB -4 column has been dented through impact ref: IMG 1320 & 1319. The upper panel section to the column casing WTH-4/PTE and the central panel to column casing WTH -4/escalator landing has been subjected to graffiti.
| 02SL - Stations (LUL) | Cxxx-NCR-001224 | NCR | Non Conformance Lighting Design / Interleaving of Lighting Circuits |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-09-27 | 2019-11-13 14:03 | 47 | 2019-08-02 13:14 | Electrical - Lighting | 1500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | PCC Numbered Cxxx-LAO-E-CER-N105_WS093_50035 GYB Level -4 Rooms 5/616 and 5/072 have been installed in conjunction with approved drawing however without interleaving circuitry.
| 02SL - Stations (LUL) | Cxxx-NCR-001225 | NCR | WTH Block D over pressure relief duct corrosion |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-09-04 | 2020-06-10 15:22 | 280 | 2019-08-07 11:34 | Mechanical - Heating Ventilation & Air Conditioning | 15000 |  | Damaged | Rework | 2 (6-60k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Following an inspection from our Ductwork specialist they have identified that due to corrosion damage caused by water ingress the duct requires replacing.
| 02SL - Stations (LUL) | Cxxx-NCR-001226 | NCR | Incorrect VCD installed within PFR-E3 Air Release ductwork system. |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-09-11 | 2019-09-23 08:25 | 12 | 2019-08-14 10:07 | Mechanical - Heating Ventilation & Air Conditioning | 2500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | During commissioning of this system it was noted that a VCD was required for the index run. It was noted after the VCD was installed that it was a different type to the other VCD's installed across the project. The as installed VCD does not have the correct fire rating and will need to be replaced.
| 02SL - Stations (LUL) | Cxxx-NCR-001227 | NCR | Material installed without MCR approval |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-10-31 | 2021-11-05 15:30 | 736 | 2021-11-04 14:39 | Electrical - General | 1500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | WTH Distribution Boards referenced DB-2601 (level +6 ) and DB-E2006 (ground floor) have Mains Surge Protection Devices installed without approval of MCR. MCR numbered 008151 has been issued pending approval.
| 02SL - Stations (LUL) | Cxxx-NCR-001228 | NCR | SCADA IO - Tunnel Fire Main header tank |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-09-30 | 2019-10-10 16:18 | 10 | 2019-08-21 09:11 | Fire - Suppression | 1000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | WI CRL1-XRL-R3-RSP-CR001-50002 Rev 4.0 Station SCADA I/O Specification rev4, section 6.10 requires tunnel fire main IO to be directly monitored by SCADA (ie direct connection from field device to SCADA RTU).Currently these points are wired via a Fire Interface Unit and then cascaded to a SCADA RTU. Note: There is no WI requirement for these Tunnel fire main points to be available on the fire alarm panel.
| 02SL - Stations (LUL) | Cxxx-NCR-001229 | NCR | GYB chilled water pump room (HRU B/766) Floor Not Laid to Fall |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-10-31 | 2019-09-10 14:35 | -51 | 2019-08-27 13:36 | Civil - Civil Engineering General | 100 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Personnel Error - Other human error | Completed |  | Floor not laid to fall in Chilled water pump room (HRU B/766) on GYB as per gated design. Floor grate leading to riser below now at risk of flooding.
| 02SL - Stations (LUL) | Cxxx-NCR-001230 | NCR | CMS Tophat issue in WTH level -1 2/068 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-11-25 | 2020-07-16 08:52 | 234 | 2019-09-30 15:16 | Electrical - Cable Management | 6000 |  | Design | Use As-Is | 3 (3-6k) | Complete | Management Problem - Inadequate supervision | Completed |  | CRL have requested the Contractor advises plans to Intrusively Inspect the other areas of work installed by __(Cxxx sub contractor) on WTH levels -1 and -2 as they appear to be subject to the CMS trunking intersections found incorrectly installed and without suitable access.
| 02SL - Stations (LUL) | Cxxx-NCR-001231 | NCR | Downpipes into Level -5 P+T area - Fire Risk assessment |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2020-07-22 | 2020-12-03 11:15 | 134 | 2019-09-04 11:05 | Civil - Drainage | 5000 |  | Incomplete Works | Rework | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | This NCR supersedes NCR 1089 and covers the down pipes into the level -5 area under the Platform and tunnel slabs only. This NCR has been raised as a number of the down pipes installed from the channel behind the GRC into the under platform space were less than the instructed 2m length.
| 02SL - Stations (LUL) | Cxxx-NCR-001232 | NCR | Red Fire Stickers |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-12-31 | 2020-05-19 14:51 | 140 | 2019-09-13 06:34 | Architectural - General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Insufficient information made available to the worker. | Completed |  | placement of the red fire labels adjacent to the dampers which are visible through the perforated black steel panels – __ panels in WTH ticket hall and WTH -4, they may be visible elsewhere. These 2 in particular were noticed and concern raised by __ – Crossrail Delivery Director on the SHELT inspection
| 02SL - Stations (LUL) | Cxxx-NCR-001233 | NCR | GYB level +4 Ductwork exhaust connections to louvre |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-10-16 | 2020-11-19 11:12 | 400 | 2019-09-18 14:16 | Mechanical - Heating Ventilation & Air Conditioning | 25000 |  | Design | Rework | 2 (6-60k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Due to water ingress through the open louvres the existing galvanized ductwork blanking plates are showing signs of corrosion. A mortar ramp was installed to try and prevent the water pooling at the bottom of the ductwork, the ductwork specialist on site has objected against the ramp. this is due to corrosion. The as installed ductwork and blanking plates are not suitable for what is required.
| 02SL - Stations (LUL) | Cxxx-NCR-001234 | NCR | WTH level -5 S4 tunnel corroding ductwork brackets |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-10-16 | 2020-02-21 14:56 | 128 | 2019-09-18 14:57 | Mechanical - Heating Ventilation & Air Conditioning | 3000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | Galvanized __ bracketry showing signs of corrosion.
| 02SL - Stations (LUL) | Cxxx-NCR-001235 | NCR | Non Installation of Power Factor Correction Equipment within each LV Switchpanel |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2020-08-10 | 2020-11-30 09:36 | 112 | 2019-09-25 07:14 | Electrical - Switchgear | 20000 |  | Design | Use As-Is | 2 (6-60k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | Non Installation of Power Factor Correction Equipment within the Main LV Switchboards (4 number) in accordance with the WI JY71.1201 Clause e.
| 02SL - Stations (LUL) | Cxxx-NCR-001236 | NCR | Earth Tray clashing with the ductwork in Riser Room 2909 WTH -1 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-11-26 | 2020-02-12 16:32 | 78 | 2019-10-01 14:05 | Electrical - Cable Management | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | Earth Tray clashing with the ductwork in Riser Room 2909 WTH -1 (tray currently sitting behind ductwork) inaccessible and set out incorrectly against the design drawings.
| 02SL - Stations (LUL) | Cxxx-NCR-001237 | NCR | Non-compliance of the slip resistance in PTE |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-11-05 | 2020-03-12 15:17 | 128 | 2019-10-08 16:04 | Architectural - Flooring | 500 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The contractor has submitted records of PTE screed and tiling installation to the project manager. The project manager has brought up that the contract is currently not in compliance with there ITP which states the minimum requirement for slip resistance testing per m2. In short the area requires 20No. tests and the contractor has performed 10No. tests. The contractor notes that the ITP does state that "larger areas (i.e platforms) can carry out fewer tests per 250m2 but must be agreed with CRL/__" The contractor request that the PM reviews this and decides on where more tests need be carried out.
| 02SL - Stations (LUL) | Cxxx-NCR-001239 | NCR | Non-compliant wall location - tunnel S4 - WTH level -5 |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2019-11-13 | 2020-10-01 14:39 | 323 | 2019-10-16 11:15 | Architectural - Brickworks/Blockworks | 20000 |  | Design | Rework | 2 (6-60k) | Complete | Management Problem - Inadequate supervision | Completed |  | The Contractor has constructed a blockwork wall in a location that was not shown on any design drawings. The wall is near the interface between the “S4” tunnel and the WTH -5 floor plate. The location of the wall creates numerous avoidable non-compliances with the Contractor’s own “Stage F Access and Maintenance Report” and CRL’s CPFRs including CPFR4991 and CPFR5012. It causes mechanical and electrical power and controls equipment associated with the platform smoke extract system to be located in a space that is classified as “confined” by the Contractor in his “Stage F Access as Maintenance Strategy”. As this equipment requires regular routine inspection and maintenance, it is unacceptable to unnecessarily locate it in an area classified as confined with no ventilation, no lighting, no PA/VA, no fire alarm and detection and restricted access routes. CRL has regularly highlighted this concern to the Contractor during the wall’s construction over a number of months. The Contractor ignored these warnings and continued to build the wall as demonstrated below: January 9th 2019: CRL first notified the Contractor of this concern on January 9th 2019. At this time (nine months ago), the wall was only three courses high. It would have been very easy to cease construction there, demolish the wall, produce a design, and build a wall in an acceptable location. The Contractor opted to ignore this opportunity. Email to the Contractor on January 9th attached. April 3rd 2019: CRL observed that the Contractor has added two more block courses to the wall, which was at that time five course high and still in the same unacceptable location. Email on the same day to the Contractor attached. June 18th 2019: CRL observed that the Contractor has added further block courses and that fire-stopping around services was complete. The wall at that time blocked off tunnel S4 from the WTH -5 floor plate. There was no means of access through the wall at this point. It was still in the same unacceptable location. Email from the same day to the Contractor attached. June 26th 2019: CRL observes that the Contractor has tried to alleviate the lack of access (which is not the root cause of this NCR) by partially demolishing the wall to facilitate installation of a small access hatch. On the same date CRL notifies the Contractor that this remains a non-compliance and that the IM would not accept it (email attached). September 6th 2019: By this time the small access hatch has been installed. Photograph attached. September 19th 2019: For the first time the Contractor issues a drawing onto eB showing a wall in this location – revision P11 of Cxxx-LAO-A-DDA-N105_6-20606. At the time of writing the wall remains in place and the smoke extract system equipment is located in a unacceptable, non-compliant position.
| 02SL - Stations (LUL) | Cxxx-NCR-001240 | NCR | Sump Pump WTH -2 FW-W01 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2020-06-30 | 2020-08-07 06:44 | 38 | 2019-10-25 07:07 | Mechanical - Public Health Engineering | 7500 |  | Design | Rework | 2 (6-60k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The sump is not compliant with EN 12056-4:2000 section 5.1. The sump should not be used as it is contaminating concrete.
| 02SL - Stations (LUL) | Cxxx-NCR-001242 | NCR | Smoke Downstand Torque Verification |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-12-06 | 2019-12-18 08:15 | 12 | 2019-11-08 15:23 | Architectural - Glazing | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The Contractor has identified discrepancies within the sub-contractor assurance documentation related to the torque values for the Type 2 and Type 4 smoke downstands. Details of these findings are contained within documents Cxxx-LAO-C-RGN-N105_WS089_Z-50025 and Cxxx-LAO-Z-MRC-N105_WS089_Z-50024 attached.
| 02SL - Stations (LUL) | Cxxx-NCR-001243 | NCR | WTH level -4 Northbox Stair pressurisation VCD |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-12-17 | 2020-02-12 16:53 | 57 | 2019-11-19 12:32 | Mechanical - Mechanical Engineering General | 1500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Installation of Index run VCD feeding the grille at WTH level -5 north box is defective. VCD and section of ductwork to be replaced.
| 02SL - Stations (LUL) | Cxxx-NCR-001244 | NCR | WTH level -4 Accomodation area Ductwork grill alteration. |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-12-17 | 2019-12-11 08:32 | -6 | 2019-11-19 12:43 | Mechanical - Heating Ventilation & Air Conditioning | 2500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | As stated in __ access and maintenance risk assessment, the ductwork grill in WTH level -4 room (TEP 5/340). Risk assessment attached.
| 02SL - Stations (LUL) | Cxxx-NCR-001245 | NCR | Light Drum - Bomb Blast Fixings - Torque |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2019-12-24 | 2020-11-09 14:19 | 321 | 2019-11-26 09:13 | Architectural - General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - NCR excessive closure due to design issue | Completed |  | As part of the Feature Light Drum installation/design, __ are required to install 2no bomb blast safety fixings per drum to the soffit of the structural slab. The Light Drums will then be tethered to the bomb blast fixing. The fixings are required to be torqued to 20nm as per the manufactures instructions, upon torqueing these fixings it became apparent that the operatives performing this task were not able to fully torque the fixings to the 20nm required due to the nut being too close to the structural slab and due to not having enough room horizontally to physically tighten the fixing.
| 02SL - Stations (LUL) | Cxxx-NCR-001246 | NCR | Manual Call Points - spacing in excess of requirements of BS5839 Pt1 |  | Crossrail | PDP | TCR - Tottenham Court Road Station (West) |  | 2020-04-30 | 2020-07-27 12:05 | 88 | 2019-11-28 11:06 | Fire - Fire Systems & General | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The current installation at TCR comprises a layout where Manual Call Points are arranged in some areas in excess of the minimum 45m spacing along exit routes. The fire strategy Cxxx-LA0-O9-RGN-N105_WS089-50005 states that the installation will be provided in accordance with BS5839-1. The strategy also sets out that the installation will be in accordance with LU standards. The Cxxx design and installation is not in line with BS 5839-1 section 20.2. The __final certification has highlighted it as a variation (non-compliance) from the standard without justification of mitigation. For the variation to be accepted a concession against LU standards would be required but would not be supported by CEG or LU.
| 02SL - Stations (LUL) | Cxxx-NCR-001247 | NCR | EFR-W10 Fan Faulty |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2020-01-02 | 2020-02-14 16:22 | 43 | 2019-12-05 09:28 | Mechanical - Heating Ventilation & Air Conditioning | 2000 |  | Equipment Breakdown | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Extract Fan EFR-W10 in fault
| 02SL - Stations (LUL) | Cxxx-NCR-001248 | NCR | Works on Artwork Screen Prior To ITP Acceptance |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2020-01-07 | 2020-01-23 10:49 | 16 | 2019-12-10 09:59 | Architectural - Walls | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | Works started on artwork screen prior to acceptance of ITP.
| 02SL - Stations (LUL) | Cxxx-NCR-001250 | NCR | __ VE Ceilings, Metal Ceilings and __ Walls |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2020-04-30 | 2020-05-18 21:06 | 18 | 2019-12-17 06:33 | Architectural - General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | It has been bought to attention that fixings to the __ VE Ceilings, Metal Ceilings and __ Wallsare of BZP type. __ have stated that the fixings are in accordance with specification and drawings and are possibly unaware of the issues associated with BZP.
| 02SL - Stations (LUL) | Cxxx-NCR-001251 | NCR | Smoke Downstand M10 Nut |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2020-01-31 | 2020-01-07 15:58 | -24 | 2019-12-19 07:52 | Architectural - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Smoke Downstand - nut on M10 bolt is not installed to match the approval drawing.
| 02SL - Stations (LUL) | Cxxx-NCR-001252 | NCR | IGuzzinni Light Drums - Tether Connections |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2020-04-14 | 2020-04-20 05:32 | 6 | 2020-01-08 09:30 | Architectural - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | It has been highlighted that the IGuzzinni Light Drums installed in the Western Ticket Hall Ground Level ,Western Ticket Hall Level -4 and Goslett Yard Box Level -4 have been installed with only 2no tethers attached to the Light Drum. The Blast load test report states that there should be a 3rd tether attached to the bracket.
| 02SL - Stations (LUL) | Cxxx-NCR-001253 | NCR | Soft flooring and door opeing interface non-compliant |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2020-08-10 | 2021-03-11 15:54 | 213 | 2020-01-12 11:50 | Architectural - Flooring | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The contractor has failed to install a compliant detail where the cove on the soft flooring meets the structural opening for door sets. The cove does not butt up to any structure and is left as an exposed end. The project manager deems this unacceptable as there is risk of damage to the system during maintenance. Furthermore the contractor was advised of this issue when the benchmark was submitted 12months ago
| 02SL - Stations (LUL) | Cxxx-NCR-001254 | NCR | __ Doors - Non-Compliant Door Finish |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2020-08-10 | 2021-04-16 10:03 | 249 | 2020-01-16 15:18 | Architectural - Doors | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | __ doors have supplied and installed Stainless Steel front of house doors that are not in line with the works information. The door finish is not consistent or near an equal finish to surrounding Stainless Steel elements produced by others.
| 02SL - Stations (LUL) | Cxxx-NCR-001255 | NCR | GYB -1 Light fitting removal |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2020-02-17 | 2020-06-18 09:08 | 122 | 2020-01-20 09:48 | Electrical - Lighting | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The Project Manager was invited out to whiteness the removal of the light fittings on GYB -1 along the escalator line. At the inspection it was deemed that there was insufficient access in place to accommodate the removal of the light fittings.
| 02SL - Stations (LUL) | Cxxx-NCR-001256 | NCR | Clear Zones Above Handrails |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2021-01-13 | 2021-01-11 16:24 | -2 | 2020-01-24 10:33 | Architectural - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | non-compliant installation of cms for comms cables in the escape and intervention stairs. In accordance with BS8300, Pt B of Building Regs, DoT Code of Practice and the LU cat I standard for stairs and ramps there cannot be any obstruction within the 600mm zone above the handrail.
| 02SL - Stations (LUL) | Cxxx-NCR-001257 | NCR | Incorrect Heights of LV9 Socket Outlets |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2020-03-24 | 2020-05-14 09:39 | 51 | 2020-01-28 11:38 | Electrical - General | 1500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Where a screed has been added to the floor slab the height of LV9 Socket Outlet is incorrect with the design intent.
| 02SL - Stations (LUL) | Cxxx-NCR-001258 | NCR | ENWA Side stream filter panel lamp test button |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2020-03-31 | 2020-06-19 08:35 | 80 | 2020-01-30 13:38 | Mechanical - Mechanical Engineering General | 2500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | During a recent site visit it was noted that the panel for the side stream filter does not have a lamp test button installed. This is a requirement within BS EN 60204-1:20006+A1 (10.3).
| 02SL - Stations (LUL) | Cxxx-NCR-001259 | NCR | Sump Pump SW-W02 air locking |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2020-03-31 | 2020-06-09 07:58 | 70 | 2020-01-30 13:57 | Mechanical - Pumps | 1500 |  | Equipment Breakdown | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | During commissioning of the waste water meters it became apparent that two out of the three pumps where air-locked.
| 02SL - Stations (LUL) | Cxxx-NCR-001260 | NCR | Non-Complian handrail and up-and-over WTH -5 Northbox |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2020-08-10 | 2020-07-28 11:32 | -13 | 2020-02-01 14:01 | Architectural - General | 500 |  | System Defect | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The PM picked up that the handrail on WTH -5 Northbox is not fit for purpose. The up and over is sufficient to pass over the HV cables. However, there is insufficient handrail between the up and over and the concrete wall. This is leaving a gap that potentially raises concerns over a possible trip hazard over the HV cables. (see attached photo).
| 02SL - Stations (LUL) | Cxxx-NCR-001261 | NCR | Sump Pump SW-W03 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2020-03-10 | 2020-06-30 09:55 | 112 | 2020-02-11 15:15 | Mechanical - Pumps | 7500 |  | Equipment Breakdown | Rework | 2 (6-60k) | Complete | Design Problem - Inadequate or defective design | Completed |  | During commissioning of the waste water meters it became apparent that the pumps where air-locked.
| 02SL - Stations (LUL) | Cxxx-NCR-001262 | NCR | Riser 1 ladder non compliant |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2020-03-10 | 2020-08-14 13:10 | 157 | 2020-02-11 15:24 | Mechanical - Mechanical Engineering General | 2500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The ladder within Western Tickethall Riser 1 to access high level within -2 is non compliant with BS EN 14122-4:2016. Figure 4. (attached)
| 02SL - Stations (LUL) | Cxxx-NCR-001263 | NCR | Non Compliance with JY 60:1301 Provision of 25% cms spare capacity for future use |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2020-09-25 | 2020-11-13 14:00 | 49 | 2020-02-12 16:26 | Electrical - Cable Management | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The contractor has installed CMS at GYB level -5 (DB-A 1501, DB-B 1502, DB-E 1503) that is currently Non-Complaint with JY60:1301 In not facilitating 25% spare capacity for future use. Further to this the Contractor and their appointed designer __ are currently in the process of undertaking a CMS sizing report/assessment that may / may not highlight further capacity issues.
| 02SL - Stations (LUL) | Cxxx-NCR-001264 | NCR | MCR for CMS Earth Break Where Station/Traction Earthing Applicable |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2020-08-10 | 2020-07-01 16:38 | -40 | 2020-02-13 11:10 | Electrical - Cable Management | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | The Contractor has submitted CRL-MCR-005862 for the earth break component to be fitted to the CMS. Whilst this MCR has been accepted by the Project Manager, it is understood that a member of the Employer's team has objected to the Contractor's proposal.
| 02SL - Stations (LUL) | Cxxx-NCR-001265 | NCR | GYB Prop paint finish |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2020-06-10 | 2020-08-05 14:09 | 56 | 2020-02-13 13:02 | Architectural - Finishes | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | The existing inherited Props in GYB escalator barrel's paint finish has not been accepted by the CRL architect. The Contractors position is that it is fit for purpose and suggest the proposed remedials are taken to ADM via the I__ and agreed to be de-scoped from the Contractor.
| 02SL - Stations (LUL) | Cxxx-NCR-001266 | NCR | Faulty Micro logic __'s |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2020-08-31 | 2020-10-21 13:14 | 51 | 2020-02-17 16:06 | Electrical - Switchgear | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Not Defined | Completed |  | Four Number __ Mirco logic units found to be faulty in the following locations:- GYB - LV-E GEN3 Way Q WTH LV-A SB1 Way J WTH LV-A SB1 Way AG WTH LV-A-SB1 Way AM
| 02SL - Stations (LUL) | Cxxx-NCR-001267 | NCR | SWP-E01 High level alarm lamp |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2020-03-19 | 2020-06-18 15:01 | 91 | 2020-02-20 09:19 | Mechanical - Pumps | 2500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The surface water sump pump panel does not have a high level alarm lamp installed. This is a requirement of the Technical Directorate - Material and Workmanship Specification: Mechanical, Electrical and Public Health JR20 Sewage Pumping CRL1-XRL-M-RSP-CR001-50005 JR20.1402 b) iii) specifies a high level alarm is required. (page 6)
| 02SL - Stations (LUL) | Cxxx-NCR-001268 | NCR | Non Maintainable speaskers in -5 GYB |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2020-08-03 | 2020-10-06 12:13 | 64 | 2020-07-06 08:54 | Communications and Control Systems - Public Address Systems | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | x3 speakers in the -5 GYB BOH area are going to be very hard to maintain due to being in close proximity to DUCT work RFL and A&M may not accept these due to this. speaker numbers Z48 16B 18B 23A
| 02SL - Stations (LUL) | Cxxx-NCR-001269 | NCR | Bund required at GYB level +2. |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2020-03-30 | 2020-11-05 09:26 | 220 | 2020-03-02 10:31 | Mechanical - Mechanical Engineering General | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The as built architectural as built shows a fall of 1:60, this has not been achieved. Consequently a bund is required around the open grated floor at the top of the riser to prevent water ingress.
| 02SL - Stations (LUL) | Cxxx-NCR-001270 | NCR | WTH level +5 leaking Differential pressure switch |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2020-03-30 | 2020-05-22 11:50 | 53 | 2020-03-02 10:48 | Mechanical - Heating Ventilation & Air Conditioning | 2000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | The differential pressure switch (WTH level -5) on the chilled water system has a leak. The Leak has caused some damage to the firestopping beneath.
| 02SL - Stations (LUL) | Cxxx-NCR-001271 | NCR | No approved MCR for valve jackets |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2020-03-30 | 2020-05-01 08:18 | 32 | 2020-03-02 12:20 | Mechanical - Mechanical Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | MCR for valve jackets not approved
| 02SL - Stations (LUL) | Cxxx-NCR-001272 | NCR | Excessive deflection on Diadem Court railings, central section |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2020-08-10 | 2021-02-19 12:18 | 193 | 2020-03-03 10:23 | Architectural - Handrail | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Following the issue of PMI 1485, the Contractor's Subcontractor installed a replacement railing to the light well upstand of the Soho Hostel (as agreed with the building owner). The original instruction did not include provision for a structural design, nor did it cover drilling any new items into the stakeholder's building so the installed railing presented the best installation within the constraints of the original instruction. The installed railing (on only one section out of the 3 installed) deflects more than would be expected when a significant force is applied. Additionally as the instruction was just for a simple reinstatement to utilise the existing fixing positions, no detailed design was carried out as this had not been requested by the Project Manager
| 02SL - Stations (LUL) | Cxxx-NCR-001273 | NCR | Door Thresholds |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2020-04-03 | 2020-05-14 14:09 | 41 | 2020-03-06 12:37 | Architectural - Doors | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | In regards to doors station wide thresholds have had to be installed to meet the performance criteria of the doors. As agreed at the I__ on 4 March 2020, all thresholds are to be left in place and highlighted yellow and this NCR is raised as a point of record.
| 02SL - Stations (LUL) | Cxxx-NCR-001275 | NCR | Full re-test / review of water mist fire suppression system. |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2020-04-06 | 2020-11-13 11:18 | 221 | 2020-03-09 12:19 | Fire - Suppression | 10000 |  | Testing and Commissioning | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Insufficient information made available to the worker. | Completed |  | Fire Suppression system water tank being drained of water.
| 02SL - Stations (LUL) | Cxxx-NCR-001276 | NCR | __ __ - D3-6/008 and D3-6/020 - Rebar cut to accommodate floor socket. |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2020-04-16 | 2020-07-21 16:12 | 96 | 2020-03-31 10:53 | Architectural - Doors | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | As part of the permanent works , __ / __ __ have cut through steel reinforcement of the GYB Level -5 Raft Slab to accommodate a double door floor socket for doors D3-6/008 and D3-6/020.
| 02SL - Stations (LUL) | Cxxx-NCR-001277 | NCR | Doors - Labels - Door Name and Performance |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2020-10-01 | 2020-11-19 19:14 | 49 | 2020-09-03 21:09 | Architectural - Doors | 500 |  | Manufacturing Defect | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Error by manufacturer in shipping or marking | Completed |  | The supply chain's for Permanent Doors __ , __ __ , __ and __ have not complied with the specification within the Works Information. as per JL20.1207 Performance Requirements, the subcontractor's were to "d) Ensure that all doorsets are clearly marked on the hinge edge, with their door number and performance, enabling them to be reconciled with their intended location". It has been identified that this has not happened on all doorsets.
| 02SL - Stations (LUL) | Cxxx-NCR-001278 | NCR | GYB External Lighting - Functionial Demonstration of Individually Controlled Luminaires |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2021-02-26 | 2021-02-05 15:20 | -21 | 2020-04-07 07:00 | Electrical - Lighting | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | GYB External Lighting - Functional demonstration test of each externally mounted luminaire via individual photocell installed adjacent to each.
| 02SL - Stations (LUL) | Cxxx-NCR-001279 | NCR | C690 __ - continuous gate line alarm at TCR |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2020-09-17 | 2020-08-14 10:11 | -34 | 2020-04-10 14:48 | Electrical - Power Distribution | 500 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Interfacing problems | Completed |  | The C690 Gate Line was giving a continuous fault alarm. No one from CRL C690, __ (the contractor) or TFL were available to attend due to the COVID-19 quarantine. The only way to turn the gate line fault alarm off was for the __/CHT SAP to attend site and to isolate the board that feeds the gate line. This approach was accepted by TfL via phone (conversation between CRL TCR Construction Manage __ and Andy Martin on 30Mar2020) and by email. On 31Mar2020 at 14:30hrs, __ have successfully isolated the power supply to the C690 Gateline.
| 02SL - Stations (LUL) | Cxxx-NCR-001280 | NCR | WTH +6 roof level Trace heating circuit 6 in error |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2020-05-29 | 2020-07-30 08:39 | 62 | 2020-04-17 12:13 | Mechanical - Mechanical Engineering General | 1500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Trace heating circuit 6 which covers the WTH Cat 5 Boosted cold water feeding the CHW plant on the roof is in error. Upon inspection it was noted that the temperature sensor cable for this circuit is damaged. photo (cable) attached. ERR1 is shown on the panel display. in the manufactures documentation section 4. Errors. (page 14) ERR1 is a short circuit sensor and the remedial is replacement. Section 3. of the manufacturers documentation (parameters) and the attached commissioning documentation confirms that if the sensor is in error the trace heating will turn on.
| 02SL - Stations (LUL) | Cxxx-NCR-001281 | NCR | Sitewide CCTV survey of drainage pipework remedials |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2020-06-26 | 2021-04-22 09:08 | 300 | 2020-04-17 13:53 | Mechanical - Mechanical Engineering General | 20000 |  | Damaged | Rework | 2 (6-60k) | Complete | Management Problem - Inadequate supervision | Completed |  | A site wide CCTV survey of all buried drainage pipework within the station has been undertaken. The scope of this survey is attached (scope drawings). The CCTV specialist where unable to complete the survey due to a number of gullies and pit covers being inaccessible for numerous reasons. (painted shut/cast in etc). CCTV survey attached.
| 02SL - Stations (LUL) | Cxxx-NCR-001282 | NCR | Non-compliant noise levels |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2021-03-26 | 2021-04-20 12:43 | 25 | 2021-01-29 13:52 | Mechanical - Heating Ventilation & Air Conditioning | 10000 |  | Design | Rework | 2 (6-60k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Following the testing and issue of the internal noise survey report (Cxxx-LAO-T1-RGN-N105_WS089_Z-50044 ) a number of areas have been highlighted as non-compliant noise levels.
| 02SL - Stations (LUL) | Cxxx-NCR-001283 | NCR | Foul water pump FW-W01 incorrect __'s installed |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2020-06-09 | 2020-06-12 11:52 | 3 | 2020-05-12 15:02 | Mechanical - Pumps | 2500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Cxxx requested their designer carried out a discrimination study between the LV distribution boards and the foul water and surface water sump panels. Upon a recent review of works to the FW-W01 system it was noted the __'s within the panel are incorrect.
| 02SL - Stations (LUL) | Cxxx-NCR-001284 | NCR | Scenario 4 (Air Velocities) Doors Slamming |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2021-02-09 | 2021-03-19 12:50 | 38 | 2020-05-15 09:52 | Mechanical - Mechanical Engineering General | 500 |  | Testing and Commissioning | Repair | 4 (0.5-3k) | Complete | External Phenomenon - Not Defined | Completed |  | During Scenario 4 (Air Velocities and Door Forces) at TCR, during test B with the TVS on full extract, doors were found to be slamming in the intervention and escape routes (5 doors as identified in the test report). Following on from the initial Air Velocities Test, another air velocities test was completed on 13th December 2020. After the test Cxxx, CEG and LU agreed the following issues were found: - Several door latches and doors need remedial action (one WTH intervention to street level latch in excess of 250N, Escape platform door over 300N on WTH due to middle seal catching) - 2 x intervention PRM doors need to be lower than 150N - Slamming identified in the two bottom (platform level on both WTH and GYB side) with SPA and TVS on All these issues need to be rectified.
| 02SL - Stations (LUL) | Cxxx-NCR-001285 | NCR | iGuzzini drum installation NCR – pull out testing |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2020-08-21 | 2020-11-09 14:09 | 80 | 2020-05-21 12:55 | Architectural - Finishes | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Information not detailed | Completed |  | The ITP for the installation of the iGuzzini Light Drums Cxxx-LAO-O4-ITP-N105_WS089_Z-50069, item number 4.6 – pull test specifies that 10% of all fixings are to be tested to 1.25x of the characteristic load of the anchor. It has been identified that an insufficient number of pull tests have been completed to satisfy this requirement. A total of 1360 __ HUS3 anchors (as per MCR Cxxx-LAO-O4-XDS-N105_WS089_Z-50232) have been installed requiring 136 pull test records, and a total of 680 sleeve anchor eye-bolts (as per MCR Cxxx-LAO-O4-XDS-N105_WS089_Z-50235) have been installed requiring 68 pull test records. There are only 20no. HUS3 and 15no. eye-bolt pull test records available. This represents a coverage of 1.5% and 2.2% respectively. Further, it should also be noted that the loads that the pull tests were carried out to were to the applied loads as identified by the designer’s structural calculation reports, and not to the characteristic loads of the anchors as stated in the ITP.
| 02SL - Stations (LUL) | Cxxx-NCR-001287 | NCR | WTH -4 Glass Balustrade |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2020-07-04 | 2021-02-26 15:15 | 237 | 2020-06-06 10:10 | Architectural - Balustrade | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The project manager has brought it to the attention of the Main contractor that the corner trim of the glass balustrade on WTH does not conform with both: -The Cxxx Specification JL32.1210 C XIV - All exposed edges to rails and support posts to have a 3mm chamfer. - The Building Standards BS6180-2011 6.6.1 - The finished barrier should have no sharp edges or projections that could cause injury to persons or damage to clothing.
| 02SL - Stations (LUL) | Cxxx-NCR-001288 | NCR | AP9C - Call point skirting |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2020-07-04 | 2020-08-25 11:49 | 52 | 2020-06-06 17:06 | Architectural - General | 500 |  | Design | Reject | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | The Project Manager has made the Main Contractor aware that a contrasting strip is required between the terrazzo floor and the stainless steel panels of the PHP. Currently this is a non-compliance with BS 8300 and LU Premises Finishes Standard S1135 item 3.4.9.
| 02SL - Stations (LUL) | Cxxx-NCR-001290 | NCR | Door and Flood Barrier |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2020-07-20 | 2020-11-05 11:50 | 108 | 2020-06-22 16:17 | Architectural - General | 500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The Main Contractor wants to make the PM aware of a clash between an external door (D2-1/016) and a demountable flood barrier. The door has been installed with an inward swing meaning, once the flood barrier is assembled the door clashes with the barrier boards. The Main Contractor has reached out to the PH design consultant who has made a statement on the possibility of using "as-is" The Main Contractor is suggesting to use as-is, for the following reasons: -The installation requires a core hole into the structural slab. This has already been cored in the current location and there is a fear that we will further weaken the slab if we core another opening in close proximity to it. -The slats that the barrier boards sit in would clash with the existing handrail if moved closer to the slab edge. -The door is not deemed a main access / escape route -The door is required to stay closed when the flood barrier is deployed -When the flood barrier is deployed this becomes primary and the use of the door becomes secondary -The door leads to an area for maintenance access so accommodation of, and for Persons with Reduced Mobility, is not applicable to this. · The flood barrier will not be used very regularly (i.e. only for training or emergency procedures)
| 02SL - Stations (LUL) | Cxxx-NCR-001291 | NCR | Segregation of Emergency lighting cabling within CMS |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2020-07-13 | 2020-07-31 08:38 | 18 | 2020-06-29 12:49 | Electrical - Lighting | 2000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Whilst undertaking the final reviews for the assurance documentation associated with the Emergency Lighting a contradiction within clause JV20.1309 (item K) Distribution Circuit Cables and clause JV40.1302 (item O) Emergency Lighting of the Materials and Workmanship Requirements Volume 3 (Cxxx-LAO-E-RSP-N105_WS089-50001) has been identified. The clauses differ in the requirements for the separation of Emergency Lighting cables within CMS. The current installation is aligned to the requirements of JV20.1309.
| 02SL - Stations (LUL) | Cxxx-NCR-001292 | NCR | UV filters to be permanently removed |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2020-08-03 | 2020-09-16 14:09 | 44 | 2020-07-06 14:11 | Mechanical - Public Health Engineering | 15000 |  | Design | Rework | 2 (6-60k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The Cxxx Designer (__) has confirmed that the UV filters currently installed in the WTH and GYB are not fit for purpose, are not required by CRL and LU specifications, and are not required for Statutory purposes. The UV filters, currently isolated due to faults, are to be permanently removed from GYB and the WTH. The associated power supplies and CMS shall also be removed. All affected public health, electrical and BMS assurance documentation shall be revised, including redline and as-built drawings, O&M manuals and Care & Custody plans.
| 02SL - Stations (LUL) | Cxxx-NCR-001293 | NCR | Faulty chilled water temperature sensor |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2020-08-06 | 2020-07-30 08:24 | -7 | 2020-07-09 15:13 | Mechanical - Heating Ventilation & Air Conditioning | 1500 |  | Equipment Breakdown | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Faulty chilled water temperature sensor (__ VF20-1B54NW)
| 02SL - Stations (LUL) | Cxxx-NCR-001294 | NCR | Great Chapel Street maintenance shaft lifting beam |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2020-11-06 | 2021-02-05 14:17 | 91 | 2020-07-06 14:20 | Mechanical - Mechanical Engineering General | 10000 |  | Design | Rework | 2 (6-60k) | Complete | External Phenomenon - Not Defined | Completed |  | Stage F access and maintenance shows lifting beam at Great chapel street. No lifting beam design or installed
| 02SL - Stations (LUL) | Cxxx-NCR-001295 | NCR | GYB CAT5 booster pump comms fault |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2020-08-03 | 2020-08-25 08:01 | 22 | 2020-07-06 14:27 | Mechanical - Public Health Engineering | 1500 |  | Equipment Breakdown | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The Cat5 boosted pump set at GYB has a fault. __ to review and repair. No communication between pump 1 and panel.
| 02SL - Stations (LUL) | Cxxx-NCR-001296 | NCR | Defective welds identified on fan support frames |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2020-08-03 | 2021-04-09 10:28 | 249 | 2020-07-06 16:01 | Mechanical - Mechanical Engineering General | 20000 |  | Manufacturing Defect | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | It is noted that a number of specialist supplied as installed fan frames and piston brackets have been installed with potential defects of the welds. An independent survey of the welds has been performed and noted a number of defects including:- - weld splatter - poor weld profile.
| 02SL - Stations (LUL) | Cxxx-NCR-001297 | NCR | Emergency DBs not separated from LV-A and LV-B DBs in LEER Room |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2020-08-04 | 2020-08-19 16:17 | 15 | 2020-07-07 14:21 | Electrical - Power Distribution | 2000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Emergency DBs not separated from LV-A and LV-B DBs in LEER Room
| 02SL - Stations (LUL) | Cxxx-NCR-001298 | NCR | Waterproofing - System failure |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2021-01-15 | 2021-02-05 10:17 | 21 | 2020-07-13 05:49 | Civil - Civil Engineering General | 100000 |  | Design | Repair | 1 (>60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The Contractor notifies the Project Manager that there continues to be a water leak coming through the +1 slab on WTH (Block C and D). The leak has continued since the installation of the waterproof membrane installed in May 2020.
| 02SL - Stations (LUL) | Cxxx-NCR-001299 | NCR | Damage to Recon Strone cills WTH |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2020-08-17 | 2020-10-22 14:27 | 66 | 2020-07-20 10:04 | Architectural - Masonary | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The PM has observed damage to the reconstituted stone sills on Block C. Most of the damaged seen is to the lower edge of the sill and the corners. The example attached is on the south elevation. This damage needs to be repaired and then properly protected.
| 02SL - Stations (LUL) | Cxxx-NCR-001300 | NCR | Cable Identification inconjunction with CRL1-XRL-M-RSP-CR001-50088 JY82.3205 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2020-09-30 | 2020-09-30 13:31 | 0 | 2020-07-20 11:12 | Electrical - General | 1000 |  | Incomplete Works | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | A sample of the as installed sub-main cabling installation has been identified without all of the required identification installed.
| 02SL - Stations (LUL) | Cxxx-NCR-001301 | NCR | __ - Pre-construction Documentation MCR/ITP |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2020-08-18 | 2020-11-27 16:18 | 101 | 2020-07-21 12:04 | Architectural - Doors | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Lack of approval Code 1 procedures excessive | Completed |  | Cxxx __ is raising this NCR based on __ a supplier/sub-contractor of __ __ manufacturing doors sets without an approved Code 1 MCR and Manufacturing ITP. Doors affected : D3-2/004 D3-2/007 D3-3/003 D3-3/004 D3-3/024a D3-3/024b D3-3/025 D3-4/008 D3-4/011 D3-A/001 D3-B/004 D3-C/002 D3-D/002 D2-2/009 D2-2/013 D2-2/015 D2-2/017 D2-2/018 D2-2/025 D2-2/026 D2-3/036
| 02SL - Stations (LUL) | Cxxx-NCR-001302 | NCR | Motorised Fire Damper plate positioning preventing Damper plate install |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2020-08-18 | 2020-08-25 16:00 | 7 | 2020-07-21 16:01 | Mechanical - Heating Ventilation & Air Conditioning | 10000 |  | Incorrect Installation | Rework | 2 (6-60k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The motorised fire rated dampers have been installed to close to the soffit which doesn't allow for the damper plate install.
| 02SL - Stations (LUL) | Cxxx-NCR-001303 | NCR | Speaker non Maintainable |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2020-08-25 | 2020-10-16 08:47 | 52 | 2020-07-28 09:50 | Communications and Control Systems - Public Address Systems | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Speaker has been installed before ductwork was and now speaker is unmaintainable
| 02SL - Stations (LUL) | Cxxx-NCR-001304 | NCR | PAVA JB unmaintainable due to WIFI WAP |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2020-09-11 | 2020-12-10 11:32 | 90 | 2020-07-29 10:50 | Communications and Control Systems - Public Address Systems | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | AP4 east a WIFI WAP has been installed over a PAVA JB which makes the JB unmaintainable
| 02SL - Stations (LUL) | Cxxx-NCR-001305 | NCR | Installation of ventilation louvre and associated steelwork without accepted design drawings |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2020-08-26 | 2021-01-13 13:52 | 140 | 2020-07-29 15:54 | Mechanical - Heating Ventilation & Air Conditioning | 4000 |  | Supervision/Management | Rework | 3 (3-6k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | This NCR has been raised by CRL (__) following collaborative discussions between the author and Cxxx's __. Both agreed that CRL shall in this instance raise the NCR. ------------------------------------------------------------------ Cxxx has installed a series of ventilation system components at GYB level +4 without having issued design drawings to CRL. Cxxx has therefore failed to comply with its own Project Quality Plan (Cxxx-LAO-O4-STP-N105_WS089-50001) and various ITPs. The works installed without having issued design drawings to CRL includes; a) a ventilation louvre and associated steel supports at GYB level +4. These components are part of the PFR-E4 stair pressurisation system. b) stainless steel ductwork at GYB +4 serving SEF-E1/E2. This ductwork replaced previously installed mild steel ductwork of differing geometry. c) stainless steel ductwork at GYB +4 serving AHU-E1/E2. This ductwork replaced previously installed mild steel ductwork of differing geometry. d) stainless steel ductwork at GYB +4 serving EFR-E1. This ductwork replaced previously installed mild steel ductwork of differing geometry. In all of the above cases, CRL has for the past 6 months been repeatedly requesting that Cxxx issue design drawings for these components. Alas no drawings have been provided. Regarding item 'a', CRL understands that Cxxx intends to install further ductwork blanking plates surrounding the louvre and that this work is imminent. A consequence of doing so will be that the louvre and steelwork are obscured from view and therefore unavailable for inspection. If this occurs, the blanking plates will be fully removed by Cxxx to enable CRL inspection of the louvre and supporting steelwork. For items b, c and d there are also outstanding MCRs associated with the new ductwork. This NCR has been discussed between __ (CRL) and __ (Cxxx) who jointly agreed that CRL would raise the NCR.
| 02SL - Stations (LUL) | Cxxx-NCR-001306 | NCR | __ Hus3 fixings used in concrete blockwork wall to support ductwork |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2020-09-02 | 2020-09-11 15:04 | 9 | 2020-08-05 12:25 | Mechanical - Heating Ventilation & Air Conditioning | 2500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | During a recent inspection it has been noted that some of the ductwork at GYB level -4 has been installed using __ Hus3 fixings into a block wall.
| 02SL - Stations (LUL) | Cxxx-NCR-001307 | NCR | Aqualeak – Replacement of faulty control Unit in Block C |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2020-09-10 | 2020-09-08 09:21 | -2 | 2020-08-13 09:56 | Mechanical - Public Health Engineering | 5000 |  | Equipment Breakdown | Rework | 3 (3-6k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | When this WG2 unit for Block C “Dean Street locaion” was set up by __ on last site visit July 2020 and tested by running approx 500 litres of water through the system the External Water Meter Pulse on the display did not count up in unison with the Internal Water Meter Pulse on the display. Also when the unit is powered down then power re-instated the External reading resets back to 000 and the Internal reading reverts back to a value of 039 even though the previous count prior to power down was higher than this. Other WG2 units on site retain their last known pulse counts when power is returned.
| 02SL - Stations (LUL) | Cxxx-NCR-001308 | NCR | Intake Louvre Meshes |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2021-02-24 | 2021-08-31 07:06 | 188 | 2020-08-12 13:30 | Mechanical - Heating Ventilation & Air Conditioning | 5000 |  | Damaged | Rework | 3 (3-6k) | Complete | Supervision - Insufficient supervision | Completed |  | During routine maintenance, by the project maintenance manager, it has been noted that the insect screen/mesh on the back of the intake louvres (at locations WTH +0 CIR-PL 1/788 and GYB +1 FAN A/769) is very brittle and are becoming damaged during maintenance/cleaning.
| 02SL - Stations (LUL) | Cxxx-NCR-001309 | NCR | Damper Interface CMS installed across MFD damper plates |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2020-09-09 | 2020-09-11 14:58 | 2 | 2020-08-12 13:37 | Mechanical - Heating Ventilation & Air Conditioning | 2500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The MFD damper interface CMS has been installed in such a way that it will prevent replacement of the damper in the event of failure. The damper plate fixings within FAN 3/770 have been covered by conduits preventing their removal.
| 02SL - Stations (LUL) | Cxxx-NCR-001310 | NCR | WTH Block C - Oxford Street waterproofing |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2020-10-31 | 2020-11-30 15:56 | 30 | 2020-08-13 12:18 | Architectural - General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | It was identified that the gated design intent was not replicated by the subcontractor __’s drawings had not been replicated on site during an installation by __.
| 02SL - Stations (LUL) | Cxxx-NCR-001311 | NCR | Unmaintainable PAVA JB |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2020-09-14 | 2020-10-06 08:55 | 22 | 2020-08-17 06:45 | Communications and Control Systems - Public Address Systems | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | PAVA JB has been covered up by third party WAP making JB unmaintainable
| 02SL - Stations (LUL) | Cxxx-NCR-001312 | NCR | Cable bending radius |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2020-10-30 | 2020-10-27 10:03 | -3 | 2020-08-20 10:38 | Communications and Control Systems - Radio | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Radio cable within totems in GYB have exceeded the bending radius
| 02SL - Stations (LUL) | Cxxx-NCR-001313 | NCR | (Further to NCR 1298) - +1 Slab leak - Chemical Residue |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2020-09-30 | 2020-12-23 07:37 | 84 | 2020-09-02 18:08 | Civil - Civil Engineering General | 75000 |  | System Defect | Use As-Is | 1 (>60k) | Complete | Discipline/Workmanship - Contamination | Completed |  | The Contractor notifies the Project Manager that the residue from the +1 slab leak on WTH Block D & C is not solely rainwater. On investigation it is evident that all or part of the waterproofing system that has been applied to the +1 slab is breaking down and finding its way through to the ground floor leaving a hardened brown paste that has the visual properties of an amber resin. In light of this the Contractor has: • Approached a specialist (__'s) to review the current situation on-site. (Site Visit booked 04/09/2020) • Approached to __ to review the current stance of __ membrane. (Report Pending) • Given samples of both the residue and the accelerator component of the __ system to __ for chemical analysis/comparison. (Report Pending) The Contractor notifies the Project Manager that currently there is an ongoing investigation to the source of the chemical residue.
| 02SL - Stations (LUL) | Cxxx-NCR-001314 | NCR | GYB level +1 door clash with RWP |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2020-10-06 | 2020-10-15 14:32 | 9 | 2020-09-08 13:33 | Mechanical - Public Health Engineering | 1500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | The door installed at GYB +1 when opened clashes with the Rain water pipe. Drawing of location attached.
| 02SL - Stations (LUL) | Cxxx-NCR-001315 | NCR | Chilled Water System - Dosing pots lacking sufficient flow |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2020-10-06 | 2020-12-04 14:23 | 59 | 2020-09-08 13:46 | Mechanical - Heating Ventilation & Air Conditioning | 5000 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | During a recent site visit by one of our sub contractors it was noted during annual dosing of the CHW system that both dosing pots at GYB and WTH were in a poor condition. (site report attached)
| 02SL - Stations (LUL) | Cxxx-NCR-001316 | NCR | WTH -2 off the wall damper insulation |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2020-10-09 | 2020-11-20 17:00 | 42 | 2020-09-11 14:57 | Mechanical - Heating Ventilation & Air Conditioning | 7500 |  | Workmanship | Rework | 2 (6-60k) | Complete | Design Problem - Inadequate or defective design | Completed |  | To ensure we can get the correct installation of insulation around the ductwork between the off the wall damper (ref MFD W181) part of the battery room extract system EFR W3, we need to move the duct away from the CMS.
| 02SL - Stations (LUL) | Cxxx-NCR-001317 | NCR | Accoutic Drums - Dummy Drum material non compliance |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2020-10-12 | 2020-11-20 12:33 | 39 | 2020-09-14 08:08 | Architectural - General | 50000 |  | Material | Repair | 2 (6-60k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | WTH Ground Floor - Dummy Acoustic drum internal material replacement. The drums had be removed and re-worked off-site and reinstated, upon re-inspection and review of assurance paperwork it was found that the non compliant material was used and remains in these drums. Investigation ongoing - technical review of materials under review.
| 02SL - Stations (LUL) | Cxxx-NCR-001318 | NCR | Lack of ITP prior to works |  | Crossrail | PDP | TCR - Tottenham Court Road Station (West) |  | 2020-10-09 | 2020-11-10 08:51 | 32 | 2020-09-17 10:42 | Architectural - Ceilings & Soffits | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Remedial works to replace acoustic material within the acoustic 'drums' over Western ticket hall escalator was commenced without an accepted ITP in place.
| 02SL - Stations (LUL) | Cxxx-NCR-001319 | NCR | Chillers E1 and E2 Alarm Fault |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2020-12-31 | 2021-03-08 13:11 | 67 | 2020-09-17 11:52 | Mechanical - Heating Ventilation & Air Conditioning | 5000 |  | Testing and Commissioning | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | BMS Indication of Chillers E1 and E2 alarm fault. Alarm condition to be investigated. BMS only fails the chillers on loss of run status not on faults/alarms.
| 02SL - Stations (LUL) | Cxxx-NCR-001320 | NCR | Fire Detection alternative design |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2020-11-13 | 2020-12-01 12:29 | 18 | 2020-09-17 12:14 | Fire - Detection | 10000 |  | Design | Repair | 2 (6-60k) | Complete | Design Problem - Inadequate or defective design | Completed |  | WTH Escalator ledge behind (media screen) proposed alternative design. SID Reference 2/044 .
| 02SL - Stations (LUL) | Cxxx-NCR-001321 | NCR | __ fault with ATS |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2020-11-13 | 2020-11-20 17:06 | 7 | 2020-09-28 09:55 | Electrical - Switchgear | 500 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | __s are monitoring status on the BMS. __ have visted site to investigate one alarm showing: FWP ATS. __ have been rearranged to attend site on the 05/10/2020 with Burnell Switchgear.
| 02SL - Stations (LUL) | Cxxx-NCR-001322 | NCR | Unmaintainable section of GYB Platform Smoke Extract system ductwork |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2020-11-03 | 2021-03-10 15:28 | 127 | 2020-10-06 14:44 | Mechanical - Mechanical Engineering General | 5000 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Punchwork Cxxx-PWK-00611 item 3 states: “3. Re-open T10053.1014. Site demonstration required to show how the ‘SMACNA’ ductwork at level -5 is cleaned”. A joint site inspection was held on October 30th between CRL, Cxxx and Cxxx’s ductwork cleaning specialist subcontractor ‘Duct Busters’ to determine whether the ‘SMACNA’ ductwork at the southern end of the GYB -5 circulation area 6/045 can be cleaned safely, and whether the installation complies with BESA Guide TR19 with respect to provision of access doors for ductwork cleaning. There are two existing access doors that could be used to provide entry into the duct for cleaning and inspection purposes. Duct Busters stated that these doors should be a minimum of 450mm x 450mm to provide a safe access route, however the two existing doors are only 400mm x 250mm and 345mm x 345mm and therefore need to be increased in size. Furthermore, these two access doors are approximately 30m apart, and Duct Busters also confirmed that additional access doors are required for safety purposes to ensure that an operative is always with 7.5m of an access door.
| 02SL - Stations (LUL) | Cxxx-NCR-001323 | NCR | Escalator Skirting Lighting Inrush and Dali Lighting Control |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2021-02-09 | 2021-02-19 08:47 | 10 | 2020-10-12 09:26 | Electrical - Lighting | 3000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | WTH Escalator numbered 18, 19 & 20. Circuit protective devices constantly tripping upon energisation (high inrush) and skirting lighting unable to be suitably controlled via the __ Lighting Control system.
| 02SL - Stations (LUL) | Cxxx-NCR-001324 | NCR | LV boards show invalid when in remote mode |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2021-01-15 | 2020-12-21 09:34 | -25 | 2020-10-15 12:54 | Communications and Control Systems | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Inspection points not adequate | Completed |  | Both SWB A and B in remote mode show “Invalid” at the RCC. This behaviour was first noted at the July Bismarck test. This is due to conflicting signals produced by the LV boards at TCR
| 02SL - Stations (LUL) | Cxxx-NCR-001325 | NCR | Lightning Protection System / Earthing - Damaged Cabling WTH Roof |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2020-11-24 | 2020-12-15 22:24 | 21 | 2020-10-20 13:23 | Electrical - General | 5000 |  | Damaged | Use As-Is | 3 (3-6k) | Complete | Management Problem - Inadequate supervision | Completed |  | During remedial works to the WTH Level +1 roof (Block C & D) the Lightning Protection / Earthing cabling has been damaged in 13 number locations.
| 02SL - Stations (LUL) | Cxxx-NCR-001326 | NCR | ENWA sidestream filter Breakdown (WTH) |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2020-11-18 | 2020-11-12 08:32 | -6 | 2020-10-21 08:30 | Mechanical - Mechanical Engineering General | 1500 |  | Equipment Breakdown | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | During maintenance of the side stream filter it was noted that the circulation pump was faulty and that there was a faulty actuator on one of the control valves.
| 02SL - Stations (LUL) | Cxxx-NCR-001327 | NCR | UTX ducts - ingress of debris |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2020-11-18 | 2021-04-01 10:16 | 134 | 2020-10-21 11:22 | Civil - Civil Engineering General | 15000 |  | Design | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | During a site visit it was noted that the UTX Ducts have Debris within them.
| 02SL - Stations (LUL) | Cxxx-NCR-001328 | NCR | Incorrect Asset ID labels |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2020-11-18 | 2021-03-25 16:57 | 127 | 2020-10-21 09:27 | Mechanical - Mechanical Engineering General | 3000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Incorrect Asset ID's installed when reviewed against as-built schematics
| 02SL - Stations (LUL) | Cxxx-NCR-001329 | NCR | Damage to Door Contact |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2020-11-23 | 2020-11-17 13:42 | -6 | 2020-10-26 12:09 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | On site walk in the -2 GYB area noticed Cxxx Door contact hanging out (Picture Attached of DC and ID)
| 02SL - Stations (LUL) | Cxxx-NCR-001330 | NCR | Damage to EFR-W10 Fan support Plinth |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2020-12-01 | 2020-11-27 15:46 | -4 | 2020-11-03 08:27 | Mechanical - Heating Ventilation & Air Conditioning | 1500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | During inspection of the lagging at WTH level -4 mezz (southbox) it was noted that part of the fan support plinth has broken away.
| 02SL - Stations (LUL) | Cxxx-NCR-001331 | NCR | Motorised Fire Damper - Electrical interface termination between manufacturer and field connection |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2020-12-01 | 2021-02-15 10:21 | 76 | 2020-11-03 08:31 | Mechanical - Heating Ventilation & Air Conditioning | 2500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | During a routine site walk it was noted that the over pressure relief dampers to one of the HV rooms at WTH level -4 was slightly open. upon investigation it was noted that the motorised fire damper on the extract was shut, causing the room to over pressurise. Upon investigation of the extract damper, a loose connection was found in the interfacing junction box between the manufacturers wiring and the field wiring.
| 02SL - Stations (LUL) | Cxxx-NCR-001332 | NCR | Motorised Fire Damper installation at WTH -4mezz |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2020-12-01 | 2021-02-26 18:25 | 87 | 2020-11-03 13:54 | Mechanical - Heating Ventilation & Air Conditioning | 30000 |  | Design | Rework | 2 (6-60k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Unable to install motorised fire damper plates as per manufacturers instructions. Dampers MFD-W113, MFD-W114 and MFD-W118 affected
| 02SL - Stations (LUL) | Cxxx-NCR-001333 | NCR | Failure to meet the minimum requirements for ductwork cleaning. |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2021-07-12 | 2021-07-20 08:17 | 8 | 2020-11-11 12:48 | Mechanical - Heating Ventilation & Air Conditioning | 7500 |  | Planning | Rework | 2 (6-60k) | Complete | Material/Preservation Problems - Not Defined | Completed |  | Following issue of the September 2020 Care & Custody report (Cxxx-LAO-Z-LRC-N105_WS089_Z-50011) the ductwork cleanliness sampling demonstrated that the ductwork cleanliness failed to meet the minimum requirements.
| 02SL - Stations (LUL) | Cxxx-NCR-001334 | NCR | Aqualeak Meter Reading Discrepencies |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2020-12-16 | 2021-02-17 10:51 | 63 | 2020-11-18 16:14 | Mechanical - Public Health Engineering | 3000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | During investigative works to determine the cause of the aqualeak unit going into alarm, it was noted that the external meter was not counting however the internal meter was. A new meter was ordered and installed and the issue persisted. The meter that was removed was checked and when spun by hand the meter counted. It was then clear the issue was to do with flow.
| 02SL - Stations (LUL) | Cxxx-NCR-001335 | NCR | iGuzzini drum manufacturing NCR – outstanding documentation |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2021-01-18 | 2021-01-07 15:58 | -11 | 2020-11-19 13:09 | Architectural - Finishes | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | The iGuzzini Light Drum Manufacturing Quality Packs for TSR1 & TSR2 (Cxxx-LAO-O7-LRC-N105_WS089_Z-50269), TSR3 & TSR4 (Cxxx-LAO-O7-LRC-N105_WS089_Z-50271), and TSR5 (Cxxx-LAO-O7-LRC-N105_WS089_Z-50245) are missing a number of verifying documents.
| 02SL - Stations (LUL) | Cxxx-NCR-001336 | NCR | barrell drop |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2021-01-15 | 2021-01-28 09:27 | 13 | 2020-12-03 11:33 | Architectural - Urban Realm | 500 |  | Incomplete Works | Repair | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | London Gin Club (LGC) barrel drop in relation to Cxxx-PMI-01805 - GEN: Completion of works associated with the London Gin Club (LGC) WTH - Urban Realm. existing barrel drop cover to be raised to street levels. If replacement required agree other details with gin club. As it is there asset.
| 02SL - Stations (LUL) | Cxxx-NCR-001337 | NCR | Geothermal Pipe Damage |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2021-01-17 | 2021-02-19 12:13 | 33 | 2020-12-15 11:29 | Civil - Geotechnical Engineering | 10000 |  | Damaged | Repair | 2 (6-60k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | During the crane base formwork installation/striking it was noted that a geothermal pipe has been damaged. The pipe is cast into the OSD basement slab and has been hit by a drill whilst the ops were installing the bolts for the PERI props. See attached mark-up and photo's for information
| 02SL - Stations (LUL) | Cxxx-NCR-001338 | NCR | GYB +1, Fire Compartmentation non compliance |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2021-02-23 | 2021-03-12 16:28 | 17 | 2021-01-26 08:58 | Mechanical - Heating Ventilation & Air Conditioning | 6000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The current install around MD-E19 on Goslett Yard Box level +1 does not provide the required fire compartmentation.
| 02SL - Stations (LUL) | Cxxx-NCR-001339 | NCR | Missing CRL Inspections of Concrete Sealer -2 - +6 WTH |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2021-02-04 | 2021-03-01 09:53 | 25 | 2021-01-11 10:46 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Procedure Problem - Lack of procedure | Completed |  | CRL have not been invited to concrete wall sealer inspections on IRF submitted within quality pack missing sigantures. Retro inspections need to be carried out. with IRF signed and dated as such.
| 02SL - Stations (LUL) | Cxxx-NCR-001340 | NCR | OSD Shear Keys |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2021-02-10 | 2021-02-04 12:27 | -6 | 2021-01-13 10:04 | Civil - Civil Engineering General | 0 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | 20No. shear key pockets were to be formed in the +1 level slab of WTH Block C. 19No. were formed in correct location or concrete omitted to allow for future confirmation of final locations (ref IMG_3541.jpg & 3542 take 04/05/2017 and supplied to OSD by D. __ 20/09/2020) and 1No. in a mirrored position. The rebar was installed as per drawings available at the time. After a review by CRL\__\OSD in Nov\Dec 2020, the final depth was confirmed, revised position for 1No was confirmed and the removal of rebar was checked and confirmed. The attached “Cxxx-OVE-Cxxx-SITE-SK-DW01 Alterations to WTH Block C Level +1 Reinforcement to accommodate OSD shear keys Draft Rev A (003).pdf” refers to the works to be carried out to suit the requirements of the OSD.
| 02SL - Stations (LUL) | Cxxx-NCR-001342 | NCR | FLUKE Calibration Certificate for Gas conventional system |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2021-02-18 | 2021-02-19 12:07 | 1 | 2021-01-21 12:01 | Fire - Suppression | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Information not detailed | Completed |  | Certificate of calibration provided for a FLUKE meter was incomplete. the certificate was provided (page 1) but the test data (pages 2 and 3) were missing.
| 02SL - Stations (LUL) | Cxxx-NCR-001343 | NCR | Assurance Documentation |  | Crossrail | PDP | TCR - Tottenham Court Road Station (West) |  | 2021-03-12 | 2021-07-09 11:19 | 119 | 2021-02-12 17:23 | Architectural - Balustrade | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | Assurance documentation required for the install the safety handrail system beyond the platform end walls has not been put in place as is contractually required. Unless specifically instructed by Crossrail the contractor is required to supply this information prior to the commencement of works. In summary the missing items are to include but not limited to: An approved ITP An accepted RSS inspection check sheet Detailed design drawings An accepted benchmark or sample It is acknowledged that the work programme is being driven by access to the sites and that the product is an ‘off the shelf’ system however the assurance documentation is required including the eventual as-built drawings noting earthing straps by others.
| 02SL - Stations (LUL) | Cxxx-NCR-001344 | NCR | Trace heating system remedial works due to Cxxx-NCR-001315. |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2021-03-19 | 2021-04-12 15:42 | 24 | 2021-02-19 08:29 | Mechanical - Mechanical Engineering General | 2500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | As part of Cxxx-NCR-001315 the dosing pots at both GYB level +2 and WTH level +6 where relocated to the -2 levels. This has now left a length of trace heating cable/element that is now redundant.
| 02SL - Stations (LUL) | Cxxx-NCR-001345 | NCR | Presence of pseudomonas in the chilled water systems. |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2022-08-26 | 2022-08-18 15:04 | -8 | 2021-02-19 09:16 | Mechanical - Mechanical Engineering General | 10000 |  | System Defect | Rework | 2 (6-60k) | Complete | Design Problem - Inadequate or defective design | Completed |  | During routine sampling in November it was noted that the 4 samples (2no. GYB and 2no. WTH) failed to meet the BSRIA criteria due to recording Pseudomonas levels over the guideline limit. Nitrate reducing bacteria was also found in the sample at GYB level -2.
| 02SL - Stations (LUL) | Cxxx-NCR-001346 | NCR | Earth Bar labels with no DAAID |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2021-03-05 | 2021-03-17 15:27 | 12 | 2021-02-26 15:10 | Information Management - Asset Information | 0 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Earth Bar labels have not got the Earth Bars IDs on the label as at the time of labelling the IDs were not available to us. We have now inputted those IDs into ADCS (037) under the Design Alternative ID column and they have now been added to the schematics. Proposing a Use as-is change
| 02SL - Stations (LUL) | Cxxx-NCR-001347 | NCR | Installation of Damper Plates WTH Level -3 |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2021-04-09 | 2021-04-21 14:12 | 12 | 2021-03-05 18:25 | Mechanical - Heating Ventilation & Air Conditioning | 10000 |  | Incomplete Works | Rework | 2 (6-60k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Damper Plates to be installed within the CER Riser WTH Level -3
| 02SL - Stations (LUL) | Cxxx-NCR-001348 | NCR | Installation of Damper Plates |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2021-04-09 | 2021-04-21 15:04 | 12 | 2021-03-05 18:32 | Mechanical - Heating Ventilation & Air Conditioning | 5000 |  | Incomplete Works | Rework | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Damper Plates to be installed within the AHU Plantroom WTH Level -2
| 02SL - Stations (LUL) | Cxxx-NCR-001349 | NCR | RIR submitted incorrectly - Signed Approver having previously left the project. |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2021-04-02 | 2021-04-13 15:25 | 11 | 2021-03-05 18:41 | Information Management - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | RIR transmittal issued with the Approver name having previously left the project.
| 02SL - Stations (LUL) | Cxxx-NCR-001350 | NCR | Disassembly of commissioned ventilation systems – WTH |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2021-04-07 | 2021-03-26 17:41 | -12 | 2021-03-10 17:40 | Mechanical - Heating Ventilation & Air Conditioning | 3000 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | *This NCR has been raised by CRL following the Cxxx Contractor's refusal to raise new NCRs* During a site inspection unrelated to ventilation systems it was discovered by chance that ventilation ductwork serving EFR-W1, EFR-W2, and possibly also EFR-W4 within 2/908 (WTH) has been disassembled. It is understood that the reason for this is to provide access to enable the Contractor to complete his fire-stopping. The Contractor had not informed the CRL mechanical FAE (__) of this work. The affected ductwork systems have been fully commissioned and signed off at the IRN, PCC and PAC phases.
| 02SL - Stations (LUL) | Cxxx-NCR-001351 | NCR | WTH Ground Floor Bin Store - Ventilation |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2021-07-08 | 2021-10-08 14:49 | 92 | 2021-04-16 09:14 | Mechanical - Heating Ventilation & Air Conditioning | 10000 |  | Design | Rework | 2 (6-60k) | Complete | Design Problem - Inadequate or defective design | Completed |  | WTH Ground floor bin store - lack of natural ventilation provision provided.
| 02SL - Stations (LUL) | Cxxx-NCR-001352 | NCR | WTH intervention staircase identified non-compliant noise levels |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2021-05-17 | 2021-04-30 14:45 | -17 | 2021-04-19 14:15 | Mechanical - Heating Ventilation & Air Conditioning | 10000 |  | Testing and Commissioning | Rework | 2 (6-60k) | Complete | Design Problem - Inadequate or defective design | Completed |  | NCR 1282 identified non-compliant noise levels to 5No. zones within the WTH intervention staircase areas. To resolve this issue the volume control dampers to these zones have been fully opened with the fan speeds set to match the requirements for these areas. Whilst testing to prove compliance within these zones further acoustic non-compliant levels have been identified. These are listed below. There are other zones in this system that whilst compliant are at the upper limits of compliance. Attached schedule for ref Resolution Cxxx intend to re-test all areas of both WTH and GYB air release zones with the dampers open and adjust the fan speeds to identify compliance with BS12101-6 2005 & the employers requirements related to noise levels.
| 02SL - Stations (LUL) | Cxxx-NCR-001354 | NCR | Lifting Eye Installation Out of sequence with ITP Approval |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2021-04-29 | 2021-04-30 14:02 | 1 | 2021-04-28 14:33 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Lifting eyes were installed out of sequence with the specific ITP sign off.
| 02SL - Stations (LUL) | Cxxx-NCR-001355 | NCR | Firestopping at OSD interface |  | Crossrail | PDP | TCR - Tottenham Court Road Station (West) |  | 2021-07-13 | 2021-06-15 13:04 | -28 | 2021-06-15 10:46 | Fire - Compartmentation | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Supervision - Other | Completed |  | As part of the interface with the Over Site Developer, __ raised C423-RFI-000028 querying the completeness of the firestopping works at the interface between the station and the over site development, as follows and attached: - RFI to confirm details in below circled areas with regards to firestops. Vertical fire-stopping requirements between residential entrances and station areas as ground floor. Architects assume a REI 120 rating here (circled below), however these areas of cladding are within the station scope due to subcontractor design. Further information required in these areas. Please also see attached 200819_stationCladding EntranceMarkUP. Annotated request / details required. Remedial works have been undertaken by the Cxxx Contractor to address the concerns and have been inspected for completeness, as recorded in the attached IRF. This records that the works were satisfactorily completed by the Cxxx Contractor and that further works by the Over Site Developer are required to complete the interfacing details. As this is dependent upon a third party, it is therefore advised that a punchwork (perhaps an OBS might be easier to generate and assign) is generated in order for Crossrail to inspect the interface at a later date once the __ works have been completed. If any further works are required by the Cxxx Contractor they will be captured as a PWK item for future management.
| 02SL - Stations (LUL) | Cxxx-NCR-001356 | NCR | Cable label vs AIMS database discrepancy |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2021-10-15 | 2021-10-14 08:54 | -1 | 2021-10-07 13:44 | Information Management - Asset Information | 0 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Supervision - Other | Completed |  | A discrepancy between the as installed cable label data and what has been input into the AIMS database differ. This is due to a limit of 40 characters per label. An example of this has been sent to __ for review. (email attached)
| 02SL - Stations (LUL) | Cxxx-NCR-001357 | NCR | Cable circuit number asset information for dual fed cables |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2021-10-15 | 2021-10-19 07:17 | 4 | 2021-10-07 14:28 | Information Management - Asset Information | 0 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | Within the AIMS quality report, it has been noted that a number of cable circuit numbers have been populated with a dash.
| 02SL - Stations (LUL) | Cxxx-NCR-001358 | NCR | Dean Street paving levels at interface with __ |  | Crossrail | PDP | TCR - Tottenham Court Road Station (West) |  | 2022-02-18 | 2022-04-06 10:25 | 47 | 2021-10-12 08:58 | Civil - Streets & Highways | 9000 |  | Incorrect Installation | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The paving to Dean Street has not been laid to the design levels and does not comply with the WCC acceptable falls and, as such, is resulting in ponding outside the fire escape door to the __ retail property. The surface levels rise from the interface at the door threshold to the north towards Oxford Street and the area immediately outside of the door threshold is nominally flat. Additionally, the developer of the property (__) has reported water ingress beneath the door as a result of the ponding during heavy rainfall. This issue is preventing TCR from discharging its consent for the satisfactory reinstatement of the highway and is also preventing GPE from discharging their consents with WCC. The Contractor is required to develop a scheme to address these issues and obtain acceptance from WCC.
| 02SL - Stations (LUL) | Cxxx-NCR-001359 | NCR | Lack of lighting in GYB level -5 (2/133, 2/134, 2/135) |  | Crossrail | PDP | TCR - Tottenham Court Road Station (West) |  | 2021-11-19 | 2021-10-22 11:27 | -28 | 2021-10-12 09:58 | Electrical - Lighting | 10000 |  | Design | Use As-Is | 2 (6-60k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The room beneath the escalators in the -5 level of the GYB structure (2/133, 2/134, 2/135) has not been fitted with any permanent lighting to facilitate access for inspection. LU have been consulted to determine whether provision to plug in temporary lighting will suffice but are not willing to accept this as a long term mitigation, therefore permanent lighting will need to be fitted.
| 02SL - Stations (LUL) | Cxxx-NCR-001362 | NCR | L21731-Drainage Screen not labelled |  | Contr | LAO | TCR - Tottenham Court Road Station (West) |  | 2021-12-03 | 2021-11-10 10:56 | -23 | 2021-11-05 10:18 | Information Management - Asset Information | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | The requirement for L21731-Drainage Screen is for the assets to be labelled.
| 02SL - Stations (LUL) | Cxxx-NCR-001363 | NCR | Off-Site ‘Wind Resistance Testing’ has not been carried out as required in the Architectural Specifications. |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2021-12-09 | 2021-12-06 11:41 | -3 | 2021-11-24 16:42 | Architectural - Doors | 0 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | A surveillance was carried out on the compliance of fire doors installed in Tunnel Vent Shaft (TVS) locations. A noise and pressure report were issued by Cxxx ‘Internal Noise and Pressure Requirements Cxxx-__-H-RGN-CRG03-50036 (rev 4). On checking the compliance of the Installed doors at Tottenham Court Road (TCR), the Material Compliance Record (MCR) ‘__ __ door’ Cxxx-LAO-Y-XDS-N105_WS089_Z-50112 (Rev 2), it was found that the MCR contained calculations for 3Kpa pressure rating, but did not contain testing evidence to validate the calculations. Which is a requirement of the TCR Architectural Specification.
| 02SL - Stations (LUL) | Cxxx-NCR-001364 | NCR | Presence of iron contaminants within the chilled water system |  | Crossrail | PDP | TCR - Tottenham Court Road Station (West) |  | 2022-08-26 | 2022-08-18 15:11 | -8 | 2021-12-06 08:57 | Mechanical - Heating Ventilation & Air Conditioning | 15000 |  | System Defect | Rework | 2 (6-60k) | Complete | Design Problem - Inadequate or defective design | Completed |  | During monitoring of the chilled water system to address the presence of pseudomonas under Cxxx-NCR-001345, traces or iron deposits above acceptable levels have been detected in the chilled water system. This is required to be addressed prior to handover to London Underground.
| 02SL - Stations (LUL) | Cxxx-NCR-001365 | NCR | LV Main Switchboards Operating/Functioning Outside Crossrail Accepted and Commissioned Parameters |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2022-01-07 | 2022-03-14 10:53 | 66 | 2021-12-17 16:46 | Electrical - Switchgear | 500 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | The Project Manger raises his immediate concerns in relation to the Main LV Switchboards “Operational Failures” at TCR and subsequent impact/risk to the wider/external CRL commissioning activities (due to switching limitations being imposed on the wider power supply network as a result of the current switchgears intermittent and perturbed state). It is noted that the equipment is not functioning as per earlier testing and that the root cause of this is not currently known. Regardless, this is a non-conformance and needs rectification, for which __ are being asked to support. Despite having been FAT/SAT Tested and Commissioned, it was noted during associated Bismark testing and remote switching/testing activities (date of 03-04/10/2021) that the equipment was operating/functioning outside of the commissioned/expected parameters. This was reported to The contractor __s (__) (dated 05/10/2021 07/10/2021 21/10/2021). Due to the uncertainty of the root cause and for the purpose of records CRL-OBS-35864 was raised. The Projector Manger requests the Contractor to immediately investigate the root cause and restore the equipment to the original SAT/CRL accepted status through means of applicable testing/functional operation (LOCAL/REMOTE/AUTOMATIC) and confirm by response that the equipment is functioning to all applicable specification/standards and original test scenarios and is achieving all functional/expected parameters (without limitations) post completion of this exercise. Additional Note Added 22.01.2022 The ETH issues have been investigated by __ which resulted in the identification of a faulty Phase Failure Relay which was subsequently replaced by the Contractor and the issues in the ETH would appear to have been resolved (the PM thanks the Contractor for the swift resolve at the ETH). Unfortunately there is still issues within the WTH resulting in intermittent operational limitations/failures with the associated PLC standing down as a result of these switching operations and requiring unacceptable manual intervention. The PM attended a meeting with the Contractor on the 21/01/2022 which resulted in agreement that the Contractor was to compile a test script and utilise a process of test elimination and root cause analysis approach to identify and correct the current issues/limitations. The PM awaits the testing scenario and plan to undertake/execute the works (dates/times etc) and the attendance/organisation of any PLC specialists with urgency and will assist to the best of his ability in facilitating any access restrictions/limitations should they occur with the Contractors planned works. The Contractor is requested to ensure any plans are comprehensively co-ordinated around others (known/planned works) prior to submitting dates to avoid unnecessary rejection.
| 02SL - Stations (LUL) | Cxxx-NCR-001366 | NCR | WTH Column C/3 L+1 Soffit Crack |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2022-05-20 | 2022-05-19 11:44 | -1 | 2022-03-22 12:24 | Civil - Civil Engineering General | 6000 |  | Damaged | Rework | 3 (3-6k) | Complete | Previous Construction - Problems based on previous construction errors | Completed |  | Further to a visual inspection of the L+1 soffit from Ticket Hall level, carried out by __ in February 2022, CRL were advised that a surface crack appears to have formed around the column at GL C/3. Refer to attached location plans and site photos ('Cxxx-NCR-001366 Location Plans and Site Photos.pdf'). It is noted that repairs were carried out around this column in 2017, further to the below NCR, and this crack may be as a result of delamination of the previously-completed repairs: Cxxx-NCR-000730 GL C/3 Truss Column & +1 Soffit Damage This area is to be further inspected by __ to verify this, prior to being suitably repaired.
| 02SL - Stations (LUL) | Cxxx-NCR-001367 | NCR | PLT AP2W Misaligned GFRC Panel |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2022-04-22 | 2022-05-03 19:02 | 11 | 2022-03-22 12:27 | Architectural - Ceilings & Soffits | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Error by manufacturer in shipping or marking | Completed |  | Gasket remedial works were carried out as part of the below POWK, which was subsequently closed on eB: Cxxx-PWK-00756 Gasket remedial works to GFRC However, it has been noticed on site that one of the GFRC panels at high level in AP2W which was reinstated, has not been installed flush with the adjacent panel. Refer to attached location plans and site photos ('Cxxx-NCR-001367 Location Plans and Site Photos.pdf'). This will hence need to be removed in order to be able to fully inspect the area behind it to rectify any issues that may be causing this misalignment, prior to reinstalling the panel.
| 02SL - Stations (LUL) | Cxxx-NCR-001368 | NCR | TCR - Missing Cavity/Smoke Barriers Between Secondary Lining and GFRC Panels |  | Crossrail | XRL | TCR - Tottenham Court Road Station (West) |  | 2022-08-19 | 2022-07-22 17:10 | -28 | 2022-06-13 13:52 | Architectural - Ceilings & Soffits | 7000 |  | Incomplete Works | Rework | 2 (6-60k) | Complete | Previous Construction - Problems based on previous construction errors | Completed |  | As part of CRL-NDF-00235 the IM has identified a number locations between the secondary concrete lining and GRC panels at the soffit of the platform cross-passages where the required cavity/smoke barrier has either been omitted or removed in error. Refer to attached site photos illustrating this omission adjacent to the CMS at the following locations: 1. 5/191 (AP3E) – evidenced as missing in CRL-NDF-00235 2. 5/197 (AP3W) – evidenced as missing in CRL-NDF-00235 The following locations have also been referenced in the NDF and will need to be checked as part of this NCR, as agreed with Cxxx: 3. 5/192 (AP4E) – referenced in CRL-NDF-00235 4. 5/198 (AP4W) – referenced in CRL-NDF-00235 5. 5/194 (AP1) – referenced in CRL-NDF-00235 6. 5/190 (AP2E) – referenced in CRL-NDF-00235 7. 5/195 (AP2W) – referenced in CRL-NDF-00235 8. 5/199 (AP7a) – referenced in CRL-NDF-00235 9. 5/200 (AP7b) – referenced in CRL-NDF-00235 10. 5/207 (AP8) – referenced in CRL-NDF-00235 It has also been agreed to carry out spot checks along the westbound platform, as the ITP Records for this area (Cxxx-LAO-O7-LRC-N105_WS089_Z-50192 Rev.1.0) are not as thorough as those for all other areas. Refer to ITP Records linked to this NCR as well as the attached PowerPoint pack 'Cxxx - PLT Cavity Barriers Behind GFRC Rev.2.0' which summarises all checks carried out by CRL when reviewing this issue.
| 02SL - Stations (LUL) | Cxxx-NCR-000099 | NCR | Vibration in adjacent properties as a result of site excavation |  | Contr |  | FAR - Farringdon Station (West) |  | 2011-08-10 | 2011-11-15 11:58 | 97 | 2011-08-03 | Civil - Excavation | 500 |  | Supervision/Management | Reject |  | Complete |  | Completed |  | During the excavation of the East Ticket Hall basement slab, vibrations were experienced in properties adjacent to the site. A complaint was received 27th July relating to vibrations within there property. The property was visited during the vibration, and it was assessed that while the vibration was evident, works would proceed, and the vibration was limited in time. __ agreed to action local monitoring.
| 02SL - Stations (LUL) | Cxxx-NCR-000130 | NCR | site water supply |  | Contr |  | FAR - Farringdon Station (West) |  | 2011-10-19 | 2012-01-19 09:04 | 92 | 2011-08-24 | Utilities Engineering - Water | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | A temporary supply has been established off a hydrant supply on a 1 month concession. Pipe work on the outside of the hoarding was up protected. No blue tag No double return valve The primary reason for the non-conformance was that the conditions of the hydrant licence were not effectively comunicated to the site team installing the temporary pipework.
| 02SL - Stations (LUL) | Cxxx-NCR-000150 | NCR | Raising the working platfrom at the WTH |  | Contr |  | FAR - Farringdon Station (West) |  | 2011-09-19 | 2011-09-20 15:11 | 1 | 2011-09-05 | Civil - Fill | 500 |  | System Defect | Use As-Is |  | Complete |  | Completed |  | Thw works commenced without an approved MCR or ITP. This happened due to a failure to undertand that these were required believing as they were TW they would be covered under the TW procedure.
| 02SL - Stations (LUL) | Cxxx-NCR-000151 | NCR | Commencing the Bentonite slab without an approved ITP in place |  | Contr |  | FAR - Farringdon Station (West) |  | 2011-09-19 | 2011-09-14 11:38 | -5 | 2011-09-05 | Civil - Civil Engineering General | 500 |  | System Defect | Use As-Is |  | Complete |  | Completed |  | The slab did not have an approved ITP in place prior to the slab being constructed. This situation occured due to a failure to understand that temporary works required ITP's to be in place.
| 02SL - Stations (LUL) | Cxxx-NCR-000152 | NCR | Diesel Particulate Filters BG36 piling rig |  | Contr |  | FAR - Farringdon Station (West) |  | 2011-09-19 | 2011-10-18 08:21 | 29 | 2011-09-05 | Environmental - Air Quality | 500 |  | Planning | Use As-Is |  | Complete |  | Completed |  | The BG36 piling rig conforms to EU emissions standard stage 2. The retro fitting of a diesel particulate filter would cost circa £40k, impair engine performance and negate the manufacturers warranty. As such it is not feasible to make the modification.
| 02SL - Stations (LUL) | Cxxx-NCR-000161 | NCR | Excavation of obstruction |  | Contr |  | FAR - Farringdon Station (West) |  | 2011-09-27 | 2011-10-18 08:26 | 21 | 2011-09-13 | Civil - Excavation | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | -Slope not as per temporary works design -Spoil storage on top of the excavation pit higher than as per design
| 02SL - Stations (LUL) | Cxxx-NCR-000200 | NCR | Strain gauge installation locations |  | Contr |  | FAR - Farringdon Station (West) |  | 2011-11-04 | 2011-11-15 12:00 | 11 | 2011-10-21 | Utilities Engineering - Gas | 500 |  | System Defect | Use As-Is |  | Complete |  | Completed |  | (1) On Gas Pit 5, gauges were installed at angles off TDC of -50o,20o and 85o. On Gas Pit 6, gauges were installed at angles off TDC of approx -80 o, -20o, 55o. These positions were agreed with the NGG representative (Frank Barkley) on site on the 15th October following conversations with Rodney Guinn and the NGG designer. (2) Non destructive testing (N__) was carried out on the available area of the gas main surface. Testing was required around the full circumference of the pipe. Approximately 40% of the pipe circumference was tested on both gas pit 5 and 6.
| 02SL - Stations (LUL) | Cxxx-NCR-000206 | NCR | Electrical Continuity pile reinforcement |  | Contr |  | FAR - Farringdon Station (West) |  | 2011-11-10 | 2011-11-07 10:46 | -3 | 2011-10-27 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | On pile R901 the threads of the bar were not protected with foam and tape allowing concrete to bond onto the threads
| 02SL - Stations (LUL) | Cxxx-NCR-000216 | NCR | Commencement of Smithfield Market Mechanical Installation Works |  | Contr |  | FAR - Farringdon Station (West) |  | 2011-11-11 | 2011-11-15 11:10 | 4 | 2011-11-04 | Civil - Civil Engineering General | 500 |  | System Defect | Reject |  | Complete |  | Completed |  | Mechanical installation works within Smithfield Market commenced on 25th October 2011 without the Project Manager's acceptance of the design for the supports and fabrication drawings.
| 02SL - Stations (LUL) | Cxxx-NCR-000218 | NCR | Missed Planned Surveillances |  | Contr |  | FAR - Farringdon Station (West) |  | 2011-11-09 | 2012-02-23 08:51 | 106 | 2011-11-04 | Civil - Civil Engineering General | 500 |  | System Defect | Reject |  | Complete |  | Completed |  | Cxxx have not undertaken any surveillances as required by the contract and their own surveillance schedule.
| 02SL - Stations (LUL) | Cxxx-NCR-000219 | NCR | Utilities Plan: Non-Conformance |  | Contr |  | FAR - Farringdon Station (West) |  | 2011-11-11 | 2012-02-20 14:04 | 101 | 2011-11-04 | Civil - Civil Engineering General | 500 |  | System Defect | Rework |  | Complete |  | Completed |  | The Utilities Coordinator has not been approving permits to dig
| 02SL - Stations (LUL) | Cxxx-NCR-000222 | NCR | Casting of Siding Screen Bases without Method Statement |  | Contr |  | FAR - Farringdon Station (West) |  | 2011-11-21 | 2012-03-30 18:13 | 130 | 2011-11-07 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Reject |  | Complete |  | Completed |  | 1. Works Commencing without Documentation in Place On 2nd and 3rd of November 2011 7 no. foundations were constructed (excavated, form work installed, reinforcement fixed and concrete poured) without any of the documentation listed in technical requirements section being accepted by CRL (or LU). 2. Failure to follow Construction Phase Plan Although no accepted method statement was in place prior to the works commencing the operatives on site were undertaking the works received a Daily Activity Briefing and were working to a Task Briefing Sheet. This is not in accordance with the Cxxx Construction Phase Plan as stated above. 3. Design Change without Correct Approvals During the excavation and installation of the foundations existing concrete footings/ structures were encountered. This prevented the excavation reaching 1.0 m depth as required by the original __ design (Cxxx-LOS-C-CER-M123-50039 rev 3.0). The resultant foundations were constructed to a depth of 500mm with dowel bars installed to connect the new footings to the existing concrete base. Although __ followed an internal design procedure for changing an element of works designed internally, acceptance was not obtained from either CRL or LU before the works were constructed. Why The principal cause of the incident was a misunderstanding about whether the completed scope had already been covered in approved documentation because of inadequate communication and confused documentation. The Project Engineer allowed work to be completed, unaware that the appropriate approvals weren’t in place. This was a failure in full compliance with project procedures. The Non-conformance Report has proved difficult to close out because the Project Engineer, responsible at the time of the incident, left before reporting had been completed and the Quality Manager has not been fully involved in reporting since the incident; a reflection of his part-time status on the Project.
| 02SL - Stations (LUL) | Cxxx-NCR-000225 | NCR | Long Lane vault grouting |  | Contr |  | FAR - Farringdon Station (West) |  | 2011-12-28 | 2012-02-28 18:44 | 62 | 2011-11-08 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Vault 10 was cored and grouted without inspection from Crossrail
| 02SL - Stations (LUL) | Cxxx-NCR-000226 | NCR | Plate Bearing Test SH-W1 Working Platform |  | Contr |  | FAR - Farringdon Station (West) |  | 2011-11-22 | 2011-11-15 10:56 | -7 | 2011-11-08 | Civil - Fill | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | An IRF was not raised and subsequently the tests where not witnessed by CRL
| 02SL - Stations (LUL) | Cxxx-NCR-000234 | NCR | Breech of __224 Boundary Agreement |  | Contr |  | FAR - Farringdon Station (West) |  | 2011-11-18 | 2011-12-09 14:40 | 21 | 2011-11-11 | Fire - Fire Systems & General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Following a meeting with Crossrail and __ of LUL on the 15/11/11, it was decided that there were several breaches of the __224 boundary agreement. In relation to item 1 – maintaining 6m clear zone: • Scaffold storage rack next to Lindsey Street bridge needs to move • Rubble from the demolition of the IMR building needs to move* In relation to item 2 – maintaining fire points • Fire points not in locations shown on the __224 In relation to item 3 – safe access • Uneven surface (with the potential to get worse during wet weather) on the route towards the SER • Lack of toe board on the scaffold handrail on the old platform edge • Unacceptable gap between the bottom handrail and the platform surface • Uneven Loose wood and an aluminium tower left on the platform *It must be noted that __ were only made officially aware of the __224 boundary after the IMR demolition had occurred. At this point it was not possible to move the IMR demo rubble for safety and accessc reasons.
| 02SL - Stations (LUL) | Cxxx-NCR-000241 | NCR | Damaged manhole ETH |  | Contr |  | FAR - Farringdon Station (West) |  | 2012-07-28 | 2012-07-27 15:12 | -1 | 2011-11-16 | Civil - Civil Engineering General | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | In this instance this manhole was dug under permit 048 for piling and installation of the guide walls. The brickwork manhole in question is circled on the attached scan on the right at the South East perimeter of the site at high level. The damage to the brickwork pit underneath the hoarding line can also be viewed on the attached two photographs. The brickwork manhole was identified by the permit issuer on the plan however the manhole was not visible within the site because the lid of the manhole was buried beneath a VCB block. The VCB block had the perimeter hoarding on the South East corner fixed to it. The outermost point of the brickwork manhole was buried lower than the lid beneath the ground surface just inside the hoarding line on the East Ticket Hall site. When digging with the excavator for the guide wall, the edge of the bucket caught the outermost corner of the pit wall. The pit wall was buried beneath the ground and the excavator bucket pulled the corner of the brick manhole with it. This corner of the brickwork manhole was damaged by the excavator as a result. The damage exposed power cables within the service pit which __ always assumed as live until it was confirmed otherwise. Immediate action was taken to seal the hole with ply and displaying 'live cable' signage until further investigation was carried out on the manhole and the contents of it. A desk top study was revisited to conclude whether the assumed owner __ was correct. It was concluded that __ were the asset owner and they were asked to come to site to determine the status of the cable. The pit has been inspected and __ have confirmed that the cable within the pit is dead. __ have now cut the cable within the manhole and provided __ with and extraction certificate. The extraction certificate is attached to this NCR and __ have also provided __ with confirmation that the manhole is now obsolete and can be demolished or back filled. This confirmation e-mail has also been attached.
| 02SL - Stations (LUL) | Cxxx-NCR-000242 | NCR | fill not covered by Method Statement |  | Contr |  | FAR - Farringdon Station (West) |  | 2011-11-30 | 2012-02-20 15:15 | 82 | 2011-11-16 | Civil - Fill | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | deliveries of 6F2 fill were received at ETH which is covered by a Method Statement. the fill was then transferred down to the lower level and this was covered only by a task briefing sheet. the reason for this occurring was due to an error as the standard __ procedure states that detailed Task Briefing sheets can be used in place of method statements for simple tasks. this procedure is not stated in the CPP and therefore not approved by CRL.
| 02SL - Stations (LUL) | Cxxx-NCR-000251 | NCR | No IRF for First Plate bearing test for Low level Ramp |  | Contr |  | FAR - Farringdon Station (West) |  | 2011-11-27 | 2012-03-05 09:24 | 99 | 2011-11-21 | Civil - Fill | 500 |  | Planning | Reject |  | Complete |  | Completed |  | No IRF was received for first plate bearing test (Friday morning 18/11/11)
| 02SL - Stations (LUL) | Cxxx-NCR-000252 | NCR | Soil sampling on pit 5 |  | Contr |  | FAR - Farringdon Station (West) |  | 2011-12-05 | 2012-01-19 09:07 | 45 | 2011-11-21 | Utilities Engineering - Gas | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Samples were not taken on Gas pit 5 and consequently soil testing was not carried out for this excavation due to a failure of the sub-contractor.
| 02SL - Stations (LUL) | Cxxx-NCR-000255 | NCR | Alarm plan |  | Contr |  | FAR - Farringdon Station (West) |  | 2011-12-07 | 2012-01-19 09:09 | 43 | 2011-11-23 | Surveying - Instrumentation and Monitoring | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Trigger levels (LUL Area A manual levelling) have been breached without the alarming has been sent out and the action plan has not been followed. __ would like to bring attention to the following: 1. The concerned area is outside of the zone of influence therefore the risk of “real” movements due to Crossrail works is very low (recorded ground movements on the LU track do not cause an immediate safety risk and are not caused by Cxxx core scope piling works). 2. Cross-check with UCIMS data was not possible due to lack of information available. 3. Information about works from 3rd parties in the concerned area to allow an interpretation of the results not available. 4. Trigger level was not activated in the data base for LUL Area A due to wrong understanding that for the levelling result a twist and cant calculation will be performed instead of a trigger level (this was clarified during the SRG meeting shortly before the occurrence the NCR).
| 02SL - Stations (LUL) | Cxxx-NCR-000256 | NCR | fault on temp measurement for strain guage |  | Contr |  | FAR - Farringdon Station (West) |  | 2011-12-08 | 2012-02-23 14:54 | 77 | 2011-11-24 | Utilities Engineering - Gas | 500 |  | Damaged | Use As-Is |  | Complete |  | Completed |  | Following re-testing of the strain gauges previously installed in the gas main, it transpires that the cable to one of the gauges within pit 5 has been damaged. This damage has been caused to the cable of the temperature sensor on the gauge however, the strain reading component is fully intact. As a result of this damage, it is not possible to obtain a temperature reading from the specific gauge. It should however be clarified that strain readings can still be obtained from all gauges. The effects of this non conformance are considered negligible as temperature variations between gauges at that depth are likely to be negligible, particularly considering that the temperature of the gauge will be governed by that of the cast iron gas main. The temperature readings from the two other gauges can therefore be used to compensate for thermal effects. Furthermore, a 1degree change in temperature on the gauge will cause an apparent strain of 11µ?. This figure is deemed negligible relative to the strains which typically cause concern to infrastructure.
| 02SL - Stations (LUL) | Cxxx-NCR-000267 | NCR | Pile cage skid spacer damage |  | Contr |  | FAR - Farringdon Station (West) |  | 2011-12-15 | 2012-01-23 10:16 | 39 | 2011-12-01 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Damaged | Use As-Is |  | Complete |  | Completed |  | Reduced cover
| 02SL - Stations (LUL) | Cxxx-NCR-000268 | NCR | VMBS Reporting |  | Contr |  | FAR - Farringdon Station (West) |  | 2011-12-15 | 2012-03-05 11:05 | 81 | 2011-12-01 | Civil - Civil Engineering General | 500 |  | System Defect | Reject |  | Complete |  | Completed |  | During Cxxx last review it was highlighted that all three of the plans where not acceptable. VMBS Reports show these plans have not been submitted or submitted late. In addition, there are a high number of unplanned vehicle movements associated with your site(s), meaning these have not been planned and the TCC is subsequently unable to effectively evaluate your plans.
| 02SL - Stations (LUL) | Cxxx-NCR-000281 | NCR | Commencing Work in Smithfield Market with MS Not Signed |  | Contr |  | FAR - Farringdon Station (West) |  | 2012-02-14 | 2012-02-20 15:21 | 6 | 2011-12-12 | Construction Health & Safety - Construction Health & Safety General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | __ would like to bring attention to the following: 1. The method statement was submitted on the 15/11 and returned back to Cxxx on 24/11. These works were low risk, yet program critical (testing allowed the market car-park to be reopened) and __ did not follow the correct sign-off process. 2. A signed/dated task briefing was in place for these works and Smithfield Market was made aware that these works were being carried out. 3. Smithfield Market, City of London and Crossrail were in attendance during the commissioning works (albeit at different times). All parties were happy that the works were being carried out safely.
| 02SL - Stations (LUL) | Cxxx-NCR-000304 | NCR | WTH W2 Rebar exposed at the top of R915 |  | Contr |  | FAR - Farringdon Station (West) |  | 2012-01-24 | 2012-02-06 15:37 | 13 | 2012-01-10 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The concrete was low on R915 to allow access to the sonic tubes without the need to later break the top of the pile down. The pile was cast to 106 mOD then before the concrete was set the concrete from the top was dug out to expose the top of the tubes. This also caused the exposure of 40mm of the top lifting ring of the cage. This will be the same for all future piles with sonic tubes in. An FCD will follow.
| 02SL - Stations (LUL) | Cxxx-NCR-000317 | NCR | Electrically continuous bar |  | Contr |  | FAR - Farringdon Station (West) |  | 2012-02-03 | 2012-02-28 13:11 | 25 | 2012-01-20 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | No coupler was placed at the top of Pile 951.
| 02SL - Stations (LUL) | Cxxx-NCR-000318 | NCR | Cast Level Pile 950 |  | Contr |  | FAR - Farringdon Station (West) |  | 2012-02-03 | 2012-05-14 08:26 | 101 | 2012-01-20 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Material | Rework |  | Complete |  | Completed |  | Pile 950 was cast to a level 1.5m below PPL (106). During the extraction of the last 8m of casing a void, created during the removal of a previous obstruction, caused the concrete to slump down more than expected as a volume of concrete flowed into the void. This resulted in the unsupported spoil falling on top of the fresh concrete.
| 02SL - Stations (LUL) | Cxxx-NCR-000319 | NCR | Cage too high on pile 946 |  | Contr |  | FAR - Farringdon Station (West) |  | 2012-02-03 | 2012-06-29 14:50 | 147 | 2012-01-20 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Material | Repair |  | Complete |  | Completed |  | Pile 946 has the cage couplers at +127-151mm, therefore out of tolerance by +52-76mm. (see attached sketch) This is because the concrete that was pumped into the pile, although it passed the slump test, was of a much stickier consistancy than batches previously delivered to site. This resulted in the cage rising during the concrete pour.
| 02SL - Stations (LUL) | Cxxx-NCR-000320 | NCR | Pull-Out Test Failure - Siding Screen Columns |  | Contr |  | FAR - Farringdon Station (West) |  | 2012-02-06 | 2012-01-31 23:06 | -6 | 2012-01-27 | Civil - Civil Engineering General | 500 |  | Material | Rework |  | Complete |  | Completed |  | During the first phase of pull-out testing (19/01/2012), only 6no. tests were done, with one of the bolts failing at 8kN.
| 02SL - Stations (LUL) | Cxxx-NCR-000324 | NCR | Bentonite Support Fluid - Testing |  | Contr |  | FAR - Farringdon Station (West) |  | 2012-01-27 | 2012-01-31 16:26 | 4 | 2012-01-27 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | 1 - The Contractor could not demonstrate that the on-site testing of the support fluid was undertaken by laboratories accredited by UKAS or similar, acceptable national body or by persons accredited to a similar standard. There was no record of the Contractor’s proposal for acceptance of alternative testing standard. 2 - • The Marsh cone viscosity test was undertaken without stirring the sample prior to filling the cone • The person undertaking the tests was unaware of the requirements and method for regular calibration of the mud balance • The person undertaking the tests was unaware of the requirements and method for checking the accuracy of the funnel • The person undertaking the test was unaware why the fluid loss was measured over a 7 minute period and factored up by four times. The above finding demonstrated that the testing person provided by the Contractor is not skilled in the subject of support fluid testing. 3- No record were made available to demonstrate compliance with the above requirement 4 - The contractor was performing a 7 minute test and multiplying the filtrate by a factor of 4.
| 02SL - Stations (LUL) | Cxxx-NCR-000331 | NCR | Male Mix Design |  | Contr |  | FAR - Farringdon Station (West) |  | 2012-02-29 | 2012-03-07 08:11 | 7 | 2012-02-16 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | A) Concrete placed in piles without prior approval. Cowcross Street: 1) Mix Design 20th Sept - Using admixtures CP105 & CSP313 instead of CSP340. (CSP340 is a combination of the 2 admixtures and was unfortunately not availiable in the Kings Cross plant until the 8th November 2011) 2) Mix design difference from 20th and 30th sept is due to the mix needing CP105 (to stay workable for a long enough period of time), but none placed when batching into Pile R901 3) 8th Nov Cprrect admixture used. (CSP340) 4) 16th Dec - The concrete cube results were within specification, but on the lower limit, therefore after discussions with the concrete supplier the material amounts were changed to increase the strength. 5) 17th Jan - Due to a material error, where 2 loads of concrete were rejected for a high slump (260 & 250mm) and the loads that were placed although within tolerance had a 'sticky' workabililty thus causing the cages to rise. The admixture was reduced. 6) 17th Jan - The reduction in admixture was still not enough to stop the 'stickyness', therefore the original material amounts were used. 7) An issue was found, but the source was unable to be determined, therefore trial mixes were carried out with differing materials. Lindsey street; 1) Stepney and Canning Town as per approved mix 2) Kings Cross used CP105 & CSP313 instead of CSP340 3) 8th Nov. Kings Cross used approved mix 4) 16th Dec, same changes as with Cowcross street. B) The issues with the concrete on the 17th Jan caused the pile cages to rise in R946 & C713 and also casued concern with the flow of concrete within the pile.
| 02SL - Stations (LUL) | Cxxx-NCR-000338 | NCR | High level escalator piles installed without guide wall |  | Contr |  | FAR - Farringdon Station (West) |  | 2012-02-20 | 2012-02-28 17:43 | 8 | 2012-02-06 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | 2no female piles E908 and E906 were installed without a guide wall. this was not covered by a method statement. Method Statement Cxxx-LOS-O1-GMS-M123-50067 revision 2.0 states that the secant piles will be installed using a guidewall for initial positioning of casing. Each pile was set out by the survey engineer. The casing position was checked by the survey engineer prior to and during drilling. The casing position was checked along two axes prior to inserting the casing into the ground. Once the casing is 4-5m into the ground, the position was checked once more along two axes. All survey results were recorded by the survey engineer.
| 02SL - Stations (LUL) | Cxxx-NCR-000357 | NCR | W1 cages - slab connection detail |  | Contr |  | FAR - Farringdon Station (West) |  | 2012-11-10 | 2012-11-01 09:24 | -9 | 2012-02-16 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Design | Rework |  | Complete |  | Completed |  | Piles 708-709, 713-715 have been constructed with pile cages that do not include the full 40mm diameter U-bar horizontal slab couplers that will facilitate the construction of the circular shaft level 7 slab, as shown in drawing Cxxx-CWN-D-DDL-M123_Z-96021. Rather, they have been installed as per the detail in the cage drawings issued in FCD 260, 275 & 300 with each U-bar replaced by two separate kinked bars tack welded to the pile cage. Background Cxxx, through the issue of the fabrication drawings attached to FCD 260, 275 & 300, implicitly proposed the change to the Cxxx design due to the fact that if the cages were installed with the full 40mm diameter U-bar horizontal slab couplers, as designed by Cxxx, there would be insufficient space to construct adequate concrete cover between the U-bar steel and the outside edge of the augured male pile. This is due to it being impossible to bend 40mm reinforcing steel bars to match the radius of the helical / circular link steel that the couplers are designed to extend from – thus the 40mm U-bar would protrude beyond the radius of the helical / circular link steel and reduce the concrete cover at the ‘back’ of the pile at that location. This use of two kinked bars tack welded to the pile cage in place of a U-bar and subsequently embedded in the cast pile, as proposed by __ through Cxxx, had previously been approved by CRL and Cxxx for inclusion in the square shaft (SH-W2) pile cages. Therefore, Cxxx had no reason to believe that the proposal would not be acceptable for the circular shaft (SH-W1) As well as those five piles described above (708-709, 713-715) that were constructed with kinked bars tack welded rather than with U-bar couplers an additional, six re-bar cages for piles (705, 710,711,712,716 & 717) were fabricated with kinked bars tack welded rather than with U-bar couplers but not installed in the permanent works. Cxxx proceed with ‘approved’ design The fabrication drawings attached to FCD 260, 275 & 300 were accepted in principle by CRL / Cxxx with the request that full weld details should be provided. It was not made clear that this was a hold point or that there was any reason why fabrication and installation of the pile cages should not continue and it was understood by all parties present at the engineering meeting (barring Cxxx) that this request was simply a follow-up paperwork exercise to ensure that the welds were covered by the __’s CARES certification. Fabrication of the pile cages commenced on 04/01/12. Proof of CARES certification of the welds was provided through the attached letter - dated 21/12/12 - that was presented to CRL / Cxxx by Cxxx at the weekly engineering meeting directly proceeding that date. Cxxx, concerned that the kinked bar embedment alone would be not be sufficient to provide a structural connection, requested further information on the weld detail in order to satisfy themselves that the welds would be sufficiently robust as to provide this structural connection. Again, the significance of this request was not appreciated by all other parties present at the engineering meeting and no hold point to fabrication or installation of the pile cages was introduced. In response a further letter from __, also attached, (dated 24/01/12) was presented by Cxxx at the weekly engineering meeting held on 08/02/12. This detailed __’s opinion that although the tack welds were simply temporary works to hold the bars in position until the cage was installed, the embedment of the bars was sufficient to provide the structural connection necessary. It was noted at this meeting that one cage was already installed (713) and more were following. Cages continued to be installed until 15/02/12 when CRL / Cxxx called a hold to further fabrication and installation of the male cages at the circular shaft (SH-W1) until the issue could be discussed further at the engineering meeting the next day. At this meeting, Cxxx made clear their concerns that the embedment was not sufficient and confirmed later that day that the embedment was indeed not sufficient for the installed 40mm kinked coupler bars. CRL acknowledges that FCD 260, 275 & 300 issuing fabrication drawings for the pile cages to the circular shaft (W1) were accepted in principle by CRL with the comment that full details of welds should be provided by Cxxx. Neither CRL’s response to these FCDs or the subsequently raised PMIs 167 & 168 made it clear that work should not proceed with the fabrication of these pile cages or their inclusion in the permanent works until the weld detail had been provided and had been demonstrated to be structural. Therefore CRL further acknowledges that the non-definitive response to FCDs 260, 275 & 300 and the corresponding ambiguous PMIs may have contributed towards the resultant non-conformance.
| 02SL - Stations (LUL) | Cxxx-NCR-000363 | NCR | ETH cage locations & electrical continuity |  | Contr |  | FAR - Farringdon Station (West) |  | 2012-03-07 | 2012-04-18 10:29 | 42 | 2012-02-22 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | 1. __ did not follow the FCD procedure 2. Electrical continuity installed as per attached sketch. No electrical continuity provided in pile B302, electrical continuity provided in B304 and B204. Reason for change: some cages were installed into different piles to keep up with the programme and avoid delays. The cages were identical to the ones meant for those piles, However one was missing electrical continuity. 3. Due to cage changes, in piles B302 and B304 the foam finishes 150mm above cut off level.
| 02SL - Stations (LUL) | Cxxx-NCR-000380 | NCR | C717 - Coupler missing from a slab connector. |  | Contr |  | FAR - Farringdon Station (West) |  | 2012-11-10 | 2012-10-25 16:19 | -16 | 2012-03-19 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Material | Repair |  | Complete |  | Completed |  | One of the pairs of couplers (including U-Bar) from either the 85.000mOD or the 84.400mOD level is not present in the completed pile. The coupler came off during the tandem lifting of the cage. The Foreman was immediately notified however the pile was at a stage of completion that the cage had to be placed due to time constrants and instability that may be casued as a result of getting a new cage sent to site. __ have been made aware and an extra check is now being made to the slab connections to ensure they can cope with the lifting procedure.
| 02SL - Stations (LUL) | Cxxx-NCR-000381 | NCR | R929 & R930 - Out of Possitional Tollerance |  | Contr |  | FAR - Farringdon Station (West) |  | 2012-03-27 | 2012-05-17 17:16 | 51 | 2012-03-20 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Pile 930 has the centre position at ground level (106mAOD) 117mm into the SH-W2 shaft. It is out of plan position, but still has the required overlap. Pile 929 has the centre position at ground level (106mAOD) 286mm along the SH-W2 wall towards pile 628. It is out of plan position and also may not have the required overlap at the bottom of the primary pile. (See attached drawing) These piles have been installed out of position due to the lack of guide wall scallops in this corner area. There was such a small area of guide wall remaining once R629a was constructed that the lead tube of R930 was placed twice in order to construct the pile in a position as close to the design location as was possible without the assistance of a guide wall. Pile 929 was drilled on a Saturday when the engineer had placed the pin in the scallop on the Friday. The pin must have been knocked and the scallops insufficient as it was only found to be out of position once the full pile had been drilled and the cage placed. (Engineer drawing the line for the coupler orientation, found the line not in the centre of the casing)
| 02SL - Stations (LUL) | Cxxx-NCR-000382 | NCR | Escalator piles blind bore length infill material |  | Contr |  | FAR - Farringdon Station (West) |  | 2012-03-21 | 2012-05-10 13:43 | 50 | 2012-03-14 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Design | Use As-Is |  | Complete |  | Completed |  | Blind bore length of 2no female piles E908 and E906 were infilled with female concrete mix C8/10 instead of self compacting gravel. This is due to safety reasons as the rig will have to track over this area to install the additional scope piles and a concrete infill will have more stability than the gravel. FAR-CRL FCD-Cxxx-00337 was raised after piles have been casted. without a guide wall. this was not covered by a method statement. Method Statement Cxxx-LOS-O1-GMS-M123-50067 revision 2.0 states that the secant piles will be installed using a guidewall for initial positioning of casing.
| 02SL - Stations (LUL) | Cxxx-NCR-000383 | NCR | Incorrect mortar used on heritage brickwork repair |  | Contr |  | FAR - Farringdon Station (West) |  | 2012-03-21 | 2012-03-23 12:43 | 2 | 2012-03-14 | Civil - Civil Engineering General | 500 |  | Design | Rework |  | Complete |  | Completed |  | The brickwork pier was broken back, with the removed bricks being re-used as the new facade bricks. However, the existing brickwork in that area made use of lime mortar joints whereas the replaced brickwork used ordinary mortar.
| 02SL - Stations (LUL) | Cxxx-NCR-000397 | NCR | Pile 919 cage too low |  | Contr |  | FAR - Farringdon Station (West) |  | 2012-04-19 | 2012-06-28 10:00 | 70 | 2012-04-10 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | The finished level of the cage was 359mm low (105.556mOD), resulting the couplers to be between -365mm to -379mm from the design height of the couplers. See attached sketch for exact positions. This was caused due to the hanging chains being removed from the cage when not enough concrete was in the pile to hold the weight of the cage.
| 02SL - Stations (LUL) | Cxxx-NCR-000399 | NCR | No test cubes taken for pile B933 |  | Contr |  | FAR - Farringdon Station (West) |  | 2012-04-25 | 2012-04-23 11:42 | -2 | 2012-04-11 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | No cubes taken for female pile B933
| 02SL - Stations (LUL) | Cxxx-NCR-000405 | NCR | Pile R964 - Casings within pile |  | Contr |  | FAR - Farringdon Station (West) |  | 2012-10-15 | 2012-10-04 18:49 | -11 | 2012-04-19 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Equipment Breakdown | Use As-Is |  | Complete |  | Completed |  | 22.5m of Casing is within Pile R964 as per the attached sketch. This happened becasue the pile needed topping up with bentonite after the first few casings had been removed. As the men where placing the bentonite pipe the pipe knocked the leaver on the Osciallator releasing the clamps holding the casings. The self weight of the casings was too much for the ground to support, therefore they dropped down to the base of the pile.
| 02SL - Stations (LUL) | Cxxx-NCR-000406 | NCR | WTH Crane Platform Ground Slab - Non compliance with accepted TWD |  | Contr |  | FAR - Farringdon Station (West) |  | 2013-05-25 | 2013-04-29 15:17 | -26 | 2012-04-19 | Civil - Civil Engineering General | 500 |  | System Defect | Repair |  | Complete |  | Completed |  | The base slab to the WTH Crane Platform was constructed on 16/04/12 not in accordance with the accepted temporary works design drawings: Cxxx-LOS-C-DDA-M123_Z-TW072(04),Cxxx-LOS-C-DDB-M123_Z-TW073(03) & Cxxx-LOS-C-DDD-M123_Z-TW075 (04). Specifically: the slab length was extended approx 7.0m, a separation detail was included between the slab and the guide-wall, C35/40 concrete was placed rather than C16/20 and the slab was poured up against an unformed guidewall face which may have reduced the slab's effective width. None of the these changes were agreed in advance with CRL, as per the technical requirement.
| 02SL - Stations (LUL) | Cxxx-NCR-000410 | NCR | Farringdon Rd 36" Gas Main - Unreliable readings from 3no strain gauges |  | Contr |  | FAR - Farringdon Station (West) |  | 2012-11-30 | 2012-11-28 08:13 | -2 | 2012-04-20 | Utilities Engineering - Gas | 500 |  | System Defect | Rework |  | Complete |  | Completed |  | 18no strain gauges have been installed, however, readings transmitted to date from 3no of the 18no strain gauges are not as anticpated. This suggests that these 3no strain gauges are either defective or have not been installed correctly, as per the document referenced above.
| 02SL - Stations (LUL) | Cxxx-NCR-000427 | NCR | W1 - sonic logging tubes - blockages |  | Contr |  | FAR - Farringdon Station (West) |  | 2012-05-18 | 2012-06-01 15:09 | 14 | 2012-05-15 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | See attached sketch. (5No piles were tested.) C712 is open for 29m on all tubes. (last 3m blocked) C713 is fully open. C719 has one tube blocked at 3m depth. C724 has one tube blocked at 15m depth. C727 has one tube blocked at 6m depth.
| 02SL - Stations (LUL) | Cxxx-NCR-000428 | NCR | Inclinometer tubes. WTH |  | Contr |  | FAR - Farringdon Station (West) |  | 2012-05-22 | 2012-07-06 13:48 | 45 | 2012-05-15 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Material | Rework |  | Complete |  | Completed |  | Inclinometer tubes in piles R905 & R912 SH-W2 and C714 & C718 SH-W1 are not free the full length of the tube. R905 is free to 21m, R912 is free to 12m, C714 is free to 25m and C718 is free to 5m.
| 02SL - Stations (LUL) | Cxxx-NCR-000433 | NCR | Pile C712 - Electrically continous |  | Contr |  | FAR - Farringdon Station (West) |  | 2012-07-20 | 2012-08-08 08:53 | 19 | 2012-05-15 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Material | Rework |  | Complete |  | Completed |  | Further to FAR-CRL FCD-Cxxx-00378 we were unable to swap the threaded bar from pile C712 to C706. Therefore the cage in C712 does not have a threaded bar.
| 02SL - Stations (LUL) | Cxxx-NCR-000443 | NCR | ETH Geothermal Loops 24hours pressure test |  | Contr |  | FAR - Farringdon Station (West) |  | 2012-05-31 | 2012-06-28 09:19 | 28 | 2012-05-25 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Design | Use As-Is |  | Complete |  | Completed |  | The pressure observed after 24hous dropped in all loops down to 3,7 – 3,8 bar. __ responded as following (see attached Email): The purpose of the pressure test is to ascertain that there are no leaks in the installed loop. A leak would be evidenced by a dramatic decrease in pressure. When the pipe is initially pressure tested this has the effect of “blowing-up” the pipe like a balloon. As the pipe expands (volume increases) the pressure drops. The pressure is topped-up back to its starting pressure periodically and this is repeated for a set period of time or until there is no discernible drop in pressure, at which time the pipe is considered fully expanded. The pressure should then be released quickly to the testing pressure (4 bar) and held. Characteristically, there should be a “bounce” in the pressure as the loop returns to its shape followed by a gradual decay in pressure as the pipe settles. The extent of the bounce and the subsequent decay can be affected by a number of factors. 1. Air in the loop 2. Pipe diameter 3. Pipe length 4. Water temperature 5. Pipe temperature 6. Ambient air temperatures throughout the day and changes in temperature throughout the day 7. Direct sunlight on the pipe 8. How quickly the pressure is built up 9. How quickly the pressure is released 10. The length of time of each constituent part of the test All of these factors are variable and makes it difficult to predict the final pressure in each and every situation on simple short loops. What is predictable though is that if there is a leak then the pressure will drop quite dramatically and quickly. The pressure dropping from 4.0 bar to 3.7-3.8 bar does not indicate a leak, a much lower pressure would be evidenced. It would suggest that either a. There is air in the loop or b. The pipe was not fully expanded on the initial pressure test. Neither of these situations are unacceptable It is reassuring to note that the loops held pressure during the extended pressure test which reaffirms the points made above. The down side of using the extended pressure tests is the programme implications that this will have on following on works.
| 02SL - Stations (LUL) | Cxxx-NCR-000444 | NCR | Excavation level |  | Contr |  | FAR - Farringdon Station (West) |  | 2012-06-01 | 2012-06-28 10:14 | 27 | 2012-05-25 | Civil - Excavation | 500 |  | System Defect | Rework |  | Complete |  | Completed |  | The excavated level of the deeper bay in the W2 shaft was found to be lower, at 101.47mAD, than the design level of 102.1mAD. As a result the layout of the bay was also not in accordance with the design. The level of the high point directly adjacent to the piles was at the correct level of 102.9mAD. The remedial action taken has been to backfill the deeper bay to the design level. By extracting the information on the engineers/surveyors level books the information provided shows that the calculations they made on excavation levels were correct. The Temporary bench marks on site were also checked and they were correct. The site operatives had stated that they dug to the levels they were given. Therefore based on this the findings were inconclusive. However some assumptions can be made. The detail is included in the attachment but can be summarised as. A. The laser level might have been knocked. B The laser level went out of level. C. The site operatives Misunderstood Information they were given D. The site operatives did not use the staff/receiver correctly and over dug the pit.
| 02SL - Stations (LUL) | Cxxx-NCR-000446 | NCR | Level and Orientation of slab connections. W1 |  | Contr |  | FAR - Farringdon Station (West) |  | 2012-06-01 | 2012-06-18 12:40 | 17 | 2012-05-28 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Material | Rework |  | Complete |  | Completed |  | See attached As-Built survey showing piles. At S-3 The upper bar is maximum +84 (NCR00348, pile 714 +118), Lower bar is maximum -294. The cages have crept lower within the concrete. The bars were set at the correct level (Signed off in the Pile packs).
| 02SL - Stations (LUL) | Cxxx-NCR-000447 | NCR | W2 Piles after exposure |  | Contr |  | FAR - Farringdon Station (West) |  | 2012-06-01 | 2012-06-22 11:03 | 21 | 2012-05-30 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Material | Repair |  | Complete |  | Completed |  | Within the W2 shaft between pile 904 the the adjacent females (603 & 604) there is a gap where the concrete has not slumped into the void left by the casing being extracted. Also within W2 some of the female piles have slumped/have soft concrete at the top. 904 has exposed rebar due to the breakdown of the noddle of concrete for the bracket insulation knocked off extra concrete from within the pile. (approx 250mm2)
| 02SL - Stations (LUL) | Cxxx-NCR-000449 | NCR | Non-compliance to SPERW clause 3.5.5 |  | Contr |  | FAR - Farringdon Station (West) |  | 2012-06-14 | 2012-07-18 18:10 | 34 | 2012-05-28 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Equipment Breakdown | Use As-Is |  | Complete |  | Completed |  | During the construction of piles U201 and U202 the duration set in SPERW clause 3.5.5 was exceeded (the email attached has the time durations). The duration exceedances were caused by the bentonite plant breaking down and an operating issue with the piling rig's cleaning bucket respectively. Cxxx were working to method statement Cxxx-LOS-O1-GMS-M123-50066 Rev 4.0 Section 1.6.1.6 - Pile bores are not to be exposed for more then the least period practicable. To achieve this no piles drilled below the base of the casing shall be left open over night unless flooded with Bentonite. The Bentonite loss and settling under the given soil permeability conditions is expected to be insignificant, so that flooding the borehole up to the base os the casing is deemed to be sufficient at any rate without need for further activities during night time. During a workign shift sufficient supervision is provided by the crew's presence on site.
| 02SL - Stations (LUL) | Cxxx-NCR-000450 | NCR | Pile U201 Hydrofracture without accepted ITP |  | Contr |  | FAR - Farringdon Station (West) |  | 2012-06-08 | 2012-07-02 12:29 | 24 | 2012-05-29 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Planning | Use As-Is |  | Complete |  | Completed |  | The Hydrofracturing of pile U201 was done under a conditional Code 2 of the ITP for installation of the bearing piles (attached) Item 61. This item's information referenced the ITP for Base grouting which had not been issued to CRL for initial review at time of Hydrofracture. No checksheet for acknowledging the Hydrofracture of each TAMS system was successful was included in the instalaltion bearing pile ITP either.
| 02SL - Stations (LUL) | Cxxx-NCR-000464 | NCR | Inclinometer R908 W2 |  | Contr |  | FAR - Farringdon Station (West) |  | 2012-06-11 | 2012-06-22 11:01 | 11 | 2012-06-08 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Damaged | Rework |  | Complete |  | Completed |  | Inclinometer tube in Pile R908 is only 25m deep. When we tried to install the inclinometer pipe it did not manage to go full depth. A rig with a continuous flight auger was used to unblock it, but it only managed to get to 25m. I have spoken to the company who did the drilling and they said there was no possibility of going deeper as they exhausted all possibilities when on site Friday.
| 02SL - Stations (LUL) | Cxxx-NCR-000475 | NCR | Drilling through inclinometer in pile 937 SH-W2 |  | Contr |  | FAR - Farringdon Station (West) |  | 2012-06-27 | 2012-06-28 10:20 | 1 | 2012-06-13 | Civil - Geotechnical Engineering | 500 |  | Damaged | Use As-Is |  | Complete |  | Completed |  | In pile number 937 the inclinometer tube had been cast into the pile to the correct depth and was intact. Base readings were taken on the inclinometers and accurate results were being obtained during analysis of the data. During fixing of the brackets for the square shaft wailers on pile 937 the operatives drilled through one of the inclinometers for one anchor on the bracket. The operatives were not briefed which piles the inclinometers were installed. However in addition to this the position of the anchor bolts had changed from what was on the original design so that the anchor could be fixed in a position to miss the rebar installed within the pile as this was significantly more than on the original design drawings. Further readings have been taken and an anomaly now appears on the graphs produced from the data at the exact depth and location where the tube was drilled through. Accurate readings can still be obtained from the inclinometer and it is clearly apparent to the surveyors doing the analysis of the data that the anomaly is due to the location of the hole and therefore can be discarded.
| 02SL - Stations (LUL) | Cxxx-NCR-000480 | NCR | ETH Basegrouting - works commencing without CRL signatures |  | Contr |  | FAR - Farringdon Station (West) |  | 2012-06-25 | 2012-07-09 13:14 | 14 | 2012-06-16 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | The Method Statement Cxxx-LOS-O1-GMS-M123-50092 was revised with addressed comments on 28/05/2012 and new comments were forwarded to __ on 31/05/2012. The commenced grouting works were low risk, yet program critical. In an effort to not to delay the program it was agreed between __ and CRL, that the comments/changes will be addressed in an SNC Cxxx-LOS-01-CCN-M123-50040 Rev.01 and further forwarded for clarification to Cxxx (refer to attached Mail dated on 01/06/2012). Cxxx responded on 06/06/2012 that they have no comments on the SNC proposals and therefore the MS LOS-O1-GMS-M123-50092 Rev.03 can be signed of Code 1. The SNC itself was signed off code 1 by CRL on 12/06/2012 Other relevant documentation like ITP - Cxxx-LOS-O4-STP-M123-50044 Rev.02 was signed Code 1 by CRL on 08/06/2012 and the MCR – Cxxx-LOS-O4-XDS-M123-50104 was signed Code 2 on 07/06/2012. __ would like to bring attention to the following: 1. At that stage on commencing the works, all persons reviewing these documents were aware that the quality of the content for this documentation was understood to be at an acceptable level when works commenced. 2. A signed/dated task briefing was in place for these grouting works was made aware that these works were being carried out. 3. Crossrail was in attendance during the grouting works. All parties were happy that the works were being carried out safely and the results were satisfactory.
| 02SL - Stations (LUL) | Cxxx-NCR-000489 | NCR | Crane platform |  | Contr |  | FAR - Farringdon Station (West) |  | 2012-08-03 | 2012-08-22 12:11 | 19 | 2012-06-21 | Structural Engineering - Structural Engineering - General | 500 |  | Design | Rework |  | Complete |  | Completed |  | Height of platform is approx 500mm low as incorrect levels were used in design.
| 02SL - Stations (LUL) | Cxxx-NCR-000492 | NCR | Continuity of construction ETH Bearing piles |  | Contr |  | FAR - Farringdon Station (West) |  | 2012-07-11 | 2012-08-21 13:27 | 41 | 2012-06-22 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Design | Use As-Is |  | Complete |  | Completed |  | The Method Statements submitted for piling did not specify a realistic time frame for completing the piles. The Local Authority constraints did not allow Cxxx to work outside the hours of 08:00-20:00. The design of the piles was such that completion of a pile within this timeframe would not be possible. This issue should have been raised before piling commenced to gain agreement on any relaxation of the specification. The attached list shows all piles on the WTH and ETH that have exceeded the construction time. As different times were recorded for ETH and WTH, the worst case times have been provided. -On the WTH, the time refers to from when the pile was flooded with bentonite, to when it was concreted. For example, a fully cased pile may be flooded with bentonite at the end of day 1, but the casings not pulled until the start of day 2; or the pile may have been flooded with bentonite if drilling commenced below the casing on day 1, and concreted on day 2. -On the ETH, the time from drilling below the casing to concreting has been recorded by the site supervisor and provided in the attached list. U201 and U202 are covered by NCR 449
| 02SL - Stations (LUL) | Cxxx-NCR-000498 | NCR | Tremie pipe concreted into pile T118 |  | Contr |  | FAR - Farringdon Station (West) |  | 2012-08-31 | 2012-08-28 17:17 | -3 | 2012-06-27 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | This NCR is being raised to cover the following conditions: 1. Losing the tremie in the pile – affecting the integrity of the concrete 2. The client was not informed when the issue occurred 3. This NCR was not raised within 24 hours of the issue occurring There is no NCR necessary for embedment within a dry bore; as our method statement does not specify an embedment for dry bores. The approved Low Level Secant ITP Cxxx-LOS-O4-STP-M123-50038 rev 2.0 (item 39) requires a maximum free fall of 10m, it does not state a minimum fall height. __ now have a better understanding of what happened regarding the tremie details. Since the last revision we have had access to the supervisor’s records (he was currently on annual leave at the time of our last revsion) to confirm the levels we were using. After having a full review of the records we have amended any conflicting details accordingly. Previous revisions had relied on the recollection of the events from the site operatives which were down to interpretation and could be subject to some error of judgement. NCR ITEM 1: 13no 3m sections (39m total) of 10" tremie pipe (steel grade S275, 6mm thick) were stuck in pile T118 (See attached steel certificate for steel information). It is assumed that the tremies were caught on the inclinometer bracket on the inside of the pile cage and the site team were not able to remove it. We assume the cause of the problem to be the inclinometer bracket as this is the first time a bracket like this has been used on the cages and this is the first time we have had an issue with the tremies getting caught. The tremies were concreted into the pile. The position of the tremie pipe is between levels 67.5mOD and 106.5mOD. The tremie was embedded 13.6m (after 3 loads of concrete) into the concrete when the operatives became aware that the pipe was stuck. This is greater than the guideline 3-6m embedment used when concreting a pile. There are no specifications that mention a maximum allowable embedment. Under instructions of __ piling engineer/Project Manager, in dry pile bores the tremie is to be lowered to the toe of the pile and then raised approx 300mm. This was to minimise segregation of the concrete. For the case of T118 the tremie was lowered to a depth of 67.529mOD (1.579m off the toe of the pile). The tremie was attached directly to the crane. The 1.579m gap between the toe of the pile and the bottom of the tremie pipe allowed sufficient concrete flow; this height remained unchanged for the first 3 loads of concrete poured. The tremie did not lift nor did it drop in level when the site team tried to lift the tubes. __ were able to reach down and remove the top section of tremie using the casing poles to pull the tremie wire that connects the two pipes together. The removal of the top tremie in this manner shows that the tremie was being supported from below - if the weight of the tremie was resting on the wire there would be no way of removing it. The remaining tremie was out of reach and was left vertically in the centre of the pile. A second tremie pipe was used to concrete the remainder of the pile. The type of bracket that is believed to have trapped the first tremie was only present on the bottom cage; therefore unlikely the second tremie would get trapped in this way. There was enough space for both tremies in the pile without risking the second one becoming snagged. The cage fabrication drawing specifies a 500mm Ø void within the cage for the tremie, however there is a much bigger a clearance in the top three cages (approx 800mmØ). After each load, the __ Supervisor measured the distance between the top of the casing and the top of the concrete inside the pile AND inside the lost tremie. Since there was no difference in the dips the supervisor did not record a separate dip on the QR6 form. The concrete in the tremie rose at the same rate as the concrete in the pile, the lost tremie can therefore assumed to be full of concrete. There was a time delay between the 3rd and 4th loads of concrete of 1hr 40mins. Peter Able, the __ Materials Expert has confirmed the quality of the pile concrete despite this delay. Please see attached email from Peter Able regarding this. Summary of events: 1. Pile was dry drilled to toe 2. The cage was installed 3. A full pile length of tremie was built and inserted into the pile 4. 3 loads of concrete were pumped into the pile raising the concrete level by 13.6m 5. The operatives then tried to lift the tremie to remove some sections and discovered they could not remove the tremie 6. The __ Supervisor then informed the __ Engineer of the issue 7. A discussion was then held within __ and the only option available was taken – salvage as much tremie as possible and continue to concrete the rest into the pile. 8. The top section of tremie and hopper removed from the pile 9. 24m of a second tremie was lowered into the pile 10. The 2nd string of tremie was inserted in the pile alongside the 1st string keeping them as central as possible. The 2nd tremie was the opposite side of the pile to the inclinometer, so it was not thought that there was a possibility of it getting stuck like the first. 11. The rest of the pile was concreted with the tremie initially 4.379m above the concrete level 12. After the 4th load of concrete was pumped into the pile the tremie was embedded in the concrete once more. 13. The rest of the pile was concreted keeping an embedment of between 3-6m 14. The lost tremie pipe filled up in equilibrium with the concrete level which was measured inside the tremie by the __ supervisor whilst casting. 15. The concrete lines were blown out into the pile 16. CRL field engineer informed of the day’s proceedings 17. NCR raised 4 days later. NCR ITEM 2: The client was not immediately informed of this incident. CRL’s field engineer was notified at the end of the day after the solution to the problem had been found and the pile concreted. The decision to concrete the pile was made by __ management.
| 02SL - Stations (LUL) | Cxxx-NCR-000499 | NCR | WTH W1 Female piles low |  | Contr |  | FAR - Farringdon Station (West) |  | 2012-07-28 | 2012-07-09 13:00 | -19 | 2012-06-28 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Females Cxxx and Cxxx are low by approx 1m as the top section crumbled during excavation. See attached photos
| 02SL - Stations (LUL) | Cxxx-NCR-000500 | NCR | W1 level-4 couplers |  | Contr |  | FAR - Farringdon Station (West) |  | 2012-07-06 | 2012-07-11 17:11 | 5 | 2012-06-29 | Structural Engineering - Reinforcement | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | Survey of the couplers shows that several are out of specification. These are illustrated in the attached sketch. This is consistent with observations from the above level (-3).
| 02SL - Stations (LUL) | Cxxx-NCR-000501 | NCR | Pile T122 left open 85-88 hours |  | Contr |  | FAR - Farringdon Station (West) |  | 2012-07-06 | 2012-08-08 10:23 | 33 | 2012-06-29 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Pile T122 was drilled to depth and flooded with bentonite on 28/6/12, ready to have the cage installed and concreted on 29/6/12. When the reinforcement cage was delivered and checked by the site team, errors were found in the cage which prevented __ from installing the cage into the pile. The cage will be returned to the fabricator for rectifying. It was not possible to fill T122 with a weak mix concrete on Friday 29/6/12 and is not possible to fill it on Sat 30/6/12 due to other site activities. The pile was filled with female mix concrete on Monday 2/7/12. Pile T122 was drilled from the bottom of casing level to the pile toe on 28/6/12 between approximately 19:00 and 20:00. At 20:00 it was flooded with bentonite. It was backfilled with concrete on 02/07/12 between 09:15 and 12:45. It was therefore supported by bentonite for 85-88 hours Levels: Piling mat 109.650mOD Bottom of casing 75.040mOD for drilling, 103.650mOD once flooded with bentonite.
| 02SL - Stations (LUL) | Cxxx-NCR-000502 | NCR | Pull-out tests on the W2-SH shaft |  | Contr |  | FAR - Farringdon Station (West) |  | 2012-07-09 | 2012-07-06 14:17 | -3 | 2012-07-02 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Upon recieving the pull-out test certificates from the sub-contractor, it was noticed that the brackets on the Eastern face and half of the Southern faces of the shaft had not been tested. Please note, all bolts that had been tested held at the designed load (60kN) for the required time (60 seconds).
| 02SL - Stations (LUL) | Cxxx-NCR-000512 | NCR | Geothermal Loop protection over pile trim zone |  | Contr |  | FAR - Farringdon Station (West) |  | 2012-07-17 | 2012-08-21 13:29 | 35 | 2012-07-10 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | The loop protection of pile U201, U202, U204 and U105 was extended 75mm below Cut Off Level but was not extended 75mm above Casting Level. The total length of protection pipe used for pile U201, U202 and U204 was approx. 1,00mtr and for pile U105 approx. 2,00 mtr instead of the required 2,93mtr (COL=104,933 & Casting Level=107,777mtr). During the installation of the preliminary pile U201 which was casted on 18/05/2012 in attendance of __ Engineer __, CRL Engineer __ and __ Supervisor __ it was observed and discussed on site during loop installation, that a loop protection of approximate 1,00mtr will be used (Instructed by __ supervisor) instead of the required 2,93mtr. This non-conformance was further discussed in the meeting held on 21/05/2012 in attendance of Cxxx, CRL, __ and __. The purpose of the meeting was to review the construction of pile U201 and verify the loop installation before continuing on with installation of remaining piles. At that stage it was understood that the reduced protection length is acceptable and further agreed that an FCD will be raised in order to relax the specified length of loop protection. The FCD 00442 was raised on 25/05/2012 and reflected the response of __, who has designed and will take over the ground heat exchanger system to connect it to ground loop collector once the piles have been exposed: "The purpose of the insulation and the plastic tube protection is two-fold a. The protect the pipe during pile break down from casting level to cut off level. b. To afford a measure of de-bonding between the loops and the concrete. Any pipe above the cut off level is purely sacrificial and is there to enable us to test the loops when in situ in the pile, before and after concreting, from the platform level. Whilst the 1000mm of protection is not unacceptable, clearly, the more protection there is to the loops, the less likelihood of damage during the breakdown. Typically the risk to the loop comes not when constructing the Energy Pile but when breaking down the pile cap to the cut off level. We shall explain to the contractor cutting down the piles the measures to be taken to mitigate damage to the loops at that time. If damage occurs to the pipes at or below the cut off level during cut down we can take measures to repair the loop if necessary. If the damage is above the cut off level the priority is to avoid any deleterious material entering the loop."
| 02SL - Stations (LUL) | Cxxx-NCR-000513 | NCR | Damaged cage spacers |  | Contr |  | FAR - Farringdon Station (West) |  | 2012-07-31 | 2012-08-21 13:30 | 21 | 2012-07-10 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Damaged | Use As-Is |  | Complete |  | Completed |  | The skid spacers on the bottom of the reinforcement on cage T151 became distorted, got damaged or dropped of when lifted and stored on the ETH site. In the top, first and second mid cage reinforcement sections of pile there was no damage to the spacers as illustrated on the attached sketch section and plan drawing and photograph. In the bottom reinforcement cage, as illustrated on the attached sketch of the four spacer groups towards the bottom of the pile the following spacers had fallen off: • Two number on the first group toward the bottom • Only one number spacer at each level towards the bottom was missing on the remaining three groups towards the bottom of the pile. The cages were checked on delivery and were in place and intact when off loaded. The cages were placed on timbers that were too small to keep the spacers from getting crushed against the ground. As a result when lifted from the location they were stored the damaged spacers fell off.
| 02SL - Stations (LUL) | Cxxx-NCR-000514 | NCR | Extensometer tube dropped into pile U105 |  | Contr |  | FAR - Farringdon Station (West) |  | 2012-07-31 | 2012-08-21 13:33 | 21 | 2012-07-10 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | In pile U105, one of the extensometer tubes in the final cage section came loose from the cage during installation and fell into the pile to an unknown depth. The extensometer tube that has dropped into the pile is 9.855m long and has an outer diameter of 63.5mm, as per __ fabrication drawing 01017398-R rev 00 (covered by FCD 477). Attached is a data sheet for the extensometer tube (also called sonic tube) showing the steel grade, size and wall thickness. The bracket holding the tube was welded on in such a way that prevented the site team from making a connection with the tube in the cage below. The site team had to manoeuvre the tube to try and get the two matched up. On doing so, the weld then failed on the bracket and the whole tube came loose from the cage and fell into the pile. As a result 1. The extensometer will not be able to be used to measure base uplift 2. The extensometer is at an unknown depth in the pile which may affect the integrity of the pile. However the attached sonic logging test result shows satisfactory profiles, and therefore sound concrete within the pile. It is unlikely that the extensometer tube is positioned in such a way that avoided the paths of each of these tests as it would have had to fall through the slab coupler bars and land completely vertically. __ were contacted immediately following the incident. They issued Cxxx with their own NCR form – see attached. It has been concluded by __ that __’s cage fabrication was of insufficient quality and their cage fabrication checks on the stirrups at their yard were insufficient also. It has also been identified that two different types of connection bars were being used at two different yards. Cxxx site cage checks were carried out in accordance with the approved ITP and reinforcement check sheets but these checks were not extensive enough. It would have been prudent to carry out random impact tests of the stirrups on some of the stirrups of a similar force that would be generated when having to manoeuvre the tubes for connection. A contributing factor also in this NCR is that the site team continued with the pile when the welds were broken and not informing CRL of this before completing the pile.
| 02SL - Stations (LUL) | Cxxx-NCR-000518 | NCR | NE corner works items completed without Code 1 acceptance on ITP |  | Contr |  | FAR - Farringdon Station (West) |  | 2012-07-26 | 2012-08-08 10:25 | 13 | 2012-07-12 | Civil - Civil Engineering General | 500 |  | System Defect | Use As-Is |  | Complete |  | Completed |  | ITP Cxxx-LOS-O4-STP-M123-50033 rev 2 for Piling Enabling Works – North East Corner ETH has been signed code 2, on the understanding that the comments would be actioned and signed off prior to the ITP items being completed. 1. ITP items completed that have not got Code 1 acceptance on the ITP a. Cast the retaining wall reinforcing beam without having an MCR submitted for the cast in plates. b. Installed new Macalloy bar and removed redundant bar c. Cut the waler beam 2. Cast the retaining wall reinforcing beam without issuing Crossrail an IRF 24 hours prior to inspection.
| 02SL - Stations (LUL) | Cxxx-NCR-000520 | NCR | Couplers |  | Contr |  | FAR - Farringdon Station (West) |  | 2012-07-27 | 2012-07-27 08:10 | 0 | 2012-07-16 | Structural Engineering - Steel Member | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | 482 couplers were to be installed in the ring beam around the circumference of the beam at the centres specified above. All 482 couplers were installed. 2no. of the top couplers on the West side of the shaft moved downwards as the concrete was poured. Please see attached photo showing the out of tolerance couplers. __ can only assume that this was due to the tying wire coming loose during the pore. The first section of completed steel was checked by __ and __ of __ & CRL respectively before the first section of shutter was erected. The rebar behind each subsequent shutter section was checked by __ prior to the shutter being erected with 3 no. with CRL in attendance and a final pre-pore check sheet (Ref Circular shaft level - 4 ring beam) was signed by both __ & __ __ & CRL Engineers. __ task briefing sheet currently states that the rebar is to be inspected before the shutters are closed up. __ assume that the tying wire was not tied rigid enough and came loose during the pore. This resulted in a distribution that does not conform to the IFC drawings.
| 02SL - Stations (LUL) | Cxxx-NCR-000521 | NCR | Pile void formers |  | Contr |  | FAR - Farringdon Station (West) |  | 2012-08-10 | 2012-08-16 17:14 | 6 | 2012-07-16 | Structural Engineering - Inserts | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | During pile installation, 5no. of the polystyrene void formers were partially broken off (piles 705, 711, 712, 719 and 721) and were found to lie above the level of the Cast ring beam S1 in between the beams at level S1 & S2. These were supposed to lie in the male piles at the centrally in the depth of each of the coupler locations (i.e. within the cast ring beams). This non conformance is not linked to where the couplers were installed to the incorrect level (see attached sketch) This shows coupler position and plan of void formers out of position. The maximum dimension of all the voids found above he ring beams in the male piles were approx 650x300mm. The depth of all the voids was limited to 90mm off the pile face as this was dictated by the thickness of the void former and the position of the pile reinforcement. Photos and sketch of void locations attached. As the void formers were covered in ply and held in place with steel strapping attached to the cages it is assumed that the void formers which were strapped to the steel cages either caught on something when being lower or bits of the polystyrene broke and became dislodged when the concrete was pored in after the cage was lowered. This may also have occurred due to the tremmie pipe being caught on the polystyrene when extracting the pipe during and after concreting. __ has stated verbally in the engineering meeting that so long as the polystyrene is raked out the void can be left as. __ stated that the void would be raked out and filled __ had no objection to this. The voids were raked out and filled after this meeting. __ are of the opinion that no further action is required.
| 02SL - Stations (LUL) | Cxxx-NCR-000522 | NCR | Finish to underside of beams/slabs |  | Contr |  | FAR - Farringdon Station (West) |  | 2012-09-28 | 2012-09-17 11:46 | -11 | 2012-07-18 | Structural Engineering - Finishes | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | Underside of level -3 beam has spacer blocks showing. This is unavoidable. Marks are also evident where rust from the reinforcement cage has dropped onto the shutter. This has caused staining in some areas. The issue with the spacer blocks showing is likely to be an issue with the remaining beams/slabs in the shaft.
| 02SL - Stations (LUL) | Cxxx-NCR-000523 | NCR | NCR procedure |  | Contr |  | FAR - Farringdon Station (West) |  | 2012-09-19 | 2012-08-21 18:42 | -29 | 2012-07-18 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Operatives carried out remedial works before NCR 521 was moved to implementation stage. A task sheet was issued to break out the void formers to understand the scale of the issue. A hold point was identified on the task sheet however, this was not verbally communicated to the operatives. Consequently, the hold point went unnoticed and the voids were filled with a high strength non-shrink grout before an inspection could be carried out.
| 02SL - Stations (LUL) | Cxxx-NCR-000524 | NCR | Pile T121 out of positional tollerance |  | Contr |  | FAR - Farringdon Station (West) |  | 2012-08-03 | 2012-08-21 13:34 | 18 | 2012-07-18 | Geotechnical Engineering - Concrete - Driven Pile | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | To core E901 the southern portion of the guidewall was removed for that was to be used to construct pile T121. This meant that when T121 was drilled the casing was able to move 56mm to the south of its plan position. This caused the pile to be constructed 31mm out of the allowed tolerance for piles cast through an embedded guidewall. More of the guidewall was removed than originally envisaged due to the increase in diameter of E901 from 1.3m to 1.5m which has been approved which has been agreed in principle as per NCR 527. See attached sketches for clarity: • Surveyed location of cast pile(MSL3930-S-ETH-Setting_Out-RevEU-01) • Eastern Entrance Advanced Works Pile Setting Out sheet 1&2 of 2 (Cxxx-SWN-S-DDA-M123_Z-26011) • Eastern Entrance SH-E3 Pile Setting out cords Sheet schedule (SWN-S-DDA-M123_Z-40112)
| 02SL - Stations (LUL) | Cxxx-NCR-000527 | NCR | Pile E901: Relocation Pile Postion and change of pile diameter |  | Contr |  | FAR - Farringdon Station (West) |  | 2012-08-08 | 2012-08-21 13:59 | 13 | 2012-07-25 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Design | Use As-Is |  | Complete |  | Completed |  | The Female Pile E901 (approx. 11,50mtr length) was constructed on 10/07/2012 with a diameter of 1500mm instead of the designed diameter 1300m. The installation of the pile was necessary in order to construct pile T121 and close the south wall of the SH-E3 Shaft. To close the wall it was necessary prior to start the construction of the temporary concrete support blocks. Drilling the pile with the designed diameter of 1300mm __ would have required to change the drilling tools on the rig from dia. 1500mm to dia. 1300mm and later back to dia. 1500mm which would require about 5 hours and lead to a delay of the piling programme. The execution of the works was commenced without accepted FCD but has been verbally accepted on 06/07/2012 by Cxxx (see attached Email from __). __ has positioned the pile offset to the west as illustrated in attached sketch so that the east outer face of the pile is in line with the position of the designed pile dia. 1300mm as requested by Cxxx.
| 02SL - Stations (LUL) | Cxxx-NCR-000530 | NCR | Base uplift movement monitoring Pile U306 and U307 |  | Contr |  | FAR - Farringdon Station (West) |  | 2012-08-20 | 2012-08-21 13:57 | 1 | 2012-07-30 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | System Defect | Use As-Is |  | Complete |  | Completed |  | During set up of the movement monitoring system on pile U306 and U307 it was not possible to install the retrievable extensometer inside the extensometer or grouting tubes. Therefore __ was not able to measure the base uplift as required according to SPERW. It appears that the tubes got slightly twisted during the extraction of the temporary casing (see attached pictures "Pile U306, U307" and sketch "Deformation Extensometer & Tams Pile U306 & U307) ). Due to the unstable soil condition it was required to use a casing of total 12mtr length (11mtr embedded). Prior to commence the grouting works CRL Engineer __ and Cxxx Representative __ were informed by __ about the circumstance and it was agreed to execute the grouting works without measuring the base movement. Both piles were grouted on Friday, 27th July 2012 in attendance of __ Engineer __ and CRL Engineer __. Two grouting circuits of each pile were charge with the theoretical grout volume and the grout quality on the return pipe was inspected. Since there was a positive grout flow on each circuit the grouting system must have been in good order. Further no observations have been made during hydrofracturing of the base which would indicate any damage of the grouting system. While the pressure and grout volume criteria were achieved, the head of pile U307 moved 0.20mm during the primary grouting stage and the head of pile U306 moved 0.24mm during secondary grouting stage (see attached __ Daily Grouting report).
| 02SL - Stations (LUL) | Cxxx-NCR-000537 | NCR | Pile T115 Sonic Tubes Damaged |  | Contr |  | FAR - Farringdon Station (West) |  | 2012-12-05 | 2013-01-09 13:19 | 35 | 2012-08-02 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | During the installation of cage T115 the sonic tubes were damaged and the pile was concreted. This raises 3 issues: 1. Installation of sonic tubes during the cage fabrication was incorrect 2. Installation of pile cage with damaged sonic tubes 3. 3no. sonic tubes are blocked approximate 1m from bottom of tube, 1 no. sonic tube is blocked approximately 13m from bottom of tube. As a result of this it is not possible to sonic log the full depth of the pile. This occurred because the exhaust clamps that stop the tubes falling out completely were installed incorrectly by the cage supplier in 2nd mid cage section. As per the cage fabrication design the top of sonic tubes installed within the bottom cage section protruded 200mm above top of cage rebar. Usually, the clamps within the Top, 1st & 2nd mid cages are positioned so the sonic tubes descend approximate 750mm out below the bottom of the cage section so they can be joined safely to the tubes in the bottom cage section below. Once the sonic tubes have been joined together, the upper cage sections are lowered down to be joined together with the cage sections below. The sonic tubes in the Top, 1st and 2nd mid cage sections are free to move up and downwards within the cage sections; therefore as the upper cage sections are lowered the sonic stay at the same height and will extend out of the 1st and 2nd mid cage section. The incorrect placement of the clamps within the 2nd mid cage section meant that when this cage section was lowered after joining the sonic tubes, the clamps prevented the sonic tubes sliding freely within the upper cage section. The weight of the 2nd mid cage section caused the sonic tubes to buckle. In an effort not to delay the construction period of the pile, the site team proceeded with the cage installation and concreting operations. Following mitigations as described in NCR 427 “W1 - Sonic logging tubes – blockages” has been undertaken: 1. Longer sonic tubes have been used to decrease the amount of connections. The tube connections between cages have been denzo taped fully as noted on QR1 once completed. 2. The base of tubes was welded shut to avoid any grout/bentonite entering. 3. The tubes have been filled with water and then flushed out the following day. 4. The cap was made out of plastic and denzo taped. The top of tubes did not protrude above the ground level to prevent tube damage/the cap ripping off. Upon further investigation and work all sonic tubes were cleared enough to be able to sonic log the majority of the pile. For tubes 1, 2, 4 the buckled pipes must have not been entirely waterproof so grout got into the pipes and filled the bottom 1m of the tubes up. Tube 3 is blocked at the point where the connection is between the bottom cage (12,860m) and the 2nd middle cage. It was not possible to clear the pipes by flushing with air and water. The sonic test probe wasn’t able to pass this point. Therefore we have to assume that the joint at this point got damaged so that this pipe is filled with grout approximate 13m from the bottom of the tube. The required tube length of pile cage T115 for sonic logging testing should be approx 43.4m. The sonic logging test report 11/D542-14 (see attached) does reflect a satisfactory test result on tube 1,2 & 4 tested over a profile length of approximate 42.1m and tube 3 tested over a profile length of approximate 30.2m. As a result of this we were not able to achieve a profile of the last 13m between tube 1-3, 2-3 and 3-4 but could test tube 1-2, 1-4 and 2-4. __ who is instructed to perform the ultrasonic crosshole integrity assessment on this project stated as follows: “If a defect is found in a pile it is usually a significant problem which may affect the piles capacity or durability, this is most likely to appear on all profiles and both arrival time and attenuation would show deviations. If a flaw is found which is less significant it may be localised to 1 or more tubes but the other tubes may show a deviation in attenuation. With this in mind if you have a few satisfactory profiles along with no problems from piling records or site knowledge ( or previous history of any anomalies) , using sound engineering judgement the conclusion most likely points towards the pile being satisfactory.”
| 02SL - Stations (LUL) | Cxxx-NCR-000538 | NCR | Level -5 pile couplers |  | Contr |  | FAR - Farringdon Station (West) |  | 2012-08-10 | 2012-08-13 08:34 | 3 | 2012-08-02 | Structural Engineering - Reinforcement | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | Similar to NCR 446 and NCR 500, couplers in nine piles are out of specification at this level (-5) also. Details are outlined on the attached survey and coupler summary. As per previous NCR's (446 and 500) on the same issue, __ propose to redrill bars 400mm into the piles and fix with HPE 385 resin. The bar length protruding from the piles will be identical to BM 59 referenced on drawing Cxxx-SWN-S-DDL-M123_6-92550 (e.g. 2m protruding from the pile - 2.4m length bar). See section B on the above drawing for location of BM59. The comparative survey attached shows that similar defects have been encountered in the level of couplers on levels -4 & -3 above as __ have excavated down the pile face and this is likely to continue as further levels are excavated. Further NCR’s will be raised in relation to this as each level is reached after excavation.
| 02SL - Stations (LUL) | Cxxx-NCR-000547 | NCR | Continuity of Construction SH-E3 Pile T113 |  | Contr |  | FAR - Farringdon Station (West) |  | 2012-09-04 | 2012-10-03 16:33 | 29 | 2012-08-09 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Design | Use As-Is |  | Complete |  | Completed |  | Pile T113 was drilled to the bottom of the casing on 06/08/2012 from 3:00pm till 6:00pm. The remaining bore was drilled on the next day morning from 7:30am till 10:00am. During the Inspection of the reinforcement cage, this was supplied by 7:00am on 07/08/2012, it was observed at 8:00am, that this cage arrived without the hanging couplers in the top cage. Without these it was not possible to hang the cage off the casing. CRL was consulted immediately. The cage was rejected of site and returned back on 08/08/2012 at 7:00am. The bore was drilled up only to 1meter above the designed pile toe level and flooded with bentonite from 10:30am till 11:35am followed by the extraction of casing from 12:00pm till 1:00pm. The remaining 1meter to the pile toe was drilled out by use of a cleaning bucket on 08/08/2012 from 7:30am till 8:00am. After testing of the bentonite parameter the installation of the reinforcement cage and lowering of tremie pile was carried out from 8:20am till 11:05am followed by pouring of concrete till 16:50pm. Total time required (see attached) from start to finish the pile installation was 49 hours and 50 minutes, the total time for flooding with bentonite until completion of concreting was 29 hours and 15 minutes. The construction sequence is such that the time periods, during which the pile was excavated below the toe of casing and the concrete placed was 33 hours and 20 minutes. The piling activities overrun the time periods agreed on PTR FCD 460 as follows: Total time pile exposed – 3hrs and 20mins Total Time pile under bentonite – 3hrs and 15mins Total Time for pile installation by 13hrs
| 02SL - Stations (LUL) | Cxxx-NCR-000555 | NCR | Incorrect Fire-Rating of Smithfield Fire Corridor |  | Contr |  | FAR - Farringdon Station (West) |  | 2012-10-19 | 2012-10-24 12:30 | 5 | 2012-08-16 | Fire - Fire Systems & General | 500 |  | System Defect | Rework |  | Complete |  | Completed |  | In the position that the L2 lintels are shown (see drawing Cxxx-SWN-S-DDA-M123_Z-26904), __ have installed 2no. 100x150 R7 lintels back to back, giving 1-hour fire rating. Where the L1 lintels are shown, __ installed a single 225x150mm R7 lintel, giving 30 minutes fire rating. There is a discrepancy between the two drawings mentioned above in that drawing Cxxx-SWN-S-DDA-M123_Z-26904 asks for a Fire Faced Naylor R7 lintel or similar in the notes, yet this only provides 30 minutes of fire-protection whereas the second drawing states that the corridor should be detailed to provide a 2hour fire rating. If spotted at the time of installation, an RFI should have been raised by __ on this issue. However, this was not spotted and Fire Faced Naylor R7 lintels were installed as described on drawing Cxxx-SWN-S-DDA-M123_Z-26904. The corridor has already been signed off and handed over to City of London with a representative signing off a Bring Into Use certificate and a H&S file.
| 02SL - Stations (LUL) | Cxxx-NCR-000562 | NCR | Load testing |  | Contr |  | FAR - Farringdon Station (West) |  | 2012-08-22 | 2012-09-06 12:08 | 15 | 2012-08-22 | Structural Engineering - Testing | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | __ carried out load testing using companies that do not have UKAS accreditation as there is no company in the UK that has this accreditation for on-site load testing. A dispensation was not obtained for this. The companies used, however, do have a construction fixing association (CFA) tester certificate. Load testing has been carried out on the W2 shaft bars, W1 shaft dowels, scaffold anchors and on other temporary works in the ETH e.g. support blocks.
| 02SL - Stations (LUL) | Cxxx-NCR-000564 | NCR | Pile T326 out of positional tolerance |  | Contr |  | FAR - Farringdon Station (West) |  | 2012-09-19 | 2012-09-19 17:14 | 0 | 2012-08-22 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | After concreting female pile T326 it was found that the pile installed was in fact in the position of male pile T126, the adjacent male. T326 was marked out on site by the __ foreman and piling assistant by counting along the guide wall from the previously cast female pile T327. The piles were miscounted, leading to the incorrect placement of T326.
| 02SL - Stations (LUL) | Cxxx-NCR-000565 | NCR | Pile E102, E103, E104 & Expandable Pile out of positional tolerance |  | Contr |  | FAR - Farringdon Station (West) |  | 2012-09-05 | 2012-09-18 16:44 | 13 | 2012-08-22 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | While the __ Supervisor was setting out Pile E901 on 22 August 2012 and checked the position of the pile by __ __ it was observed that the 4no piles E902, E903, E904 and the expendable (dummy) pile which had been constructed on 20/21 August 2012, were in incorrect positions. These 4no piles had been set out by the __ Supervisor by counting the number of piles from the end of the guide wall and spraying the pile to be drilled up to designed female pile toe level. While setting out Pile E901 it was observed that the guide wall was incorrect. The northern end of the guide wall started at pile E902 instead of E101, and the southern end extended beyond the dummy pile by one full pile. The positioning of the guide wall in this way had been discussed and agreed between one of the __ Supervisors and L&A Reinforcement during the guide wall installation. It had not been communicated to the __ Engineers or the __ supervisor, who set out the piles prior to drilling. The __ supervisor who monitored the guide wall installation was not on site during the pile construction. The guide wall had been moved because the shutter clashed with the previously cast SH-E3 guide wall. Instead of breaking out a part of the SH-E3 Guide wall so the escalator pile guide wall would fit it was decided to move the guide wall by one pile. It is not known why the shutter for the southern end of the guide wall was extended by a full pile. A pre-pour inspection check (see attached Report) was carried out by a __ Engineer on 10 August 2012 where quality checks are carried out including: Preparation of Formwork, Reinforcement & Cleanliness of pour. During this inspection it was not observed by the __ Engineer nor mentioned by the __ Supervisor or L&A Reinforcement, that the guide wall has been moved. The setting out of the guide wall was checked by __ __ and an As Built drawing (see attached Guide Wall-E PILES-01 report) submitted to __. This as built drawing shows the actual coordinates of the piles starting at E902 and finishing with the dummy pile. It does not show the extra length of guide wall to the south.
| 02SL - Stations (LUL) | Cxxx-NCR-000574 | NCR | W1 lining wall dowel bars |  | Contr |  | FAR - Farringdon Station (West) |  | 2012-09-28 | 2012-10-01 09:40 | 3 | 2012-08-31 | Structural Engineering - Reinforcement | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | Once the drilling operatives completed drilling each hole to the correct depth (400mm), it was sprayed red. On a CRL inspection (post __ inspection) it was noticed that 3no. holes out of approx 140 inspected between levels -3 and -4) were 350mm deep and needed to be re drilled to get the full 400mm. __ previously inspected approximately 60% of holes in the piles randomly. No requirement for the percentage of the total quantity of holes had been specified in previous documents however, 60% of the total was deemed adequate to assess the works considering the large number of holes. The adequacy was never included in any of the submitted documentation or agreed verbally with CRl prior to inspection. The drill bit was 400mm long and the operatives were previously told to go to the full depth of the drill. The 3no. holes which were sprayed red were not drilled to the full depth as reinforcement was hit at 350mm and the operative thought that this would be ok even though he was instructed that a minimum of 400mm embedment was required. The drilling operatives did not communicate this to the __/CRL engineer at the time of doing either inspection. This was not noticed in the __ inspection as these holes were not selected in the random process. This is an NCR against the works and not a procedural NCR. The bars were marked at 400mm during fixing to ensure that the 400mm requirement was obtained. 3 of the bars would have been fixed to 350mm depth rather than 400mm specified if it were not communicated by the __/CRL engineer to them to drill the 3 holes to 400mm post the CRL inspection and prior to fixing the dowels in these holes. By communicating the NCR to the operatives the non conformance was rectified prior to fixing the bars and therefore there is no defect.
| 02SL - Stations (LUL) | Cxxx-NCR-000575 | NCR | Incorrect Process Followed for Cowcross Street Sub-Station |  | Contr |  | FAR - Farringdon Station (West) |  | 2012-09-13 | 2012-09-13 13:37 | 0 | 2012-08-31 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Prior to the concrete pour for the Cowcross Street substation base, __ carried out an initial inspection. Following this, __ then invited Crossrail to a joint inspection on site, in an attempt to have the pre-pour sheet signed off (as per the ITP - Cxxx-LOS-04-STP-M123-50042). During the inspection, __ stated that they were ready to pour the slab. However, Crossrail noted that 3no. minor sections of mesh reinforcement were missing: firstly, the bottom mesh between the two trenches was not installed. Secondly, only one of the two vertical sections of mesh were installed between the trench and the void formers (as shown on section B-B). Thirdly, the top section of the mesh in the top slab was incomplete (to the East and West of the trenches (also shown on section B-B) In effect, the structure that __ were about to pour was not as per the design. No prior agreement had been made with __ (the designer/end-user) or Crossrail that the steel could be installed differently to the design. __ installed the missing mesh before signing off the pre-pour check sheet and continuing with the pour. Please see attached photos illustrating remedial actions completed prior to the concrete pour. __ have constructed the base to the correct __ design drawing attached. This demonstrates the mesh rebar detail __ have constructed to.
| 02SL - Stations (LUL) | Cxxx-NCR-000584 | NCR | Level -6 pile couplers |  | Contr |  | FAR - Farringdon Station (West) |  | 2012-09-25 | 2012-10-03 17:20 | 8 | 2012-09-13 | Structural Engineering - Steel Member | 500 |  | System Defect | Rework |  | Complete |  | Completed |  | Similar to NCR’s 446, 500 and 538, couplers in nine piles are out of specification at this level (-6) also. Details are outlined on the attached survey and coupler summary. As per previous NCR's on the same issue, __ propose to redrill bars 400mm into the piles and fix with HPE 385 resin. The bar length protruding from the piles will be identical to BM 12 referenced on drawing Cxxx-SWN-S-DDL-M123_7-92650 (e.g. 925mm protruding from the pile – 1.4m length bar). The comparative survey attached shows that similar defects have been encountered in the level of couplers on levels -3, -4 & -5 above as __ have excavated down the pile face and this is likely to continue as further levels are excavated. Further NCR’s will be raised in relation to this as each level is reached after excavation.
| 02SL - Stations (LUL) | Cxxx-NCR-000586 | NCR | Pile T104 construction time exceeded 30 hours |  | Contr |  | FAR - Farringdon Station (West) |  | 2012-10-31 | 2012-10-30 12:47 | -1 | 2012-09-14 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Equipment Breakdown | Use As-Is |  | Complete |  | Completed |  | Whilst drilling T104, the casing clamp became loose and 34.5m of casing dropped into the pile. Please see the attached sketch showing the position of the casings within the pile. The top of the casings were 200mm below the guide wall, and the bottom of the bore is 3.5m below the bottom of the casings. Total bore length is 38.2m. The casings were being held by the casing clamp. The rig driver slewed the rig around and slightly nudged the edge of the top casing. This caused the casings to slip through the clamp and into the pile. It is believed that the presence of muck between the casings and the clamp prevented the clamp from holding onto the casings. The bottom of the pile was filled with female mix concrete to stop the casings dropping further. The following day __ retrieved the casings by excavating 0.5m below piling mat within the guide wall either side of the pile to locating the top of the casing. These casings were then attached to the rig by inserting screws into the casing in the guide wall space and spinning the casings until all of the screws were in. The rig then raised the casings and they were reclamped at the correct level to continue drilling to the required toe depth (43.65m). Pile T104 was then cast on 14/9/12 between 16:00 and 20:00. Since drilling of this pile commenced at 13:00 on 12/9/12, the total construction time is 55 hours.
| 02SL - Stations (LUL) | Cxxx-NCR-000587 | NCR | W1 pile verticality |  | Contr |  | FAR - Farringdon Station (West) |  | 2012-10-31 | 2012-10-24 18:58 | -7 | 2012-09-13 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Survey of piles at current excavation level indicates that 4no. (piles 702, 713, 714 and 727) of the 27no. male piles are out of tolerance (see attached). Pile verticality was checked during installation using a spirit level at ground level. A spinning disc was also used to check casing verticality to 8m below ground level after the first casing is installed. A spirit level is used on each casing thereafter. No measurements from the spinning disk were recorded previously as a tick box system was used. The verticality is likely to have been effected by the variation in the stiffness between the ground and the female piles (as their stiffness changes with time). For example, if the female pile was left for a long period before drilling the male pile, the casing will tend to move to the path of least resistance which in this case appears to have been away from the centre of the shaft. Variations in the ground conditions could also have caused this. No __ equipment was used on the piling rig carrying out these works.
| 02SL - Stations (LUL) | Cxxx-NCR-000588 | NCR | Works carried out without an approved safe system of works |  | Contr |  | FAR - Farringdon Station (West) |  | 2012-10-31 | 2012-10-12 15:36 | -19 | 2012-09-14 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Men were working to recover a string of casings that had slipped below the guide wall. The workmen dug approximately 0.5m down the side of the guide wall to expose the casing attachment holes. Once fully exposed the spinner was placed over the casing and the lugs on each side were attached, the casing was then turned to allow access to the rest of the holes, once fully attached the string of casings were raised to correct height and reclamped. The method statement did not specifically state a safe system of work for digging around the side of the casing. This work commenced without a specific safe system of work in place. The NCR is for the behaviour of the site team carrying on with works without having this in place.
| 02SL - Stations (LUL) | Cxxx-NCR-000592 | NCR | T110 construction time exceeded 30 hours |  | Contr |  | FAR - Farringdon Station (West) |  | 2012-11-09 | 2012-11-13 08:05 | 4 | 2012-09-19 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Material | Rework |  | Complete |  | Completed |  | Pile T110 was not completed within 30 hours due to a defect in the cage. The timeline for T110 construction is below: 18/09/12 07:00 cage for T110 arrived on site, unable to unload it as high level cage being stored at low level and unable to install (see NCR 593) 07:00-15:00 drilled T110 to toe 15:00 cage brought over, bottom section unloaded, checked on site and installed. Unloaded 2nd section and realised the splice band and the keying off band were the wrong way round – the keying off band was actually in the wrong place within the cage. Because of this it would be impossible to install the cage as we would not be able to splice it to the cage above. This cage was sent back to the supplier for rework. 17:00 pile T110 flooded with bentonite 19/09/12 Cage at supplier’s factory being reworked. Delivered back to site 17:30 Pile T110 filled with female mix concrete 20/09/12 09:30-18:00 re-drilling and inserting casings 21/09/12 07:30-09:30 drilled below casing to toe 10:00-12:25 installed cage 12:35-13:15 set up tremie 13:20-18:30 concrete pile Total construction time: 83.5 hours Time exposed below casing: 10 hours on 18/09/12, 11 hours on 21/09/12
| 02SL - Stations (LUL) | Cxxx-NCR-000593 | NCR | Pile T129 construction time exceeded 30 hours |  | Contr |  | FAR - Farringdon Station (West) |  | 2012-11-09 | 2012-11-13 08:08 | 4 | 2012-09-19 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | High level male secant pile T129 was not completed within 30 hours due to a problem with the lifting equipment required to hang the cage off the casing. Timeline for T129 construction: 17/09/12 09:16-17:40 drilled to casing toe 18:00 cage unloaded to low level area 18/09/12 07:15-09-40 drilled to pile toe 13:35 all casings removed 14:00 discovered the hanging bars had been cut too short to hang the cage at its correct height within the pile. Ordered more, earliest delivery available was the following morning 15:20 – 16:20 flooded the pile with bentonite 19/09/12 07:00 hanging bars delivered 07:14- 11:18 cage installation 14:52-15:21 tremie set up 15:20-21:00 concrete pile (slow concrete supply) Total time for construction: 60 hours Time supported by bentonite: 29 hours Time exposed below casing: 8 hours
| 02SL - Stations (LUL) | Cxxx-NCR-000595 | NCR | Pile T130 casings cast into pile |  | Contr |  | FAR - Farringdon Station (West) |  | 2012-12-05 | 2012-11-28 12:22 | -7 | 2012-09-26 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Equipment Breakdown | Use As-Is |  | Complete |  | Completed |  | In the high level secant male pile T130 19m of casing slipped through the oscillator and dropped into the pile. The method used to remove casings from the pile is as follows: - casings within the pile are clamped in the oscillator - rig connected to casing - unclamp oscillator - lift casings using rig - jetwash bolts holding casings together to undo - undo 8no bolts, leaving 2no in (easier to take out bolts without the casings being clamped as the oscillator squashes the casing slightly out of shape) - reclamp oscillator - remove remaining 2no bolts - rig lifts upper casing off the pile Part of the oscillator operation is the use of timber blocks to make it level. These are detailed in the manufacturer’s instructions. When the casing was lifted off it was noticed that the oscillator was not level as the timber blocks had fallen out, however it had a grip on the casings in the pile. The oscillator was then adjusted to raise it in order to replace the timber blocks. The oscillator was then lowered down, at which point it levelled up and lost its grip on the casings. The casings dropped into the pile and stopped with the top of the casing 26m below the guide wall. It is not possible to remove these casings safely. Immediately following the incident, 8m of casing was installed into the top of the pile to provide edge protection and the pile was flooded with bentonite. Prior to adjusting the oscillator, either the rig should have been connected to the casings or the secondary clamp used. This secondary clamp was not used at the time as the operatives believed it was faulty and had not been fixed. This secondary clamp had not been working, a fitter visited the day before and fixed it but did not inform anyone on site that it had been fixed and did not get anyone to sign his paperwork. Both timber blocks had never fallen out of the oscillator before – this is not a common occurrence. When this happened the site team should have seen this as an unplanned situation – they should have stopped to think about the task and contacted the supervisor before carrying on. The pile was completed as per the timeline below. Location in pile Please see the attached sketch showing the location of the casings within the pile and the strata details. Timeline: Date Activity Time 25/09/12 Start drilling 08:00 Finish drilling to casing toe 16:30 Pile left overnight fully cased 26/09/12 Finish drilling to pile toe 08:30 Start extracting casings 09:00 23m casing extracted, 19m casing dropped into pile. Works stopped to investigate 10:10 8m casing inserted into pile 12:00 Pile flooded with bentonite 13:00 27/09/12 Clean base then air lift 14:00 28/09/12 Drill last 0.5m & test bentonite (passed so no air lift) Install cage 14:00 Concrete pile 19:20-23:30 Remove 8m casing from top of pile 00:00 Casing details Lengths of casings left in pile (from top down): 3x4m, 1x2m, 1x3m, 1x2m lead See attached casing catalogue for casing details Grade and thickness of the steel: the casing joints are made of quenched steel 25CrMo4 with 900-1050 N/mm² yield strength, the double wall casing bodies are made of steel S355 with 550 N/mm² yield strength. Attachments Pile pack for T130 Sketch showing location of casings and strata Casing details
| 02SL - Stations (LUL) | Cxxx-NCR-000597 | NCR | Top of concrete level |  | Contr |  | FAR - Farringdon Station (West) |  | 2012-11-06 | 2012-10-31 15:23 | -6 | 2012-09-29 | Structural Engineering - Structural Engineering - General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Survey of level -5 ring slab indicates that the top of concrete is lower than the design level of 92.35mAD in places, with a worst case of -10mm. This is outside the requirements of the specification although it would appear that the slab has deflected since the excavation beneath it commenced. Surveyed levels after casting (MSL3930-S-WTH-L-5_As Built L-5-01) and after excavation (MSL3930-S-WTH-L-5_As Built L-5-120925) are attached. While concrete levels next to the outer shutters is within specification, the shutter for the upstand kicker appears to have been low in places. This upstand consists of an aluminium radius channel with a timber radius panel fixed to its base to form the kicker illustrated in drawing Cxxx-SWN-S-DDD-M123_Z-00210. The kicker piece was hung from timbers that we fixed between the piles and the shutter. The concrete level was found to be low despite clear levels being marked on timber boards which were fixed to the piles and a further check on the kicker following its installation. The check on the kicker involved obtaining the level of the aluminium channel and subtracting from this, the thickness of the aluminium and timber radius pieces, to get the top of concrete levels. This made no allowance for general construction tolerances such as additional space between the aluminium and timber pieces and warping of the timber in wet weather. Movement of the formwork as operatives walked on it during the pouring process may also have contributed to this. A tape measure was also used to manually check the height from blinding to the underside of the timber shutter and cover prior to pouring. These were all deemed to be satisfactory by the engineer and during inspections with CRL although this would have been difficult to identify using tape. In hindsight, the level of the aluminium channel should have been set 5mm higher.
| 02SL - Stations (LUL) | Cxxx-NCR-000598 | NCR | Settlement of secondary reference points - ETH |  | Contr |  | FAR - Farringdon Station (West) |  | 2012-11-22 | 2012-11-21 13:57 | -1 | 2012-09-29 | Surveying - Instrumentation and Monitoring | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | During the check of Secondary Control (secondary reference points) it was observed that these secondary reference points had a difference in height to the initial measurement. The Secondary Control for levelling is located at the lower level of the ETH, for the 3D on the pavement and on the buildings around the ETH site. The Secondary Control for levelling within the site (for __ measurements on the LU wall) was installed on the 22/03/2012 using Primary Control points installed by CRL. The check with Primary Control was carried out on the 08/08/2012. Previously the Secondary Control has been checked internally only and not using Primary Control. Since the 08/08/2012 6 additional checks of Secondary Control back to Primary Control have been carried out. The Secondary Control points for 3d measurements at ETH were installed in June 2011. The check of the Secondary Control using Primary Control was carried out in May 2012 and September 2012. These check intervals are not in accordance with the Specification for Control of Ground Movements. For the future all Secondary Control for levelling and 3D will be checked weekly with comparison of the Primary Control according the requirements of the Specification for Control of Ground Movement. Further details about the checks carried and the result implemented are included in the report, which was submitted on EB for acceptance.
| 02SL - Stations (LUL) | Cxxx-NCR-000607 | NCR | W1 level -7 couplers |  | Contr |  | FAR - Farringdon Station (West) |  | 2012-11-06 | 2012-11-09 16:29 | 3 | 2012-10-08 | Structural Engineering - Inserts | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | Similar to NCR's 446 and 500, couplers in the piles are out of specification. Details are outlined on the attached survey and coupler summary.
| 02SL - Stations (LUL) | Cxxx-NCR-000608 | NCR | pre-installation condition survey |  | Contr |  | FAR - Farringdon Station (West) |  | 2012-12-05 | 2013-01-11 11:40 | 37 | 2012-10-12 | Surveying - Instrumentation and Monitoring | 500 |  | Planning | Use As-Is |  | Complete |  | Completed |  | No written or photographic condition survey has been carried out prior the installation of equipment. The requirement was overseen and there the photographs of each monitoring point have been taken just once after completion of the installation.
| 02SL - Stations (LUL) | Cxxx-NCR-000609 | NCR | logging of piezometer boreholes |  | Contr |  | FAR - Farringdon Station (West) |  | 2012-11-05 | 2012-11-08 19:10 | 3 | 2012-10-12 | Surveying - Instrumentation and Monitoring | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Borehole logging in conformity with BS 5930 has been carried out for the borehole in circular shaft only due to a misinterpretation of the specification. It was assumed by us that the bore hole logging of all piezometers would be not required as an extensive ground investigation programme has been completed by __ on behalf of Crossrail at WTH last year in addition to the originally completed ground investigation providing good understanding of strata.
| 02SL - Stations (LUL) | Cxxx-NCR-000612 | NCR | No cubes made for Crane Platform base |  | Contr |  | FAR - Farringdon Station (West) |  | 2012-10-31 | 2012-10-24 12:36 | -7 | 2012-10-11 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | The concrete was poured on the 16/04/12. A pre-pour sheet was signed off by John Train and __. The concrete poured was C35/40, as per the revised Form C and associated design check certificate (please see document Cxxx-LOS-C-CER-M123-50116). The target strength of the concrete is 35N/mm2 (cylinder strength) or 40N/mm2 (cube strength) after 28 days. Upon reviewing the deliverably quality records for the Crane Platform (Cxxx-LOS-O4-RGN-M123-50111), __ and Crossrail noted that no cube samples were taken during the crane platform base slab pour.
| 02SL - Stations (LUL) | Cxxx-NCR-000632 | NCR | Plunge column concrete biscuit levels incorrect |  | Contr |  | FAR - Farringdon Station (West) |  | 2012-12-05 | 2012-12-20 17:38 | 15 | 2012-11-12 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | All five biscuits in plunge column P103 are 1m too low due to a calculation error when working out the levels. Please see attached sketch showing the as built levels of the biscuits. None of the new biscuit levels falls closer than 1.6 meters to any of the shear stud levels.
| 02SL - Stations (LUL) | Cxxx-NCR-000634 | NCR | Ground Movements during piling works exceeded 5mm |  | Contr |  | FAR - Farringdon Station (West) |  | 2013-02-11 | 2013-03-22 19:33 | 39 | 2012-11-21 | Civil - Geotechnical Engineering | 500 |  | System Defect | Use As-Is |  | Complete |  | Completed |  | Refer to the attached charts extracted from Cxxx I&M Weekly Report 61 (Cxxx-LOS-B-RGN-M123-50061 Rev.1) showing ground movements around the ETH site. At a number of locations around the ETH site the amount of settlement observed during the Cxxx piling works has exceeded the 5mm allowed by clause KP10.3214 of the Civil and Structural Specification. These locations include, but are not limited to 1) London Underground tracks and retaining wall to the North of the ETH site (up to 10mm Settlement). 2) Hayne St to the East of the ETH site (up to 10mm settlement). 3) Long lane North to the South of the ETH site (up to approx. 8mm settlement). 4) Lindsey St East to the West of the ETH site (up to approx. 8mm settlement).
| 02SL - Stations (LUL) | Cxxx-NCR-000639 | NCR | Pile interlock in W2 shaft |  | Contr |  | FAR - Farringdon Station (West) |  | 2013-02-15 | 2013-01-31 17:45 | -15 | 2012-11-29 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | Excavation of the W2 shaft and exposure of the piles indicates that full interlock has not been obtained between male pile 952 and the two adjacent female piles. The discontinuity approximately 70mm wide, 4m in length and extends from 99-103mAD. This is non-conformance is likely to have arisen as the casings were not fully removed prior to the concrete setting in the pile. Following removal of the casing, the annulus between the hardened concrete and the female pile was then filled with bentonite.
| 02SL - Stations (LUL) | Cxxx-NCR-000640 | NCR | W2 level -3 coupler |  | Contr |  | FAR - Farringdon Station (West) |  | 2013-02-15 | 2013-02-04 17:54 | -11 | 2012-11-29 | Structural Engineering - Reinforcement | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | Visual inspection of the couplers in the W2 shaft indicates that the level -3 couplers are out of positional tolerance. Details of as-built coupler locations can be found on the attached summary. They confirm our fears that some of the couplers are low.
| 02SL - Stations (LUL) | Cxxx-NCR-000641 | NCR | Plunge Columns out of tolerance |  | Contr |  | FAR - Farringdon Station (West) |  | 2012-12-21 | 2013-01-09 14:04 | 19 | 2012-12-03 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Design | Use As-Is |  | Complete |  | Completed |  | See attached marked up drawing. Plunge columns P101-103 out of tolerance by 4mm, 6mm and 10mm. The fabrication tolerance in NSSS 5th edition section 7.4 allows the column itself to be manufactured to plan dimensions as per the attached sketch. This meant the guide frame had to be a certain amount larger than the column to allow for these tolerances. With the guide frame positioned in the correct place, the column would be allowed to move up to 29mm in one direction, and 18mm in the other direction within the frame, making the +/-10mm positional tolerance unachievable.
| 02SL - Stations (LUL) | Cxxx-NCR-000642 | NCR | Inclinometer tubes blocked in piles T135 and B112 |  | Contr |  | FAR - Farringdon Station (West) |  | 2012-12-21 | 2013-01-09 13:13 | 19 | 2012-12-03 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | T135 Blocked at approx. 45m. Inclinometer ends approximately 6.5m below the final excavation level (78.25). B112 Blocked at approx. 7m. Inclinometer ends approximately 4m above the final excavation level (105.4). The inclinometer is located at the corner, so that only marginal movement of wall is expected. Installation of in-soil inclinometers along Long Lane will be hardly possible as the vaults have been filled with concrete, which is positive as it provides an additional reduction of possible movements. It is assumed that the inclinometer tubes were blocked by grout ingress during pile installation.
| 02SL - Stations (LUL) | Cxxx-NCR-000643 | NCR | Blocked inclinometers in SH-E3 |  | Contr |  | FAR - Farringdon Station (West) |  | 2012-12-07 | 2013-01-09 13:15 | 33 | 2012-12-04 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Inclinometer pipes blocked/damaged during pile installation in piles T110, 113, 124, 140, 145, 152. Additional inclinometer tubes were added to piles as per FCD-Cxxx-00459/ 00479/ 00483. Inclinometers were installed into additional piles T104 111, 114, 125, 138, 144, 153 The blocked or damaged tubes were grouted up to fill the voids. See attached red line drawing showing locations of inclinometers and grouted up tubes
| 02SL - Stations (LUL) | Cxxx-NCR-000644 | NCR | Pile T154 poor sonic logging results |  | Contr |  | FAR - Farringdon Station (West) |  | 2013-01-31 | 2013-03-14 17:41 | 42 | 2012-12-05 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | See attached sonic logging report for pile T154, it shows a flaw/defect at depths of approximately 28m, 33m from ground level and at the base of the pile. Looking at the QR6 pile concreting log for pile T154 it can be seen that the flaws have occurred where there was approximately an hour‘s wait for concrete. We can assume that this longer than usual wait means that there are cold joints in the pile at 28m and 33m from ground level. These cold joints are the most likely cause of the flaws in the sonic logging data. The factual data at the base of the pile is showing a complete loss of energy and arrival time which means the ultra sonic pulse passing between the tubes at this elevation is passing through material which is completely different to the rest of the pile. This is usually attributed to an uneven base. The concrete test cubes taken for this pile came back with a mean 28 day strength of 61N/mm2 - well above the design strength of 45N/mm2. The bentonite tests show that the bentonite was within the specified limits. The QR2 Pile Record has the box ticked for ‘Base Cleaned’.
| 02SL - Stations (LUL) | Cxxx-NCR-000645 | NCR | W2-SH: Waler - Bracket connection washers too small |  | Contr |  | FAR - Farringdon Station (West) |  | 2012-12-14 | 2012-12-21 13:12 | 7 | 2012-12-05 | Civil - Civil Engineering General | 500 |  | Material | Rework |  | Complete |  | Completed |  | Plate washers at the connection between the S2 brackets and walers were found to be 2mm thick (45mm circumference with a 28mm hole).
| 02SL - Stations (LUL) | Cxxx-NCR-000647 | NCR | W2-SH: Incorrect Length of Diagonal Truss Plates (S1-S2) |  | Contr |  | FAR - Farringdon Station (West) |  | 2012-12-21 | 2012-12-21 13:15 | 0 | 2012-12-11 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | One of the diagonal truss members located between S1 and S2 steelwork is 20mm too long to attach to the existing connection details.
| 02SL - Stations (LUL) | Cxxx-NCR-000648 | NCR | W2-SH: S2 Bracket Installed Out of Tolerance |  | Contr |  | FAR - Farringdon Station (West) |  | 2012-12-21 | 2012-12-20 11:46 | -1 | 2012-12-11 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The bracket on Pile R915 has been set around 70mm further towards the centre of the shaft than other brackets at the S1 and S2 levels. This was down to a combination of a bulge in the pile and human error; the bulge in the pile was most likely due to an area of weak ground during the piling works, the concrete flowing into this area and leaving a 70mm 'bulge' on the pile face. The surveyor then set a level on pile R915, but did not perform a check which would have identified the bulge. Instead, the pile was drilled and the bolts were resined into place at the correct embedment. Upon hanging the bracket, the surveyor realised that it would be sat around 70mm too far into the shaft. However, as the bars were already resined into position, it would not have been possible to achieve the correct bolt embendment depth should the face of the pile now be broken back.
| 02SL - Stations (LUL) | Cxxx-NCR-000649 | NCR | Pile T137 Blocked Sonic Tube |  | Contr |  | FAR - Farringdon Station (West) |  | 2013-01-31 | 2012-12-20 17:34 | -42 | 2012-12-11 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | See attached sonic logging report for Pile T137 – there is one sonic tube which is blocked for the bottom 25m of the pile. Also see attached marked up drawing showing the location of the blocked tube within the pile. The blockage is on the east side of the pile – i.e. the outside of the shaft. It is likely that the tube has been blocked by grout ingress during the pile concreting process. The concrete test cubes from pile T137 have been tested and have a mean 28 day strength of 57.75N/mm2, above the design strength of 45N/mm2. looking at the pile pack for T137 (also attached) it can be seen from the QR6 pile concreting log that the concrete slump tests were all within the specified limits, and all concrete was placed in a timely manner. The graph shows a good profile with a slightly wider base. The pile was completed under bentonite and the bentonite test record shows that it complied with the specified limits.
| 02SL - Stations (LUL) | Cxxx-NCR-000650 | NCR | Inclinometer too short in pile B120 |  | Contr |  | FAR - Farringdon Station (West) |  | 2013-05-31 | 2013-05-24 12:44 | -7 | 2012-12-13 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | Inclinometer was installed to only 17.9m from piling platform level instead of the full length of the pile of 29.65m. This was discovered only when the commisioning readings came through from the inclinometer. it is assumed that the bottom of the inclinometer casing is blocked by grout ingress.
| 02SL - Stations (LUL) | Cxxx-NCR-000652 | NCR | W2-SH: Bolts between bracket and whaler below required torque |  | Contr |  | FAR - Farringdon Station (West) |  | 2012-12-21 | 2012-12-20 12:18 | -1 | 2012-12-14 | Civil - Civil Engineering General | 500 |  | System Defect | Rework |  | Complete |  | Completed |  | 2 bolts connecting bracket and whaler (toward the piles) at Pile R926 were found to be of torque less than 160Nm. This was down to the __ Engineer (NCR initiator) checking the bolts and then permitting Crossrail to check this bracket to whaler connection before __ had formally handed it over to __. As the __ Engineer had previously checked the bolt torque as adequate only a few hours earlier, the most likely reason could be because __ were still undertaking splice plate bolt tightening immediately next to this bracket, relieving tension in the bolts. Thus, the check was conducted on an item which was formally classed as Works In Progress.
| 02SL - Stations (LUL) | Cxxx-NCR-000653 | NCR | W2-SH: Short threads on bolts between piles and brackets |  | Contr |  | FAR - Farringdon Station (West) |  | 2012-12-21 | 2012-12-21 13:21 | 0 | 2012-12-18 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | 8no. bolts on Level S2 connecting the brackets to the piles were identified with no thread visible from the nut. These were on brackets attached to Pile R946, R956 & R928. More specifically, 6no. of these bolts were flush with the nut and 2no. were recessed by one thread. The occurred because the bracket was brought too far forward when being lined and levelled (30mm further forward) and to exacerbate the holes may have been drilled marginally deeper than the required 480mm embedment. This meant there was not enough clearance for one thread beyond the bolts when our subcontractors fitted the brackets.
| 02SL - Stations (LUL) | Cxxx-NCR-000654 | NCR | W2-SH: Some underside washers too small |  | Contr |  | FAR - Farringdon Station (West) |  | 2012-12-21 | 2013-01-02 08:33 | 12 | 2012-12-20 | Civil - Civil Engineering General | 500 |  | System Defect | Rework |  | Complete |  | Completed |  | 2no. washers between the underside waler-bracket connections at Pile R914 were found to be of the old type 2mm thick with 45mm OD, and not the revised 6mm type with 72mm OD. This occurred because the __ Engineer (initiator) checked all of the upperside washers including those at bracket Pile R914, but not all the underside washers at every bracket.
| 02SL - Stations (LUL) | Cxxx-NCR-000655 | NCR | Incorrect Coupler Levels at Slab -4 Level |  | Contr |  | FAR - Farringdon Station (West) |  | 2013-02-15 | 2013-02-27 15:44 | 12 | 2013-01-03 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | Please see attached as-built drawings of the couplers currently exposed following Phase 3A excavation. A further as-built will be attached when Phase 3B is completed.
| 02SL - Stations (LUL) | Cxxx-NCR-000656 | NCR | Loose bolts on S3 waler connection |  | Contr |  | FAR - Farringdon Station (West) |  | 2013-02-01 | 2013-01-28 13:49 | -4 | 2013-01-14 | Civil - Structural Engineering | 500 |  | System Defect | Rework |  | Complete |  | Completed |  | In accordance with the above referenced ITP, a joint witness point inspection was undertaken between CRL and __ for the bolt tightness of waler splice connections in the S3 props within the WTH SH-W2. After completing their own internal checks on Watson's installation work, __ invited CRL for inspection of the waler connections. However, CRL's random sample of bolt tightness checks found two bolts on the top splice plate of the waler connection between piles R919 and R917 to be finger tight only and not at the required torque value of 160Nm as defined in the ITP. This NCR therefore represents a failure in Cxxx's self certification system for quality and has accordingly been raised by CRL.
| 02SL - Stations (LUL) | Cxxx-NCR-000657 | NCR | S3 Waler-Bracket Connection Plate Incorrectly Fabricated (W2-SH) |  | Contr |  | FAR - Farringdon Station (West) |  | 2013-01-31 | 2013-01-30 17:12 | -1 | 2013-01-21 | Civil - Civil Engineering General | 500 |  | Material | Repair |  | Complete |  | Completed |  | The waler-bracket connection plate should line up precisely with the bracket attached to the pile. However, the bracket fixed to Pile R952 and the waler-bracket connection plate attached to the S3 waler do not line up. Please see attached photos.
| 02SL - Stations (LUL) | Cxxx-NCR-000658 | NCR | Drawings not issued to CRL prior to steel installation (W2-SH) |  | Contr |  | FAR - Farringdon Station (West) |  | 2013-02-28 | 2013-02-25 12:31 | -3 | 2013-01-21 | Civil - Civil Engineering General | 500 |  | System Defect | Use As-Is |  | Complete |  | Completed |  | Although __ and __ had an approved 3D model and the relevant drawings approved informally via emails, __ did not issue an up to date drawing register or pack of approved installation drawings to Crossrail prior to the installation of levels S1 and S2 in the W2-SH. __ use the A-Site document control system to comment on/approve/reject __ drawings. However, the permissions and notification elements were not functioning correctly during the on-site installation of S1 and S2.
| 02SL - Stations (LUL) | Cxxx-NCR-000659 | NCR | W2-SH: Insufficient cubes for strength testing in Phase S2a |  | Contr |  | FAR - Farringdon Station (West) |  | 2013-02-06 | 2013-01-28 13:51 | -9 | 2013-01-23 | Civil - Civil Engineering General | 500 |  | Planning | Use As-Is |  | Complete |  | Completed |  | Insufficient grout cubes were made for compressive crushing to provide confirmation of 40N/mm2 required strength. Sufficient cubes should have been made to cover a minimum period until the compressive strength has been reached, based on an engineering judgement of the early strength gains achieved previously in the cold weather. The cubes had to be tested in short periods to meet or better the programme requirements. These samples were from 3 separate grout pouring sessions undertaken on the 29th (1no.) and 30th November 2012 (2no.) for bracket grouting at piles R956 to R921 clockwise, i.e. Phase 2a (15 brackets in total, see plan attached). __ created 4no. grout cubes per pour (12 in total for the 3 sets in question) as per ITP item 29. See below for results achieved: Grout cube set 1 (Pour 1): 8.9 and 14.1N/mm2 @2days, 21.5 and 24.2N/mm2 @3days Grout cube set 2 (Pour 2): 25.0 and 28.9N/mm2 @2days, 34.7 and 36.0N/mm2 @3days Grout cube set 3 (Pour 3): 21.1 and 30.0N/mm2 @3days, 37.9 and 39.6N/mm2 @4days Testing all 4 cube samples left none for the 7 day or 28 day result. Typically >40N/mm2 is achieved within 3 days but due to winter conditions the duration for typical strength gain development was longer than normal, despite following the manufacturer specification for lower temperature working (i.e. using warmer water). Phase 2b brackets were grouted on the 9-11th December 2012 which all achieved the required strength of 40N/mm2, see below: Grout cube set 4 (Pour 4): 46.5N/mm2 @6days; 53.2, 55.1 and 54.0N/mm2 @8days Grout cube set 5 (Pour 5): 21.2N/mm2 @2days, 33.3N/mm2 @3days, 39.1 and 40.0N/mm2 @5days Grout cube set 6 (Pour 6): 31.1N/mm2 @2days; 44.0, 43.5 and 42.3N/mm2 @4 days Grout cube set 7 (Pour 7): 28.0N/mm2 @2days; 44.1, 43.4 and 42.7N/mm2 @3 days These grouting sessions were completed using the same technique as in Phase 2a, with similar site temperatures (2oC) and so __ projected the grout cube strength (see proposed answer below).
| 02SL - Stations (LUL) | Cxxx-NCR-000662 | NCR | W2-SH Slab level -5 Coupler Positions |  | Contr |  | FAR - Farringdon Station (West) |  | 2013-04-05 | 2013-04-03 10:57 | -2 | 2013-02-11 | Civil - Civil Engineering General | 500 |  | System Defect | Repair |  | Complete |  | Completed |  | Please see attached as-built drawings of the couplers currently exposed following Phase 4 excavation. 22no. piles have couplers out of tolerance in terms of level and 12no. piles in terms of rotation. (Please note that some piles have couplers which are out of tolerance in both height and rotation).
| 02SL - Stations (LUL) | Cxxx-NCR-000664 | NCR | W2-SH: Pile verticality out of tolerance |  | Contr |  | FAR - Farringdon Station (West) |  | 2013-04-05 | 2013-04-26 12:41 | 21 | 2013-02-14 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | At least 8 piles within the W2-SH are out of the 1:200 required tolerance. Those which have an affect on the steel installation are: R914, R915, R917, R923, R924, R929, R937 and R955 (see below for their surveyed orientations). R914 (9.0mm/m, 1:111) R915 (12.5mm/m, 1:80) R917 (14.3mm/m, 1:70) R923 (15.2mm/m, 1:66) R924 (10.2mm/m, 1:98) R929 (8.8mm/m, 1:114) R937 (9.0mm/m, 1:111) R955 (8.8mm/m,1:114) This occurred because of supervisor error as the pile logs were completed showing verticality within tolerance. Therefore the supervisor failed to ensure the spinning disc verticality checks as per MS were being carried out or done correctly. As this is a human error related NCR, in future all rigs should be fitted with a verticality system so the driver can monitor during the dig. These can be printed off and inspected by the engineers and managers to double check that the site team are working within the correct tolerances.
| 02SL - Stations (LUL) | Cxxx-NCR-000665 | NCR | Clash of S4 vertical hangers with TBM envelope |  | Contr |  | FAR - Farringdon Station (West) |  | 2013-04-09 | 2013-04-03 11:01 | -6 | 2013-02-19 | Civil - Structural Engineering | 500 |  | Design | Rework |  | Complete |  | Completed |  | 1. During the Cxxx Contractor's review of their sub-contractor’s detailed design for the SH-W2 S4 props, it was established that the vertical connection below the stiffener plates along GL2 would clash with the TBM envelope shown in Cxxx drawing Cxxx-SWN-S-DDL-M123_Z-76906. This is a non-conforming design. 2. The Cxxx Contractor then proceeded to install the S4 props along GL 2, with the clashing vertical hanger sections still in place. Therefore the current installation does not meet the requirements of the Works Information with regards to the TBM aperture that must be maintained. Accordingly, the current site installation is non-compliant and requires re-working. This is a Defect.
| 02SL - Stations (LUL) | Cxxx-NCR-000666 | NCR | Incorrect documentation in place prior to SH-W2 S4 bolt tightness inspections |  | Contr |  | FAR - Farringdon Station (West) |  | 2013-03-20 | 2013-03-11 11:57 | -9 | 2013-02-20 | Civil - Structural Engineering | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | This is a procedural NCR. CRL were invited to undertake witness point inspections for the bolt tightness of the S4 props and walers in the SH-W2 shaft. However, prior to the commencement of the inspection on site, the contractor was unable to show CRL signed check sheets from __ and __ to confirm that checking of bolts had been undertaken in accordance with the revised procedure defined in NCR 656. CRL were therefore unable to proceed with the inspection as planned. It is noted that physical checking on site had been undertaken correctly by both __ and __, hence this is a procedural NCR which reflects a failure in the Contractor's QMS in relation to the availability of correct documentation to provide CRL assurance over the Contractor's self certification of their work prior to CRL inspection.
| 02SL - Stations (LUL) | Cxxx-NCR-000667 | NCR | Pull-out testing Levels S4-S6 |  | Contr |  | FAR - Farringdon Station (West) |  | 2013-02-27 | 2013-02-25 08:24 | -2 | 2013-02-20 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The bolts at level S4 were pull out tested to 60kN. No failures were recorded.
| 02SL - Stations (LUL) | Cxxx-NCR-000668 | NCR | W2-SH: Incorrect process - Grouting of Slab level -5 couplers |  | Contr |  | FAR - Farringdon Station (West) |  | 2013-03-21 | 2013-03-18 08:31 | -3 | 2013-02-25 | Civil - Civil Engineering General | 500 |  | Planning | Use As-Is |  | Complete |  | Completed |  | __ took the decision to proceed at risk with the solution to the slab level -5 couplers being out of tolerance. The couplers at this level clashed directly with the temporary works (i.e the steel waler beams). __ surveyed the couplers in each of the piles, analysed which were out of tolerance and proposed remedial actions via NCR 662. These actions mirrored those of NCRs 655 and 640 (slab levels -4 and -3 respectively). Unfortunately, the program dictated that the walers be installed just one day after the coupler survey was complete. The remedial action of drilling and fixing new bars/couplers is not possible after the waler has been installed. __ had the choice of not attempting any remedial work, or carry out what they thought was the correct solution before receiving confirmation from Crossrail/their designers. __ chose to proceed at risk.
| 02SL - Stations (LUL) | Cxxx-NCR-000669 | NCR | W2-SH: Level S4 Rework of Props |  | Contr |  | FAR - Farringdon Station (West) |  | 2013-03-25 | 2013-02-28 08:26 | -25 | 2013-02-25 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | __ (__'s sub-contractor) found that the final two steel props (connecting into the Western waler) would not fit at the final stages of S4 steel installation. Please see attached sketch for the locations of the two props that are being discussed in this NCR.
| 02SL - Stations (LUL) | Cxxx-NCR-000670 | NCR | Insufficient embedment for S5 pile/bracket connection |  | Contr |  | FAR - Farringdon Station (West) |  | 2013-03-29 | 2013-03-11 15:31 | -18 | 2013-03-05 | Structural Engineering - Concrete Member | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | During a CRL witness point inspection for the embedment depths of drilled holes for the pile/bracket connections at level S5 within the WTH SH-W2, one drilled hole in pile R919 was found to have an embedment of only 300mm rather than the minimum requirement of 480mm. It was apparent that the drilling operation for this hole might have penetrated a sonic logging tube within the pile, causing grout to flow into the hole and reduce the measured embedment depth. This would explain Contractor's assertion that the hole had been measured with the correct embedment during their checks on Friday 01 March 2013, but was subsequently measured with an embedment of 300mm on Monday 04 March 2013 during the CRL inspection.
| 02SL - Stations (LUL) | Cxxx-NCR-000671 | NCR | Cutting of Hellical Bars in the W2-SH |  | Contr |  | FAR - Farringdon Station (West) |  | 2013-04-05 | 2013-04-11 17:04 | 6 | 2013-03-05 | Civil - Civil Engineering General | 500 |  | Damaged | Use As-Is |  | Complete |  | Completed |  | During both the breaking back of the pile face concrete and drilling for brackets, it has been noticed that some of the helical bars in the piles have been damaged or bent. __ state clearly in both the propping method statement (Cxxx-LOS-O1-GMS-M123-50102) and the Square Shaft Briefing that no hellicals are to be cut/damaged without prior permission from Crossrail and their designers. The following piles have been damaged (please note, this is at the S5 steel level so all damage is between 87.2 - 86.5mAD): Pile 910: There are 2no. hellicals which have been slightly damaged by drilling (>70% of the hellical's diameters remain in tact) Pile 911: 6no. hellicals have been slightly damaged by drilling (>50% of the hellical's diameters remain in tact). 5no. bars have been bent due to breaking, but are fully in tact. Pile 914: 1no. hellical has been slightly damaged by drilling (>80% of the hellical's diameter remains in tact). 3no. bars have been bent due to breaking, but are fully in tact. 1no. bar has been cut at one end and is subsequently loose from the concrete. Pile 915: 4no. hellicals have been slightly damaged by drilling (>50% of the hellical's diameters remain in tact). 4no. bars have been bent due to breaking, but are fully in tact. Pile 917: 2no. hellicals have been slightly damaged by drilling (>50% of the hellical's diameters remain in tact). 5no. pairs of bars have been bent due to breaking, but remain fully in tact. Pile 923: 2no. pairs of hellicals have been bent due to breaking, but are fully in tact. Pile 929: 1no. pair of hellicals have been slightly damaged by drilling (>50% of the hellical's diameters remain in tact).
| 02SL - Stations (LUL) | Cxxx-NCR-000672 | NCR | Incorrect Spacing of Shear Links in W2-SH Piles |  | Contr | LOS | FAR - Farringdon Station (West) |  | 2014-07-01 | 2014-06-12 14:09 | -19 | 2013-03-06 | Civil - Civil Engineering General | 400000 |  | Workmanship | Use As-Is | 1 (>60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | To facilitate installation of the S5 steel waler beams within the WTH SH-W2 shaft (approx 86mAD), it was required to break out the cover zone of several secant piles which were found to be out of vertical tolerance (See NCR664). During this break-out operation, it was noticed that the spacing of the shear links around the vertical cage connection was non-conforming for a number of piles in the shaft. Further investigation, using both intrusive and non-intrusive techniques found many of the SH-W2 piles to have a non-conforming spacing of shear links at the vertical cage connection. In some instances shear links have been poorly spaced, with ‘clusters’ of links present where they should have been equally spaced. In other places, all of the loose shear links are bundled at the top of the lower cage. In some places, the loose links appear to have been removed. Please refer to proposed answer section of this NCR for further details on the as-built condition of the shear links in the SH-W2 piles.
| 02SL - Stations (LUL) | Cxxx-NCR-000675 | NCR | W2-SH: Breaking Out Pile R917 (Levels S4-S6) |  | Contr | LOS | FAR - Farringdon Station (West) |  | 2014-06-27 | 2014-01-10 17:56 | -168 | 2013-03-15 | Civil - Civil Engineering General | 700 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Due to the fact that Pile R917 is out of tolerance in terms of verticality, the pile face had to be broken back in order to be able to install the walers at S4 and S5. Further to this, the face of the pile between the S4 and S5 walers had to be broken out in order to install the vertical twin I-sections and their splice plates. (The breaking out allows the bolts on the back splice plate to be installed). The pile face has been broken out to such an extent that the helical bars and shear links are clearly visible. Cxxx would also like to use this NCR to gain permission to continue with this regime of breaking pile R917 (and the adjoining female pile R617) between level S5 and S6 walers. Again, this must be carried out in order to install the large twin I-section steel running between S5 and S6. Once again, __ are proposing to break out as little as possible, whilst also ensuring that no helical bars or shear links are damaged.
| 02SL - Stations (LUL) | Cxxx-NCR-000676 | NCR | W2-SH: Re-drilling couplers for slab Level -4 |  | Contr |  | FAR - Farringdon Station (West) |  | 2013-04-28 | 2013-04-24 14:20 | -4 | 2013-03-15 | Civil - Civil Engineering General | 500 |  | System Defect | Rework |  | Complete |  | Completed |  | As part of NCR655, several bars were re-drilled and couplers refixed at the slab level -4. However, both Cxxx and Crossrail failed to notice that only 4no. couplers had been identified in Pile R913. The rotation of the pile cage means that the second column of couplers was never exposed and indeed is buried within the female pile. The attached photo shows this clearly. In effect, only half the number of couplers are available to Cxxx in Pile R917.
| 02SL - Stations (LUL) | Cxxx-NCR-000679 | NCR | W2-SH: Weld Failure on Thrust Plates at Level S2 |  | Contr |  | FAR - Farringdon Station (West) |  | 2013-07-05 | 2013-06-25 16:00 | -10 | 2013-03-26 | Civil - Civil Engineering General | 500 |  | System Defect | Use As-Is |  | Complete |  | Completed |  | During the initial Ultrasonic testing on the 19.12.2012, the thrust plates in the NE (LD6-LDe) and SW corners (LD1-LDa) were found to have welds that were faulty. Similarly, the NW (LD1-LDe) and SE (LD6-LDb) corners were also shown to have cracks within their welds. This was raised prior to the sign-off of the permit to load. The welds in the NE and SW corner were repaired on the 20.12.2012 and the permit to load was signed off, without any further comments on the NW and SE corners. Crossrail’s field engineer then picked up on this anomaly during the review of the S2 DQR package. As a result, __ instructed further tests on the NW and SE corners. These were also found to have failed on the Ultrasonic testing.
| 02SL - Stations (LUL) | Cxxx-NCR-000681 | NCR | Damaged Helical Bars in the W2-SH Piles |  | Contr |  | FAR - Farringdon Station (West) |  | 2013-05-31 | 2013-06-03 11:14 | 3 | 2013-05-01 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | During both the breaking back of the pile face concrete and drilling for brackets, it has been noticed that some of the helical bars in the piles have been damaged or bent. __ state clearly in both the propping method statement (Cxxx-LOS-O1-GMS-M123-50102) and the Square Shaft Briefing that no helicals are to be cut/damaged without prior permission from Crossrail and their designers. There are no broken helicals. There are 15no. piles with damaged helicals (between 86.965 and 81.400mAD). Two piles (R923 and R925) have been broken back from the slab coupler area to the bottom of the walers (around 3.1m).
| 02SL - Stations (LUL) | Cxxx-NCR-000682 | NCR | Incorrect Spacing of Shear Links in W1-SH Piles |  | Contr | LAO | FAR - Farringdon Station (West) |  | 2014-06-27 | 2014-05-09 16:53 | -49 | 2013-04-24 | Civil - Geotechnical Engineering | 25000 |  | Workmanship | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the installation of the steel structure within the SH-W2 shaft it was discovered that the installation of the shear reinforcement in the area where cage parts have been connected via couplers has been executed incorrectly. Non-intrusive survey was carried within the SH-W1 to identified potential variations within the arrangement of and spacing between shear reinforcement bars (horizontal / diagonal helicals and links) within the piles. The outcome of the survey confirmed that the installation of the shear reinforcement within the affected areas was partly carried out incorrectly. For details please refer to the attached report.
| 02SL - Stations (LUL) | Cxxx-NCR-000686 | NCR | W2-SH: Incorrect process for breaking out piles (Level S6) |  | Contr |  | FAR - Farringdon Station (West) |  | 2013-05-16 | 2013-05-13 10:38 | -3 | 2013-05-09 | Civil - Civil Engineering General | 500 |  | System Defect | Use As-Is |  | Complete |  | Completed |  | Breaking out of piles at Level S6 was undertaken before __ was in receipt of confirmation from Crossrail/Cxxx to do so, therefore this is a procedural NCR.
| 02SL - Stations (LUL) | Cxxx-NCR-000687 | NCR | W2-SH Slab level -5 Coupler Positions |  | Contr |  | FAR - Farringdon Station (West) |  | 2013-06-14 | 2013-06-11 11:44 | -3 | 2013-05-10 | Civil - Civil Engineering General | 500 |  | System Defect | Rework |  | Complete |  | Completed |  | Please see attached as-built drawings of the couplers currently exposed following Phase 6 excavation. 27no. piles have couplers out of tolerance in terms of level and 23no. piles in terms of rotation. (Please note that some piles have couplers which are out of tolerance in both height and rotation).
| 02SL - Stations (LUL) | Cxxx-NCR-000688 | NCR | Nominal concrete cover piles |  | Contr |  | FAR - Farringdon Station (West) |  | 2013-06-14 | 2013-05-30 09:33 | -15 | 2013-05-14 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Damaged | Use As-Is |  | Complete |  | Completed |  | During the installation of the additional inclinometer in pile B919 either pile B119 or B120 was affected. Concrete was first hit at a depth of 24m, at the bottom of the male pile the segment of the circle containing concrete made approximately 2/3 of the total circle (drilling of the borehole with 100mm diameter). Attached sketch shows that the concrete cover is intact up to the depth of 24m and then is reduced gradually by maximal 62mm at the bottom of the male pile. No reinforcement has been reached over the course of the works. The male pile was affected as the required distance to the inclinometer has been underestimated. The reduction in pile base is marginal therefore the load bearing capacity is not affected. The reduction of the concrete cover is localised leaving still sufficient concrete cover to the pile reinforcement. The annulus between the borehole sides and inclinometer tube has been grouted, sealing the pile concrete surface. The piles are acting in this depth and in long term as bearing elements so that the vertical reinforcement will be mainly required (if reinforcement at all is needed to transfer vertical loads into the ground) which have a bigger concrete cover.
| 02SL - Stations (LUL) | Cxxx-NCR-000690 | NCR | Caxton Slab Backpropping Alterations |  | Contr |  | FAR - Farringdon Station (West) |  | 2013-06-25 | 2013-06-17 15:06 | -8 | 2013-06-11 | Civil - Civil Engineering General | 500 |  | System Defect | Use As-Is |  | Complete |  | Completed |  | The TW designer confirmed the changes to the temporary works design (for the backpropping and crane matt position on Caxton slab), but Cxxx did not submit the changes to Crossrail in either the SNC or revised DCC format prior to using the 250T crane. This NCR is purely procedural. The revised Gass tower layout and crane mat positions were approved by Cxxx's TW designer prior to the first use of the crane. Please see attached correspondance between Cxxx Project Engineer and the Cxxx TW designer, along with further correspondance between the Cxxx TW designer and the Cxxx TW designer.
| 02SL - Stations (LUL) | Cxxx-NCR-000691 | NCR | Exposed Rebar in the W2 Shaft |  | Contr | LOS | FAR - Farringdon Station (West) |  | 2014-06-27 | 2014-01-10 17:19 | -168 | 2013-06-17 | Civil - Civil Engineering General | 2000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In some places, for various reasons, the concrete cover has been broken out at several different levels of various piles, revealing the rebar in the piles. __ subsequently submitted a suitable cold galvanising product via both FAR-CRL NCR-Cxxx-00675 (W2-SH: Breaking Out Pile R917) and Cxxx-LOS-O4-XDS-M123-50147 (MCR for __). When painted on to the exposed rebar, the galvafroid will protect the rebar until such a time that the lining wall is cast in front of the pile face.
| 02SL - Stations (LUL) | Cxxx-NCR-000692 | NCR | Out of Date N__ Qualification Certificate |  | Contr |  | FAR - Farringdon Station (West) |  | 2013-06-25 | 2013-06-24 17:06 | -1 | 2013-06-24 | Civil - Civil Engineering General | 500 |  | System Defect | Use As-Is |  | Complete |  | Completed |  | The welds for the S6 steelwork were visually inspected by __ of __. His initial competency certificate for visual inspection expired on 27th February 2013, with his new certificate only being issued on the 20th March 2013. Between this period, he carried out inspections on welds leading to the issue of 4no. weld conformity certificates.
| 02SL - Stations (LUL) | Cxxx-NCR-000693 | NCR | Distortion of vertical hanger between S4 and S6 |  | Contr |  | FAR - Farringdon Station (West) |  | 2013-09-02 | 2013-08-12 14:25 | -21 | 2013-07-11 | Civil - Structural Engineering | 500 |  | Damaged | Use As-Is |  | Complete |  | Completed |  | Please refer to attached photo. During a site visit undertaken by the Project Manager on 08 July 2013, it was noticed that the connection between one vertical hanger section spanning between S5 and S6 was exhibiting signs of distortion at the connection with the S5 props. The vertical hanger in question is located near GL 1/E, under the node point between S5 prop line 3 and the S5 box section to the south side of the shaft. Crossrail are in the process of raising this item as a Defect in accordance with the contract.
| 02SL - Stations (LUL) | Cxxx-NCR-000694 | NCR | Leaking Piles in SH-W2 Shaft |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2014-09-30 | 2014-05-28 12:39 | -125 | 2013-12-04 11:03 | Shafts - Shafts General | 28000 |  | Damaged | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Weeping of water along Piles R618 and R651. Weeping of water is the state in which droplets of water have formed on the surface of the wall and coalesce with other droplets. The coalesced water has not remained stationary on the wall surface, but instead has flowed down the wall and in turn has a build up of moss which indicates long term weeping.
| 02SL - Stations (LUL) | Cxxx-NCR-000700 | NCR | Incorrect Spacing of Shear Links in ETH Piles |  | Contr | LAO | FAR - Farringdon Station (West) |  | 2014-03-14 | 2014-03-31 17:56 | 17 | 2014-02-10 09:39 | Civil - Geotechnical Engineering | 200000 |  | Workmanship | Repair | 1 (>60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | This non-conformance report covers all shear link spacing non-conformances found in secant piles B101 – B313 within the ETH south basement area. Following the incorrect spacing of shear links in the W2-SH and W1-SH WTH Piles (NCRs 672 and 682 respectively), confidence was sought after with the ETH Piles which were also constructed by __. From the outset, __ had proposed that a shear links problem did not exist for the ETH Piles (Cxxx-LOS-C-RGN-M123-50228), although CRL's concerns regarding this report were identified in the response Cxxx-PMC-02087. CRL's concerns were verified when both RSK (non-intrusive) and __ intrusive surveys were undertaken on these piles whereby it was discovered that some of these piles contained large gaps at the vertical reinforcement cage connection region around 112mAOD (upper pile cage connection). In some instances shear links have been poorly spaced, with ‘clusters’ of links present at the top or the bottom where they should have been equally spaced. While in others, the loose links that were supplied tied to the cage appeared to have been removed. The ETH Shear Links Survey Report (Cxxx-LOS-C-RGN-M123-50235) was issued to CRL provding a comprehensive outline of the shear links as-built information. During the intrusive investigation works, discrepancies between the non-intrusive and intrusive survey results were discovered. These were further investigated and documented by RSK in their Geophysical Report (Cxxx-LOS-C-RGN-M123-50236) which includes all non-intrusive information and explanations for the identified discrepancies. Following concerns raised with regard to the accuracy of these non-intrusive surveys combined with the sensitiity of the CRL Designer's analysis, further intrusive surveys were required. These were undertaken by CRL's main works contractor, Cxxx, and their recorded survey information can be found in Cxxx--C-RGN-M123-51298. Overall, there were a total of 11 'phantom' points on 10 different piles. These were determined by aligning the Cxxx surveyed shear link levels and gaps between them against the correspoding RSK shear link levels and gaps between them. There are a total of 203 points identified by RSK as shear links within the intusive survey extents, meaning ~5.5% of the shear links were 'phantoms' (11/203 = 5.418%), located at: Pile B101 (113.300mAOD) Pile B108 (112.250mAOD) Pile B110 (113.120mAOD) Pile B116 (112.540mAOD and 112.150mAOD) Pile B117 (112.870mAOD) Pile B120 (112.050mAOD) Pile B121 (113.420mAOD) Pile B122 (113.310mAOD) Pile B125 (113.280mAOD) Pile B202 (112.990mAOD) This corresponds to the percentage of phantom points specified by Cxxx in their ETH Pile Shear Links Survey Commentary (Cxxx-LOS-C-RGN-M123-50235) after having undertaken intrusive surveys on 23no. piles. The total number of piles with intrusive surveys undertaken (Cxxx and Cxxx combined) is 40no. out of 47no. piles. The discrepancies between the non-intrusive and intrusive survey results can be summarised as follows: 1) Positional discrepancies – There were several occasions where shear links were found albeit out of level tolerance. These developed as a result of many interfaces/engineers between these surveys and the two survey types not always being taken on the same area of the pile face which were exacerbated by angled shear links within the piles (refer to ETH Shear Links Survey Report Appendix). In addition, some of RSK's measurements were made in less accurate 'Time Mode' and were also affected by poor pile surfaces whereby the antenna wheel would catch on the rough pile surface, relaying less accurate data. 2) "Possible" or 'Lower Confidence' links - There were a number of shear links identified by RSK as “possibles”. There were a total of 49 of these, of which 13 had been verified when intrusively surveyed (6no. were already identified in the ETH Shear Links Pile Survey Report and an additional 7no. from Cxxx's intrusive surveys). There are two "possible" points which were not actually found i.e. Phantom shear links and a further two were not found, but from Cxxx's analysis are considered the Upper Lifting Band, however deeper intrusive surveys would be required to confirm these. See the comprehensive list below: Pile B103 (point 112.070mAOD) - Verified Pile B106 (point 112.490mAOD) - Verified Pile B109 (point 113.470mAOD) – Upper Lifting Band (deeper intrusive req. to confirm) Pile B114 (point 113.520mAOD) – Verified Pile B116 (point 113.530mAOD) – Verified Pile B120 (point 112.400mAOD) – Phantom Pile B120 (point 112.710mAOD) – Verified Pile B121 (point 111.970mAOD) - Verified Pile B122 (point 113.500mAOD) – Verified Pile B123 (point 112.850mAOD) – Verified Pile B125 (point 113.280mAOD) – Phantom Pile B201 (point 112.660mAOD) – Verified Pile B203 (point 112.660mAOD) - Verified Pile B204 (point 113.250mAOD) - Verified Pile B301 (point 111.860mAOD) - Verified Pile B303 (point 113.020mAOD) - Verified Pile B303 (point 112.930mAOD) - Upper Lifting Band (deeper intrusive req. to confirm) 3) Lifting bands - There are horizontal lifting bands located within the pile cages which were also detected by RSK. The ETH Shear Link Piles Survey identifies lifting bands from the non-intrusive data based on their as-built information from the Pile Packs and/or a +/-50mm from the anticipated lifting band level. It is worth noting that these were not included in the count of 'phantom' shear links as they are not considered within any analysis as providing structural capacity.
| 02SL - Stations (LUL) | Cxxx-NCR-000337 | NCR | Starting Works Without An Signed ITP |  | Contr |  | FAR - Farringdon Station (West) |  | 2012-10-16 | 2012-10-23 13:15 | 7 | 2012-10-02 | Utilities Engineering - Water | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Works commenced on both the diversion of the 4" water main at the northern pit in Farringdon Road and the installation of the rider main across Greville Street without an accepted ITP in place.
| 02SL - Stations (LUL) | Cxxx-NCR-000400 | NCR | PMI 031 - 300mm diameter rider main - cracked pipe |  | Contr |  | FAR - Farringdon Station (West) |  | 2012-11-30 | 2012-12-03 09:45 | 3 | 2012-10-25 | Utilities Engineering - Water | 500 |  | Material | Rework |  | Complete |  | Completed |  | During pressure test of the 300mm diameter ductile iron pipe installed in Farringdon Road at the Greville Street junction, a leak was noticed. Following investigation, it was noticed there was a crack at the welded section of the pipe. Please refer to attached pictures showing the cracked pipe.
| 02SL - Stations (LUL) | Cxxx-NCR-000471 | NCR | PMI 031 - 200mm diameter ductile iron pipe with a pin hole |  | Contr |  | FAR - Farringdon Station (West) |  | 2012-12-07 | 2012-12-20 09:34 | 13 | 2012-11-15 | Utilities Engineering - Water | 500 |  | Material | Rework |  | Complete |  | Completed |  | After visual check and installation of 200mm diameter ductile iron pipes at Greville Street, pressure test was carried out on 09.10.2012. The pressure test failed and a jet of water from the pipe was noticed by the flange which meant we couldn't get a pressure test.
| 02SL - Stations (LUL) | Cxxx-NCR-000477 | NCR | WTH - NCR - Backfill underside of piling mat - No test certificate for material |  | Contr |  | FAR - Farringdon Station (West) |  | 2012-12-07 | 2013-01-30 15:53 | 54 | 2012-11-16 | Civil - Geotechnical Engineering | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Test certificate has not been issued yet. To comply with the requirements of PMI 69, excavations are required to be backfilled prior to certificate being ready. Compaction regime outlined on ITP will be enforced.
| 02SL - Stations (LUL) | Cxxx-NCR-000505 | NCR | WTH - Circular Shaft Access |  | Contr |  | FAR - Farringdon Station (West) |  | 2012-12-20 | 2013-01-07 08:02 | 18 | 2012-11-28 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | Modifications had been made to the circular shaft's original scaffold access design, that had been submitted to Crossrail, under document reference Cxxx--C-CER-M123-50015 Rev 1. This document required that the staircase was provided with horizontal ties into the secant pile wall at 2m vertical centres above the level -5 ring beam, whereas the as-built condition only had three ties above this level. The plan location of the access staircase differed on site to avoid covering an inclinometer with the scaffold access bridge between ground level to the staircase. In addition, allowed operatives to use the staircase without firstly issuing a Permit to Load. Pull out tests were not carried out by a UKAS accredited operative.
| 02SL - Stations (LUL) | Cxxx-NCR-000525 | NCR | Concrete Pads for Rider Main Cradles |  | Contr |  | FAR - Farringdon Station (West) |  | 2013-01-18 | 2013-01-17 10:46 | -1 | 2012-12-07 | Utilities Engineering - Water | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | The pads for the rider main cradles were constructed as shown on the Temporary Works Drawings i.e. 400 x 400 x 150mm. The pads were then drilled for bolting the cradles onto the pads. Following the insertion and tightening of the bolts, we noticed some of the pads had cracked.
| 02SL - Stations (LUL) | Cxxx-NCR-000529 | NCR | Under Pressure Tees for the 14" and 30" Trunk Mains |  | Contr |  | FAR - Farringdon Station (West) |  | 2013-01-18 | 2013-01-07 12:22 | -11 | 2012-12-07 | Utilities Engineering - Water | 500 |  | Material | Repair |  | Complete |  | Completed |  | The 14" and 30" trunk mains were callipered by UTS on site prior to manufacturing the UPT's. When they came to install them on site, both the UPT's did not fit around the trunk mains.
| 02SL - Stations (LUL) | Cxxx-NCR-000535 | NCR | WTH Corrosion and pitting to reinforcing bars. |  | Contr |  | FAR - Farringdon Station (West) |  | 2012-12-21 | 2012-12-19 17:06 | -2 | 2012-12-07 | Shafts - Linings | 500 |  | Material | Reject |  | Complete |  | Completed |  | Reinforcement delivered to site was found to have excessive corrosion and pitting. The reinforcement had been on site for one week, and the level of corrosion was greater than expected.
| 02SL - Stations (LUL) | Cxxx-NCR-000538 | NCR | Gap in monitoring data on inclinometers and 3D prisms |  | Contr |  | FAR - Farringdon Station (West) |  | 2012-12-14 | 2013-01-29 12:34 | 46 | 2012-12-07 | Surveying - Instrumentation and Monitoring | 500 |  | Planning | Use As-Is |  | Complete |  | Completed |  | Not been monitored since hand over of instrumentation.
| 02SL - Stations (LUL) | Cxxx-NCR-000549 | NCR | Procedural Non-Compliance |  | Contr |  | FAR - Farringdon Station (West) |  | 2012-12-21 | 2013-02-01 14:00 | 42 | 2012-12-14 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Carrying out works on site without an approved method of work in place.
| 02SL - Stations (LUL) | Cxxx-NCR-000550 | NCR | PMI 032 - Not working in accordance with Temporary Works Design |  | Contr |  | FAR - Farringdon Station (West) |  | 2013-01-18 | 2013-01-18 16:18 | 0 | 2012-12-14 | Utilities Engineering - Water | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | Not working in accordance with the approved Temporary Works Design Package Cxxx--C-CER-M123-50010
| 02SL - Stations (LUL) | Cxxx-NCR-000569 | NCR | Undertaking SCL Trials in non-compliant conditions |  | Contr |  | FAR - Farringdon Station (West) |  | 2013-01-23 | 2013-01-23 12:52 | 0 | 2013-01-09 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Reject |  | Complete |  | Completed |  | Air temperature on the day was 2 to 3 degrees and the temperature of the concrete mix varied between 11 and 14 degrees. Subsequently, the required early strength was not achieved. Non-compliant results may have been as a result of unsuitable air and mix temperature.
| 02SL - Stations (LUL) | Cxxx-NCR-000571 | NCR | PMI 031 - Faulty valve on the 14" main |  | Contr |  | FAR - Farringdon Station (West) |  | 2013-02-22 | 2013-01-31 16:40 | -22 | 2013-01-11 | Utilities Engineering - Water | 500 |  | Material | Rework |  | Complete |  | Completed |  | Following the drilling of the 14" main in the south pit, a valve which was installed onto the UPT beneath the drilling rig could not be fully shut. This prevented the removal of the drilling rig and installing the line stop onto the valve.
| 02SL - Stations (LUL) | Cxxx-NCR-000578 | NCR | Submission of test results within the specified time. |  | Contr |  | FAR - Farringdon Station (West) |  | 2013-01-30 | 2013-01-31 08:25 | 1 | 2013-01-16 | Tunnelling - Linings - Sprayed Concrete | 500 |  | System Defect | Use As-Is |  | Complete |  | Completed |  | The Project Manager has yet to receive full test reports for trials carried out between the 21st of November and the 4th of December 2012.
| 02SL - Stations (LUL) | Cxxx-NCR-000586 | NCR | PMI 031 - 14 inch Linestop at the north pit |  | Contr |  | FAR - Farringdon Station (West) |  | 2013-02-01 | 2013-01-31 16:06 | -1 | 2013-01-21 | Utilities Engineering - Water | 500 |  | Material | Rework |  | Complete |  | Completed |  | Following the installaton of the linestop onto the 14" trunk main, the linestop did not go through to the bottom of the pipe when it was engaged. The linsetop RAM got stuck between the first and second notch when the CCTV camera showed element was just entering the trunk main.
| 02SL - Stations (LUL) | Cxxx-NCR-000587 | NCR | PMI 031 - 30 inch Linestop at the north pit |  | Contr |  | FAR - Farringdon Station (West) |  | 2013-04-05 | 2013-04-08 11:10 | 3 | 2013-01-21 | Utilities Engineering - Water | 500 |  | Material | Rework |  | Complete |  | Completed |  | During engaging of the linestop on the 30" trunk main, the studded bar which joins the linestop housing and the linestop RAM pulled apart and water started gushing out at the joint.
| 02SL - Stations (LUL) | Cxxx-NCR-000594 | NCR | Digital signiture incorrectly used on Heritage Management Plan |  | Contr |  | FAR - Farringdon Station (West) |  | 2013-02-22 | 2013-02-21 11:31 | -1 | 2013-01-22 | Environmental - Build Heritage and Townscape | 500 |  | Supervision/Management | Reject |  | Complete |  | Completed |  | A Heritage Management Plan was submitted with electronic signatures (prior permission not sort on one of the signees). This was a revision to a code 1 document to make changes to two contact names - no other changes were made to the management plan.
| 02SL - Stations (LUL) | Cxxx-NCR-000656 | NCR | Piling: non-compliance with Method Statement |  | Contr |  | FAR - Farringdon Station (West) |  | 2013-02-27 | 2013-02-28 13:06 | 1 | 2013-02-13 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The attached photos show the following: 1.Site arisings were used to back-fill the core, although part of the core was backfilled with sand. 2. Arisings have fallen into the annulus.
| 02SL - Stations (LUL) | Cxxx-NCR-000659 | NCR | WTH Bored Piling |  | Contr |  | FAR - Farringdon Station (West) |  | 2013-02-28 | 2013-02-28 13:17 | 0 | 2013-02-14 | Civil - Geotechnical Engineering | 500 |  |  | Use As-Is |  | Complete |  | Completed |  | Cages are being manufactured with 2no reservation tubes which is not as per the IFC drawing.
| 02SL - Stations (LUL) | Cxxx-NCR-000661 | NCR | WTH - Piling - 2No Geothermal Pipes Only Above PPL |  | Contr |  | FAR - Farringdon Station (West) |  | 2013-03-01 | 2013-03-01 16:31 | 0 | 2013-02-15 | Civil - Geotechnical Engineering | 500 |  | Design | Use As-Is |  | Complete |  | Completed |  | Pile 212 has therefore been constructed as per __ drawing 02481-GL-DET-02 Rev F, with only 2No geothermal piles protruding above PPL.
| 02SL - Stations (LUL) | Cxxx-NCR-000679 | NCR | WTH - Piling - Steel Reinforcement Spacers |  | Contr |  | FAR - Farringdon Station (West) |  | 2013-03-08 | 2013-03-04 07:36 | -4 | 2013-02-22 | Civil - Geotechnical Engineering | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Spacers for piling cage are fabricated in steel and coated in a UPVC sleeve. This effectively means metal parts will be within the cover zone, albeit isolated in the sleeve. The spacers in question were used in 2 piles (S 212 & U217) before this issue became apparent. The spacers were subject to an MCR which is Code 1 (Cxxx--C-LRC-M123-50015).
| 02SL - Stations (LUL) | Cxxx-NCR-000706 | NCR | WTH - Piling - Pile 212 - Base Grouting - Reference Beam Supports |  | Contr |  | FAR - Farringdon Station (West) |  | 2013-03-19 | 2013-04-02 15:22 | 14 | 2013-03-05 | Civil - Geotechnical Engineering | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Bearing plates for reference beam of pile 212 were less than 2m away from the pile. This was caused by insufficient space on site due to change in Cxxx/Cxxx hoarding line and additional materials on site. Obstruction encountered on pile 221 (subsequent pile to 212) resulted in a delay in installation of liners by 1 day. The liners for pile 212 had therefore to remain at ground level obstructing the base grouting operations to pile 212.
| 02SL - Stations (LUL) | Cxxx-NCR-000713 | NCR | ETH Plate Bearing tests |  | Contr |  | FAR - Farringdon Station (West) |  | 2013-03-20 | 2013-03-22 14:32 | 2 | 2013-03-06 | Civil - Fill | 500 |  | System Defect | Use As-Is |  | Complete |  | Completed |  | did not follow the activity plan and invite a crossrail rep to witness the plate bearing testing of the piling platform with IRF form
| 02SL - Stations (LUL) | Cxxx-NCR-000719 | NCR | Working outside sheetpiling Pre Start Checklist |  | Contr |  | FAR - Farringdon Station (West) |  | 2013-03-07 | 2013-03-08 10:29 | 1 | 2013-03-07 | Civil - Civil Engineering General | 500 |  | System Defect | Use As-Is |  | Complete |  | Completed |  | started sheetpiling works adjacent to Lindsey Street Bridge following the approval of City of London. did not re submit a signed pre start checklist showing that the document had been approved prior to the works and worked of the previosu document which allowed the installation of a different run of sheetpiles
| 02SL - Stations (LUL) | Cxxx-NCR-000723 | NCR | WTH - Piling - Pile U214 - Construction time |  | Contr |  | FAR - Farringdon Station (West) |  | 2013-03-21 | 2013-03-28 14:55 | 7 | 2013-03-07 | Civil - Geotechnical Engineering | 500 |  | Planning | Use As-Is |  | Complete |  | Completed |  | It was interpreted that construction period for an unsleeved pile begins when excavation advances past the clay plug at the bottom of a temporary casing. This should have been clarified on a subsequent FCD. Casing for Pile U214 was sunk on Monday 4th of March, prior to this FCD being issued and approved. Excavation for Pile U214 only advanced past the clay plug in the temporary casing on Thursday 7th of March. Discussions in Engineering Meeting of the 5th of March have concluded that interpretation was correct. FCD 00721 has been issued.
| 02SL - Stations (LUL) | Cxxx-NCR-000731 | NCR | Operative making cubes for __ not UKAS Accreditated |  | Contr |  | FAR - Farringdon Station (West) |  | 2013-03-27 | 2013-04-05 10:32 | 9 | 2013-03-12 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Slump test, making cube samples and cube storage carried out by __ for the Tower crane piles __ not UKAS accredited laboratory or similar. __ operative unable to prove UKAS accreditation or similar
| 02SL - Stations (LUL) | Cxxx-NCR-000732 | NCR | Section 61 variation |  | Contr |  | FAR - Farringdon Station (West) |  | 2013-03-22 | 2013-04-03 11:50 | 12 | 2013-03-12 | Environmental - Noise and Vibration | 500 |  | Planning | Repair |  | Complete |  | Completed |  | The works under the section 61 were consented for - as confirmed by __ (EHO at the CoL). However, technically there was an element of works from the sheet piling - vibrating initial section - missing from the s61.
| 02SL - Stations (LUL) | Cxxx-NCR-000735 | NCR | WTH Piling - Incorrect concrete mix (load) on pile U214 |  | Contr |  | FAR - Farringdon Station (West) |  | 2013-05-09 | 2013-05-01 09:51 | -8 | 2013-03-12 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | The 4th Load poured into pile U214 was the incorrect mix and meant for an alternative contract. A 7.7m3 load of C28/35, CIIIB+SR, MCC 360, W/C 0.50, DC-3, S4 was accidently placed into the pile instead of the specified C35/45, CIIIB+SR, MCC 360, W/C 0.45, DC-4, F5.
| 02SL - Stations (LUL) | Cxxx-NCR-000736 | NCR | WTH Piling - Energy piles testing |  | Contr |  | FAR - Farringdon Station (West) |  | 2013-04-22 | 2013-04-24 16:41 | 2 | 2013-03-12 | Civil - Civil Engineering General | 500 |  |  | Use As-Is |  | Complete |  | Completed |  | The Test for Pile S221 was carried out for 18 hours only instead of 24 hours following completion of concreting.
| 02SL - Stations (LUL) | Cxxx-NCR-000737 | NCR | WTH Piling Bentonite Testing (ph level) |  | Contr |  | FAR - Farringdon Station (West) |  | 2013-04-05 | 2013-04-08 09:24 | 3 | 2013-03-20 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Pile 102, 221 and U214 Bentonite Testing sheet ph levels are below the ones on Table KP10-01. ITP Cxxx--C-ITP-M123-50028 hold point not followed by piling subcontractor
| 02SL - Stations (LUL) | Cxxx-NCR-000751 | NCR | WTH - Layering to Pour 6 Lining Wall within the Circular Shaft (SH-W1) |  | Contr |  | FAR - Farringdon Station (West) |  | 2013-04-26 | 2013-04-19 13:13 | -7 | 2013-03-15 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | On striking shutters to Pour 6 lining walls, layers appear to have been formed due to the inadequate supply of concrete. are to assess whether these layers are indeed 'cold joints' leading to possible water ingress. Please see photograph attached of evidence of layering.
| 02SL - Stations (LUL) | Cxxx-NCR-000752 | NCR | WTH - Void between S2 downstand kicker and lining wall in the circular shaft (SH-W1) |  | Contr |  | FAR - Farringdon Station (West) |  | 2013-04-26 | 2013-04-19 13:20 | -7 | 2013-03-15 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Void discovered between S2 downstand kicker and lining wall (Pour 6). Void approximately 300mm wide, 50mm high and 70mm deep.
| 02SL - Stations (LUL) | Cxxx-NCR-000778 | NCR | Water added to one of the concrete wagons while pouring grout shaft No.2 base |  | Contr |  | FAR - Farringdon Station (West) |  | 2013-03-29 | 2013-04-09 09:53 | 11 | 2013-03-22 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | 40lt of water were added to the first concrete wagon poured into the shaft base. The concrete passed the slump test for an S3 mix, but close to the S2 limit. As it was a bit to hard to be pumped, one of the subcontractor engineers decided to do it without asking the supplier.
| 02SL - Stations (LUL) | Cxxx-NCR-000831 | NCR | Grout cube at Grout Shaft 2 ring 4 didn't reach 1.5N/mm2 at 24 hours |  | Contr |  | FAR - Farringdon Station (West) |  | 2013-04-26 | 2013-04-17 11:25 | -9 | 2013-04-12 | Geotechnical Engineering - Compensation Grouting | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Grout cube taken from grout mix used to grout back ring 4 at Grout Shaft 2 was damaged while being taken out of the mould as it wasn't set. Cube strength reached 0.6N/mm2 at 2 days.
| 02SL - Stations (LUL) | Cxxx-NCR-000833 | NCR | Procedural Non-Compliance with ITP for ETH Tower Crane Base |  | Contr |  | FAR - Farringdon Station (West) |  | 2013-05-03 | 2013-05-15 19:01 | 12 | 2013-04-15 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | 1. Carried out works on site without an the approved pre-start works in place 2. Have not followed ITP for the works, in this case the works at the Tower Crane base were there were H, W or R points. 3. Records could not be available upon request
| 02SL - Stations (LUL) | Cxxx-NCR-000840 | NCR | Procedural Non-Compliance - ETH: Installation of Materials without formal approval |  | Contr |  | FAR - Farringdon Station (West) |  | 2013-05-03 | 2013-05-15 18:27 | 12 | 2013-04-17 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | • has carrying out the installation of waterproofing works for the capping beam works - LU siding screen (level -1) at the ETH, without formal acceptance of Materials (MCRs).
| 02SL - Stations (LUL) | Cxxx-NCR-000843 | NCR | WTH - Piling - Pile 211 - Geothermal loop below cut off level |  | Contr |  | FAR - Farringdon Station (West) |  | 2013-05-14 | 2013-04-25 17:11 | -19 | 2013-04-18 | Civil - Geotechnical Engineering | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | On pile 211, one of the closed geothermal loops was installed in the cage without sufficient lenght to allow it to clear the pile cut-off level (photo attached)
| 02SL - Stations (LUL) | Cxxx-NCR-000854 | NCR | Failure to have Temporary Electrics ITP signed off before starting works |  | Contr |  | FAR - Farringdon Station (West) |  | 2013-05-06 | 2013-05-14 17:27 | 8 | 2013-04-22 | Electrical - Electrical Engineering General | 500 |  | Planning | Rework |  | Complete |  | Completed |  | Failure to have Temporary Electrics ITP in WTH signed off before starting works
| 02SL - Stations (LUL) | Cxxx-NCR-000857 | NCR | Procedural Non-Compliance with ITP Intervention Point for Capping Beam - ETH |  | Contr |  | FAR - Farringdon Station (West) |  | 2013-05-03 | 2013-05-15 19:07 | 12 | 2013-04-23 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Carrying out works on site without an the approved pre-start works revision in place
| 02SL - Stations (LUL) | Cxxx-NCR-000858 | NCR | ETH Procedural Non Conformance - Configuration Management of TWD drawings |  | Contr |  | FAR - Farringdon Station (West) |  | 2013-05-17 | 2013-05-17 17:44 | 0 | 2013-04-23 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Constructed to a drawing revision of temporary works that CRL has not accepted when constructing the RC Tower Crane base.
| 02SL - Stations (LUL) | Cxxx-NCR-000870 | NCR | ETH Procedural Non Conformance - Management of RC Permanent drawings and Control of Change |  | Contr |  | FAR - Farringdon Station (West) |  | 2013-05-17 | 2013-05-17 17:51 | 0 | 2013-04-25 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Constructed to a drawing revision of permanent works that CRL has not accepted when constructing the Rebar for the Capping Beam Level -1. Drawings used on site for the capping beam level -1 are: Cxxx-ATK-S-DWG-M123_2-50100 C02 (rev 11) Cxxx-ATK-S-DWG-M123_2-50101 C02 (rev 12) - this has not been approved yet as Cxxx are currently reviewing it) Cxxx-ATK-S-TSC-M123_2-50100 C02 (rev 10) Cxxx-ATK-S-TSC-M123_2-50101 C02 (rev 12) – this has not been approved yet as Cxxx are currently reviewing it) Cxxx-ATK-S-TSC-M123_2-50103 C01 (rev 11) Cxxx-ATK-S-DWG-M123_2-50103 C01 (rev 11) The DRIR Rev 12 was sent to Cxxx on the 16.04.13 for approval
| 02SL - Stations (LUL) | Cxxx-NCR-000880 | NCR | Grout cube at Grout Shaft 1 ring 4 didn't reach 1.5N/mm2 at 24 hours |  | Contr |  | FAR - Farringdon Station (West) |  | 2013-05-10 | 2013-05-02 09:28 | -8 | 2013-04-30 | Geotechnical Engineering - Compensation Grouting | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Grout cube taken from grout mix used to grout the back of Ring 4 at Grout Shaft 1 was damaged while being taken out of the mould as it wasn't set. Cube strength reached 0.8N/mm2 at 24 hours.
| 02SL - Stations (LUL) | Cxxx-NCR-000881 | NCR | WTH - Piling - Bentonite test temperature below 20 degrees Celsius |  | Contr |  | FAR - Farringdon Station (West) |  | 2013-05-31 | 2013-05-28 08:17 | -3 | 2013-04-30 | Civil - Geotechnical Engineering | 500 |  | Planning | Use As-Is |  | Complete |  | Completed |  | Bentonite on piles 101, 102, 212, 214, 217, 220 and 221 was tested with ambient temperature below 20°C.
| 02SL - Stations (LUL) | Cxxx-NCR-000884 | NCR | Nozzlemen competency demonstration in line with Works Information |  | Contr |  | FAR - Farringdon Station (West) |  | 2013-05-15 | 2013-05-17 16:04 | 2 | 2013-05-01 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Reject |  | Complete |  | Completed |  | As of 18:00 on 01/05/13, three nozzlemen (__, __ and __) had sprayed in two pilot tunnel advances. 1. __ sprayed TH1. He had not sprayed an overhead panel and therefore did not meet KT20.2107 c) or the Cxxx Nozzleman Assessment Document. 2. __ sprayed TH1a. He had not sprayed vertical and overhead panels at Farringdon however, Cxxx stated that he had done so on another CRL job. No evidence of this was provided (non-compliance with KT20.2107 c)). 3. __ sprayed sealing layer only. No relevant certificates of competency and training could be presented on request from CRL (non-compliance with KT20.2107 b) ii)) and he had not completed the written assessment (non-compliance with Cxxx QSP). __ had sprayed a vertical and overhead panel (nightshift 30/04/13) from which the cores were pending inspection. 4. The appropriate checks identified in the ITP, Cxxx--C4-ITP-M123-50002 Rev 3, were not carried out. 5. It should also be noted that the ITP check sheet records were requested to determine who had sprayed the pilot tunnel advances. These were not available and this was recorded as an unsatisfactory observation.
| 02SL - Stations (LUL) | Cxxx-NCR-000926 | NCR | ETH - Lindsey Street bridge blinding level |  | Contr |  | FAR - Farringdon Station (West) |  | 2013-06-07 | 2013-06-07 17:29 | 0 | 2013-05-15 | Civil - Concrete Pavement | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | The blinding layer in arches 2 and 3 is between 105 and 135mm thick and as a result the blinding level is high by 30 to 60mm.
| 02SL - Stations (LUL) | Cxxx-NCR-000928 | NCR | Grout Shaft - Class of concrete used in base |  | Contr |  | FAR - Farringdon Station (West) |  | 2013-05-23 | 2013-05-21 09:58 | -2 | 2013-05-16 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Class C30/37 concrete was used.
| 02SL - Stations (LUL) | Cxxx-NCR-000939 | NCR | Quality management system for concrete production |  | Contr |  | FAR - Farringdon Station (West) |  | 2013-06-28 | 2013-06-22 14:48 | -6 | 2013-05-21 | Tunnelling - Linings - Sprayed Concrete | 500 |  | System Defect | Rework |  | Complete |  | Completed |  | The concrete production quality management processes are not fully integrated into the Certified quality management system.
| 02SL - Stations (LUL) | Cxxx-NCR-000941 | NCR | Fluid Loss Not Brought To The Attention Of Crossrail |  | Contr |  | FAR - Farringdon Station (West) |  | 2013-06-21 | 2013-06-21 15:25 | 0 | 2013-05-21 | Tunnelling - Grouting | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | This incident occurred on 1st to 3rd May and this process was not followed as the incident was only brought the the attention of Crossrail on 5th May when a meeting was set up to discussion the issues associated with heave which occurred during TAM drilling
| 02SL - Stations (LUL) | Cxxx-NCR-000955 | NCR | SCL on site testing |  | Contr |  | FAR - Farringdon Station (West) |  | 2013-06-24 | 2013-06-21 16:16 | -3 | 2013-05-22 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Planning | Use As-Is |  | Complete |  | Completed |  | Pump Operators, Shift Engineers and Technicians who are doing testing in FAR are not trained by a person from UKAS accredited testing house. They are briefed to carry out tests according to BS/EN standards and procedures by Senior Materials Technician.
| 02SL - Stations (LUL) | Cxxx-NCR-000959 | NCR | CRL document control process failings |  | Contr |  | FAR - Farringdon Station (West) |  | 2013-06-05 | 2013-06-07 17:19 | 2 | 2013-05-23 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed |  | didn’t update the comments for the previous revisions for documents Cxxx-NRI-C-XCS-M123-50038 and Cxxx--C-XCS-M123-50468 didn't create the document relationship for the document Cxxx--C-RGN-M123-50298 entered incorrect eB document numbers for SNC to document Cxxx--C-RGN-M123-50328 and Cxxx--C-CCN-M123-50052 Incomplete CMDL metadata on eB for document Cxxx--C-XST-M123-50036 Non-compliant, incomplete or badly presented “messy” covers. (we will brief team ) Permissions for CRL Doc Cons omitted for document Cxxx--C-RGN-M123-50368 Comments Sheets not logged for documents sent For Acceptance to document Cxxx--U-GMS-M123-50026 No permissions for CRL DCs for comments sheets, so, not possible to populate or “drop” the needed file on eB for document Cxxx--C-XCS-M123-50629
| 02SL - Stations (LUL) | Cxxx-NCR-000962 | NCR | SRG Data and Trigger raising |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-07-01 | 2013-07-18 13:00 | 17 | 2013-05-22 | Surveying - Instrumentation and Monitoring | 500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete |  | Completed |  | Deflection of sheet pile wall in front of Lindsey Street Bridge caused amber breaches of targets 1, 3 and 4 on the 16/05/2013 and 3, 4 and 4a on 17/05/2013. The data was not presented at the SRG on 17/05/2013 and the relevant procedures detailed in Cxxx Action Plan (Cxxx--C-STP-M123-50109 Rev 2.0) were not followed.
| 02SL - Stations (LUL) | Cxxx-NCR-000963 | NCR | Varification of Cxxx prisms in Moorgate Spur |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-07-01 | 2013-07-18 14:19 | 17 | 2013-05-22 | Surveying - Instrumentation and Monitoring | 500 |  |  | Repair | 4 (0.5-3k) | Complete |  | Completed |  | have not provided manual verification of the Cxxx data in the Moorgate Spur (with the exception of Lindsey Street Bridge)
| 02SL - Stations (LUL) | Cxxx-NCR-000964 | NCR | Submission of Installation Reports |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-07-31 | 2013-07-31 13:23 | 0 | 2013-05-22 | Surveying - Instrumentation and Monitoring | 500 |  |  | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | The provision of installation reports and baseline reports for ground movement monitoring is significantly overdue. The same considerations applies to both instrumentation installed by and by others which has been hander over to Cxxx (from Cxxx) - in this case, a takeover report is required.
| 02SL - Stations (LUL) | Cxxx-NCR-000977 | NCR | The inclinometer at monitoring point T104 in the Eastern ticket Hall was damaged during pile break down on the 15th May. |  | Contr |  | FAR - Farringdon Station (West) |  | 2013-06-05 | 2013-06-06 11:04 | 1 | 2013-05-29 | Geotechnical Engineering - Grouting Instrumentation | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | The inclinometer was damaged during pile breakdown because the reservation tube was not de-bonded when the pile was constructed; the pile was constructed by the Advanced Works contractor Cxxx
| 02SL - Stations (LUL) | Cxxx-NCR-000986 | NCR | WTH - Piling - Concreting female piles without tremie |  | Contr |  | FAR - Farringdon Station (West) |  | 2013-06-15 | 2013-06-17 12:23 | 2 | 2013-05-31 | Civil - Geotechnical Engineering | 500 |  | Planning | Use As-Is |  | Complete |  | Completed |  | Method statement did not clearly state how female secant piles on a dry bore would be concreted. Pouring female pile no tremmie pipe was used. This is standard practice when pumping concrete into dry piles with no reinforcement but this was not included in the approved method statement. The piles are dry and have no reinforcement with dimensions 16.5m in length & 900mm of diameter). The concrete was brought to the pile via the Schwing 1250 pump with sieve at the point of discharge from the concrete wagon. The discharge into the pile was direct from the solid pipe 'L'Bend, from top of casing level (+106.5m).
| 02SL - Stations (LUL) | Cxxx-NCR-000987 | NCR | WTH - Piling - Pile 201 - Blocked base grouting tubes |  | Contr |  | FAR - Farringdon Station (West) |  | 2013-06-15 | 2013-06-17 12:26 | 2 | 2013-05-31 | Civil - Geotechnical Engineering | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | During 2nd cycle of base grouting on Pile 201, base grouting tubes got blocked. This was due to the grout finding a channel connecting the grouting ciruits and grout passing into an adjacent TAM. A grout packer got stuck in one tube and two tubes got blocked upon completion of two phases of grouting. As a result the completion of the second and 3rd phase of the Base Grouting could not be completed in line with the approved ITP to be completed >3hrs and <24hrs of completion of each circuit.
| 02SL - Stations (LUL) | Cxxx-NCR-000992 | NCR | Early strength tests - missing three hour tests |  | Contr |  | FAR - Farringdon Station (West) |  | 2013-06-21 | 2013-06-20 16:39 | -1 | 2013-06-03 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | For four advances (out of 6), the 3 hour test has not been performed up to 02/06/13. In 3 of the 4 instances, the test has been carried out at 4 hours. This is largely due to the strength of the HILTI cartridges (green cartridge) and the strength gain of the concrete at 3 hours i.e. the concrete being too weak to allow for a compliant test to be carried out with the green cartridge.
| 02SL - Stations (LUL) | Cxxx-NCR-000993 | NCR | Beam test - Fibre content and compressive strength of cores |  | Contr |  | FAR - Farringdon Station (West) |  | 2013-06-24 | 2013-06-20 16:26 | -4 | 2013-06-03 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | During the beam test on 11/05/13 only 4 cores where taken (as per ITP).
| 02SL - Stations (LUL) | Cxxx-NCR-000998 | NCR | Daily tunnel monitoring |  | Contr |  | FAR - Farringdon Station (West) |  | 2013-06-18 | 2013-06-19 09:44 | 1 | 2013-06-04 | Tunnelling - Linings - Sprayed Concrete | 500 |  | System Defect | Rework |  | Complete |  | Completed |  | Due to the commencement of the excavation of the advance Invert 14 shortly before the time of monitoring, access could not be gained to the pilot tunnel to record the data. This was a breakdown in the system. The importance of the daily monitoring was not sufficiently communicated to the site team. The sequencing of the work to facilitate these readings had not been investigated in sufficient detail as this particular sequence had not occurred before.
| 02SL - Stations (LUL) | Cxxx-NCR-001002 | NCR | ETH Procedural NCR working wihtout signed off prestart checklist |  | Contr |  | FAR - Farringdon Station (West) |  | 2013-06-26 | 2013-06-24 16:41 | -2 | 2013-06-05 | Civil - Civil Engineering General | 500 |  | Planning | Use As-Is |  | Complete |  | Completed |  | Excavation commenced down to Level -2 prior to official aproval of documentation
| 02SL - Stations (LUL) | Cxxx-NCR-001007 | NCR | ETH Procedural Non conformance - Started works without an accepted ITP |  | Contr |  | FAR - Farringdon Station (West) |  | 2013-06-20 | 2013-06-24 17:09 | 4 | 2013-06-06 | Civil - Excavation | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Excavation and deconstruction works commenced at South Basement Level 0 without having an accepted ITP.
| 02SL - Stations (LUL) | Cxxx-NCR-001008 | NCR | ETH Procedural Non conformance – No following MS and SAP sequence of works |  | Contr |  | FAR - Farringdon Station (West) |  | 2013-06-24 | 2013-06-21 11:06 | -3 | 2013-06-06 | Civil - Excavation | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | "MS and SAP sequence of work no followed on site and not briefed" Excavation and Demolition of retaining wall started without following the sequence of works
| 02SL - Stations (LUL) | Cxxx-NCR-001016 | NCR | ETH Non conformance – Damaging existing pile cages during breaking out activity for capping beam. |  | Contr |  | FAR - Farringdon Station (West) |  | 2013-06-25 | 2013-06-25 17:52 | 0 | 2013-06-10 | Civil - Demolition/Site Clearance | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed |  | have not taken care when breaking down the concrete of the existing secant piles and have damage the pile cages at South Basement high level, (photos attached). There was poor Supervision / Management and Workmanship and also Damaging of the existing rebar needed for construction of capping beams
| 02SL - Stations (LUL) | Cxxx-NCR-001020 | NCR | Pile Cap K reinforcement |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-07-04 | 2013-07-04 14:40 | 0 | 2013-06-11 | Structural Engineering - Reinforcement | 1500 |  | Damaged | Repair | 4 (0.5-3k) | Complete |  | Completed |  | The operative accidentally cut off 10 numbers of 40mm dia. rebars from one of the piles and 2 numbers of 40mm dia. rebars from another. The piles are part of pile cap K. PLease see the attcahed drawings for the locations and asbuilt.
| 02SL - Stations (LUL) | Cxxx-NCR-001021 | NCR | Damage to finish of Capping Beam Level -1 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-08-28 | 2013-08-28 18:16 | 0 | 2013-06-11 | Architectural - General | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete |  | Completed |  | Caping beam scratched during excavation beneath the beam by mechanical excavator. See photo attached
| 02SL - Stations (LUL) | Cxxx-NCR-001023 | NCR | In-Tunnel Monitoring not Carried Out |  | Contr |  | FAR - Farringdon Station (West) |  | 2013-06-25 | 2013-06-19 11:13 | -6 | 2013-06-11 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Monitoring bolts were installed at advance B27 at array locations M6 & M7, and base readings were taken on 08.06.13 - it was later noted that the data was corrupt when transferred on to the system. The surveyors should have carried out base line readings on 09.06.13, but these were missed due to communication issues, meaning the 1st monitoring was not carried out until 10.06.13 (2 days after installation).
| 02SL - Stations (LUL) | Cxxx-NCR-001024 | NCR | Incorrect Kwikastrip Installation |  | Contr |  | FAR - Farringdon Station (West) |  | 2013-06-25 | 2013-06-25 12:18 | 0 | 2013-06-11 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | 07.06.13 D/S - Kwikastrip has been installed to Advance 25TH at the joints between the bench and invert. The excavation level was low due to over-excavation, and therefore in order to install to the correct level the gang propped up the Kwikastrip using pieces of shotcrete / rubble. The covering engineer on shift at the time was less experienced than the regular shift engineer and this contributed to the inadequate profile control for the excavation sequence. Kwikastrip should of been placed directly on to the ground level - Note horizontal level of Kwikastrip can be adjusted by + / - 200mm.
| 02SL - Stations (LUL) | Cxxx-NCR-001027 | NCR | Early age strength tests every third advance |  | Contr |  | FAR - Farringdon Station (West) |  | 2013-07-05 | 2013-06-20 16:30 | -15 | 2013-06-11 | Tunnelling - Linings - Sprayed Concrete | 500 |  |  | Use As-Is |  | Complete |  | Completed |  | STW2 Pilot Between advance 1 and advance 5 of the Pilot there was a gap of 4 advances. In some of the advances all the required testing didn’t take place. In advance 5 no 3 hour test took place; in advance 6, no 1 hour test took place and in advance 8, no 3 hour test took place. In advance 27, no 3 or 6 hour test took place. STW2 Enlargement In advance 4, no 3 hour test took place; in advance 18, no 3 hour test took place and in advance 24, no 3 hour or 6 hour test occured instead a 5 hour test was done.
| 02SL - Stations (LUL) | Cxxx-NCR-001030 | NCR | STW2-PL1 - Minimum lining thickness not achieved - TH16 |  | Contr |  | FAR - Farringdon Station (West) |  | 2013-07-01 | 2013-06-25 12:37 | -6 | 2013-06-11 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Retrospective review of the recorded excavation profile for top heading 16 highlighted an area of under-excavation, between 1 o'clock and 3 o'clock, of up to 96mm. The spray vs excavation profile comparison raised concerns that the minimum lining thickness had not been achieved. Proof drilling proved that, in an area of approximately 1m squared, the minimum lining thickness had not been achieved by up to 120mm. This is contrary to the requirements of both the design drawing and the RESS. Cover Shift Engineer encountered difficulty in setting out excavtion profile due to unusual shape of tunnel at transition between STW2 and PL1. Proof drilling was required to determine if the issue was in the survey data recorded or actual under excavation.
| 02SL - Stations (LUL) | Cxxx-NCR-001032 | NCR | PMI 029 - Making of concrete cubes |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-07-23 | 2013-07-12 13:46 | -11 | 2013-06-12 | Utilities Engineering - Water | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not qualified | Completed |  | When repairing the section of the City Branch of the Fleet Sewer which was broken into in order to connect the hose for overpumping, 3 no. concrete cubes were taken on 04/06/2013. It was noticed that the concrete was poured to the top of the cube mould instead of doing it in 3 no. 50mm layers. Instead of compacting the layers with a steel tamping bar, the mould was picked up and dropped repeatedly for compaction.
| 02SL - Stations (LUL) | Cxxx-NCR-001033 | NCR | PMI 061 - Concrete cubes left uncovered |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-07-03 | 2013-07-12 13:14 | 9 | 2013-06-12 | Utilities Engineering - Water | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete |  | Completed |  | Concrete cubes were made on site on 05.06.2013 during the concrete pour of the thrust block in the north compound excavation and the concrete cubes were left uncovered on site.
| 02SL - Stations (LUL) | Cxxx-NCR-001034 | NCR | PMI 061 - Concrete cubes left uncovered |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-07-03 | 2013-07-12 13:16 | 9 | 2013-06-12 | Utilities Engineering - Water | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete |  | Completed |  | Concrete cubes were made on site on 11.06.2013 during the pour of the concrete roadbase in the south compound. The pour was done at night and the concrete cubes were left uncovered on site till the following morning.
| 02SL - Stations (LUL) | Cxxx-NCR-001040 | NCR | Data upload to UCIMS |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-07-19 | 2013-07-19 18:01 | 0 | 2013-06-14 | Surveying - Instrumentation and Monitoring | 500 |  |  | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Lack of procedure | Completed |  | The contractor have not been uploading data as per the afore-mentioned requirements. In some cases, UCIMS has not been updated since December 2012. This applies to all instrumentation (manual and automated data) being measured by the Cxxx contract.
| 02SL - Stations (LUL) | Cxxx-NCR-001042 | NCR | WTH - Crane set-up over backpropping underneath Caxton House Slab |  | Contr |  | FAR - Farringdon Station (West) |  | 2013-06-28 | 2013-06-18 09:00 | -10 | 2013-06-14 | Civil - Civil Engineering General | 500 |  | Design | Rework |  | Complete |  | Completed |  | operating outside of the approved Forms 2 & 3 designs (Cxxx--C-XST-M123-50030 & Cxxx--C-CER-M123-50069). Crane outrigger mat not directly over the as-built backpropping.
| 02SL - Stations (LUL) | Cxxx-NCR-001047 | NCR | ETH - Placing of insitu concrete from greater than 2m |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-07-01 | 2013-07-04 12:01 | 3 | 2013-06-17 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Concrete was placed in capping beams D & F using a pump. The bottom of the tremmie pipe was located around 3.3m to 3.6m above the base of the pour during concreting
| 02SL - Stations (LUL) | Cxxx-NCR-001049 | NCR | ETH Level 0 - 1.2m dia. piles starter bars |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-07-04 | 2013-07-10 18:59 | 6 | 2013-06-17 | Structural Engineering - Reinforcement | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete |  | Completed |  | The 32mm dia. starter bars for 1.2m dia. pile caps K& L have been cut off below the lifting band leaving 1.4m long starter bars protruding into the pile cap. Eurocode requires an anchorage of 43 x bar dia – equates to 1376mm for 32mm dia bar.
| 02SL - Stations (LUL) | Cxxx-NCR-001050 | NCR | ETH Damaged inclinometer |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-08-16 | 2013-08-15 17:17 | -1 | 2013-06-17 | Geotechnical Engineering - Ground Investigation | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | In the process of breaking down piles, the inclinometer in pile no. B308 was pierced as shown in the attached photo.
| 02SL - Stations (LUL) | Cxxx-NCR-001053 | NCR | ETH Pile Starter bars in Two Storey Basement |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-07-04 | 2013-07-10 18:52 | 6 | 2013-06-17 | Structural Engineering - Reinforcement | 3500 |  | Damaged | Repair | 3 (3-6k) | Complete |  | Completed |  | In the process of re-bending the rebars on site using the proprietary bending machine, some of the rebars damaged beyond repair.
| 02SL - Stations (LUL) | Cxxx-NCR-001058 | NCR | PMI 029 - Break out of sewer in wrong location |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-07-19 | 2013-07-16 12:36 | -3 | 2013-06-19 | Utilities Engineering - Water | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | During the works carried out on the City Branch of the Fleet Sewer, an overpumping system had to be set up in order to remove and replace the circular section of the City Branch of the Fleet sewer. Due to the inadequate information gathered from the CCTV survey, trial holes and Works Site Information provided by __, the sewer was broken into in the wrong location at the downstream end.
| 02SL - Stations (LUL) | Cxxx-NCR-001061 | NCR | Installation of shallow datum 2 without an approved ITP |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-07-17 | 2013-07-05 15:11 | -12 | 2013-06-19 | Surveying - Instrumentation and Monitoring | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Lack of procedure | Completed |  | Shallow datum 2 in Cowcross street was installed without an approved ITP from CRL. The ITP is currently on eB.
| 02SL - Stations (LUL) | Cxxx-NCR-001062 | NCR | Tunnel Safety Card |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-10-25 | 2013-10-24 16:27 | -1 | 2013-06-19 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Reject | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | Not all of the employees who are entering SCL tunnels in Farrington have Tunnel Safey Card.
| 02SL - Stations (LUL) | Cxxx-NCR-001068 | NCR | Structural Fibre Performance - failure of beam specimens |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-08-22 | 2013-08-19 17:09 | -3 | 2013-06-23 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Three beam specimens (Site Ref. FAR17-1, FAR17-2, FAR17-3) were tested in accordance with BS EN 14651 with the aim of achieving the requirements in (1) above. All three test specimens achieved the required strength for D1S1.8 (D1 as described in (4) above). However, all three test specimens failed to achieve the required strength for D3S1.4 (D3 as described in (4) above). The rate of increase of Crack Mouth Opening Displacement (CMOD) for FAR17-1, 2 and 3 was noted as 0.00379mm/s, 0.00417mm/s and 0.00331mm/s respectively. The test report indicates that the rate of increase was much faster and the method not as described in (2) above. All three specimens did not comply with (3) above (residual strengths were less than 1.26MPa i.e. 10% less than the required 1.4MPa).
| 02SL - Stations (LUL) | Cxxx-NCR-001074 | NCR | Fibre quantity and wash out tests |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-08-23 | 2013-08-23 11:41 | 0 | 2013-06-24 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Not Defined | Completed |  | 1. Most of the times only one washout has been taken instead of three. 2. During enlargement advances 19-33 (108 m3) no wash outs where taken. 3. Fibre content was less than 80 % of the desing fibre content on (min 28 kg/m3) 04/05/13 result was 27.4 kg/m3. 28/05/13 result was 25.7 kg/m3. 17/06/13 result was 26.1 kg/m3.
| 02SL - Stations (LUL) | Cxxx-NCR-001075 | NCR | Early Strength testing - missing test and low results |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-08-22 | 2013-08-22 18:00 | 0 | 2013-06-24 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | 1. Tests have not done for every third advance. 2. Tests have been missed for different ages. 3. Instead of three hour four hour test have been done. 4. Test results have been low. Tables with missing information attached to the NCR.
| 02SL - Stations (LUL) | Cxxx-NCR-001081 | NCR | Modulus of elasticity |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-08-18 | 2013-08-15 21:16 | -3 | 2013-06-25 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | Tests have been done for 1 day and 32 days (instead of 28 days).
| 02SL - Stations (LUL) | Cxxx-NCR-001083 | NCR | ITP Low Early Strengths from 5% Accelerator Dose |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-08-07 | 2013-08-07 16:01 | 0 | 2013-06-26 14:30 | Tunnelling - Linings - Sprayed Concrete | 500 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | When applying SCL around reinforcement it is good practice to lower the accelerator dose and spray slowly and evenly in order to mitigate against 'shadowing' behind bars. This approach was taken when spraying at the CPI Junction with PL1. However, because of the low dosage used (5%), the early strength targets required under the current ITP were not achieved. A note was made in the ITP to highlight the reason for the low strengths as above.
| 02SL - Stations (LUL) | Cxxx-NCR-001084 | NCR | ETH - Concrete Cubes left uncovered on site |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-08-28 | 2013-08-16 13:44 | -12 | 2013-06-26 17:50 | Structural Engineering - Concrete Member | 500 |  | System Defect | Rework | 4 (0.5-3k) | Complete |  | Completed |  | Cubes where left uncovered on site in contradiction to clause KF10.2204(m) which states the cubes should be cured in a maner identical to the concrete in the works. Cubes left in moulds for greater than 3 days in contradiction to BSEN12390-2 Cubes were for the thurst block pour Cast on Friday 21/6/13 picked up 26/6/13. Mould numbers 102,209,22and 69
| 02SL - Stations (LUL) | Cxxx-NCR-001085 | NCR | ETH - Procedural Non Conformance control of reinforcement drawings |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-07-11 | 2013-07-16 17:24 | 5 | 2013-06-27 16:35 | Structural Engineering - Reinforcement | 500 |  | System Defect | Rework | 4 (0.5-3k) | Complete |  | Completed |  | The reinforcement drawings being used on site for the Level 0 capping beams were not approved by crossrail. The drawings were developed by __ and issued unofficially to site to allow progress prior to the issuing of PMI 138 which includes changes to the capping beams. The site team were using the drawings to mitigate the delay caused by the late design changes.
| 02SL - Stations (LUL) | Cxxx-NCR-001086 | NCR | WTH - Piling - PIle 212 - Out of Tolerance |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-07-31 | 2013-07-23 10:40 | -8 | 2013-06-28 08:53 | Civil - Geotechnical Engineering | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | Civil and Struct Specification specifies bored pile tolerance as 25mm in plan, 1:200 verticality. Pile S212 was installed to verticality of 1:194.4 and plan position to 9mm. Several attempts were made to install the casing to tolerance but small osbtructions in the ground prevented this from happening.
| 02SL - Stations (LUL) | Cxxx-NCR-001088 | NCR | Thickening layer rebar encapsulation |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-08-16 | 2013-08-07 12:24 | -9 | 2013-06-28 14:28 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Due to additional splicing of reinforcement at CP1, which was carried out because of incorrect steel length; coring was required to confirm the spraying of this spliced connection was carried out satisfactorily and that no shadowing was evident - This was done and accepted. Additional cores were also carried out on the mesh installation around CP1, which highlighted shadowing, encapsulation and lamination in localised areas.
| 02SL - Stations (LUL) | Cxxx-NCR-001089 | NCR | KWIKASTRIP JOINTS AT STW2/PL1 ENLARGEMENT |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-08-05 | 2013-08-02 16:04 | -3 | 2013-06-28 17:17 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Information not detailed | Completed |  | Cores were taken through the Kwikastrip joints to confirm application of SCL was adequate as required by KT20. 3No. cores were initially carried out, 2 of which were in good condition, but 1 was shown to be poor with shadowing / minor encapsulation present. In the RESS Meeting held on 26th of June, it was requested cores at joint locations between Top Heading and Bench, and Bench and Invert. 3 Cores were taken on the RHS of the STW2/PL1 Enlargement at joint locations on the eye for CP1 Breakout. After visual inspections, and according to RESS Minutes from RESS Meeting held on 27th of June, rebound and shadowing was encountered in one core situated at the joint between Top Heading and Bench. It can be stated that advances where the cores reflected bad workmanship were bench 31 and bench 35 of the STW2/PL1 Enlargement. At that stage, core register was not set up, therefore it cannot be stated an accurate level and chainage. As an action from this NCR, core register is being used to record any defect and proof quality of lining.
| 02SL - Stations (LUL) | Cxxx-NCR-001092 | NCR | Failure to produce Calibration Certificated for HDAD |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-07-31 | 2013-07-31 10:07 | 0 | 2013-07-01 15:41 | Geotechnical Engineering - Compensation Grouting | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | __ were unable, when asked, to produce a valid calibration Certificate for the HDAD equipment used in the checking of completed Tams.
| 02SL - Stations (LUL) | Cxxx-NCR-001093 | NCR | Failure to produce user Manual for HDAD |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-08-02 | 2013-07-31 11:56 | -2 | 2013-07-01 15:51 | Geotechnical Engineering - Compensation Grouting | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Geosica were unable, when asked, to produce a users manual for the HDAD testing equipment being used on completed Tams
| 02SL - Stations (LUL) | Cxxx-NCR-001095 | NCR | ETH - Pile B305 broken down further than allowable tolerance |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-08-12 | 2013-07-30 19:04 | -13 | 2013-07-04 08:14 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | Pile B305 was brocken down approximately 70mm below cut off level. Photo attached
| 02SL - Stations (LUL) | Cxxx-NCR-001096 | NCR | Primary project control survey checks |  | Crossrail | PDP | FAR - Farringdon Station (West) |  | 2013-09-17 | 2013-09-18 14:53 | 1 | 2013-07-05 06:37 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | No evidence was made available during surveillance QS435-03 to demonstrate that the Contractor had carried-out his own checks on the supplied control points and submitted a report on his findings within 6 weeks of the relevant access date to the CRL Project Manager as required by Works Information clause 6.2.3. In addition no evidence was made available with respect to the establishment and implementation of an acceptable checking frequency of Contractor established controls back to the primary project controls, as specified by Works Information clauses 6.3.2 & 6.3.
| 02SL - Stations (LUL) | Cxxx-NCR-001097 | NCR | Concrete temperature too high (more than 35 C) |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-07-31 | 2013-08-01 10:04 | 1 | 2013-07-05 08:03 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper storage of material | Completed |  | KT20.3206 part B - The temperature of the wet mix concrete shall be between 15°C and 35°C at all times during batching, delivery and at the point of spray application. The temperature at advance 4 was recorded as being 32 degs at the point of spraying (tested in the hopper of the __ __ robotic sprayer), when spraying commenced. The line was kept live while excavation was completed, then due to concrete sitting in the line, coupled with being an axceptionally hot day, the temperature at the POCA reached 37 degs when checked prior to spraying the sealing layer. The maximum allowable termperature was 35 degs. As the sealing layer was only temprary works, and the face needed to be sealed this was used, but only in this area - No permanent works concrete was sprayed with this mix. Prior to spraying the primary lining, the line was cleared, and the water tank drawined / refilled with cool water. The lining was then sprayed and temperature recorded as being 32 degs, and acceptable.
| 02SL - Stations (LUL) | Cxxx-NCR-001099 | NCR | TaM TM2091 - Length, Short of Design |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-08-31 | 2013-08-08 19:20 | -23 | 2013-07-05 15:58 | Geotechnical Engineering - Compensation Grouting | 500 |  | Design | Rework | 4 (0.5-3k) | Complete |  | Completed |  | Obstruction encountered in Tams TM2091 requiring the termination of drilling activity. These obstructions were not pre-empted nor have they been identified to date. The repercussions of which are that Tam TM2096 is 1.5 m short of design length 57.5 TM2091 56 of 57.5m (-1.5m)
| 02SL - Stations (LUL) | Cxxx-NCR-001100 | NCR | WTH - Piling - Pile 215 - Concreting after 24h of removal of last 4m of bore |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-07-30 | 2013-07-30 13:04 | 0 | 2013-07-09 12:06 | Civil - Geotechnical Engineering | 500 |  | Equipment Breakdown | Use As-Is | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | FCD 473, revising Specification Clause KP10.1205, establishes that excavation of the last 4 metres of pile should take place on the day of concreting. For pile 215 this is was not followed. Concreting started 25 hours after removal of the 4m plug on the 4/7/13.
| 02SL - Stations (LUL) | Cxxx-NCR-001102 | NCR | TaM TM2087 - Length Short of Design |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-08-31 | 2013-08-08 19:14 | -23 | 2013-07-05 16:12 | Geotechnical Engineering - Compensation Grouting | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Obstruction encountered in Tams TM2087 requiring the termination of drilling activity. These obstructions were not pre-empted nor have they been identified to date. The repercussions of which are that Tam TM2087 is 3m short of design length 69 TM2087 66 of 69m (-3m)
| 02SL - Stations (LUL) | Cxxx-NCR-001103 | NCR | Flow Test Done Incorrectly |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2013-07-19 | 2013-07-19 15:22 | 0 | 2013-07-05 17:21 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Durring a surveillance of flow testing of concrete it was observed that the person was not doing the flow test was not doing it as per specification
| 02SL - Stations (LUL) | Cxxx-NCR-001104 | NCR | Insufficient communication |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-07-19 | 2013-07-19 16:03 | 0 | 2013-07-05 17:25 | Geotechnical Engineering - Compensation Grouting | 500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | have insufficient systems in place in order to provide CRL with accurate and timely information with regard to tam drilling and installation
| 02SL - Stations (LUL) | Cxxx-NCR-001105 | NCR | WTH - Pile 203 concrete out of tolerance |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-07-26 | 2013-07-25 08:39 | -1 | 2013-07-09 08:37 | Civil - Civil Engineering General | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | During the concrete pour for pile 203, the last 5 loads exceeded the 2 hours limit from time of batching to completion of discharge (Under Clause KF10. 3202 of the specification). Loads 817457, 811976, 817458, 811978 and 817460 were batched at 17:36, 17:46, 18:06, 18:06 and 18:23, started discharging at 19:30, 19:45, 20:06, 20:25, 20:42 and completed discharge at 19:39, 19:55, 20:18, 20:34 and 20:53, respectively.These loads were tested prior to discharge with a flow between 530 and 570 mm. (See table attached) The concrete supplier experienced difficulty in one of its batching plants and to supplement used the approved back up plant. As a result due to cross communication between plants some loads arrived at the same time resulting in delay in pouring. Once the volume had been batched the batcher closed the plant. As the supervisor needed to bring concrete to above cut off level and the batched volumes were still in spec with regards to material testing this was deemed the best course of action as opposed to a cold joint and potential contamination with bentonite.
| 02SL - Stations (LUL) | Cxxx-NCR-001106 | NCR | On site testing |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2013-07-23 | 2013-07-15 12:02 | -8 | 2013-07-09 15:33 | Utilities Engineering - Water | 500 |  | System Defect | Reject | 4 (0.5-3k) | Complete |  | Completed |  | All on site and off site testing shall be carried out by laboratories accredited by UKAS or similaraccepteable National Body or by persons accredited to a similar standard. The samples shall be taken by staff appointedby the laboratory. The requirement for for UKAS Accreditation may be waived for the testing of systems and their components, subject to an alternative testing proposal by the Contractor and the acceptance of the proposal by the Project Manager. This relate to slump & flow testing and the making of the concrete cubeS on site
| 02SL - Stations (LUL) | Cxxx-NCR-001107 | NCR | ETH - Level 0 Capping Beams Bar Cracked during pile breakdown |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-08-28 | 2013-08-13 13:12 | -15 | 2013-07-10 18:06 | Civil - Civil Engineering General | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | A starter bar in pile B126 was cracked during pile breakdown damageing the structural integrity of the reinforcement bar. Photo attached
| 02SL - Stations (LUL) | Cxxx-NCR-001108 | NCR | ETH - Piles B122, B126 & B124 cracked below cut off level |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-08-12 | 2013-08-13 17:50 | 1 | 2013-07-10 18:16 | Civil - Civil Engineering General | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | Piles B126 & B124 have been cracked below cut off level during breakdown down of the piles. See photos attached
| 02SL - Stations (LUL) | Cxxx-NCR-001109 | NCR | Issues with early strength during spraying of TH9 at CP1 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-08-14 | 2013-08-15 21:15 | 1 | 2013-07-11 00:25 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | While spraying the Advance 9TH as part of CP1 (Cross Passage 1) construction on 03.07.13 back shift, the early strengths were unusually high. The compressive strength measured using a penetrometer reached 0.53N/mm2 after only 10 minutes which is a typical result of the 1hr strength, and at 1 hr a penetrometer test was unable to be carried out implying that the compressive strength was greater than 1N/mm2 (which is the max measureable with the penetrometer). We identified a problem with the POCA display, therefore we could not accurately determine the accelerator dosage. it can be assumed that it was too high due to the strengths.
| 02SL - Stations (LUL) | Cxxx-NCR-001110 | NCR | 28 day flexural strength beam test failed due to quality of concrete spray |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-02-28 | 2014-02-04 12:15 | -24 | 2013-07-11 01:27 | Tunnelling - Linings - Sprayed Concrete | 55000 |  | Material | Use As-Is | 2 (6-60k) | Complete | Material/Preservation Problems - Not Defined | Completed |  | Test panel was sprayed on 11.06.13 for Advance 33TH of the STW2 Enlargement works. Flexural beams were taken and sent to __ ('s UKAS accredited testing house) to carry out flexural strength beam testing. Beams failed 28 day testing, and a layer of rebound was evident along the side of the beam. The 90 day beams were tested at 29 days and one out of three of these failed.
| 02SL - Stations (LUL) | Cxxx-NCR-001111 | NCR | SCL early strength testing |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-08-07 | 2013-08-07 17:57 | 0 | 2013-07-11 04:19 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Other human error | Completed |  | Minimum spacing between each nail for early strength testing as part of SCL requirements should be 80 mm. When carrying out testing on advance 24 of CP1 this was not adhered to and spacing in places were reduced to 50 mm.
| 02SL - Stations (LUL) | Cxxx-NCR-001112 | NCR | Probing at CH9.700 - Not achieving the required probe length due to obstructions |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-08-07 | 2013-07-26 17:12 | -12 | 2013-07-11 14:27 | Tunnelling - Tunnelling General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | During the course of the probing works carried at CP1 CH9.7 TH15 a number of obstructions were encountered preventing full penetration of probe references PP3, PP5, PP7 and PP9.
| 02SL - Stations (LUL) | Cxxx-NCR-001113 | NCR | Thermometers used to measure concrete temperature on site not having ID numbers on them |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2013-07-26 | 2013-07-26 08:16 | 0 | 2013-07-11 17:24 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | During a surveillance being done on thermometers it was noted that there were no identification markings on any of the the thermometers which are used to measure the temperature of the concrete and also the the thermometer in the tunnel.
| 02SL - Stations (LUL) | Cxxx-NCR-001114 | NCR | Outstanding MCR for grout used to backfilled cores at STW2/PL1 Enlargement and CP1 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-08-07 | 2013-08-09 15:26 | 2 | 2013-07-11 15:06 | Tunnelling - Tunnelling General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | It was requested on the RESS meeting to backfill the cores taken from the lining at STW2/PL1 Enlargement and CP1. Approximately 15no. cores were backfilled with an appropiate material following manufacturer's instructions, but no MCR was submitted for approval as per KT20 Specification.
| 02SL - Stations (LUL) | Cxxx-NCR-001115 | NCR | Failure to Inform Project manager of required waiverfrom Clause |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-08-08 | 2013-08-08 17:03 | 0 | 2013-07-11 16:17 | Geotechnical Engineering - Compensation Grouting | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | On discovering that Clause 20.12 of the Works information 2B was not fully conformable failed to contact the Project Manager to request a waiver to the clause. The Clause states that "All on-site and off-site testing shall be carried out by Laboratories accredited by UKAS or similar, acceptable national body or by persons accredited to a similar standard. The samples shall be taken by staff appointed by the Laboratory, the requirements for UKAS accreditation may be waived for the testing of systems and their components, subject to an alternative testing proposal by the contractor and the acceptance of the proposal by the project manager" Although External testing of cube strength is being conducted by a UKAS approved Company, on-Site testing of Viscocity, Flow, and Bleed are not. This is due to the fact that there are no companies in the UK accredited by UKAS for these tests. did however employ a UKAS accredited Company to train site operatives to best practice for testing Grout on SIte.
| 02SL - Stations (LUL) | Cxxx-NCR-001117 | NCR | Inclinometer at monitoring point Cxxx-IM-B313 had to be extended above the reinforcement for the capping beam |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-07-26 | 2013-07-26 16:34 | 0 | 2013-07-12 09:47 | Geotechnical Engineering - Geotechnical Monitoring | 500 |  | System Defect | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Inclinometer monitoring point Cxxx-IM-B313, constructed by the Advanced Works contractor, was not installed to allow the top of the reservation tube and inclinometer casing to extend above the top of the Cxxx design capping beam.
| 02SL - Stations (LUL) | Cxxx-NCR-001120 | NCR | Calibration of testing equipment and maintenance of schedule |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2013-10-08 | 2013-10-04 13:00 | -4 | 2013-07-17 14:59 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | During recent surveillances carried out by CRL SCL Field Engineers it was noted that are not maintaining a schedule of all inspection, measuring and test Equipment used for the works which should include records of the calibration of Equipment to nationally recognised standards. Calibration records were not available for inspection and identifiable serial numbers were missing from testing equipment. It was also noted that Calibration Procedure failed to include SCL testing equipment i.e. MEYCO Penetrometers, __ DX450SCT and __ HAT28/C.
| 02SL - Stations (LUL) | Cxxx-NCR-001121 | NCR | Training SCL personnel for on-site early strength testing |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2013-08-22 | 2013-08-16 19:46 | -6 | 2013-07-13 16:20 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Training Deficiency - No training provided | Completed |  | Training to the relevant British Standards has not been carried out in full for all the personnel required to undertake on-site testing. The training matrix (Cxxx--C4-LST-M123-50003) submitted 09/07/13 shows that 2 of the 7 engineers (none of which are the 4 shift engineers) required to carry out testing has been trained for the needle penetrometer and HILTI stud driving test. CRL FE __ carried out a surveillance on the needle penetrometer test on 23/06/13 (Cxxx-XRL-O4-RGN-M123-50002). This report found that one of the shift engineers had been carrying out the needle penetrometer test incorrectly. Training records were requested but could not be provided. Subsequently, the training matrix mentioned above show that this engineer had not been trained. The training booklet supplied to the engineers was scrutinised during this surveillance. The booklet did not align directly with BS 14488-2 – the importance of a perpendicularly applied force to the substrate was omitted as well as zeroing the gauge on the penetrometer prior to applying the force. The relaxation of the works information requirements through FCD-000897 was accepted on the proviso that training would be given to all relevant parties. This has not been carried out sufficiently.
| 02SL - Stations (LUL) | Cxxx-NCR-001122 | NCR | WTH pile 202 Geothermal loop |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-08-08 | 2013-08-08 07:27 | 0 | 2013-07-18 18:27 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | One of the valves of geothermal loop in pile 202 was unable to be extended above concrete casting level due to insufficient length of pipe installed at the fabrication stage. This fact affects directly the flow test that must be done after pouring as the valve is covered in concrete preventing the flow test from being carried out. All previuos test were succesful. See pictures attached. The 24hr pressure test has still been maintained and was successful - suggesting no damage to the pipe during concreting.
| 02SL - Stations (LUL) | Cxxx-NCR-001123 | NCR | ETH - Low cover to rebar in LSB pier 3/4 slab |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-08-28 | 2013-08-28 18:04 | 0 | 2013-07-15 17:36 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | The concrete cover to some of the rebar in bays 1 and 3 of LSB pier 3/4 is below the minimum specified on the temporary works drawings.
| 02SL - Stations (LUL) | Cxxx-NCR-001126 | NCR | WTH SHW2 wrong contain of cement in the foam concrete base mix |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-08-23 | 2013-07-29 13:56 | -25 | 2013-07-15 19:17 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | The base mix of the foamed concrete poured in the SHW2 shaft contained 350kg/m3 of cement instead of the 445kg/m3 specified in the P445 concrete mix design. The delivery tickets for the first five loads showed that the mix delivered was P445. As soon as were made aware of this error, which was highlighted by __ who were managing the pour, the pour was stopped immediately and all the concrete wagons were refused and sent away. In total around 50m3 of foamed concrete was poured using the incorrect mix. The maximum height of the concrete placed is between 150 and 200mm. (see attached photos) __ has indicated that 1 N/mm2 at 28 days strength is expected to be achieved by the foamed concrete poured. 6no. cubes were taken in order to assess the strength that the foamed concrete will achieve. They will be tested at 3, 7 and 28 days.
| 02SL - Stations (LUL) | Cxxx-NCR-001127 | NCR | ETH Possible cold joint on Capping Beam K |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-08-28 | 2013-08-28 18:07 | 0 | 2013-07-16 14:10 | Structural Engineering - Structural Engineering - General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper handling of material | Completed |  | A possible cold joint appeared on the western face of the pile cap K upon removal of the formwork.
| 02SL - Stations (LUL) | Cxxx-NCR-001128 | NCR | ETH Making good on Pile cap K |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-08-28 | 2013-08-28 18:10 | 0 | 2013-07-16 14:22 | Structural Engineering - Finishes | 500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | Small amount of remedial works were completed on capping beam K prior to the process being agreed with the Field Engineers.
| 02SL - Stations (LUL) | Cxxx-NCR-001129 | NCR | Over-Excavation of Advance CP1 B/I 37 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-08-07 | 2013-07-26 17:33 | -12 | 2013-07-16 17:01 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | During the excavation of CP1 advance Bench Invert 37 it was found that an open excavation of approximately 3m was exposed on the left hand side of the advance. As the current RESS showed the advance length as 2.15m, the Shift Engineer and Engineering Inspector raised concerns and stopped the excavation. It was then found by checking the exposed spray leading edge from the previous Bench Invert 34 that it had been sprayed short. During the completion of the advance B/I 37 a number of contributing factors were found: 1) While the excavation and sealing of B/I 34 were completed as per the RESS chainages, the primary was brought up vertically from the leading edge at the bottom of the invert. Due to the inclined nature of the B/I advances this lead to a reduced primary lining wall at the top of the advance. 2) Once excavation commenced on B/I 37, the sealing layer ahead of the leading edge on B/I 34 was broken as is normally the case. This increased the open side wall by approximately 0.5m at the top of the advance. 3) Shift Engineer set out chainage lead marks and started excavator operator on excavation of advance as per RESS on RHS and left face to undertake production testing. When he returned, the excavator operator had pulled the bucket from RHS to LHS inaccurately creating an over excavation on the LHS of approximately a further 0.35m. These factors combined created the 3m, or 0.85m over-dig at advance B/I 37.
| 02SL - Stations (LUL) | Cxxx-NCR-001130 | NCR | SHW2 foam concrete density out of specification |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-08-16 | 2013-08-14 16:05 | -2 | 2013-07-17 14:59 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | The P445 foam concrete used to backfill the SHW2 shaft was pumped using a M52 mobile pump. Due to the pumping pressures, the density of the foam concrete at the bottom of the shaft was greater than the density of the foam concrete discharged in the mobile pump hopper. As expected, it took several loads for the __ technicians to work out the correct quantity of foaming agent to be added to the base mix. Because of this, the density of several loads poured on 16th and 17th of July were therefore out of specification. The density is highlighted in the foam concrete placement site control record sheets attached
| 02SL - Stations (LUL) | Cxxx-NCR-001131 | NCR | ETH - Lap length of BM 5 capping beam M |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-07-31 | 2013-07-30 16:51 | -1 | 2013-07-17 13:45 | Structural Engineering - Reinforcement | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On inspection the lap length of BM5 at the location on the attached sketch was 1900mm as opposed to the 49 x dia = 1960mm as specified. __ were contacted as the bars were at a stage were it could not be adjusted. They have stated they design on a lap length of 1925mm and as such approval is required from Cxxx for the reduced lap length.
| 02SL - Stations (LUL) | Cxxx-NCR-001133 | NCR | BFK were unable to produce complete drilling records on request by CRL. |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-08-14 | 2013-08-08 17:13 | -6 | 2013-07-17 17:04 | Geotechnical Engineering - Compensation Grouting | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete |  | Completed |  | were unable to produce complete drilling records on request by CRL. Although some records have been made available, for information, throughout production, were unable to present submitable documentation in a timely manner as stated in Clause 20.2.
| 02SL - Stations (LUL) | Cxxx-NCR-001134 | NCR | Installation of PVC Drainage pipes within Arch 2-LSB without MCR being approved |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-07-31 | 2013-07-31 19:57 | 0 | 2013-07-17 18:08 | Civil - Civil Engineering General | 500 |  | Material | Rework | 4 (0.5-3k) | Complete |  | Completed |  | MH 2 was constructed and 110mm dia. PVC sockets were installed during the construction. Also a 250mm dia. pipe was installed in vault 3, in a process of repairing the existing drainage prior to installing the RC slab rebar for bay1 of pier 1/2(S). work was stopped on 16/07/13. The works were carried out while the MCRs were still under review. MCRs were submitted on 16/07/2013 to CRL for approval.
| 02SL - Stations (LUL) | Cxxx-NCR-001135 | NCR | Incorrect Kwikastrip Installation CP1 Adv. TH33 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-08-07 | 2013-08-07 17:01 | 0 | 2013-07-17 18:24 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the excavation of CP1 Bench Invert 37, whilst pulling down the Kwikastrip reinforcement bars to align for the connection, it was found that the bars were at the incorrect spacing. On closer examination it was found that the __ Kwikastrip was type M17S, rather than M22S. Type M22S is required in lining walls greater than 3000mm in design thickness. As the CPI primary lining wall at this chainage is 350mm this is a non conformance. Please refer to material compliance record Cxxx--C4-LRC-M123-50016 to clarify the difference between __ M17s & M22s.
| 02SL - Stations (LUL) | Cxxx-NCR-001136 | NCR | Failure to Record Pull Out Testing CP1 Adv. TH36 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-08-16 | 2013-08-12 21:32 | -4 | 2013-07-17 19:25 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | At the end of spraying the primary lining at advance CP1 Top Heading 36 a steel panel was sprayed for pull out testing in line with the requirement for every third advance to be tested as stated in the SCL Inspection and Test Plan Cxxx--C4-ITP-M123-50013. However, during the excavation of the following advance Bench Invert 37 the panel was accidentally destroyed. As the current advance was a Bench Invert, access to the lining wall was not safe to record the testing in situ. The results for the 4 hour, 6 hour and 12 hour pull out testing were therefore not recorded.
| 02SL - Stations (LUL) | Cxxx-NCR-001137 | NCR | ETH Pile no. B122 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-08-01 | 2013-07-30 19:03 | -2 | 2013-07-18 17:39 | Civil - Structural Engineering | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Insufficient information made available to the worker. | Completed |  | The pile number B122 at the south side of the Two Storey Basement has been cropped down to the blinding level, leaving no upstand.
| 02SL - Stations (LUL) | Cxxx-NCR-001138 | NCR | ETH Scaffolding tube left in the pile cap K |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-08-28 | 2013-08-28 18:18 | 0 | 2013-07-26 11:18 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete |  | Completed |  | A length of scaffolding tube used as an edge protection on top mat steel was cast in pile cap K2 (the upstand).The length of the tube left in the concrete is believed to be approximately 500mm.
| 02SL - Stations (LUL) | Cxxx-NCR-001139 | NCR | WTH Pile 202 Construction Time |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-08-06 | 2013-08-08 13:33 | 2 | 2013-07-18 18:38 | Civil - Civil Engineering General | 500 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | Pile 202, time period between commencement of excavation past casing and completion of placement of concrete exceeded the timeframe of FCD 00473 (amendment of clause KP10.1205.j.ii)
| 02SL - Stations (LUL) | Cxxx-NCR-001140 | NCR | ETH - Procedural- Bars found missing in Capping Beam Pre pour inspection |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-08-16 | 2013-08-12 17:47 | -4 | 2013-07-19 17:24 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete |  | Completed |  | During the pre pour inspection with crl field engineer 6 no coupled bars where missing. Bars were installed follwoing inspection and prior to concreting
| 02SL - Stations (LUL) | Cxxx-NCR-001141 | NCR | ITP Intervention Point Not Being Followed |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2013-09-27 | 2013-09-25 16:57 | -2 | 2013-07-19 19:28 | Tunnelling - Grouting | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | During a surveillance done on the DAD (Deviation after drilling) Survey activity of the TAMs installed in Grout Shaft 2, it was noticed that sleeve grouting was done shortly after DAD was finished. On the ITP Cxxx--C-ITP-50077 it shows this is a Hold Point and a CRL Review Point and this means that have to satisfy themselves that the Parameters listed in the ITP have been meet before they proceed to the next activity which is sleeve grouting and this is not being done on site.
| 02SL - Stations (LUL) | Cxxx-NCR-001142 | NCR | ETH - Procedural - Ducts for geothermal pripes cast into capping beam without approval |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-08-16 | 2013-08-12 10:34 | -4 | 2013-07-23 15:37 | Structural Engineering - Concrete Member | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | Ducts have been cast into a capping beam in the south of the trapezoidal shaft for the geothermal pipework inline with Cxxx-FCD-001093. The FCD was not closed out prior to casting the beam.
| 02SL - Stations (LUL) | Cxxx-NCR-001143 | NCR | Core Quality at CP1 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-02-28 | 2014-02-04 12:16 | -24 | 2013-07-23 17:55 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Workmanship | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A range of cores taken from the SCL primary lining at CP1, 3 of which were of poor quality, showing signs of shadowing and lamination. These 3 were taken at CH 6.65 (Core 2), 19.072 (Core 7) & 29.144 (core 9). Please see attached CP1 core report detailing the above defects.
| 02SL - Stations (LUL) | Cxxx-NCR-001144 | NCR | ETH - Damage to capping beam K during excavation |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-08-28 | 2013-08-28 18:12 | 0 | 2013-07-23 18:12 | Civil - Civil Engineering General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | A section of capping beam K has been chipped off during excavation below it.
| 02SL - Stations (LUL) | Cxxx-NCR-001145 | NCR | Damage to Third Party Sewer at St John Street Detail 'A' |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-08-07 | 2013-07-29 15:26 | -9 | 2013-07-24 14:43 | Utilities Engineering - Water | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | During the excavation and temporary works installation at Detail 'A' on St John Street the brickwork outstanding to the manhole for the sewer culvert that runs directly through the centre of the excavation was unearthed. The depth and shape of the brickwork was not as expected and thought to be like the other redundant brickwork found at this location. As with the other redundant brickwork operatives removed the top course of brickwork to install the sheet piles but in doing so damaged the top of the sewer culvert resulting in a hole approximately the size of two bricks.
| 02SL - Stations (LUL) | Cxxx-NCR-001146 | NCR | Non-conformities not being resolved in a timely manner |  | Crossrail | PDP | FAR - Farringdon Station (West) |  | 2013-08-09 | 2013-08-08 17:15 | -1 | 2013-07-25 07:32 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not qualified | Completed |  | NCR FAR-CRL NCR-Cxxx-00940, NCR Cxxx-NCR-001121 & Surveillance Report QS435-04document the absence of training for personnel employed in the sampling and testing of fresh and young concrete. ( a requirement of Works Information volume 2B clause 20.8 "The Contractor shall ensure that staff nominated for undertaking sampling, inspection and testing activities are appropriately trained and competent to carry out the particular activities to which they have been assigned" ) The Contractor has failed to resolve the NCRs in a timely manner.
| 02SL - Stations (LUL) | Cxxx-NCR-001147 | NCR | ETH casting in the cast iron sleeves without an approved MCR |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-08-16 | 2013-08-16 17:06 | 0 | 2013-07-26 12:08 | Civil - Civil Engineering General | 500 |  | Material | Rework | 4 (0.5-3k) | Complete |  | Completed |  | Four cast iron ducts were installed in pile cap N to be used as sleeves for 65mm dia. fire main and 42 dia. domestic main without having an MCR in place.
| 02SL - Stations (LUL) | Cxxx-NCR-001148 | NCR | ETH Incoming water services builderswork |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-08-16 | 2013-08-16 17:07 | 0 | 2013-07-26 12:13 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete |  | Completed |  | casting in four ducts in pile cap N without an approved drawing
| 02SL - Stations (LUL) | Cxxx-NCR-001149 | NCR | Change of RES Sequence |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-08-29 | 2013-08-27 17:29 | -2 | 2013-08-01 20:41 | Tunnelling - Linings - Sprayed Concrete | 500 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | Changes to excavation sequence were agreed in SRG / RES meeting. Breakdown in communication between site team and management lead to these changes not being implemented as expected.
| 02SL - Stations (LUL) | Cxxx-NCR-001150 | NCR | Failure to Record Flow Testing CP1-CH1 TH5 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-08-29 | 2013-08-21 13:00 | -8 | 2013-08-01 20:42 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate resources | Completed |  | On Night Shift 26/07/13 the pumpmen from Gang A failed to record Flow Tests for the Advance TH5.
| 02SL - Stations (LUL) | Cxxx-NCR-001151 | NCR | ETH the SAP not being correctly up revved |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-08-13 | 2013-08-13 16:47 | 0 | 2013-07-30 08:31 | Communications and Control Systems - General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete |  | Completed |  | The SAP ref no. Cxxx--C-STP-M123-50046 was up revved to revision two without being signed again for the second time by all the reviewers. The SAP was however, revised by __ (the author) and approved by both __ (Agent) and__ (Sub Agent) before being re-submitted as revision two to Crossrail.
| 02SL - Stations (LUL) | Cxxx-NCR-001152 | NCR | Demonstration of compliance - dosing of accelerator |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2013-08-30 | 2013-08-29 09:05 | -1 | 2013-07-31 17:57 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Not Defined | Completed |  | In the materials meeting of 25/07/13, it was requested that the Contractor provide evidence of compliant dosing of accelerator. It was agreed that evidence of complaince would be demonstrated by means of a print our from the __. This evidence has not been provided in a timely manner.
| 02SL - Stations (LUL) | Cxxx-NCR-001153 | NCR | Commencement of works without all relevant documentation signed off by Crossrail |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2013-08-22 | 2013-08-13 13:30 | -9 | 2013-08-01 11:58 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Construction of the CP1-CH1 connection tunnel (part of Phase 3a) commenced without having all relevant documentation signed off by Crossrail. The WTH: Action Plan: Cxxx - West Ticket Hall Area - Surface Movements (Cxxx--C-STP-M123-50093) had not been accepted Code 1 prior to commencement of the works. These works can be defined as 'settlement inducing works' and the Action Plan is a fundamental document to control such movements. LUL comments had not been addressed. This is a failure of the Procedure for Readiness Review and Certification Packages as this document was not highlighted as 'not accepted' prior to commencement of works.
| 02SL - Stations (LUL) | Cxxx-NCR-001154 | NCR | TaM TN2033 - Length Short of Design |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-09-20 | 2013-09-05 09:38 | -15 | 2013-08-01 10:09 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | The TAM TN2033 has hit an obstruction at a depth of 64m. The design length is 73m.
| 02SL - Stations (LUL) | Cxxx-NCR-001155 | NCR | TaM TN2035 plan bearing changed |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-08-29 | 2013-08-14 12:01 | -15 | 2013-08-01 10:20 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Previous Construction - Interfacing issues | Completed |  | TaM TN2035 plan bearing was changed in order to reduce the risk of hitting the In-ground instrument (IB13) pre-installed to the date of dirlling. This change to the bearing of the TaM originated the TaM to be apart from each other at the outter boundary of the treatment area of about 4.7m where specification requires 4m.
| 02SL - Stations (LUL) | Cxxx-NCR-001156 | NCR | Incorrect implementation of submission and acceptance procedure in line with readiness review tracker |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-08-15 | 2013-08-13 21:11 | -2 | 2013-08-01 15:42 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | The readiness review tracker failed to capture the latest revision of the site activity plan entitled CPI Concrete Batching, Cxxx--C4-STP-M123-50128, resulting in our incorrect implementaion of the submission and acceptance procedure as detailed in Section KT20.2102 from Cxxx-SCL Specifcation sprayed concrete lining KT20 document.
| 02SL - Stations (LUL) | Cxxx-NCR-001157 | NCR | Failed beams at 28 days |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-02-03 | 2014-04-25 17:40 | 81 | 2013-08-01 17:17 | Civil - Tunnelling | 20000 |  | Workmanship | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | Following the 28 day flexural strength tests on a set of beams taken during CP1 Invert 13 on the 4th July, 2 out of 3no. beams failed. We are currently awaiting the report from the test lab for further information. Please return this NCR so that further information can be input as we know more. Mandatory fields within this NCR template will be completed based on assumption to allow the NCR to be raised.
| 02SL - Stations (LUL) | Cxxx-NCR-001158 | NCR | ETH - Excavation works commenced without ETH Action Plan in place |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2013-08-15 | 2013-08-13 16:07 | -2 | 2013-08-01 19:04 | Civil - Civil Engineering General | 500 |  | Planning | Rework | 4 (0.5-3k) | Complete |  | Completed |  | Excavation works at the ETH commenced before ETH: Action Plan Cxxx – East Ticket Hall Area (Cxxx--C-STP-M123-50094) was appropriately decaled by CRL.
| 02SL - Stations (LUL) | Cxxx-NCR-001159 | NCR | Procedural-Starting work without Pre-Start Check Sheet sign off by Crossrail |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-08-16 | 2013-08-19 09:40 | 3 | 2013-08-02 12:14 | Civil - Civil Engineering General | 500 |  | Planning | Rework | 4 (0.5-3k) | Complete |  | Completed |  | The installation of ShapeAccelArrays (SAA) within the trenches in Lindsey Street Bridge started without a Pre-Start Checklist being signed off by Crossrail.
| 02SL - Stations (LUL) | Cxxx-NCR-001160 | NCR | Error in checking procedure for input into "Amberg" software, resulting in discrepancies between asbuilt and design levels |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-09-13 | 2013-09-12 14:57 | -1 | 2013-08-06 10:00 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Supervision/Management | Use As-Is | 3 (3-6k) | Complete | Personnel Error - Other human error | Completed |  | Procedure for checking design input data to TMS software was not followed. An error in the input data was not discovered and this lead to discrepancy in level between design and as-built in the invert of CP1.
| 02SL - Stations (LUL) | Cxxx-NCR-001161 | NCR | Flow test carried out with too much water |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-09-12 | 2013-09-12 11:26 | 0 | 2013-08-06 01:52 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not qualified | Completed |  | It has been witnessed that a flow test was carried out on 29th July incorrectly and too much water was used to wet the flow table. This was an isolated occurrence
| 02SL - Stations (LUL) | Cxxx-NCR-001162 | NCR | Core holes filled with incorrect grout |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-09-05 | 2013-08-16 19:57 | -20 | 2013-08-06 02:02 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete |  | Completed |  | 4 cores holes on advance 51B, were grouted using Webber Cem grout, oppose to the approved __ GP non shrink grout.
| 02SL - Stations (LUL) | Cxxx-NCR-001163 | NCR | Installation of invert monitoring point not carried out as per activity plan |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-09-20 | 2013-09-19 17:36 | -1 | 2013-08-06 02:13 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | Invert monitoring point not installed as detailed in the activity plan (Cxxx--C4-STP-M123-50133 Rev 1.0)
| 02SL - Stations (LUL) | Cxxx-NCR-001164 | NCR | Penetroemeter readings taken incorrectly |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-09-14 | 2013-09-12 15:00 | -2 | 2013-08-06 02:16 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | Penetrometer readings taken incorrectly by cover engineer (__). Due to work load of the engineer on shift, it was requested to the cover engineer to carry out the penetrometer test. CRL Inspector on shift witnessed the testing not being carried out according to current SAP, basically, the device was not applied perpendicularly to ht esurface of the sprayed concrete layer . Engineer to be rebriefed in the current SAP (Cxxx--C4-STP-M123-50014).
| 02SL - Stations (LUL) | Cxxx-NCR-001174 | NCR | WTH - Piling - Pile 819 - Concrete out of 2h time |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-08-23 | 2013-08-12 14:01 | -11 | 2013-08-06 13:14 | Civil - Geotechnical Engineering | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | Clause KF10.3202 specifies concrete to be placed and compacted 2h after addition of water (batching). Pile 819 was poured with all loads apart from the first one discharged over 2h. All loads finished discharging after 2h. All loads were tested for flow, all results between 550 and 570mm flow which is between the allowable 530 to 660mm of F5. Concrete pour record attached. A set of cubes was also taken from load 3 (5 loads in total). This pile does not include sonic logging tubes. 7 day results attached.
| 02SL - Stations (LUL) | Cxxx-NCR-001175 | NCR | WTH - Piling - Females piles 524 & 526 out of vertical tolerance |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-08-26 | 2013-08-23 16:32 | -3 | 2013-08-06 13:34 | Civil - Geotechnical Engineering | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not qualified | Completed |  | Civil & Struct Spec clause KP10.3231 requires secant piles to have a vertical tolerance of 1:200. Pile 524 was built with verticality 1:142 into the shaft. Pile 525 was built with verticality 1:111 into pile 827.
| 02SL - Stations (LUL) | Cxxx-NCR-001177 | NCR | WTH - Piling - Pile 816 - Deeper Toe Level |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-08-26 | 2013-08-27 17:57 | 1 | 2013-08-06 14:45 | Civil - Geotechnical Engineering | 500 |  | Equipment Breakdown | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | Schedule Cxxx-SWN-S-DDA-M123_Z-76027 specifies a toe level of pile E816 as 73.000 mLHD. Due to a failed delivery preventing completion of the pile on the 25/7/13 and in order to still comply with BS EN 1536:2010 cl 8.2.1.8 __ extended the toe of the pile E816 to 70.470mLHD. This pile was constructed on 26/7/13 in order to comply with FAR-CRL FCD-Cxxx-00473.
| 02SL - Stations (LUL) | Cxxx-NCR-001178 | NCR | NO MCR for BFK 17.1 Hanson Mix and Cxxx |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-08-22 | 2013-08-21 12:48 | -1 | 2013-08-08 16:58 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Rework | 4 (0.5-3k) | Complete |  | Completed |  | 17.1 mix was used on SH-W2 Softeye West, there was no accepted MCR in place for this mix.
| 02SL - Stations (LUL) | Cxxx-NCR-001179 | NCR | No accepted ITP in place prior to works commencing on SH-W2 Soft Eyes |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-09-08 | 2013-09-05 17:28 | -3 | 2013-08-08 17:04 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Planning | Rework | 4 (0.5-3k) | Complete |  | Completed |  | No accepted ITP in place prior to work commencing in SH-W2 soft eyes
| 02SL - Stations (LUL) | Cxxx-NCR-001180 | NCR | Installation of Data logger at the ETH without an approved method statement |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-08-23 | 2013-08-19 15:51 | -4 | 2013-08-09 15:57 | Surveying - Instrumentation and Monitoring | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | A Data logger was isntalled at the ETH prior to approved method statement by CRL.
| 02SL - Stations (LUL) | Cxxx-NCR-001181 | NCR | Beam Failures CP1 Adv TH27 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-02-28 | 2014-02-04 12:18 | -24 | 2013-08-13 07:38 | Tunnelling - Linings - Sprayed Concrete | 55000 |  | Material | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | Beams taken in CP1 Advance TH27 for flexural tensile strength testing failed at 28 day test
| 02SL - Stations (LUL) | Cxxx-NCR-001182 | NCR | SHW2 East Eye - Face Open Longer than 3 Hrs |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-09-12 | 2013-09-05 17:31 | -7 | 2013-08-13 10:18 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Equipment Breakdown | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | SHW2 - Face was open 6hrs 30 mins before sealing. Details as follows: * Concrete was ordered at 11:30am, to allow works to commence on east eye. This was batched at 12:00, and on site for 13:00. * By the time wagon was in from holding bay, and flows etc completed, break out of east eye commenced at 13:45. Face was exposed at 14:15. * Brokk broke down at 14:00, so a 2nd Brokk stopped work on the west eye to continue breaking piles on the east eye. * 2nd brokk broke down at 14:40, and break out continued using 5t excavator with pecker. * Flows were re-done each hour, and the 16:00 test failed with a 350mm flow after being on site 3hrs / 4 hrs following batching. Note, the life span of this mix is 6hrs. * Called s at 16:20 and requested a 2nd load - needed to empty 1st load on site and this wagon would return to us. * Spoke with __s as the 3 hrs for sealing the face will expire at 17:15. Whether we should seal using CPI or wait until the next load arrives. He was happy that the ground conditions were good, and that less than half of the top heading were exposed so agreed we should wait for the next s wagon to arrive to seal. Concrete was expected to arrive on site at 17:30. * Called s 17:45 - 1st wagon not back to the depot yet so they have taken a seperate wagon from Kings Cross depot, which was expected to be with us by 18:45. * Spoke with __s at 18:00 as to whether we should seal using CPI or wait for the 2nd s wagon to arrive. Ground conditions were good, so we decided to to wait. * Wagon arrived on site at 19:20, and by the time flows etc were completed, and skips loaded - sealing the face commenced at 20:45
| 02SL - Stations (LUL) | Cxxx-NCR-001184 | NCR | Cxxx Data upload to UCIMS |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-10-30 | 2013-11-19 17:03 | 20 | 2013-08-13 13:49 | Surveying - Instrumentation and Monitoring | 500 |  | System Defect | Repair | 4 (0.5-3k) | Complete | Procedure Problem - Not Defined | Completed |  | In accordance with the Specification for the Control of Ground Movement Volume 2C clause 1.2.1.8, the Contractor is required to incorporate all monitoring information to the Crossrail UCIMS database. Although much of the Cxxx-owned monitoring is being regularly uploaded to UCIMS, there remains a number of points which are not being uploaded regularly.
| 02SL - Stations (LUL) | Cxxx-NCR-001185 | NCR | ETH - Concrete cubes lost by test consult for capping beam pour F |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-08-29 | 2013-08-20 13:22 | -9 | 2013-08-15 12:06 | Structural Engineering - Concrete Member | 500 |  | System Defect | Rework | 4 (0.5-3k) | Complete |  | Completed |  | Capping beam pour F was 84m^3 and as such 2 sets of cubes were taken by the test consult technician. The first set of cubes completed on the pour have been lost. The second set have been tested and passed the compressive strength test.
| 02SL - Stations (LUL) | Cxxx-NCR-001186 | NCR | TN2077 - out of deviation tolerance |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-08-30 | 2013-08-21 09:30 | -9 | 2013-08-16 08:15 | Geotechnical Engineering - Compensation Grouting | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | AT Moorgate Spur 2 Shaft Tam TN2077 is out of horizontal deviation toleance by 50mm.
| 02SL - Stations (LUL) | Cxxx-NCR-001187 | NCR | ETH - General workmanship in installation of first two props and waler |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-09-02 | 2013-09-02 20:08 | 0 | 2013-08-19 17:24 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete |  | Completed |  | During the installation of the first two props there have been some errors in the workmanship. Namely - grade 10.9 bolts installed as opposed to 8.8. Gaps not closed up between waler and prop. The grout between the thrust block and the endplate appears to have shrunk and as such a gap has opened up. Holding down bolt cut not leaving the required 3 threads from the end of the nut.
| 02SL - Stations (LUL) | Cxxx-NCR-001188 | NCR | ETH - __ check sheets not be completed during prop installation |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-09-02 | 2013-09-02 20:10 | 0 | 2013-08-19 17:43 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete |  | Completed |  | During the installation of the first two props, the bolts were torqued and marked as per the ITP however the check sheet was not filled out. The deliveries were checked on arrival as per the ITP and again the check sheets were not filled out.
| 02SL - Stations (LUL) | Cxxx-NCR-001189 | NCR | Pre-treatment carried out before in a sector of TAMs prior to FCD being approved |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-10-15 | 2013-10-02 16:25 | -13 | 2013-08-19 18:51 | Civil - Geotechnical Engineering | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | The pre-treatment in Sector 7 on MS2 was on hold, until the FCD to allow this operation was agreed and approved by CRL. However, the pre-treatment has been carried out and taken to a 50% completion stage. Sector 7 Tams: : . tam array segment between 033o and 127o relative to North (sketch attached)
| 02SL - Stations (LUL) | Cxxx-NCR-001190 | NCR | WTH - Piling - Base grouting - Uplift not achieved |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-09-04 | 2013-08-23 07:46 | -12 | 2013-08-20 14:39 | Civil - Geotechnical Engineering | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | ICE SPERW B3.5.11.4 states that all bearing piles should achieve an uplift of 0.2 - 2mm when base grouted. The base grouting has been carried out and no piles have achieved uplift within the required parameters except one, pile 214. The first 8 piles were base grouted over 2 phases, and subsequent to RFI 761, all other piles were base grouted over 3 phases. __ have used the __ Ranking Method to assess base grouting of all piles and __ deems all piles as successfully base grouted.
| 02SL - Stations (LUL) | Cxxx-NCR-001191 | NCR | Density of loads of Foam Concrete found outside Acceptable range |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-09-11 | 2013-08-22 11:35 | -20 | 2013-08-21 16:17 | Shafts - Shafts General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | As a part of Phase 2 foam concrete placement in the square shaft to facilitate the TBM passage, P595 Mix is being used which has got a target density of 1200kg/cu.m. In accordance with the approved ITP document ref number: Cxxx--C-ITP-M123-50040, Rev 4, the acceptable range of the density is + -100kg/cu.m which equates to a range of 1100-1300 kg/cu.m. On 20th of August’13, during the foam concrete placement using a M52 mobile concrete pump, it was found that 11 loads of concrete (out of 37 loads in total) were outside the acceptable density range. believes there could be several reasons for the loads to go outside the acceptable density range. For example, pumping pressure caused by the mobile concrete pump could aid in the loss of foam resulting high densities. Also the length of travel of foamed concrete from the top to the bottom of the shaft through the pump line could aid in the loss of foam resulting high density. Due to having densities outside the acceptable range for 11 loads, thinks this is a non - compliance to works information and hence the NCR. Please see attached foam concrete placement site control record sheet for clarity which clearly highlights the loads which were found outside the acceptable density range. It can be seen that the maximum density found outside the acceptable range was 1392 kg/cu.m (Load : 23).
| 02SL - Stations (LUL) | Cxxx-NCR-001192 | NCR | WTh - Piling - Pile 217 - Geothermal pipe test 24h 3.1 bar |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-09-12 | 2013-08-28 15:04 | -15 | 2013-08-22 12:30 | Civil - Geotechnical Engineering | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | JT 20 Energy Piles Specification (Cxxx-SWN-C2-RSP-M123-00001) and ITP Cxxx--C-ITP-M123-50098 point 16 requires a 4 bar 24 hour pressure test on Geothermal Pipes on OSD piles following concreting. For pile U217, the pressure after 24hrs from concreting was 3.1 bar but no less. All tests carried out before hand were as required with no pressure loss.
| 02SL - Stations (LUL) | Cxxx-NCR-001193 | NCR | TN1010 - Out of Horizontal Deviation |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-09-26 | 2013-09-04 09:48 | -22 | 2013-08-22 15:07 | Geotechnical Engineering - Compensation Grouting | 500 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Not Defined | Completed |  | Tam TN1010 at Moorgate Spur 1 is out of horizontal Tolerance by 166.83mm according to HADA tests conducted
| 02SL - Stations (LUL) | Cxxx-NCR-001194 | NCR | ETH - Trapezoidal Shaft - Temporary Steel Platform Missing & Additional Shear Studs |  | Contr | BAM | FAR - Farringdon Station (West) |  | 2013-09-19 | 2013-09-09 15:21 | -10 | 2013-08-22 19:00 | Structural Engineering - Steel Member | 1500 |  | System Defect | Rework | 4 (0.5-3k) | Complete |  | Completed |  | Temporary Steel Platform - Beams B12 and B13 are missing shear studs that will need to be welded to the flange and Beam B17 has additional shear studs that need cutting off. Beam B5 is missing the 300mm kick plate.
| 02SL - Stations (LUL) | Cxxx-NCR-001195 | NCR | WTH - Piling - Concrete out of time - Piles 101 207 & 221 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-09-10 | 2013-08-28 14:52 | -13 | 2013-08-23 09:42 | Civil - Geotechnical Engineering | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Other human error | Completed |  | Clause KF10.3202 specifies concrete to be placed and compacted 2h after addition of water (batching). Pile 101 - Load number 1 started started discharging 2:10h and finished discharging 2:20h after batching PIle 207 - Loads number 4 and 7 started discharging before 2h of batching but finished 2:15h after PIle 207 - Loads number 5 and 6 started discharging 20/25 mins after the 2h cut off limit Pile 221 - Loads number 2 and 3 started discharging before 2h of batching but finished 2:10h and 2:40h after respectively All loads complied with required flow before pouring. Please find attached concrete pour records. No cubes were taken form these loads. Please find attached sonic logging reports for the piles in question.
| 02SL - Stations (LUL) | Cxxx-NCR-001196 | NCR | WTH - Piling - Base grouting - Pile 207 - 3h between grout phases |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-09-12 | 2013-09-09 15:37 | -3 | 2013-08-23 11:25 | Civil - Geotechnical Engineering | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Other human error | Completed |  | Pile 207 - Base grouting - Third cycle started prior to 3h period between cycles ITP Cxxx--C-ITP-M123-50097 point 24 requires 3h between base grouting phases on OSD piles Third phase was started 2:30h after the second phase. __/ are confident from the results of the third phase that base grouting on this pile has been successful.
| 02SL - Stations (LUL) | Cxxx-NCR-001197 | NCR | Incorrect strain gauge mounting block welded onto prop |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-09-06 | 2013-09-05 19:56 | -1 | 2013-08-23 10:12 | Geotechnical Engineering - Geotechnical Monitoring | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | The pair of strain gauge mounting blocks welded onto the south raking prop in gridline 6, ETH Trapezoidal Shaft, at prop circumference location 315° are not correct. For each strain gauge one mounting block should have a single screw fixing and the second should have two screw fixings. At the location in question a pair of two screw fixing mounting blocks have been installed.
| 02SL - Stations (LUL) | Cxxx-NCR-001198 | NCR | Foam Concrete Densities outside Acceptable Range for the pours taken place between 19th of Aug to 22nd Aug'13 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-09-13 | 2013-08-28 15:45 | -16 | 2013-08-23 11:05 | Shafts - Shafts General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Not Defined | Completed |  | As a part of Phase 2 Foam concrete placement in the Square Shaft –SHW2, in order to facilitate the TBM Passage, P595 Mix is being used which has got a traget density of 1200kg/cu.m. In accordance with the approved ITP doc ref number: Cxxx--C-ITP-M123-50040, Rev 4, the acceptable range of density is + - 100kg/cu.m. which equates to a range of 1100-1300 kg/cu.m. Foam concrete is being placed in the square shaft using M52 Concrete pump located on the Caxton Slab. Due to the pressure caused by piston of the pump and due to the length of travel of foam concrete from the top of Caxton Slab to the bottom of the shaft, several loads which have been pumped so far from Monday, the 19th of Aug’13 till Thursday, the 22nd of Aug’13 have resulted higher densities at the discharge location which is outside the acceptable range of the desired density. Please see below a summary of loads which have been found outside the acceptable density range at the discharge location between Monday, the 19th of Aug’13 & Thursday, the 22nd of Aug’13. Monday-19th of Aug’13: - 4 out of 23 loads were found outside the acceptable density range. See attached “Foam concrete placement site control record sheet – Load No: 1,2,3 &4. Maximum density found was 1486 kg/cu.m. Tuesday-20th of Aug’13:- 11 out of 37 loads were found outside the acceptable density range. NCR-001191 has been already raised and closed out to capture this issue. Wednesday -21st Aug’13:- None out of 45 loads were found outside the acceptable density range. Thursday-22nd Aug’13:- 8 out of 33 loads were found outside the acceptable density range. See attached “Foam concrete placement site control record sheet – Load No: 7, 9,10,11,12,13, 20 & 24. Maximum density found was 1506 kg/cu.m. Due to having densities outside the acceptable range for the loads mentioned above, thinks this is a non-compliance to the Works Information, hence the NCR.
| 02SL - Stations (LUL) | Cxxx-NCR-001199 | NCR | Base Mix loads out of spec - Foam Concrete placement taken place between Mon-19th Aug'13 and Thursday-22nd Aug'13 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-09-20 | 2013-08-28 16:10 | -23 | 2013-08-23 13:47 | Shafts - Shafts General | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate resources | Completed |  | During the placement of foam concrete in the Square Shaft –SHW2 between Monday, the 19th of Aug and Thursday, the 22nd of Aug’13, few loads of base mix were processed to produce Foam Concrete which were over two hours from the time of batching. See below a summary of the loads which were processed outside the specification. Monday -19th of Aug:- No Loads were outside the spec. Tuesday- 20th of Aug:- 3 out of 37 loads were out in spec by max 16 mins. Wednesday-21st Aug:-3 out of 45 loads were out of spec by max 17 mins. Thursday – 22nd Aug:- 8 out of 36 loads were out of spec by max 48 mins. Due to the facts mentioned above, believes this is non –compliance to Clause – KF10.3202 (c) of Civil & Structural Specification,hence, the NCR. Please see attached copies of foam concrete placement site control record sheets highlighted in Red for clarity.
| 02SL - Stations (LUL) | Cxxx-NCR-001200 | NCR | ETH - Bolts on temporary platform cast too low |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-09-10 | 2013-09-10 15:54 | 0 | 2013-08-27 16:11 | Structural Engineering - Bolted Connections | 1000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete |  | Completed |  | 2no bolts holding the column in the south west corner of the temporary platform have been cast too low within the capping beam and as such the nut cannot be screwed down far enough to show a full thread above the nut. See photos attached
| 02SL - Stations (LUL) | Cxxx-NCR-001201 | NCR | Foam Concrete densities outside acceptable range for pours taken place on 23 August and 27 August |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-09-11 | 2013-08-29 15:51 | -13 | 2013-08-28 16:54 | Shafts - Shafts General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper handling of material | Completed |  | As a part of Phase 2 Foarm concrete placement in SHW2, in order to facilitate the TBM Passage, P595 Mix is being used. On 23/08/13 the target density was 1200kg/cu.m (+- 100kg/cu.m) and on 27/08/13 the target density was 1300kg/cu.m (+- 100kg/cu.m). On 23/08/13, during the foam concrete placement using a M52 mobile concrete pump, it was found that 2 loads of concrete (out of 24 loads in total) were outside the acceptable density range. On 27/08/13, during the foam concrete placement using a M52 mobile concrete pump, it was found that 5 loads of concrete (out of 29 loads in total) were outside the acceptable density range. believes there could be several reasons for the loads to go outside the acceptable density range. For example, pumping pressure caused by the mobile concrete pump could aid in the loss of foam resulting high densities. Also the length of travel of foamed concrete from the top to the bottom of the shaft through the pump line could aid in the loss of foam resulting high density. Please see below a summary of loads which have been found outside the acceptable density range at the discharge location on 23/08/13 and 27/08/13. 23/08/13 - 2 out of 24 loads were found to be below the acceptable density range. See attached Foam concrete placement site control sheet - Loads number 9 and 12. The minimum density was found to be 1079 kg/cu.m 27/08/13 - 5 out of 29 loads where found to be outside the acceptable density range. See attached 'Foam concrete placement site control record sheet' - Loads 4, 6, 7 and 12 where above the density range with a maximum value of 1480kg/cu.m and load 15 was below the density range with a minimum value of 1170kg/cu.m. Due to having densities outside the acceptable range, thinks this is a non compliance to works information and hence the NCR.
| 02SL - Stations (LUL) | Cxxx-NCR-001202 | NCR | DN800 DI Pipework failed pressure test |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-09-17 | 2013-09-16 07:46 | -1 | 2013-09-03 10:53 | Utilities Engineering - Water | 5000 |  | Workmanship | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | The newly installed DN800 DI pipework along Farringdon Road was tested from the north to south pit on Farringdon Road and the pressure test failed. The pipes were pumped to a pressure of 8.5bar (i.e. operating pressure + 5bar) but the pressure was immediately dropping as soon as the pump was turned off. Sections of the pipe had undergone pressure testing and passed before backfilling but there was the section south of the reception pit which couldn’t be tested because it had to be backfilled immediately due to the movement of the West Ticket Hall’s crane on 27.07.2013.
| 02SL - Stations (LUL) | Cxxx-NCR-001203 | NCR | Type A Thrust Block cast in Wrong position |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-10-14 | 2013-10-09 11:03 | -5 | 2013-09-02 17:20 | Civil - Civil Engineering General | 1000 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Type A thrust blocks within Arch 2, Lindsey street Bridge were set-up using Tony Gee co-ordinates provided on drawing: Cxxx--C-DDL-M123_WS098_Z-10001. On fitting the Type A diagonal member, It has been found that the diagonal props don’t fit the gap between the thrust block and the vertical prop. have carried out an as built and found that the co-ordinates provided by Tony Gee do not correspond with Tony Gee Diagonal member dimensions given on drawing Cxxx--C-DDL-M123_WS098_Z-10009 & Cxxx--C-DDD-M123_WS098_Z-10010 ( the drawings used to manufacture the Props). The thrust blocks are 250mm closer to pier 1/2 (S). have notified Tony Gee about the design issue. Tony Gee is reviewing the design and will be advising of any suitable solution. This is not a field problem. It is a design/ detailing problem by Tony Gee.
| 02SL - Stations (LUL) | Cxxx-NCR-001204 | NCR | ETH - Bolts for Prop P12 cut too short |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-10-01 | 2013-09-30 15:57 | -1 | 2013-09-02 17:11 | Structural Engineering - Bolted Connections | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Insufficient surveillance of subcontractors | Completed |  | The bolts conneccting the bottom of prop P12 to the baseplate were cut during installation of the prop and as such not enough thread comes through the nut to comply with the ITP. Location sketch and photos attached.
| 02SL - Stations (LUL) | Cxxx-NCR-001205 | NCR | Formal submission of Temporary Works Design Check Certificate |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2013-09-24 | 2013-09-24 16:46 | 0 | 2013-09-03 10:17 | Tunnelling - Linings - Sprayed Concrete | 500 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | It was agreed in the Construction Meeting of Tuesday 27th of August that a CATIII Temporary Works Design check certificate be submitted to the Project Manager for acceptance prior to commencement of the CH1 pilot tunnel. Construction of the CH1 pilot tunnel commenced on Friday 30/08/13. The check certificate had not been formally submitted as of Monday 02/09/13. The design check certificate refers to a design brief (Cxxx--C4-RGN-M123-50889) which has not been submitted to the Project Manager for acceptance. The procedures described in Part 22 of the Works Information have not been followed.
| 02SL - Stations (LUL) | Cxxx-NCR-001206 | NCR | TaMs TBU042 not installed up to design length |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-10-04 | 2013-10-02 08:24 | -2 | 2013-09-06 09:43 | Geotechnical Engineering - Compensation Grouting | 1000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Previous Construction - Interfacing issues | Completed |  | TaMs TBU042 at Butchers Ramp were not installed up to design length due to boreholes partially collapsing during the TAM installation process. This is as a consequence of the more sandy clay being encountering at Butcehrs Ramp.
| 02SL - Stations (LUL) | Cxxx-NCR-001207 | NCR | TaMs TBU018 not installed up to design length |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-10-04 | 2013-10-02 08:26 | -2 | 2013-09-06 09:46 | Geotechnical Engineering - Compensation Grouting | 1000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Previous Construction - Interfacing issues | Completed |  | TaMs TBU018 at Butchers Ramp were not installed up to design length due to boreholes partially collapsing during the TAM installation process. This is as a consequence of the more sandy clay being encountering at Butcehrs Ramp.
| 02SL - Stations (LUL) | Cxxx-NCR-001208 | NCR | TaMs TBU012 not installed up to design length |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-10-18 | 2013-10-15 13:59 | -3 | 2013-09-06 09:49 | Geotechnical Engineering - Compensation Grouting | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | TaMs TBU012 at Butchers Ramp were not installed up to design length due to boreholes partially collapsing during the TAM installation process. This is as a consequence of the more sandy clay being encountering at Butcehrs Ramp.
| 02SL - Stations (LUL) | Cxxx-NCR-001209 | NCR | TaMs TBU009 not installed up to design length |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-10-04 | 2013-10-02 08:29 | -2 | 2013-09-06 09:52 | Geotechnical Engineering - Compensation Grouting | 1000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Previous Construction - Interfacing issues | Completed |  | TaMs TBU009 at Butchers Ramp were not installed up to design length due to boreholes partially collapsing during the TAM installation process. This is as a consequence of the more sandy clay being encountering at Butcehrs Ramp.
| 02SL - Stations (LUL) | Cxxx-NCR-001210 | NCR | WTH - Piling - Base Grouting - Under-achieving grout - Piles 203 213 and 218 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-09-27 | 2013-09-18 17:21 | -9 | 2013-09-06 12:48 | Civil - Geotechnical Engineering | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | OSD piles on the WTH are all base grouted. ITP Cxxx--C-ITP-M123-50097 Rev 6 Code 1 requires grout to achieve 25N/mm2 at 28 days. Grout in the base of Piles 203, 2013 and 218 did not achieve the required strength. Summary of the results (28 day cube result report for pile 203 still outstanding from attachments but results are quoted below. Will be uploaded asap): [Pile and Phase] [Date] [Ticket] [28 day 1] [28 day 2] [28 Day Avg] [56 day 1] [56 day 2] [56 day Avg] [203 - Phase 2&3] [11/07/13] [S1181512] [21.8N/mm2] [19.6N/mm2] [20.7N/mm2] [213 - Phase 3] [02/05/13] [S1163240] [18.0N/mm2] [15.3N/mm2] [16.7N/mm2] [21.1N/mm2] [21.9N/mm2] [21.5N/mm2] [218 - Phases 2&3] [30/04/13] [S1163238] [21.4N/mm2] [21.0N/mm2] [21.2N/mm2] Piles U203, U213 and S218 low results grout was always used in the second and third phases, where minimal volume of grout injections were achieved. Low strength grout should have minimal affect on the capacity of the base of the pile. On pile U203, 78 litres of grout were injected over phase 2&3 to an average strength of 20.7N/mm2 average at 28 days. __/ are awaiting the 56 day cube results for Crossrail review. These will be uploaded as soon as they are available. On pile U213, 883 litres of grout were injected over phase 1&2 to an average strength 29.8N/mm2 and only 25l of the under achieving grout in phase 3. On pile S218, 415 litres were injected in phase 1 with grout strength of 29.1N/mm2 and only 14.5l and 18l in 2nd and 3rd phase respectively to 21.2N/mm2 average at 28 days.
| 02SL - Stations (LUL) | Cxxx-NCR-001213 | NCR | WTH - Piling - Base grouting - Pile 205 - 3rd phase - missplaced cube results |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-09-20 | 2013-09-16 08:20 | -4 | 2013-09-06 14:42 | Civil - Geotechnical Engineering | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Lack of procedure | Completed |  | WTH OSD pile base grouting ITP (Cxxx--C-ITP-M123-50097) requires for a set of cubes per cycle/mix to be taken. For pile 205, cubes for the third phase have been misplaced/mislabelled and therefore there is no verification of strength of a sample for this day.
| 02SL - Stations (LUL) | Cxxx-NCR-001214 | NCR | Non-compliance with probing for sheet piles ITP |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-09-27 | 2013-09-18 17:22 | -9 | 2013-09-11 09:05 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Inadequate/insufficient tooling. | Completed |  | The ITP for the probing works states that the 6F2 will be backfilled and compacted in layers in accordance with the Highway Specification Series 600. are using a roller for the top metre in accordance with this specification. Due to space restraints and the use of trench boxes in certain areas it is not possible to use a roller or ramax to compact over full depth. have been using a hydraulic wacker plate attached to the end of our excavator. can not prove the wacker plate in accordance with the Highways specification as no information is available on the mass per metre squared of the wacker, as this will depend on the force applied by the excavator. have carried out plate bearing tests on completed runs and the required value of 600kN/m2 has been achieved. This NCR covers Runs a and C only. have spoken to the sheet piling mat designers regarding this matter and they have confirmed that this is acceptable. This confirmation is attached as well as the bearing test results.
| 02SL - Stations (LUL) | Cxxx-NCR-001215 | NCR | TaMs TBU033 not installed up to design length |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-10-07 | 2013-10-02 08:32 | -5 | 2013-09-09 15:13 | Geotechnical Engineering - Compensation Grouting | 1000 |  | Design | Rework | 4 (0.5-3k) | Complete | Previous Construction - Interfacing issues | Completed |  | TaM TBU033 at Butchers Ramp was not drilled to final length due to an unknown obstruction being encountered at 27m. TaM length is to 27m out of planned length of 34.5m.
| 02SL - Stations (LUL) | Cxxx-NCR-001216 | NCR | Certification and test results of the SCL constituent materials |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2013-10-01 | 2013-09-29 13:35 | -2 | 2013-09-10 14:31 | Tunnelling - Linings - Sprayed Concrete | 500 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | The Contractor’s records were not fully current and as such he could not demonstrate compliance with Works Information volume 2B part 20.7 with respect to proving compliance to relevant standards for dry concrete mix used in SCL construction. For example a significant portion of aggregate test records were not current and information supplied to demonstrate mix consistency was incomplete and unclear on how the water cement ratio was effected.
| 02SL - Stations (LUL) | Cxxx-NCR-001217 | NCR | Re-mixing of fresh concrete samples prior to testing |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2013-10-14 | 2013-10-11 17:04 | -3 | 2013-09-10 14:38 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | It was witnessed that the re mixing did not take place, furthermore the remixing container, as described in clause 4.5 of BS EN 12350-5:2009 was not available in the testing area.
| 02SL - Stations (LUL) | Cxxx-NCR-001221 | NCR | Site Activity Plans |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-09-29 | 2013-09-29 13:32 | 0 | 2013-09-12 11:23 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Latest Revisions of Activity Plans not displayed on site.
| 02SL - Stations (LUL) | Cxxx-NCR-001222 | NCR | Thermometer used on site did not have calibration certificate |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-09-30 | 2013-09-29 13:33 | -1 | 2013-09-12 16:08 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | Thermometer found on site today did not have calibration certificate. Thermometers used before where calibrated by UKAS laboratory (C__1 and C__2) but they both broke down. Spare thermometers did not have calibration certificates and had not sent them to laboratory to get calibrated.
| 02SL - Stations (LUL) | Cxxx-NCR-001223 | NCR | Flow testing kit |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-09-29 | 2013-09-25 12:57 | -4 | 2013-09-12 16:23 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | Flow cone interior not smooth - covered with concrete (picture attached). Tamping bar not mark and out of tolerance required by standard (picture attached).
| 02SL - Stations (LUL) | Cxxx-NCR-001224 | NCR | ETH - Temporary Steel Platform - Precast Planks Installed Incorrectly |  | Contr | BAM | FAR - Farringdon Station (West) |  | 2013-11-12 | 2013-11-08 11:36 | -4 | 2013-09-13 11:23 | Civil - Structural Engineering | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | Plank type 13 at the south-west corner of the temporary steel platform was installed 175mm away from the kickplate in line with the side faces of plank types 1 used on the southern elevation of the temporary steel platform. All adjacent plank type 14's heading north from plank type 13 (SW corner) are all installed tight against one another but have all been installed the same 175mm out of correct position. The initial plank type 13 (SW corner) should of been installed tight against the kick plate on the southern elevation. This has caused problems trying to install the final plank type 13 at the northern end of this line of planks in the north-west corner of the temporary steel platform.
| 02SL - Stations (LUL) | Cxxx-NCR-001225 | NCR | FCD discussed and agreed but not processed through PTR |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-10-01 | 2013-09-17 15:30 | -14 | 2013-09-17 12:01 | Surveying - Instrumentation and Monitoring | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | Verbal agreement was made with Cxxx, FCD was not processed through PTR prior to works starting, procedural NCR. Staff briefing on process carried out.
| 02SL - Stations (LUL) | Cxxx-NCR-001226 | NCR | Density check not taken as per ITP for AE conc of wraparound |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-10-18 | 2013-10-10 09:43 | -8 | 2013-09-17 15:27 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | First level of AE concrete was poured without meeting required frequency of density checks. 2 No. samples where misssed. Please note that the samples that where obtained met requirements
| 02SL - Stations (LUL) | Cxxx-NCR-001227 | NCR | temporary works was not submitted to CRL in time |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-10-15 | 2013-10-15 17:12 | 0 | 2013-09-17 18:15 | Geotechnical Engineering - Compensation Grouting | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | The package for temporary works GS1 drilling Rig Support Frame was not submitted to CRL in time and the works proceeded over the weekend without submission or acceptance. The permit to load was issued by the temporary works co-ordinator on the agreement that the re-issue of the certificate that was issued on Friday would be signed correctly, the designers risk assessment, CV’s and the checkers calculations would be submitted to CRL. are still waiting for the certificate and the CV’s to be sent by __.
| 02SL - Stations (LUL) | Cxxx-NCR-001228 | NCR | ETH - No Calibartion Certifiacte for Impact Wrench |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-10-02 | 2013-09-18 14:04 | -14 | 2013-09-18 09:42 | Civil - Civil Engineering General | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | Steel work eretcion subcontractor torqued up bolts in temporary platform as per the ITP howvere could not provide calibartion certfiacte for the impact wrench used
| 02SL - Stations (LUL) | Cxxx-NCR-001229 | NCR | ETH – Clash between permanent works and propping design |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-01-17 | 2013-12-18 09:27 | -30 | 2013-10-10 18:43 | Structural Engineering - Steel Member | 20000 |  | Design | Repair | 2 (6-60k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The plan position of the P1 secondary props (3 no.) on grid line 5.5 to 4 as shown on Temporary Works drawing Cxxx--C-DWG-M123-50139 do not match the positions shown on drawing Cxxx-SWN-S-DDA-M123_Z-26983. In addition the waling position was defined on the Cxxx drawing from which the temporary works design was developed. It has become apparent that the waling level provided clashes with position of the permanent works inclined props
| 02SL - Stations (LUL) | Cxxx-NCR-001230 | NCR | Concrete for Thrust Walls at Detail 'A' 16" Water Main |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-10-30 | 2013-10-23 08:54 | -7 | 2013-09-27 08:33 | Utilities Engineering - Utilities General | 1000 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Following concrete delivered from __ cast for 16” thrust block at Detail 'A' on Friday afternoon (20/09/13) at approximately 18.20, it became apparent when formwork around the thrust block struck on Saturday (21/09/2013) that concrete was very brittle and appeared deficient in cement content. Upon further inspection concrete which had then been cast for about 18 hours could be broken off by hand and was clearly understrength. As this thrust block was integral and critical to the TBM pass, we could not afford to wait for a 7 day concrete strength test to establish the characteristic strength, hence the decision was made to demolish the concrete and re-cast the thrust block.
| 02SL - Stations (LUL) | Cxxx-NCR-001231 | NCR | Manual Monitoring of Farringdon Road During Soft Eye Breakout |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2013-10-14 | 2013-10-04 11:24 | -10 | 2013-09-23 18:21 | Surveying - Instrumentation and Monitoring | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | This is to notify of s non-conformance to monitor all instruments in the zone of influence of the SHW2 soft eye breakout. Although it was acknowledged in the I&M engineering meeting on 16/08 that adequate monitoring was being presented at the SRG, the specification requires all manual monitoring within the zone of influence of SCL to be carried out daily (assuming soft eye breakout is to be considered SCL)
| 02SL - Stations (LUL) | Cxxx-NCR-001232 | NCR | STW2-PL1 - Minimum Lining thickness not achieved - TH16 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-05-09 | 2014-05-02 17:05 | -7 | 2013-09-25 09:22 | Tunnelling - Linings - Sprayed Concrete | 32500 |  | Workmanship | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | (NCR-Cxxx-01030 "STW2-PL1 - Minimum lining thickness not achieved -TH16" was closed by error). Retrospective review of the recorded excavation profile for top heading 16 highlighted an area of under-excavation, between 1 o'clock and 3 o'clock, of up to 96mm. The spray vs excavation profile comparison raised concerns that the minimum lining thickness had not been achieved. Proof drilling proved that, in an area of approximately 1m squared, the minimum lining thickness had not been achieved by up to 120mm. This is contrary to the requirements of both the design drawing and the RESS. Cover Shift Engineer encountered difficulty in setting out excavtion profile due to unusual shape of tunnel at transition between STW2 and PL1. Proof drilling was required to determine if the issue was in the survey data recorded or actual under excavation.
| 02SL - Stations (LUL) | Cxxx-NCR-001235 | NCR | ETH Installation of walers and propping - Two Storey Basement - South side |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2013-10-25 | 2013-10-18 18:31 | -7 | 2013-09-30 17:31 | Civil - Structural Engineering | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | have started the installation of walers and propping at the Two Storey Basement (South side) without the Pre-start check sheet in places as Hold point of the ITP and also without the complete acceptance of documentation for this activity
| 02SL - Stations (LUL) | Cxxx-NCR-001236 | NCR | South Basement - L0 Capping Beam S - Void in Concrete Under Box-Out |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-10-29 | 2013-10-29 09:33 | 0 | 2013-09-30 17:45 | Structural Engineering - Concrete Member | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | Once the formwork was struck for L0 Capping Beam S a void was noticed on the Eastern face below the box out. Please see attached photos for details.
| 02SL - Stations (LUL) | Cxxx-NCR-001237 | NCR | TaMs TBU026 not installed up to design length |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-10-25 | 2013-10-17 13:04 | -8 | 2013-10-02 12:17 | Geotechnical Engineering - Compensation Grouting | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | TaM TBU026 at Butchers Ramp has not been drilled to final length due to an unknown obstruction being encountered. TaM length is currently 42m out of planned design length of 61m.
| 02SL - Stations (LUL) | Cxxx-NCR-001239 | NCR | Damage to Inclinometer Monitoring Point Cxxx-IM-B301 in the ETH |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-10-16 | 2013-10-16 11:00 | 0 | 2013-10-02 13:03 | Geotechnical Engineering - Supported Excavations | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Previous Construction - Interfacing issues | Completed |  | Drilling for the fixings of a waler gallows bracket to the face of the secant pile in which inclinometer monitoring point (IMP) Cxxx-IM-B301 is located pierced the steel reservation tube and ABS casing of the monitoring point.
| 02SL - Stations (LUL) | Cxxx-NCR-001240 | NCR | TaMs TBU024 not installed up to design length |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-10-30 | 2013-10-16 08:32 | -14 | 2013-10-02 13:09 | Geotechnical Engineering - Compensation Grouting | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | TaM TBU024 at Butchers Ramp has not been drilled to final length due to an unknown obstruction being encountered.
| 02SL - Stations (LUL) | Cxxx-NCR-001241 | NCR | In tunnel dewatering and depressurisation Method Statement not adheared to |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-10-24 | 2013-10-18 13:45 | -6 | 2013-10-03 17:17 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | An alternative method was used to that detailed in the Method Statement during probing activities
| 02SL - Stations (LUL) | Cxxx-NCR-001242 | NCR | ETH-SB-Temp Prop MCRs Not Approved |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-10-18 | 2013-10-18 17:48 | 0 | 2013-10-04 16:14 | Civil - Structural Engineering | 500 |  | Planning | Rework | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | The following MCRs are not approved for the temporary propping works for the ETH South Basement: - Cxxx--C-LRC-M123-50227 - Cxxx--C-LRC-M123-50248 - Cxxx--C-LRC-M123-50233 - Cxxx--C-LRC-M123-50289 will installed the temporary propping without approval for these MCRs. The props will however not be loaded until all above MCRs are approved.
| 02SL - Stations (LUL) | Cxxx-NCR-001244 | NCR | Started Pre-Augering On Site Without Up To Date Tall Plant Concession |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2013-10-28 | 2013-10-15 13:15 | -13 | 2013-10-07 12:55 | Civil - Excavation | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Pre Augering for Sheet Piling started on site without an up to date Tall Plant Concession being submitted and approved. The Tall Plant Concession that was approved had in a different type of rig and a different method for installing the sheet piles. In the Tall Plant Concession it stated that a __ was to be used but instead a__ was being used and also this document stated the rig will only be used to drive the first 3 sheet piles after which a friction unit will be mounted on the piles and only a crane will be in operation as opposed pre-augering before all sheet piles and installing with the same machine
| 02SL - Stations (LUL) | Cxxx-NCR-001245 | NCR | Deficient TAM setting out in Charterhouse Square shaft |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-11-29 | 2013-11-28 10:30 | -1 | 2013-10-07 19:14 | Civil - Civil Engineering General | 50000 |  | Workmanship | Rework | 2 (6-60k) | Complete | Management Problem - Other | Completed |  | Due to errors in the setting out of the Grout Shaft and the entry points of the TAMs, these were drilled in a wrong location leaving areas of the compensation grouting area with insufficient coverage.
| 02SL - Stations (LUL) | Cxxx-NCR-001246 | NCR | Advance 69 Loss of Pull Out Test Panel |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-11-14 | 2013-11-08 15:36 | -6 | 2013-10-09 20:33 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Personnel Error - Other human error | Completed |  | On Advance TH69 Pull Out Tests were not carried out. The Shift Engineer was aware of the requirement and it was included in the Shift Briefing. Due to the tight spatial constrictions of the CH1 Pilot Tunnel, the Pit Boss was concerned about spraying the medium panel required. The decision was made to spray two small panels. These were srayed. The reason for the two small panels was communicated to the following Shift Engineer, and he in turned briefed his gang. However, just prior to spraying the next advance primary lining the two panels were knocked out by a member of the gang that had forgotten that they were required for nail testing.
| 02SL - Stations (LUL) | Cxxx-NCR-001247 | NCR | Advance TH 74 No Penetrometer Panel Sprayed |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-11-14 | 2013-11-07 16:37 | -7 | 2013-10-09 20:54 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Verbal communication problem | Completed |  | Method statement Cxxx- -C4-GMS-M123-50007 was not followed. A panel was not sprayed in accordance with the Method statement. this resulted in early strengths not being recorded.
| 02SL - Stations (LUL) | Cxxx-NCR-001248 | NCR | Failed Early Strengths |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-01-17 | 2014-01-16 09:49 | -1 | 2013-10-10 16:44 | Tunnelling - Linings - Sprayed Concrete | 1000000 |  | Material | Rework | 1 (>60k) | Complete | Material/Preservation Problems - Other | Completed |  | Various advances did not achieve the minimum specified early strength requirement.
| 02SL - Stations (LUL) | Cxxx-NCR-001249 | NCR | ETH - Trapezoidal Shaft - B3/T3 Couplers missing from Capping Beam |  | Contr | BAM | FAR - Farringdon Station (West) |  | 2013-11-09 | 2013-11-02 17:03 | -7 | 2013-10-11 16:15 | Structural Engineering - Reinforcement | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | The RC drawings for Level -2 generated by __ and approved by Cxxx currently show slab starter couplers to be installed in the capping beam at B1/T1/B3/T3 levels as shown in "Slab Starter Details" on drawing Cxxx-ATK-S-DWG-M123_3-50120 C04 that was issued on 17/07/13. This capping beam was poured on 05/06/13 in between gridlines 8 and 9 using the latest drawing at the time which was Cxxx-ATK-S-DWG-M123_3-50120 C02 which was issued on 08/02/13 that does not show any B3/T3 couplers to be installed. However, the Cxxx Level -2 RC intent drawing (Cxxx-SWN-S-DDL-M123_3-42201 C01) and the __ slab drawings (Cxxx-ATK-S-DWG-M123_3-50104 C05 and 3-50105 C05) show bars at B3 and T3 levels that need to screw into couplers into the capping beam that were not been detailed on Cxxx-ATK-S-DWG-M123_3-50120 C02 that was used at the time the capping beam was being built. These B3 and T3 couplers have recently been added to drawing Cxxx-ATK-S-DWG-M123_3-50120 C04 but there are still some couplers missing for bars south of gridline 7'.
| 02SL - Stations (LUL) | Cxxx-NCR-001250 | NCR | RSA 150*150*10 not installed on walers W9 and W5 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-11-08 | 2013-10-18 18:29 | -21 | 2013-10-16 15:33 | Civil - Civil Engineering General | 1000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Delivery of waler W5 and W9 on site, noticed that walers were missing RSA 150*150*10
| 02SL - Stations (LUL) | Cxxx-NCR-001252 | NCR | Failiure to follow BFK Temporary works procedure and carry out any inspections of the temporary hoarding since takeover of WTH site from Cxxx |  | Crossrail | PDP | FAR - Farringdon Station (West) |  | 2013-10-30 | 2013-10-31 13:00 | 1 | 2013-10-16 10:36 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Failiure to carry out any inspections of the temporary hoarding since takeover of WTH site from Cxxx
| 02SL - Stations (LUL) | Cxxx-NCR-001253 | NCR | SCL - Radial Probing not completed as per RESS |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-11-19 | 2013-11-21 17:13 | 2 | 2013-10-22 10:30 | Tunnelling - Linings - Sprayed Concrete | 30000 |  | Workmanship | Rework | 2 (6-60k) | Complete | Personnel Error - Verbal communication problem | Completed |  | During radial probing activities within CH1 Pilot Tunnel; the probing pattern, specified in the revised issue RESS, was not achieved.
| 02SL - Stations (LUL) | Cxxx-NCR-001255 | NCR | Manual Monitoring of CH1 Pilot Tunnel |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2013-11-01 | 2013-11-01 11:09 | 0 | 2013-10-18 18:30 | Surveying - Instrumentation and Monitoring | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | Manual monitoring was not undertaken as per the specification outlined in Cxxx-OVE-C2-DDJ-CR001_Z-31531 Schedule of Assets in relation to drawings Cxxx-OVE-C2-DDA-CR001_Z-31532 and Cxxx-OVE-C2-DDA-CR001_Z-31531 during the CH1 Pilot tunnel and the excavation of the East Ticket Hall.
| 02SL - Stations (LUL) | Cxxx-NCR-001256 | NCR | SCL - Ground exposed for longer than 3 hours |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-11-29 | 2013-11-28 17:12 | -1 | 2013-10-21 15:00 | Tunnelling - Linings - Sprayed Concrete | 8000 |  | Equipment Breakdown | Rework | 2 (6-60k) | Complete | Supervision - Other | Completed |  | During advance B115 in CH1 Pilot Tunnel, the face was open for more than the minimum 3 hours stipulated in the RESS.
| 02SL - Stations (LUL) | Cxxx-NCR-001257 | NCR | SCL - Early strength test panel not sprayed |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-12-02 | 2013-12-02 13:34 | 0 | 2013-10-21 14:59 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Not Defined | Completed |  | During advance TH123 in CH1 pilot tunnel, the required test panel was not sprayed on completion of the advance.
| 02SL - Stations (LUL) | Cxxx-NCR-001258 | NCR | ETH - Prop End Plates Bowed |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-11-05 | 2013-11-04 17:51 | -1 | 2013-10-22 10:00 | Structural Engineering - Steel Member | 1000 |  | Design | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The end plates on Props TSP 8,9,10 and 11 have bowed during fabrication which means the props end plates are not flush with the connection plate on the waler.
| 02SL - Stations (LUL) | Cxxx-NCR-001259 | NCR | ETH - TSP6 prop prop connections |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-11-05 | 2013-11-04 17:46 | -1 | 2013-10-22 10:22 | Structural Engineering - Steel Member | 1000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The connection between the flange plates on prop TSP6 are not flush - This is due to the flange plates bowing out during the fabrication of the props. The flange plates should allow the props to to be bolted up flush however there are still some gaps between the props. Prop location is as per ITP +/- 10mm however plates should be flush to avoid excessive movement
| 02SL - Stations (LUL) | Cxxx-NCR-001260 | NCR | ETH - Excavation sheets incorrectly filled out |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-11-05 | 2013-11-04 17:48 | -1 | 2013-10-22 10:45 | Civil - Excavation | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Supervision - Not Defined | Completed |  | The daily excavation sheets had been filled out by the ETH team incorrectly. It stated that the excavation was within the +/-50mm tolerance wher eas the level survey showed it was 12mm outside of this.
| 02SL - Stations (LUL) | Cxxx-NCR-001261 | NCR | ETH - Procedural, installing geothermal pipework without and approved MCR |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-11-12 | 2013-11-08 19:14 | -4 | 2013-10-22 11:12 | Civil - Hydraulic Engineering | 500 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | The geothermal pipework has been installed within the reinforcement cage at level -2 trapezoidal shaft wihtout and approved MCR. If we delayed geothermal pipe installation further it would not be safe of practical to undertake the works.
| 02SL - Stations (LUL) | Cxxx-NCR-001262 | NCR | SCL - Welding Procedure |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-03-28 | 2014-03-28 16:40 | 0 | 2014-02-27 11:46 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | undertook site welding without an approved welding procedure in place and therefore were not able to prove and maintain the quality of the fabrication as specified in KM10.2206 (a) nor able to demonstrate the testing methods as detailed in KM10.2206 (e). This site welding activity was required to join the new muck bin frame to the steel temporary platform.
| 02SL - Stations (LUL) | Cxxx-NCR-001263 | NCR | ETH - Gallow Bracket - Horizontal Proping |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2013-11-18 | 2013-11-15 12:00 | -3 | 2013-10-25 19:03 | Civil - Structural Engineering | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | failed to carry out pre-installation checks for one of the South Basement Gallow Brackets installed under the waler beam W10 at the long lane site. The Gallow bracket was bigger than the specified design, this was just noticed during installation. proceed to cut the bracket to fit P22 horizontal Prop with out SNC in place. The SNC was issued to CRL a week after the activity took place. Refer to SNC Number (Cxxx--C-CCN-M123-51067)
| 02SL - Stations (LUL) | Cxxx-NCR-001264 | NCR | ETH - Trapezoidal Shaft - Misaligned Couplers in Beam B3 |  | Contr | BAM | FAR - Farringdon Station (West) |  | 2013-12-11 | 2013-12-12 12:32 | 1 | 2013-10-28 14:22 | Structural Engineering - Reinforcement | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | Slab Starter bars installed in the intersection of beam B3/B7 and wall W19/W5A, should have 6No couplers installed for the 6No B32-321-150 LB in the B2/T3 layers. The 6No is shown on "Level -2 slab reinforcement detail (part plan)" - drawing number Cxxx-ATK-S-DWG-M123_3-50106 C04 (highlighted and attached). have installed the couplers but didn't realize that these do not go up to the end of beam B3 since the slab kicks in ~50mm. We have only been able to install 5No L-bars because the final coupler is right next to the face of the shutter shown in the photos attached. The slab starter bars were not shown clearly on this elevation on the wall/beam drawings during the construction of the capping beam (B3). The slab starter bars are shown on Cxxx-ATK-S-DWG-M123_3-50120 C04 on "Continuation of Slab Starter Details" for the T2/B2 layers.
| 02SL - Stations (LUL) | Cxxx-NCR-001265 | NCR | Fresh fibre content |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-12-20 | 2013-12-18 10:05 | -2 | 2013-10-31 14:44 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Fresh fibre content average has been less than designed (35 m3). 24/09/13 average of fresh fibre content 27.1 m3 09/10/13 average of fresh fibre content 30.1 m3 14/10/13 average of fresh fibre content 30.6 m3
| 02SL - Stations (LUL) | Cxxx-NCR-001266 | NCR | Late submission of Overlap/Takeover reports |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-11-15 | 2013-11-12 16:38 | -3 | 2013-11-01 13:54 | Surveying - Instrumentation and Monitoring | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | In accordance with Cxxx Specification for the Control of Ground Movement Cxxx-OVE-C2-RSP-M123-00002 clause 3.1.1.3, the Contractor is required prepare a report confirming the acceptability or otherwise of the systems [installed by Others] and this should be supplied to the Project Manager within 30 days of the contract date or of the systems being commissioned, whichever is later. Although these reports were prepared by the Contractor and previously presented at the SRG, they have not been formally submitted via the contact document control system. It should be noted that these reports are neither a deliverable nor required PM acceptance.
| 02SL - Stations (LUL) | Cxxx-NCR-001269 | NCR | Traceability |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2013-11-27 | 2013-11-22 15:39 | -5 | 2013-11-06 12:29 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | On the 14/10/2013 during a Crossrail led surveillance, held at the Farringdon office, the subject; in situ concrete verification records. The Contractor has been asked to demonstrate traceability of the consignment of reinforcement for the level -2 slab. The information to be supplied in the form of a mill test certificate. After 21 days the Contractor was unable to provide this.
| 02SL - Stations (LUL) | Cxxx-NCR-001270 | NCR | Leaking Joint on Cross-Connection Steel Special Pipe at Detail A St John Street |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-12-01 | 2013-11-26 08:40 | -5 | 2013-11-06 16:11 | Utilities Engineering - Water | 5000 |  | Workmanship | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following a visit from __ on 04/11/2013 at 1400hr to commission the cross connection at Detail A. On 05/11/2013 morning __ noticed a significant amount of water within the excavation (excavation was for the CCTV survey) for the 16" water main at Detail A. __ raised this issue with at 0830hr and then immediately notified Crossrail/__. __s initial thought was that it was from a back-charge but further investigation/excavation showed ground water traced back to the cross connection. The cross connection had been commissioned by __ the day before. __ from __ confirmed the leak on the cross connection by opening the valve. To expose the leaking area __ excavated down to expose the cross connection. __ from __ re-opened the valve which confirmed visually that the leak was coming from the joint to the east side of the steel special pipe.
| 02SL - Stations (LUL) | Cxxx-NCR-001271 | NCR | ETH – Over Excavation in area with Hold Point and check sheets incorrectly filled out |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2013-12-06 | 2013-11-29 16:29 | -7 | 2013-11-06 19:20 | Civil - Excavation | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Permit to Dig183 in place with a Hold Point to 109m. have not had control on site and the excavation went beyond the hold point level to 108.8. In addition, the daily bulk excavation sheets for this week had been filled out again by the ETH team incorrectly. These bulk excavation sheets should contain all levels and any remarks accordingly with the excavation works, whether the works corresponds to day/night shifts, hold points and notes of the permits to dig and also need to be legible
| 02SL - Stations (LUL) | Cxxx-NCR-001272 | NCR | ETH - Trap shaft - MEP box outs in southwest corner of -2 slab out of position |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-12-03 | 2013-11-14 21:13 | -19 | 2013-11-11 14:04 | Structural Engineering - Concrete Member | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | The voids marked up on the attached sketch, Cxxx/SR/ETH/TRP19 are too far North by 50, 75 and 50mm respectively. There was a miscommunication between the engineers and the joiners during the setting out of the void locations. All the voids are the correct sizes and within tolerance in the East-West plane. The box-outs which form these voids have been fixed to the blinding and all the reinforcement for the -2 slab has been installed around them. Re-positioning of the voids is not possible without removing all the steel in this section of the slab. To prevent this happening again engineers will ensure joiners fully understand the setting out marks/lines provided and will check the position of the box-outs after installation but prior to the placement of reinforcement. Please see associated FCD: 'FAR-CRL FCD-Cxxx-001165'
| 02SL - Stations (LUL) | Cxxx-NCR-001273 | NCR | Compliance with Vol 2B Part 22 – Temporary Works Design & Implementation |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2013-12-20 | 2013-12-20 10:49 | 0 | 2013-11-12 17:23 | Electrical - Electrical Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | Non compliance with Part 22 of Works Information in relation to MEP temporary works design. Non-conformances: - Temporary works designs not being submitted to the Project Manager 28 days in advance of procurement or erection - MEP temporary works not being listed on the Temporary Works Register - TW Design Management Plan does not include MEP scope - Temporary MEP works not being planned and coordinated with the remaining of Civil works.
| 02SL - Stations (LUL) | Cxxx-NCR-001274 | NCR | ETH - SB - Pile E109 Breakdown Too Low |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-12-09 | 2013-12-09 17:38 | 0 | 2013-11-18 14:08 | Civil - Structural Engineering | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Pile E109 should have been broken down to level 104.993mATD. The edges of pile E109 have been broken down to this level but the centre of this pile has been broken down to 104.935mATD. Please see attached photos for more details.
| 02SL - Stations (LUL) | Cxxx-NCR-001275 | NCR | ETH - South Basement - Escalator and Geothermal pile rebar cutting |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-12-09 | 2013-12-06 13:05 | -3 | 2013-11-18 14:26 | Structural Engineering - Reinforcement | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | have cut the pile reinforcement in some of the geothermal and escalator piles without confirmation this is acceptable from Cxxx. The pile reinforcement that has been cut is shown on the attached sketch and photographs.
| 02SL - Stations (LUL) | Cxxx-NCR-001276 | NCR | ETH - TRAP SHAFT - missing vertical couplers for southern plunge columns at level -2 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-01-21 | 2014-01-22 08:30 | 1 | 2013-11-19 09:21 | Structural Engineering - Reinforcement | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Drawing Cxxx-ATK-S-DWG-M123_3-50118 C05 shows 28no downward facing, vertical couplers for each of the 2no C9 columns (RC columns cast around the SE and SW plunge columns). Due to the extreme congestion of reinforcement around these plunge columns, were only able to install 4no couplers per column. 1no coupler was installed in each corner of each column. The bar mark of the installed bars is the same as that shown on the drawing. The missing couplers were only identified during a final pre-pour inspection by a engineer the nightshift before the concrete pour.
| 02SL - Stations (LUL) | Cxxx-NCR-001277 | NCR | Poor Quality Cores in CH1 Pilot Tunnel |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-12-20 | 2013-12-19 09:02 | -1 | 2013-11-21 16:12 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | noticed poor quality particularly at the joint locations even after the implementation of new ATP (NCR 1143)
| 02SL - Stations (LUL) | Cxxx-NCR-001278 | NCR | Out of Calibration Pressure Gauges – Geothermal Pipe Installation |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-12-20 | 2013-12-18 15:44 | -2 | 2013-11-27 17:36 | Systems - Drainage/Pumping Systems | 500 |  | System Defect | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | A number of out calibration pressure gauges where located on site of testing Geothermal Loops. __ were not using the out of date gauges at the time.
| 02SL - Stations (LUL) | Cxxx-NCR-001279 | NCR | ETH-TRAP SHAFT- Inclinometer monitoring point T119 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-12-16 | 2013-12-06 13:53 | -10 | 2013-12-02 14:25 | Civil - Structural Engineering | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Inclinometer monitoring point T119 has been cut by 1465mm and is now flush with TOC at this location (106.418 ATD). As this is not a 500mm increment the inclinometer will require re-baselining.
| 02SL - Stations (LUL) | Cxxx-NCR-001280 | NCR | ETH - Blocked Geothermal Loops |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-05-09 | 2014-05-08 17:33 | -1 | 2013-12-02 16:11 | Civil - Geotechnical Engineering | 1000 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Contamination | Completed |  | have completed pile breakdown and tested all geothermal pipes in the Eastern Ticket Hall South Basement. In total four loops in four separate piles have been found to be blocked. U101, U105 & U306
| 02SL - Stations (LUL) | Cxxx-NCR-001281 | NCR | TaM deviation out of tolerance at Butchers Ramp Shaft |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-12-19 | 2013-12-16 12:15 | -3 | 2013-12-05 15:23 | Geotechnical Engineering - Compensation Grouting | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Upon analysis of the deviation of the drilled TaMs it has been identified that the vertical tolerances along TaMs TBU018, 029, 042B, 053, 055, 060, 083, 085, 087 may not have been met and there could be a conflict with the exclusion zones identified in the design drawings.
| 02SL - Stations (LUL) | Cxxx-NCR-001282 | NCR | TaM deviation out of tolerance at Moorgate Spur 1 Shaft |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-12-19 | 2013-12-18 12:11 | -1 | 2013-12-05 15:25 | Geotechnical Engineering - Compensation Grouting | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Upon analysis of the deviation of the drilled TaMs it has been identified that the vertical tolerances along TaMs TN1010, 012, 021, 024, 032, 044, 045, 047, 051, 053 and 056 may not have been met and there could be a conflict with the exclusion zones identified in the design drawings.
| 02SL - Stations (LUL) | Cxxx-NCR-001283 | NCR | TaM deviation out of tolerance at Moorgate Spur 2 Shaft |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-12-19 | 2013-12-18 12:21 | -1 | 2013-12-05 15:32 | Geotechnical Engineering - Compensation Grouting | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Upon analysis of the deviation of the drilled TaMs it has been identified that the vertical tolerances along TaMs TN2021, 025, 027, 053, 028, 030, 036, 038, 040, 059, 065, 073, 077, 085, 094 may not have been met and there could be a conflict with the exclusion zones identified in the design drawings.
| 02SL - Stations (LUL) | Cxxx-NCR-001284 | NCR | TaM deviation out of tolerance at Moorgate Spur 3 Shaft |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-12-19 | 2013-12-18 12:35 | -1 | 2013-12-05 15:34 | Geotechnical Engineering - Compensation Grouting | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | Upon analysis of the deviation of the drilled TaMs it has been identified that the horizontal deviation along TaM TN3018b and the vertical tolerances along TaMs TN3011, 022 may not have been met and there could be a conflict with the exclusion zones identified in the design drawings.
| 02SL - Stations (LUL) | Cxxx-NCR-001285 | NCR | TaM deviation out of tolerance Charter House Square Shaft |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2013-12-19 | 2013-12-16 13:16 | -3 | 2013-12-05 15:36 | Geotechnical Engineering - Compensation Grouting | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Upon analysis of the deviation of the drilled TaMs it has been identified that the vertical tolerances along TaMs TCS021, 027, 033, 041, 044, 045, 049B may not have been met and there could be a conflict with the exclusion zones identified in the design drawings.
| 02SL - Stations (LUL) | Cxxx-NCR-001286 | NCR | ETH - Trapezoidal Shaft - MPI Results for Plunge Column Works at Level -2 |  | Contr | BAM | FAR - Farringdon Station (West) |  | 2014-01-10 | 2013-12-19 08:36 | -22 | 2013-12-05 18:08 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Interfacing problems | Completed |  | The structural steel subcontractor (__) has been asked to provide MPI test certificates for welding works that were completed to the plunge columns in the Level -2 slab. More than 21 days have passed and the subcontractor has still not provided the test certificates even though the test was witnessed by a engineer with the MPI tester who verified on site that the welds had passed on the day of testing.
| 02SL - Stations (LUL) | Cxxx-NCR-001287 | NCR | SHW3 pile cut off level |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-01-10 | 2014-01-08 09:14 | -2 | 2013-12-06 15:34 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Inadequate/insufficient tooling. | Completed |  | The Eastern face of SHW3 secant piles has been exposed and piles broken to cut off level (piles E806, E805, E804, E803, E802, E801, E832, E831) The cut off level of these piles is 104.115m LHD as per drawing Cxxx-SWN-S-DDA-M123_Z-76027 and no information on the pile cut off tolerances has been found referenced. Due to the nature of the piling breakdown works, the tools available to carry on these works and the inexistence of pile cut off level tolerances, the level of 104.115 has not been achieved across the full pile area. The cut off level varies from 104.115 to blinding level generally and on some localised areas the cut off level is 104.025. (pile E806, E802, E831 - see attached photos)
| 02SL - Stations (LUL) | Cxxx-NCR-001289 | NCR | Damage to Secondary Trust Block |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-01-10 | 2013-12-18 09:23 | -23 | 2013-12-11 12:36 | Civil - Civil Engineering General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Personnel Error - Not Defined | Completed |  | During the installation of one of the primary steel props a small section of a secondary trust block was damaged. No reinforcement has been exposed.
| 02SL - Stations (LUL) | Cxxx-NCR-001290 | NCR | Loss of Strain Gauge Data on Level 2 of WTH SH-W2 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-03-07 | 2014-03-05 11:35 | -2 | 2013-12-12 10:27 | Surveying - Instrumentation and Monitoring | 500 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Not Defined | Completed |  | 32 Strain gauges on Level 2 of SH-W2 went offline/did not present readings on the 30/07/2013 leaving 16 operational. According to drawing number Cxxx-SWN-C2-DDA-M123_Z-40064 Strain Gauges should be read every 15 minutes, this hasn't been achieved. The reason why the strain gauges failed is because the Logger Box, into which the gauge cabling fed, collapsed onto the waler snagging a significant number of the gauge cables. Our investigations have revealed that one of the bolts holding the timber beam onto the face of the piles was removed and one end of the timber batten supporting the Logger Box was sawn off. It is believed that we will not gain any more information investigating the causes as currently no-one seems to know how the __ Logger Box fell off the face of the sheet piles. The Corrective Action will still need to be agreed; if Cxxx is required to re-instate the gauges for levels -2 & -3 we estimate it will take four days on site. This is only to check through and reconnect the damaged cables caused by the ‘failure’ of the Logger Box support frame and does not include any time re-instating gauges which have failed as a result of being struck by debris / lifting operations.
| 02SL - Stations (LUL) | Cxxx-NCR-001291 | NCR | Strain Gauge Out Alignment on Primary Props |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-01-10 | 2013-12-18 08:54 | -23 | 2013-12-12 15:00 | Surveying - Instrumentation and Monitoring | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | One of the strain gauge blocks installed on primary prop P4/3 was found to be out of alignment.
| 02SL - Stations (LUL) | Cxxx-NCR-001292 | NCR | Primary Trust Block installed in Incorrect Position |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-01-10 | 2014-01-06 10:48 | -4 | 2013-12-12 19:02 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During installation of the middle primary prop at Eastern Ticket Hall South Basement, became aware that lower trust blocks were incorrectly set out 50 mm too close to the upper thrust block.
| 02SL - Stations (LUL) | Cxxx-NCR-001293 | NCR | Batching of fibres |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-01-31 | 2014-01-31 10:03 | 0 | 2013-12-16 11:12 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | Manual batching of fibres in Silvertown batching plant from August 2013 until January 2014 (permanent works CH1 Enlargement - 12 advances).
| 02SL - Stations (LUL) | Cxxx-NCR-001294 | NCR | Lift pit capping slab out of spec |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-01-21 | 2014-01-15 17:07 | -6 | 2013-12-17 18:03 | Civil - Concrete Pavement | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Verbal communication problem | Completed |  | The capping slab over the redundant lift pit on the Caxton Slab, was cast using a different grade of concrete then the grade specified on the drawing. Drawing No: Cxxx--C-DWG-M123-50290 Rev-C01 calls for C40/50. The concrete used is a 17.2 SCL mix MCR:- Cxxx--C4-LRC-M123-50041 which is a C28/34.
| 02SL - Stations (LUL) | Cxxx-NCR-001295 | NCR | ETH SB - Capping Beam 0 Column Starters |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-01-17 | 2013-12-19 18:26 | -29 | 2013-12-19 14:02 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | A number of column starter bolts in capping beam 0 are out of alignment following a post concrete survey. C17 Column along GL6 max +10mm C17 Column along GL7 max -18mm C18 Column along GLC max +101mm C18 Column along GLB’ max -26mm C18 Column along GLD & 2 max -23mm
| 02SL - Stations (LUL) | Cxxx-NCR-001296 | NCR | Monthly testing |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-01-17 | 2014-01-17 15:18 | 0 | 2013-12-19 11:44 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | Monthly testing not done for December.
| 02SL - Stations (LUL) | Cxxx-NCR-001297 | NCR | Non-submission of periodic readiness review trackers |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-01-22 | 2014-01-28 08:40 | 6 | 2014-01-08 15:23 | Civil - Civil Engineering General | 500 |  | Planning | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | The contractor have not submitted readiness review trackers for two periods
| 02SL - Stations (LUL) | Cxxx-NCR-001299 | NCR | SCL - RESS Not followed in CH1 Enlargement |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-01-31 | 2014-01-22 07:44 | -9 | 2014-01-17 11:40 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | R.E.S.S. Not followed
| 02SL - Stations (LUL) | Cxxx-NCR-001300 | NCR | Internal Monitoring Installation 23-28 Charterhouse Square |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2014-02-04 | 2014-02-03 13:05 | -1 | 2014-01-21 10:13 | Surveying - Instrumentation and Monitoring | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | This NCR is to capture the non-conformance of approving a design change due to site restrictions for the internal monitoring of 23-28 Charterhouse Square through the formal FCD process. This design change from Cxxx-OVE-C2-DDA-CR001_Z-31402 was approved through an interface meeting with Cxxx on 12/12/2012, however this cahnge was not formally submitted by FCD.
| 02SL - Stations (LUL) | Cxxx-NCR-001301 | NCR | SNC wasn’t signed off before the works were carried out |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-02-07 | 2014-01-30 08:53 | -8 | 2014-01-24 15:33 | Civil - Concrete Pavement | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | Short notice change wasn’t signed off prior the works were being carried out - agreeing the change in scope to the original MS
| 02SL - Stations (LUL) | Cxxx-NCR-001302 | NCR | Concrete pour prior to TW check |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-02-17 | 2014-02-04 14:59 | -13 | 2014-01-27 14:40 | Civil - Concrete Pavement | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | The access ramp to the aggregate bays was cast prior to having the loadings check carried out by the temporary works department. I had cancelled the concrete delivery and informed both the civils team and the SCL team of the requirement. The Civils team had completed the form work during th day shift and the ramp area was ready. That night shift, the SCL team had a load of shotcreat out of spec, so instead of dumping it decided to be helpful and cast the ramp.
| 02SL - Stations (LUL) | Cxxx-NCR-001303 | NCR | WTH - OSD pile breakdown |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-03-28 | 2014-03-13 12:17 | -15 | 2014-02-04 08:41 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | While carrying out OSD pile breakdown, some of the pile cage reinforcement has been bent. Please see attached labelled photos.
| 02SL - Stations (LUL) | Cxxx-NCR-001304 | NCR | Concrete Ticket numbers not being recorded on the Sprayed concrete early strength testing Checksheet |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-03-02 | 2014-02-28 15:14 | -2 | 2014-01-31 14:49 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | During a surveillance on traceability of shotcrete being delivered from s to Farringdon SCL works it was observed that a number of Sprayed concrete early strength testing Checksheets did not have the concrete ticket numbers written on them.
| 02SL - Stations (LUL) | Cxxx-NCR-001305 | NCR | ETH SB - Pile breakdown out of tolerance |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-02-28 | 2014-02-27 09:42 | -1 | 2014-02-03 15:32 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During pile breakdown works for Slab -2 Beam 9 South Basement two number piles were broken down out of tolerance. Pile E105, see attached photo, has correct lap however the centre of the pile has been broken down too low at 104.898m ATD (95mm). Pile U201 has poor cut off finish on edges of piles. Lowest cut off point at 104.893m ATD however pile centre has correct level of 104.992m ATD.
| 02SL - Stations (LUL) | Cxxx-NCR-001306 | NCR | ETH - Trapezoidal Shaft - Capping Beam J Pocket of Debonded Concrete |  | Contr | BAM | FAR - Farringdon Station (West) |  | 2014-02-18 | 2014-02-17 14:58 | -1 | 2014-02-04 10:12 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | During striking the formwork for capping beam J (Beam B11) that was poured on 30/01/14, a pocket of concrete came out of the face with the shutter (photos attached). This occurred because a pocket of concrete had become debonded by the foam sheeting that was used to protect the face of the wall starter couplers that come out of the face for Wall W15. During the pour, concrete must have dislodged the foam sheeting and got around the back of it causing the debonding pocket.
| 02SL - Stations (LUL) | Cxxx-NCR-001308 | NCR | Early MEP and Structural Fixing Works for Cast-in Elements |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-02-18 | 2014-02-18 12:48 | 0 | 2014-02-04 11:01 | Mechanical - Public Health Engineering | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The design drawings for early MEP works for cast-in elements of PH drainage and electrical earthing systems, and structural steel column fixing bolts, have undergone at Gate 3 approval review and were granted 'conditional approval.' The conditions however have not been fully cleared and drawings therefore not issued for construction prior to the programmed works on site. The Gate conditions apply to assurance evidence requirements and are not related to the technical merits of the design indicated on the drawings. Following discussions and agreement with CRL the planned works will go forward in accordance with the programme; this NCR is recorded in recognition that the associated drawings have not yet been officially issued as for construction status. Gate conditions are being addressed as expeditiously as possible.
| 02SL - Stations (LUL) | Cxxx-NCR-001309 | NCR | Fibres stored at Silvertown and Vic Deep not stored under cover |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-03-06 | 2014-03-05 11:17 | -1 | 2014-02-04 13:51 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper storage of material | Completed |  | During a surveillance at Silvertown on the 17/1/14 it was observed that large bags of fibres where being stored in the open. The bags where open weave which are not waterproof and do let in moisture which means that s can not guarantee the fibres will remain dry as required by the manufactuers. This was also observed during a surveillance by crossrail on the 22/1/14 at victoria deep.
| 02SL - Stations (LUL) | Cxxx-NCR-001310 | NCR | Monitoring of temperatures of admixtures at Silvertown and Vic deep not taking place |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-03-06 | 2014-03-04 15:26 | -2 | 2014-02-04 13:57 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Other | Completed |  | During a surveillance at Silvertown on the 17/1/14 it was observed that s do not monitor the temperature of the admixtures TamCem HCA & TamCem 60. This was also observed during a surveillance by crossrail on the 22/1/14 at victoria deep.
| 02SL - Stations (LUL) | Cxxx-NCR-001311 | NCR | SCL - Incorrect Kwika-strip installation CH1 Enlargement |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-02-28 | 2014-02-27 10:44 | -1 | 2014-02-06 08:32 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | During advance B40 in CH1 Enlargement tunnel the Kwika-strip was not installed as per procedure detailed in the activity plan "Installation of Kwika-strip Reinforcement", resulting in subsequent damage to the Kwika-strip. (see attached Picture)
| 02SL - Stations (LUL) | Cxxx-NCR-001312 | NCR | SCL - CH1 Adv 64 Flow not to ITP |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-03-07 | 2014-02-28 13:40 | -7 | 2014-02-05 19:30 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | On Advance 64 Flow test was 480mm, this is below the stated range in ITP :- Cxxx--C4-ITP-M123-50002
| 02SL - Stations (LUL) | Cxxx-NCR-001313 | NCR | Sockets on building facade |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-02-19 | 2014-02-11 07:17 | -8 | 2014-02-05 17:36 | Surveying - Instrumentation and Monitoring | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | This NCR is issued because building sockets were not installed as per Cxxx photomontages. Please find marked up Cxxx photomontages showing the alternative installations. This installation consist of a Precise levelling point (Stud) located on the pavement with close proximity to the original design. An FCD should have been issued prior to any alteration in installation, hence issuing this NCR.
| 02SL - Stations (LUL) | Cxxx-NCR-001314 | NCR | ETH - Trapezoidal Shaft - Props P26 & P27 - Submission of MCR information & Approval of Drawings in time for Construction |  | Contr | BAM | FAR - Farringdon Station (West) |  | 2014-02-21 | 2014-02-19 18:41 | -2 | 2014-02-06 14:14 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | Due to the lack of response from __ and the late receival of information to for materials approval information, this has delayed the submission of the MCR CHS Props (Cxxx--C-LRC-M123-50233) to include the information for Props P26 & P27. Also during the inspection of the props at __ yard on 03/02/14, site engineer (__) was given some new drawings by __ (__a) that had not received prior to inspection or given time to gain 3rd party approval from TW designer (__ - __) in order to approve these drawings and add this to the TW DRIR (Cxxx--C-LRG-M123-50023) in time for CRL acceptance. In accordance with the current programme dates, will be installing these props at our own risk. will submit the MCR on 07/02/14 for CRL acceptance. Note, the drawings are currently being added to the TW DRIR and are in the process of the being issued to CRL.
| 02SL - Stations (LUL) | Cxxx-NCR-001315 | NCR | ETH - Blocked Geothermal Loop in Pile U202 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-05-09 | 2014-05-08 17:39 | -1 | 2014-02-06 13:36 | Civil - Civil Engineering General | 1000 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Contamination | Completed |  | During Geothermal pipe testing in Pile U202, __ confirmed one loop out of four has become blocked. Attempts to unblock the loop have been unsuccessful.
| 02SL - Stations (LUL) | Cxxx-NCR-001316 | NCR | ETH - Trapezoidal Shaft - Bottom Mat Weldable Coupler levels on the South face of SE plunge column at Level -2 |  | Contr | BAM | FAR - Farringdon Station (West) |  | 2014-03-07 | 2014-02-20 11:34 | -15 | 2014-02-07 11:21 | Structural Engineering - Welding | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During excavation works to expose the south face of the south east plunge column at level -2 in order to construct Beam B10, it was noticed that the weldable couplers that have been welded in the position of the bottom mat of Beam B10 have been welded on at the wrong level. During the welding works, the weldable couplers were placed at the same level at the level -2 slab that is 1m thick. Unfortunately, Beam B10 is 1.3m deep so the couplers need to be installed at a level approximately 300mm lower from where it has been currently installed as shown in the attached photo.
| 02SL - Stations (LUL) | Cxxx-NCR-001317 | NCR | ETH - Incorrect Permit to Dig Level |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-02-21 | 2014-02-20 17:37 | -1 | 2014-02-07 16:51 | Civil - Excavation | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Incorrect permit to dig level issued to operatives for excavation works in Eastern Ticket Hall South Basement. Level stated on permit 105.518m however operatives required level to 104.918m for capping beam excavation.
| 02SL - Stations (LUL) | Cxxx-NCR-001318 | NCR | ETH - Trapezoidal Shaft - Cavity Wall Drainage Pipes |  | Contr | BAM | FAR - Farringdon Station (West) |  | 2014-04-05 | 2014-03-28 17:21 | -8 | 2014-02-08 14:36 | Mechanical - Piping | 5000 |  | Design | Repair | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | During construction of the trapezoidal shaft level -2 slab, were told by __ that we were ok to install a 50mm diameter plastic pipe into the slab at suitable locations as shown on the Cxxx-SWN-S-DDD-M123_Z-00110_C01 at 10m c/c. Due to all MEP drawings being provisional status, the site team reverted to Cxxx drawing because we were not provided by __ any further positional information or a drawing showing a different sized pipe made from a different material as shown on Cxxx--P-DDA-M123_3-25404_P01.1. I've attached the provisional drawing showing the locations of the pipes should have installed had this design been issued for construction.
| 02SL - Stations (LUL) | Cxxx-NCR-001319 | NCR | ETH - Procedural Non Conformance – Geotechnical Logging Control |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2014-03-07 | 2014-03-07 15:31 | 0 | 2014-02-10 11:04 | Civil - Excavation | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Supervision - Other | Completed |  | Incorrect geotechnical logging from of the excavation works in Eastern Ticket Hall South Basement Bulk Excavation Check sheets are part of the ITP (Cxxx--C-ITP-M123-50085, item 6, Hold Point) and were not filled properly for a week (03.02.14 to 07.02.14). Inconsistent sites levels were reported to the SRG meeting on a daily basis. The weekly data has been revoke by CRL and will replace it with the correct information.
| 02SL - Stations (LUL) | Cxxx-NCR-001320 | NCR | OSD Pile Breakdown Level Exceeded - WTH |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2014-03-28 | 2014-03-13 13:10 | -15 | 2014-02-10 13:10 | Civil - Excavation | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | While carrying out the OSD pile breakdown to cut off level is required to be 75mm above the blinding. This level has been exceeded on 3 piles to date and in some places the cut off level is flush with the blinding concrete. See attached photos for piles U205, U204, U217, S211
| 02SL - Stations (LUL) | Cxxx-NCR-001321 | NCR | SCL - Low early strengths during CH1 enlargement construction |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-04-09 | 2014-04-10 08:45 | 1 | 2014-02-10 17:09 | Tunnelling - Linings - Sprayed Concrete | 240000 |  | Material | Use As-Is | 1 (>60k) | Complete | Discipline/Workmanship - Other | Completed |  | Low early strengths not achieved according to ITP Cxxx--C4-ITP-M123-50024
| 02SL - Stations (LUL) | Cxxx-NCR-001322 | NCR | Incorrect calculation and presentation of Rod Extensometers |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-03-21 | 2014-03-21 11:24 | 0 | 2014-02-11 15:56 | Surveying - Instrumentation and Monitoring | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Personnel Error - Other human error | Completed |  | Following a detailed review of the extensometer data being supplied to UCIMS via the SAI software, it became apparent that the data had not been calculated and applied correctly.
| 02SL - Stations (LUL) | Cxxx-NCR-001324 | NCR | SCL - Missing 28 day compressive strength tests for CH1 pilot |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-02-25 | 2014-02-18 10:37 | -7 | 2014-02-11 14:50 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Compressive strength test core was not crushed for 28days test.
| 02SL - Stations (LUL) | Cxxx-NCR-001325 | NCR | SCL - 28 Day compressive strengths lower than Target value CH1 enlargement Adv 1 / 11 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-03-25 | 2014-03-24 12:30 | -1 | 2014-02-11 15:31 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Other human error | Completed |  | Target Value of compresive strength not reached for 28 day cores. On advance 1 (FAR225) and 11 (FAR232) of CH1 enlargement.
| 02SL - Stations (LUL) | Cxxx-NCR-001326 | NCR | SCL - 28 day Flexural strength no achieved STW3 - CH1 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-07-11 | 2014-07-25 16:05 | 14 | 2014-02-13 14:47 | Tunnelling - Linings - Sprayed Concrete | 30000 |  | Supervision/Management | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | Faliure to achieve 28 day flexural strength in accordance with Table KT20-06 - Flexural strength - 2No. of 3 failed from beams sprayed on 3/1/14 and tested @ 28 days, they failed just outside the 10% allowance -90 days, 1No. abrupt failure 2No. passed
| 02SL - Stations (LUL) | Cxxx-NCR-001327 | NCR | Automatic Inclinometer IB5 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-03-03 | 2014-03-03 13:56 | 0 | 2014-02-24 09:44 | Surveying - Instrumentation and Monitoring | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | According to Cxxx-OVE-C2-DDA-CR001_Z-31534, inclinometers should be installed 10m below the tunnel invert and the automatic inclinometer was installed only 3m below invert level. The borehole was drilled to a depth of 43m which is 10m below the SCL tunnel at 82mAOD. However the ground condition at that level was sand and gravel which meant the ground collapsed to a depth of 41.5m, discussed this with Cxxx and it was agreed to install Inclinometer tubes to that depth. Furthermore, an Automatic sensors where installed which consist of 3m long rods to a depth of 36m. Only 3m below invert level which shouldve been a Max of 39m due to the Incli casing length (41.5 i.e. 39+3 = 42 not possible) An additional Rod was installed to 39m below ground level (76m AOD) Please note that no significant movement occurred from TBM passage, see attached graph.
| 02SL - Stations (LUL) | Cxxx-NCR-001329 | NCR | ETH-TRAP SHAFT-F2 surface finish damaged on side face of capping beam J during excavation |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-03-04 | 2014-02-21 12:13 | -11 | 2014-02-18 14:16 | Civil - Structural Engineering | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | During the excavation of the soffit underneath capping beam J, the vibration caused by breaking out the back blinding has caused the surface of the side face of capping beam J to break away. It can no longer be classed as an F2 finish. Please see the attached photograph which shows the surface damage.
| 02SL - Stations (LUL) | Cxxx-NCR-001330 | NCR | Prisms Charterhouse 33-37 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-03-19 | 2014-03-25 14:51 | 6 | 2014-02-19 13:35 | Surveying - Instrumentation and Monitoring | 500 |  | System Defect | Repair | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | The Cxxx – M&W Specification KX10.3210 d) – Instrumentation & Monitoring Cxxx-OVE-Z4-RSP-CR001-00007 establish “Total station shall be capable of automatically taking readings at the specified frequency and updating their position without human assistance once programmed” The prisms on the South façade at the 33-37 Charterhouse square showed about 6mm movement following TBM; however, the prisms on the North façade of the same building shown only about 1-2mm settlement over the same time (as seen on UCIMS). This is not as expected as the TBM alignment is slightly to the north of the building and greater settlement on the north would be anticipated. The south façade is mainly read by ATS 4 and the North façade by ATS 7. Due to malfunctioning of the application that transfers fix coordinate from the master ATS (with references outside of ZOI) with the linked ATSs (which share references inside ZOI with the master ATS), the ATS 7 didn’t update its position automatically and the correction of the readings were not done properly.
| 02SL - Stations (LUL) | Cxxx-NCR-001331 | NCR | Prisms Group 2 ( ATS 18 , 15 and 13) – Erroneous Geomos Set up |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-03-19 | 2014-03-25 14:55 | 6 | 2014-02-19 16:48 | Surveying - Instrumentation and Monitoring | 500 |  | System Defect | Repair | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | An exercise comparing the readings taken among the ATS 18, the manual readings (levelling sockets) and the data coming from Cxxx (all of them on the Butcher ramp retaining wall) detected a discrepancy of 3-4mm between the ATS 18 and the other two sources of data. After the study the historical movement of the ATS 18 the main difference has been recorded during the passage of the Westbound TBM. The investigation of the behaviour of the ATS and its references concludes that some shared references located inside of ZOI were set up as fixed when they should have been free. When these references were affected by the TBM, the ATS 18 didn’t update its position properly and consequently less movement was recorded by the monitoring points.
| 02SL - Stations (LUL) | Cxxx-NCR-001333 | NCR | ETH SB - Pile breakdown out of tolerance |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-03-05 | 2014-03-05 13:20 | 0 | 2014-02-19 15:59 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Other human error | Completed |  | During pile breakdown works in Eastern Ticket South Basement Pile U209 was unfortunately broken below required cut off level. Pile U209 was cut at correct level however when drill and buster was used, a crack line below 104.993 formed. Pile still has minimum embedment of 75mm.
| 02SL - Stations (LUL) | Cxxx-NCR-001334 | NCR | SCL - Beam reports not issued within specified timescale |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-03-12 | 2014-03-05 11:38 | -7 | 2014-02-19 18:04 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Other | Completed |  | did not issue the beam reports to CRL within the specified timescales detailed in KT20
| 02SL - Stations (LUL) | Cxxx-NCR-001335 | NCR | ETH-TRAP SHAFT- Omission of horizontal couplers for lining wall lacer bars |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-03-06 | 2014-02-24 18:07 | -10 | 2014-02-20 11:04 | Civil - Structural Engineering | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Personnel Error - Other human error | Completed |  | The horizontal couplers highlighted on the attached RC drawing (Cxxx-ATK-S-DWG-M123_3-50114 C07) and photographs were installed on the wrong line during the construction of the -2 slab and capping beam H2 lower.
| 02SL - Stations (LUL) | Cxxx-NCR-001336 | NCR | SCL - Failed 28 Day Fexural Strength CH1 enlargement, I20 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-07-11 | 2014-07-25 16:08 | 14 | 2014-02-21 15:23 | Tunnelling - Linings - Sprayed Concrete | 30000 |  | Workmanship | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Faliure to achieve 28 day flexural strength in accordance with Table KT20-06 - Flexural strength - 1No. of 3 failed from beams sprayed on 16/1/14 and tested @ 28 days (failure was abrupt) - 90 days - 6no. beams, 3 no. unload - reload failure. - reference to additional steel added to thickening see FCD - 1313 (see attached) - Attached is memo of DSP for temporary state
| 02SL - Stations (LUL) | Cxxx-NCR-001337 | NCR | WTH - Level -2 Slabs - Concrete cubes for blinding |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-03-23 | 2014-03-05 09:54 | -18 | 2014-02-21 18:14 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Civil and Structural Specification and WTH Level -2 Excavation ITP (Cxxx--C-ITP-M123-50032) require a set of concrete cubes to be taken for blinding concrete per 100m3 or per pour. On the majority of blinding pours for Level -2 slabs, cubes where not taken.
| 02SL - Stations (LUL) | Cxxx-NCR-001338 | NCR | Concrete Wagon poured past three hour batch time |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-04-07 | 2014-04-07 17:31 | 0 | 2014-02-23 11:48 | Civil - Civil Engineering General | 1000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | During pour of South Basement Slab 2. Wagon 10 & 11 exceeded the three hour limit between batching and pouring concrete. decided to continue with pour thus avoiding a cold joint, Sketch Cxxx/SR/ETH/SB19 shows location of where wagon 10 and 11 cast. were unable to procure new loads due to batching plant closing. Concrete Mix used was F3 Cxxx--C-LRC-M123-50145.
| 02SL - Stations (LUL) | Cxxx-NCR-001339 | NCR | Failed inclinometer installation at SH-W3 WTH |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-03-10 | 2014-03-10 12:24 | 0 | 2014-02-24 17:19 | Surveying - Instrumentation and Monitoring | 500 |  | Incomplete Works | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | According to drawing number Cxxx-SWN-S-DDL-M123_Z-76960 5No inclinometer are require to be installed at the higher level capping beam. However, 2 out of 5 inclinometers were not installed (highlighted on attached drawing) due to issues with the reservation tubes. Naming of pile E804 and E381 are from drawing number Cxxx-SWN-S-DDA-M123_Z-76026 attached. Inclinometer in pile E804 – at approximately 2.7m below capping beam level there is a constriction in the reservation tube. After some careful handling of the inclinometer casing it was possible to install the casing to the bottom of the reservation tube. However, when grouting operation started pressure was building up and we were unable to inject grout. believe because of the constriction there was not enough space for the inclinometer casing and grout pipe after inflation, please note that was the 4th inclinometer to be installed so method used is suitable. Grouting was stopped and the installation abandoned. Inclinometer in pile E831 - at approximately 3.3m below capping beam level there is a constriction in the reservation tube which has prevented the installation of the inclinometer casing to the full depth. have installed approximately 15m of casing. The installation was stopped at this level and the instrument was not grouted. A brief explanation on why believe that de-scoping them will not have a big impact is shown in the attached sketch THM-SHW3-01.
| 02SL - Stations (LUL) | Cxxx-NCR-001340 | NCR | Slump test result over the limit |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-04-18 | 2014-03-27 19:13 | -22 | 2014-02-26 17:02 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | On 25/02/2014 poured lining walls: W2, W3 and W4 (13m3 in total) at level -3 in the trapezoidal shaft. The concrete mix design was W1 and the target value range from 80mm to 180mm. The slump test carried out for the second concrete delivery was 190mm, which is 10mm over the limit. A second test was not carried out and this concrete was used to pour the walls. The concrete was poured within the 3 hours limit since batch time.
| 02SL - Stations (LUL) | Cxxx-NCR-001341 | NCR | ETH-TRAP SHAFT- Revised position and RC detailing of Beam B10 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-03-13 | 2014-03-11 17:14 | -2 | 2014-02-27 10:49 | Civil - Structural Engineering | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | This NCR supersedes FCD-001226. As stated in FCD-001226 the 6no. 40mm diameter couplers cast into the -2 slab on the west edge of the plunge column have been installed on the wrong line. As stated in the 'actual answer' section of FCD-001226, discussed onsite with __ on Monday 24/02/14 and agreed in the Engineering meeting with Cxxx on Tuesday 25/02/14, will widen Beam B10 by 100mm in the Western direction.
| 02SL - Stations (LUL) | Cxxx-NCR-001342 | NCR | SCL - Flow testing |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-03-28 | 2014-03-27 09:21 | -1 | 2014-02-28 09:05 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not trained for the work being performed | Completed |  | Following a surveillance on the flow testing procedure, an operative was seen to be performing the test incorrectly.
| 02SL - Stations (LUL) | Cxxx-NCR-001343 | NCR | ETH - TRAP SHAFT - W4 reinforcement issue |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-03-14 | 2014-03-10 17:27 | -4 | 2014-02-28 10:16 | Civil - Structural Engineering | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Previous Construction - Problems based on previous construction errors | Completed |  | This NCR replaces FCD - 1225. The southernmost 9no of the vertical couplers for the front face of W4 have been installed on the outside of the horizontal lacers (EF1 instead of EF2). This is because the couplers in Capping beam J (above) were installed on the wrong line. This is shown in the attached marked up drawing 3-50114 marked up rev2
| 02SL - Stations (LUL) | Cxxx-NCR-001344 | NCR | SH-W3 Level -1 Capping Beam Levels |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-03-14 | 2014-03-07 16:05 | -7 | 2014-02-28 13:54 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Previous Construction - Problems based on previous construction errors | Completed |  | Please find attached a level survey of the structural slab levels of the SH-W3 Level -1 Capping Beam. In accordance with the general notes drawing Cxxx-SWN-S-DDL-M123_Z-00101, the construction tolerances for the top of a slab are +10/-0mm. In localised areas along the Eastern and Northern elevations of the beam, the structural slab level is at worse 4mm low. In the South West corner of the beam the majority of the slab level is low, by up to 8mm. The levels along the southern elevation (east side) were raised in accordance with RFI 001581 to maintain cover despite the reinforcement being high in localised areas.
| 02SL - Stations (LUL) | Cxxx-NCR-001345 | NCR | SCL - Tunnel Monitoring frequency not achieved in PTW |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-03-19 | 2014-03-14 12:27 | -5 | 2014-03-03 10:35 | Tunnelling - Tunnelling General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | During Friday 28/02/14 night shift, the planned monitoring due at 5.00am was not carried and therefore did not meet the required monitoring frequency as stipulated in KT21 Instrumentation and Monitoring of SCL Works Specification, sub section KT21.3206.
| 02SL - Stations (LUL) | Cxxx-NCR-001346 | NCR | WTH - Level -2 Slabs - Geothermal pipes - Pile U217 - Blocked loop |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-05-08 | 2014-04-15 15:03 | -23 | 2014-03-03 18:26 | Mechanical - Mechanical Engineering General | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | One of the fours geothermal pipe loops on pile U217 on the WTH is blocked due to debris ingress during pile breakdown.
| 02SL - Stations (LUL) | Cxxx-NCR-001347 | NCR | SMM - Unsuccessful Concurrent Grouting Injections |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-03-31 | 2014-03-26 12:33 | -5 | 2014-03-04 10:24 | Geotechnical Engineering - Compensation Grouting | 500 |  | Incomplete Works | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | has established that a breach of the following 2 conditions has led to non-conformities occurring in some recent grouting injections. The conditions are: • Grouting proposals prepared under Clause KC21.2106 “Concurrent Grouting Strategy and Proposals” which specify a construction control alert if less than 80% by volume of injections are completed prior to commencement of the next set of advances • That over 20% of the planned injection volume was unsuccessful due to blockages in the TaM pipes The grouting episodes that are non-conformities and the volumes unsuccessfully injected only due to blockages are (total volume achieved in brackets): CH1 62-65: 22% unsuccessful (73% achieved) CH1 86-89: 21% unsuccessful (61% achieved) PTW 13-16: 21% unsuccessful (76% achieved) CH1 118-121: 37% unsuccessful (47% achieved) PTW 17-19: 25% unsuccessful (73% achieved) CH1 126-129: 25% unsuccessful (74% achieved) PTW 32-35: 20% unsuccessful (74% achieved) The other cause of unsuccessful injections are due to reaching the cut off pressure for the injection.
| 02SL - Stations (LUL) | Cxxx-NCR-001348 | NCR | WTH Concrete Temperature Exceeding 60oC |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-04-10 | 2014-04-07 12:18 | -3 | 2014-03-04 18:21 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | installed thermocouples in the Escalator Shaft Level -1 Capping Beam pour to monitor the internal concrete temperature. The highest temperature recorded was 69.24 degrees celsius. Clause KF10.1302a states that the maximum temperature of placed concrete will not exceed 60 degree celsius.
| 02SL - Stations (LUL) | Cxxx-NCR-001349 | NCR | Fleet Sewer Monitoring Visit - February |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-03-19 | 2014-03-15 12:28 | -4 | 2014-03-05 16:53 | Surveying - Instrumentation and Monitoring | 500 |  | Incomplete Works | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Insufficient work planning by the subcontractors | Completed |  | In February 2014, did not carry out the specified monthly visit to the fleet sewer as specified in Cxxx-OVE-C2-DDJ-CR001_Z-31531.
| 02SL - Stations (LUL) | Cxxx-NCR-001350 | NCR | WTH - Level -2 Slabs - Geothermal pipes pile S211 - Repairs - Pile below cut-off level |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-05-09 | 2014-05-07 09:32 | -2 | 2014-03-07 18:58 | Civil - Civil Engineering General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Inadequate/insufficient tooling. | Completed |  | Geothermal loop on OSD Pile S211 on the WTH has a leak (captured on NCR 1346).
| 02SL - Stations (LUL) | Cxxx-NCR-001351 | NCR | ETH - Level Control for Blinding and Excavation |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-03-28 | 2014-03-24 11:48 | -4 | 2014-03-11 09:51 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Supervision - Other | Completed |  | Blinding works in Slab 4 were commencing without a survey of excavation work. It was found that the excavation had been over dug by 41mm (21mm out of tolerance). reworked and installed additional fill to bring excavation to required depth. Additionally became aware that blinding previously poured had blinding of 100mm instead of the required 50mm.
| 02SL - Stations (LUL) | Cxxx-NCR-001353 | NCR | ETH - Incorrect earth pile connection Pile T118 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-08-29 | 2014-05-13 11:50 | -108 | 2014-03-13 10:55 | Civil - Civil Engineering General | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | During construction of Capping Beam H, connected copper tail from earth mat L-2 to Pile T118, as stated in drawing Cxxx--E-DDD-M123_Z-25703 and agreed with __. However after investigation into Cxxx as-built (Cxxx-NCR-000488) no electrically continuity has been installed in Pile 118.
| 02SL - Stations (LUL) | Cxxx-NCR-001354 | NCR | Level -2 soffit - Areas requiring repair surrounding lagged geothermal pipes |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-05-09 | 2014-05-08 14:00 | -1 | 2014-03-19 12:45 | Structural Engineering - Structural Engineering - General | 1000 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During excavation work to level -3 whilst exposing the soffit of the level -2 slab surrounding the North East plunge column, an area of concrete honeycombing was identified in the same location as the lagged geothermal pipes (42No 100mm dia) in level -2 slab. The area of honeycombing is approx. 0.5m south of the NE plunge column. Please note that the lagged geothermal pipes issue was discussed previoulsy through Cxxx-RFI-001361 and Cxxx-FCD-001169, and accoridng to FCD-001169 "Cxxx inspection was carried out on site 08:15am 14/11/13 prior to Level -2 trapezoidal slab pour".
| 02SL - Stations (LUL) | Cxxx-NCR-001355 | NCR | SCL - Rebound test frequency not achieved |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2014-04-10 | 2014-04-07 15:22 | -3 | 2014-03-20 09:17 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Rebound test frequency has not been achieved. The compliance tracker for January, February and March 2014 have yet to present results from rebound tests.
| 02SL - Stations (LUL) | Cxxx-NCR-001356 | NCR | SCL - Failure to follow Temporary works design procedure |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-05-09 | 2014-05-07 17:33 | -2 | 2014-03-20 13:01 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | Faliure to follow TWD procedure, Design brief should have been submitted to TWD team outlining proposal.
| 02SL - Stations (LUL) | Cxxx-NCR-001357 | NCR | SCL - No 90 days results for Dry Shrinkage |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-05-09 | 2014-05-07 17:31 | -2 | 2014-03-20 13:38 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | No 90 day tests taken for Dry shrinkage
| 02SL - Stations (LUL) | Cxxx-NCR-001358 | NCR | WTH -2 Level Slabs - Blocked Geothermal Loops - Pile S211 |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2014-05-09 | 2014-04-15 15:07 | -24 | 2014-03-21 11:32 | Civil - Civil Engineering General | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Contamination | Completed |  | During the testing of the Geothermal Pipes on Pile S211 it became apparent that 3 pipe loops were blocked. Despite several attempts to unblock them these 3 loops will ultimately be lost in this pile. To date there are 4 no. pipe loops that have been lost from subsequent pile breakdowns.
| 02SL - Stations (LUL) | Cxxx-NCR-001359 | NCR | SCL - Started STW1 breakout without an approved Method statement in place |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-04-23 | 2014-03-28 11:29 | -26 | 2014-03-24 10:13 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Carried out work on STW1 enlargement without an approved method statement in place. Cxxx- -C4-GMS-M123-50008
| 02SL - Stations (LUL) | Cxxx-NCR-001360 | NCR | MEP Installation - lack of design approval and documentation |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2014-04-18 | 2014-04-14 12:20 | -4 | 2014-03-24 11:41 | Mechanical - Piping | 0 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | During CRL inspection of MEP cas-in items (earth mat and public health pipes), it was noted that: 1- Design changes are not documented to check against i. Additional earth mat L Bars inslatted with no FCD submitted and approved ii. Change in gully positions and sleve material with no FCD submitted and approved. FCDs Cxxx-FCD-001248, C43-FCD-001249 and Cxxx-FCD-001251 covering the above design changes were submitted after installation. Pour carried out before the design changes were approved.
| 02SL - Stations (LUL) | Cxxx-NCR-001361 | NCR | ETH Pre-pour inspections - Slab 2 - Level -2 Base slab South Basement - procedural non-conformance |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2014-04-18 | 2014-04-16 18:59 | -2 | 2014-03-24 17:19 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | construction team invited CRL Field Engineers to attend pre-pour inspections worksites when; a) the work is incomplete b) the work is not in accordance with the accepted design c) agreed design changes are not documented to check against d) inspection records have not been signed off verifying compliance This was the case for the pre-pour inspection for slab 2 area at -2level of the South Basement (Cxxx-ETH-TSB-SUB7-0006) invited CRL and Quality team for a Pre-pour check inspection at Cap Beam 9, Cap Beam 5 and Slab 2 at the south basement on the 20.02.13 at 11am planning to pour at 2pm At the time of the pre-pour inspection, the Works in the area have not been finished and by 2pm were still fixing rebar. At 1:30pm this issue was discussed with Civil’s as they were clearly not ready to pour. ETH called off the concrete wagons until works were completed around 5pm when CRL inspected the area once again. This was obviously not properly planned and the concrete activity started late. Please refer to Observation Numbers #11312, #11314 and #11315
| 02SL - Stations (LUL) | Cxxx-NCR-001362 | NCR | ETH Pre-pour inspections – Slab 3a South Basement - procedural non-conformance |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2014-04-18 | 2014-04-16 19:01 | -2 | 2014-03-24 17:31 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | construction team invited CRL Field Engineers to attend pre-pour inspections worksites when; a) the work is incomplete b) the work is not in accordance with the accepted design c) inspection records have not been signed off verifying compliance This also was the case for the pre-pour inspection for slab 3a area at -2 level of the South Basement (Cxxx-ETH-TSB-SUB7-0015) Rebar installation to slab 3a continued on the day the pour was planned. The rebar installation and levels for the kicker for the lining wall were not ready on the pre-pour inspection from CRL. had to delay the pour until get everything in place. This slab was poured in two hits on 04/03/14 & 05/03/14 with the pour curtailed at the mid point emergency construction, due to a late start of the activity. should have the area ready and inspected before planning a pour. Please refer to Observation Number #11579
| 02SL - Stations (LUL) | Cxxx-NCR-001363 | NCR | WTH - Level -2 Slabs - Drainage I2a - Test failure |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-04-08 | 2014-04-07 14:36 | -1 | 2014-03-25 17:37 | Civil - Utilities Engineering | 500 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Inadequate/insufficient tooling. | Completed |  | Hydraulic test on run of drainage on I2A failed after Inspection Request to Crossrail.
| 02SL - Stations (LUL) | Cxxx-NCR-001364 | NCR | Use of drawing Cxxx-ATK-S-DWG-M123_3-50118 without approval |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-04-18 | 2014-04-17 14:25 | -1 | 2014-03-25 08:41 | Civil - Civil Engineering General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Supervision - Other | Completed |  | used drawing Cxxx-ATK-S-DWG-M123_3-50118 C05 without being approved on eB for pour Level -2 slab 4. Additional revision, from C04, was requested to follow Cxxx--CIN-00420 to __ to change levels of wall starters so they would be flush with top of slab. then followed with communication Cxxx--CCO-00951, where ETH Construction team confirmed that they can work with the existing RC detail drawings and the amendments are no longer required.
| 02SL - Stations (LUL) | Cxxx-NCR-001365 | NCR | Quality of ITP records submission |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-04-22 | 2014-04-17 12:19 | -5 | 2014-03-25 17:33 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Hand Back ITP Records for Sub Package 3 for Capping Beam South at the ETH was submitted to Cross Rail on 18th of March'2014. Upon submission of the hand back ITP records, it was identified that some of the reinforcement delivery tickets were not authorized by Site Engineers. It was also found that the quality of scanning of some of the Concrete dockets were very poor and were difficult to read. This is a non-compliance to the works information and hence the NCR.
| 02SL - Stations (LUL) | Cxxx-NCR-001366 | NCR | Early MEP Works - ETH Level-2 - CWD pipe not installed |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2014-04-10 | 2014-04-09 15:58 | -1 | 2014-03-27 17:20 | Mechanical - Public Health Engineering | 0 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | The 100mm CWD pipe on gridlines A'/6-7' of drawing Cxxx--P-DDA-M123_3-25405 P01 (refer to Attachment_1) has not been installed.
| 02SL - Stations (LUL) | Cxxx-NCR-001367 | NCR | SCL - Missing ITP information from Advance 67 in CH1 enlargement |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-04-26 | 2014-04-02 11:53 | -24 | 2014-03-26 17:48 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Missing ITP information (advance booklet) for Adv 67 in Ch1 enlargement.
| 02SL - Stations (LUL) | Cxxx-NCR-001369 | NCR | Non-compliance against the temporary works procedure |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2014-05-07 | 2014-05-06 14:08 | -1 | 2014-03-27 13:12 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Several issues have been noted in ’s permit to load for excavation below level -2 slab down to level -3. Key issue is the incorrect pass/fail criteria been referenced, concrete strength required before de-propping of slab is fck=29MPA. Cxxx Response to RFI001404 states that fck is Cylinder strength. have used Cube strength to measure the concrete compressive strength for this permit.
| 02SL - Stations (LUL) | Cxxx-NCR-001370 | NCR | WTH - Level -2 Slabs - I2a - Cover to reinforcement - Excess Cover |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-04-18 | 2014-04-15 15:14 | -3 | 2014-03-27 12:09 | Civil - Structural Engineering | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | Steel reinforcement on small section of slab I2a on Level -2 WTH has 65mm distance between the steel and temporary concrete surface (a wall will be cast above this area). Please see sketch attached.
| 02SL - Stations (LUL) | Cxxx-NCR-001371 | NCR | Cxxx-NCR-001370 - Level -2 Slabs I2a - Reduction of Cover |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-04-15 | 2014-04-09 12:10 | -6 | 2014-03-27 12:27 | Civil - Structural Engineering | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | Steel reinforcement cover on small section of slab I2a on Level -2 WTH has 10mm reduction in distance between steel and temporary concrete surface (a wall is to be cast above this area, this distance is a maximum distance over an area). Tolerance is 0mm. Please see sketch attached
| 02SL - Stations (LUL) | Cxxx-NCR-001372 | NCR | SCL - Failed 28 Day Compressive strength due to an error within the spread sheet |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-06-20 | 2014-06-10 16:06 | -10 | 2014-03-28 10:00 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Numerical error in core tracker, lead to a NCR been incorrectly identified.
| 02SL - Stations (LUL) | Cxxx-NCR-001373 | NCR | SCL - Preparation of test panels for flexural strength tests |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2014-04-18 | 2014-04-10 15:17 | -8 | 2014-03-28 17:06 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | During the quality surveillance of 26/02/14, it was noted that the test panels for the flexural strength tests were not lined with timber. Cxxx-NCR-001157 (Flexural strength test failure) proposed timber lined panels as a mitigation measure for fibre rebound. A presentation given to CRL in early November 2013 which outlined the lining of the test panel with timber as one of the key measures to prevent recurrence of the flexural strength issue.
| 02SL - Stations (LUL) | Cxxx-NCR-001374 | NCR | Honeycombing Capping Beam L |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-05-30 | 2014-05-30 15:18 | 0 | 2014-03-28 16:36 | Civil - Civil Engineering General | 2500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | have identified honeycombing under capping beam L. Please see attached photos.
| 02SL - Stations (LUL) | Cxxx-NCR-001375 | NCR | Transporting the panels |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-04-11 | 2014-04-08 11:00 | -3 | 2014-03-28 15:36 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Panels for beam tests (sprayed on 26/02/14) not covered with polythene sheet when transported.
| 02SL - Stations (LUL) | Cxxx-NCR-001378 | NCR | WTH - Level -2 Slabs - Pile breakdown - final inspection |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-04-17 | 2014-04-04 11:38 | -13 | 2014-04-03 11:04 | Civil - Structural Engineering | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not qualified | Completed |  | Pile breakdown for Level -2 Slabs at the WTH has been completed for OSD and SH-W3 piles. The following piles have had isolated sections where piles have been over-broked to a cutoff level below the 75mm step specified in drawing Cxxx-SWN-S-DDA-M123_Z-76018. All cutoff levels are still above bldining level for surrounding slabs. Pliles affected are: U213, E817, E820, E827, E829, E830
| 02SL - Stations (LUL) | Cxxx-NCR-001379 | NCR | WTH - Level -2 Slabs - Damage to SH-W3 Capping Beam Soffit |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-05-16 | 2014-05-07 16:18 | -9 | 2014-04-03 11:37 | Civil - Civil Engineering General | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Damage to SH-W3 capping beam soffit during excavation for Level -2 Slabs on the WTH. Around 75mm deep broken concrete. See attached sketch highlighting damaged areas and photo showing damage.
| 02SL - Stations (LUL) | Cxxx-NCR-001380 | NCR | Farringdon Road - Monitoring frequency not achieved in accordance with the Works Information |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2014-04-30 | 2014-05-07 11:23 | 7 | 2014-04-01 09:15 | Surveying - Instrumentation and Monitoring | 500 |  | Planning | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Monitoring in Farringdon Road was not carried out in accordance with the Works Information. Drawing Cxxx-OVE-C2-DDJ-CR001_Z-31531 requires: -fortnightly readings for 3 months prior to shaft excavation (planned for 31/03/2014) and SCL tunnel construction (started on 26/03/2014); -weekly readings for 4 weeks after SCL tunnel construction (in this case tunnel STW3, completed 12/01/2014); Monitoring readings were not carried out in accordance with the Works Information for instrumentation including: -__ sockets on the Farringdon Road retaining wall; -Studs and 3d prisms on the east side of Farringdon Road; -Studs and __ sockets on the west side of Farringdon Road; -Studs and __ sockets in Cowcross Street. In addition, Cxxx-OVE-C2-DDJ-CR001_Z-31531 note 5 requires that “All instrumentation to be maintained throughout construction period and immediately replaced / maintained if damaged, defective or unreadable”. Studs and 3d prisms on the east side of Farringdon Road were damaged by ’s own temporary works; new instrumentation was installed without achieving a baseline or at least an overlap period with the old instrumentation. For 3d prisms, the gap in readings is in excess of 2 months. The monitoring requirements and the missed monitoring readings were highlighted at the weekly Ground Movement Management Engineering meetings since 24/01/2014.
| 02SL - Stations (LUL) | Cxxx-NCR-001381 | NCR | Damaged Water Bar at Level -2 soffit |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-06-27 | 2014-06-20 13:06 | -7 | 2014-04-01 15:32 | Structural Engineering - Structural Engineering - General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | During the excavation to level -3, a waterbar section in the south east corner was damaged. This will be repaired prior to poring the last section of the lining wall between level -2 and -3.
| 02SL - Stations (LUL) | Cxxx-NCR-001382 | NCR | ETH SB - Damaged Waterbar Capping Beam L |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-06-06 | 2014-05-29 10:41 | -8 | 2014-04-03 10:39 | Civil - Civil Engineering General | 2000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | During breakout of blinding underneath Capping L at Level 0, a section of waterbar has been damaged. This section of water bar will be repaired before Lining Wall construction is completed. Also excess blinding behind waterbar will be broken out before Lining Wall construction.
| 02SL - Stations (LUL) | Cxxx-NCR-001383 | NCR | SCL - TH57 under mucked on the RHS of the advance |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-05-02 | 2014-04-08 11:09 | -24 | 2014-04-02 10:12 | Tunnelling - Linings - Sprayed Concrete | 6500 |  | Workmanship | Use As-Is | 2 (6-60k) | Complete | Management Problem - Inadequate supervision | Completed |  | Failure to Follow the RESS and excavate TH 57 to the correct length on RHS
| 02SL - Stations (LUL) | Cxxx-NCR-001384 | NCR | WTH Concrete Placement on I2a slab |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-04-16 | 2014-04-09 12:03 | -7 | 2014-04-02 12:28 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | One of the concrete loads used on the WTH level -2 slab I2a pour was placed outside of the specification, namely KF10.3203 h) KF10.3203 h) states that fresh concrete shall not be placed aganst existing fresh in-situ concrete which has been in position for more than sixty minutes. Concrete load with ticket number 66821015 was placed 97 minutes after the previous load on the SW corner of the slab pour.
| 02SL - Stations (LUL) | Cxxx-NCR-001385 | NCR | SCL - Missing 60 minute test for Adv1/2 RHS STW1 Enlargement |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-04-25 | 2014-04-14 12:00 | -11 | 2014-04-02 12:01 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Missed the 60 minute test for advance 1/2 RHS of STW1 enlargement. Failed to take 60 minute test according to ITP
| 02SL - Stations (LUL) | Cxxx-NCR-001386 | NCR | SCL - No excavation profile for I54 in PTW |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-05-07 | 2014-05-01 15:59 | -6 | 2014-04-02 12:51 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | 1No. excavation profile missed in I54 on PTW ITP for excavation and support not followed
| 02SL - Stations (LUL) | Cxxx-NCR-001387 | NCR | SCL - Missing pull out test for Advance TH53 in PTW |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-05-02 | 2014-05-01 15:53 | -1 | 2014-04-02 12:57 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | No Pull out tests captured for (4/6/12hrs) on advance TH53
| 02SL - Stations (LUL) | Cxxx-NCR-001388 | NCR | SCL - Missing 1 Day core results for adv 64 /105 in CH1 enlargement |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-05-02 | 2014-05-01 11:42 | -1 | 2014-04-02 16:20 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Missed 1 day compressive strength results for Advances 64 /105 No 1 day results per 50m3 wil construsting CH1
| 02SL - Stations (LUL) | Cxxx-NCR-001389 | NCR | WTH - Level -2 Slabs - I2a concrete pour - Curing procedure |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-04-18 | 2014-04-15 17:55 | -3 | 2014-04-04 15:33 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | WTH Level -2 Slabs method statement Cxxx--C-GMS-M123-50296 specifies concrete curing methods. None of these were followed immediately after the pour as per this document on the pour if I2a. Frost blankets were installed but only once the concrete was hard enough to walk on, 8h after the pour.
| 02SL - Stations (LUL) | Cxxx-NCR-001390 | NCR | 33-37 Charterhouse Square Monitoring |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2014-04-30 | 2014-05-06 09:38 | 6 | 2014-04-04 13:14 | Surveying - Instrumentation and Monitoring | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Personnel Error - Other human error | Completed |  | This is a notification for a non-conformance of the monitoring to be maintained on 33-37 Charthouse Square and the missed frequency or readings. As per drawing Cxxx-OVE-C-DDJ-CR001_Z-30823 and Cxxx-OVE-C-DDJ-CR001_Z-30822. During the handover from Cxxx there were a total of 20 new prisms installed by Cxxx to replace the damaged handed over ones. During this process there were 2No prisms that were not installed in the same location as Cxxx. There are also 2 lines of prisms that are read by an ATS the sight lines for these prisms has been blocked by a third party tree. It has been agreed with Cxxx that these prisms can be descoped due to the conflict that it would cause with 3rd parties. As a result these have not been read automatically to specification. A row of invar scales that were broken when handed over from Cxxx have been replaced with sockets, two of these sockets were not read according to specification during TBM passage due to access.
| 02SL - Stations (LUL) | Cxxx-NCR-001392 | NCR | WTH - Level -2 Slabs - PIle U213 - Lost geothermal loop |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-08-01 | 2014-05-28 09:15 | -65 | 2014-04-04 17:09 | Civil - Geotechnical Engineering | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Contamination | Completed |  | A geothermal loop on pile U213 is damaged/blocked beyond repair
| 02SL - Stations (LUL) | Cxxx-NCR-001394 | NCR | WTH Level -2 slab pour surface cracks |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-08-29 | 2014-08-14 09:09 | -15 | 2014-04-04 18:22 | Civil - Civil Engineering General | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Cracks were found on WTH level -2 pour I2a due to not applying curing agent on fresh concrete face as per described on method statement. WTH level -2 base slab I2a has been cast on Tuesday 1st April 2014. Pour was completed around 18h30 and curing agent was not applied on its completion. Curing mat was placed around 06h00 on the 2nd April, when possible to walk on it. The maximum temperature on the core of the slab while curing was 44.4C (via thermo-couplers) at 05h00 of the 2nd April. Lowest temperature during the night of the 2nd April was 10C. Cracks found follow a random pattern with width up to 1.4mm From existing literature (Technical Report No.22 – Fourth Edition, Non-structural cracks in concrete, Concrete Society), by not applying curing agent and due to the type and pattern of existing cracks, it is acknowledged that we have cracks on this slab due to Plastic Shrinkage (see attached photos and Table 1,Classification of non-structural cracks). Average 7 day cube compressive strenght is 52.6 N/mm2
| 02SL - Stations (LUL) | Cxxx-NCR-001395 | NCR | ETH - L-3 Weldable Couplers at Incorrect Level |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-04-19 | 2014-04-15 17:37 | -4 | 2014-04-05 03:04 | Structural Engineering - Reinforcement | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Due to ambiguity on __ L-3 slab drawings couplers were installed at the incorrect level on the North West Plunge Column North face and North East Plunge Column West face.
| 02SL - Stations (LUL) | Cxxx-NCR-001396 | NCR | Ventilation Temporary Works Design |  | Crossrail | PDP | FAR - Farringdon Station (West) |  | 2014-04-23 | 2014-05-07 11:15 | 14 | 2014-04-09 12:07 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | Design Management Plan, Cxxx--C-STP-M123-50009 & Short Notice Change Procedure, Cxxx--C-GPD-M123-50006, has not been followed with regard to the design and installation of temporary ventilation within the SCL worksites. 1. Due to changes in construction sequence assessments and changes to the venitilation design have been required by 's Temporary Works Designer. These changes have not been recorded and submitted to CRL via the Short Notice Change process. 2. Works have proceeded onsite without a accepted ventilation design in place. This is evident of the works that were carried out in CH1 and also for works currently being carried out within STW-1. Also note that the temporary works designer stated that the set-up for the CH1 works proposed by the construction team was not sufficient.
| 02SL - Stations (LUL) | Cxxx-NCR-001397 | NCR | SH-W3 Plastic conduit in Capping Beam pour |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-04-23 | 2014-04-14 09:25 | -9 | 2014-04-09 12:28 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | A section of plastic conduit approximately 300mm long was found along the northern edge of the southern section of the SH-W3 level -1 Capping Beam. Please see attached photograph.
| 02SL - Stations (LUL) | Cxxx-NCR-001398 | NCR | SCL - Missing pull out test for Advance TH13 in STW1 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-05-12 | 2014-05-07 17:37 | -5 | 2014-04-11 11:04 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | No Pull out tests captured for (4/6/12hrs) on advance TH13
| 02SL - Stations (LUL) | Cxxx-NCR-001399 | NCR | SCL - Missing pull out test for Advance TH65 in PTW |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-05-26 | 2014-05-15 11:21 | -11 | 2014-04-11 11:05 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | No Pull out tests captured for (4/6/12hrs) on advance TH65
| 02SL - Stations (LUL) | Cxxx-NCR-001402 | NCR | SMM - Lack of baseline on XR-08 and XR-25 Rod Extensometers |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-04-30 | 2014-05-07 13:03 | 7 | 2014-04-14 14:47 | Surveying - Instrumentation and Monitoring | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | Rod Exntensometers XR 08 and XR 25 have a baseline that extends within the period of possible influence from pre-treatment works (Compensation Grouting). In accordance with KX 10, Monitoring for baseline redeags shall start a specified period before the commencement of construction (at least three months unless otherwise specified in the Contract etc). Apparent confusion existed between this requirement and that given in Cxxx-OVE-C2-DDJ-CR001_Z-31531, whereby the Baseline is defined as being 3 months prior to either Box/Shaft Construction or SCL Construction. This NCR relates to the Baseline Report Cxxx--C2-RGN-M123-50995 and the associated comments Cxxx--C2-XCS-M123-50080
| 02SL - Stations (LUL) | Cxxx-NCR-001403 | NCR | SMM - 3D Prism installation site wide - Variances from Specification |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-05-06 | 2014-04-29 10:57 | -7 | 2014-04-15 13:55 | Surveying - Instrumentation and Monitoring | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Installation of 3D targets is outlined in a number of Cxxx drawings and photomontages. Where installation has not followed these requirements, this has been highlighted in the attached set of revised photomontages.
| 02SL - Stations (LUL) | Cxxx-NCR-001404 | NCR | SCL - STW1 B40 Missing Excavation Profile |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-06-10 | 2014-06-10 08:56 | 0 | 2014-05-21 12:59 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Other human error | Completed |  | No excavation profile recorded for adv 40 in STW1
| 02SL - Stations (LUL) | Cxxx-NCR-001405 | NCR | SCL - PTW I86 achieved zero reading for early strength after 3 hrs and was removed. |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-06-06 | 2014-05-22 14:21 | -15 | 2014-04-17 19:46 | Tunnelling - Tunnelling General | 25000 |  | Material | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | No Early age strength, Advance removed and replaced with compliant SCL. KT20 - Table KT20-06 - EAS WI 20.8 is relevant as issue wasnt rectified within the shift, although every effort was made to do so.
| 02SL - Stations (LUL) | Cxxx-NCR-001406 | NCR | SCL - Excavation profile at B40 CH +16.5 in STW1 enlargement was missed. |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-05-22 | 2014-05-20 12:31 | -2 | 2014-04-17 13:16 | Tunnelling - Tunnelling General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | No excavation profile recorded an CH16.5 as per Excavation ITP
| 02SL - Stations (LUL) | Cxxx-NCR-001407 | NCR | SCL - PTW early strength failures due to mechanical fault. |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-05-23 | 2014-05-13 08:43 | -10 | 2014-04-17 18:19 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Equipment Breakdown | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | PTW achieved the following low early strength due to a pump becoming blocked over a number of advances. TH76 - 0.42 N/mm2 after 60 min TH77 - 0.30 N/mm2 after 60 min B79 - 0.27 N/mm2 after 60 min TH81 - 0.48 N/mm2 after 60 min B83 - 0.36 N/mm2 after 60 min
| 02SL - Stations (LUL) | Cxxx-NCR-001408 | NCR | SCL - PTW Enlargement I76 4 hr pull out test failed and 6 hr showed inaccurate results due to faulty gauge. |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-05-23 | 2014-05-16 16:12 | -7 | 2014-04-17 17:25 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Equipment Breakdown | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | A pull out test was required on PTW I74. Our records show that the 4hr test was carried out but it failed. The 6 hr test was carried out but it did not return an accurate reading due to a faulty gauge. (see attached checksheet)
| 02SL - Stations (LUL) | Cxxx-NCR-001411 | NCR | WTH - Curing on I2a duration |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-05-01 | 2014-05-01 11:42 | 0 | 2014-04-17 17:04 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | For completion of NCR-001389, curing to level -2 slab I1a was not in place for at least 7 days as specified on the ITP Cxxx--C-ITP-M123-50181 and on the Civil & Structural Specification - Cxxx-SWN-C-RSP-M123-00004, Clause KF10.3206 n). See curing timeline attached.
| 02SL - Stations (LUL) | Cxxx-NCR-001412 | NCR | ETH - South basement W21 lining wall - couplers for starter bars missing |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-05-15 | 2014-05-13 17:50 | -2 | 2014-04-22 10:18 | Civil - Civil Engineering General | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | At the north side of W21 lining wall couplers for horizontal starter bars are missing. The couplers should have been installed in Level L-2 in the vertical face of Beam 4 / Beam 11. Threaded starter bars (BM29 and BM30) are shown on drawing Cxxx-ATK-S-DWG-M123_Z-50301 but no couplers are shown on the reinforcement beam drawings. The W21 lining wall drawing Cxxx-ATK-S-DWG-M123_Z-50301 shows BM29 and BM30 as threaded bars. However no couplers are shown on the beam reinforcement drawings (see attached drawings). Beam 4 / Beam 11 got installed first and because nothing was shown on the rebar drawing, the beams were installed without horizontal bar couplers for W21 lining wall. Therefore this NCR is classed as a design issue and not an installation issue.
| 02SL - Stations (LUL) | Cxxx-NCR-001413 | NCR | SCL - Missing 4 hr Pull Out Test for Advance B99 in PTW |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-05-28 | 2014-05-12 09:02 | -16 | 2014-04-28 18:15 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Pull out tests were required in PTW B99 for 4, 6, & 12 hours. The 4 hour test was missed.
| 02SL - Stations (LUL) | Cxxx-NCR-001414 | NCR | ETH - L-3 - Box-out to the SE of 550 slab incorrectly positioned |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-05-14 | 2014-05-01 17:16 | -13 | 2014-04-23 13:03 | Mechanical - Public Health Engineering | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | The box out at the south east of the raised 550 slab at L-3 has been installed in the incorrect position. It is approximately 50mm further east than detailed on drawing Cxxx-SWN-S-DDA-M123_4-29301. See attached sketch which shows details of the box-out and the incorrect positioning.
| 02SL - Stations (LUL) | Cxxx-NCR-001415 | NCR | SCL - Failure of 28 day flexural Strength beams - STW1 Adv4 / PTW B47 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-08-08 | 2014-07-25 16:11 | -14 | 2014-04-24 17:59 | Tunnelling - Linings - Sprayed Concrete | 30000 |  | Material | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Failure of 28 day flexural strength requirements in STW1 adv 4 / PTW B47 in accordance with KT20 - 28 day- 1No. failure - 90 days attached -DSP letter for temporary state attached
| 02SL - Stations (LUL) | Cxxx-NCR-001416 | NCR | WTH - Level -2 - Blinding - Compressive strength results - Pour 8 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-05-09 | 2014-04-28 10:45 | -11 | 2014-04-25 12:00 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | At the WTH Level -2 Slabs, during installation of blinding, concrete cubes were not taken as per the ITP (NCR 1337 already raised). Samples were cored out following the pours and crushed. The core for the pour of 15/02/2014 (Pour 8) was taken only 7 days after the pour. Concrete compressive strength of this cylinder test was 9.1N/mm2 (as per report EX292 attached), below the 16N/mm2 (for cylinder) specified for blinding mix BU1. It is very difficult to extract another core from Pour 8 to confirm blinding strength at this location. BU1 mix has subsequently proved strength gain to 20N/mm2 (cube) at 28 days from 10.9N/mm2 (cube) at 7 days, as verified on cubes taken from Pour 11 (test EX321 results also attached).
| 02SL - Stations (LUL) | Cxxx-NCR-001417 | NCR | SCL - Failure of Early Strength and Pull Out Test for B65 & I68 in STW1 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-05-23 | 2014-05-20 12:35 | -3 | 2014-04-30 16:50 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | STW1 - Bench 65 and Invert 68 were sprayed together. EAS was not achieved up to 6 hours.
| 02SL - Stations (LUL) | Cxxx-NCR-001418 | NCR | Early MEP Works - ETH Level-2 - Connections to lightning electrodes in Slabs 1A, 1B not installed |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2014-05-23 | 2014-05-23 13:36 | 0 | 2014-04-30 16:30 | Electrical - Electrical Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | The connections LE10 and LE12, specified in drawing Cxxx--E-DDD-M123_Z-25706 P02 (gridlines A-A'/4 and 6 respectively), have not been implemented.
| 02SL - Stations (LUL) | Cxxx-NCR-001420 | NCR | WTH - Gap on I2b slab under SHW3 capping beam |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-06-12 | 2014-06-05 09:10 | -7 | 2014-05-02 16:36 | Civil - Civil Engineering General | 1000 |  | Planning | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | On completion of level -2 base slab, a gap was found under SHW3 capping beam. Dimensions and location are attached.
| 02SL - Stations (LUL) | Cxxx-NCR-001421 | NCR | Maintenance of Monitoring points |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2014-05-30 | 2014-05-27 08:56 | -3 | 2014-05-06 08:51 | Surveying - Instrumentation and Monitoring | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | A number of monitoring points were damaged and not reinstalled, during this period these points were not read.
| 02SL - Stations (LUL) | Cxxx-NCR-001422 | NCR | WTH Level -2 base slab I2b - Concrete Temperature Exceeding 60oC |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-06-13 | 2014-06-03 12:42 | -10 | 2014-05-06 12:18 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | installed thermocouples in the Level -2 base slab pour I2b to monitor the internal concrete temperature. The highest temperature recorded was 65.82 degrees celsius. Clause KF10.1302a states that the maximum temperature of placed concrete will not exceed 60 degree celsius. Similar NCR has been raised for SHW3 level -1 capping beam pour (Cxxx-NCR-001348) Curing agent and frost mats have been placed on completion and not removed to date. Cxxx will assess finish from the 08/05/14 See attached temperature data log and location of thermocouplers.
| 02SL - Stations (LUL) | Cxxx-NCR-001423 | NCR | ETH - SB Wall 21 Section A bowed wall |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-06-20 | 2014-06-20 12:20 | 0 | 2014-05-06 13:29 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following removal of formwork from Lining Wall 21 section A, see attached for Wall 21 sequence, conducted a visual inspection of concrete wall. It was noted that Wall 21 bowed out slightly, maximum 8mm, from required setting out line. Evidence shown in attached photos.
| 02SL - Stations (LUL) | Cxxx-NCR-001425 | NCR | Exceeding 2 hours from batching to discharge for Connection Wall |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-05-27 | 2014-05-13 12:04 | -14 | 2014-05-08 14:00 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Inadequate/insufficient tooling. | Completed |  | poured the connection wall between the Level -1 and the Level -2 capping beams around the escalator shaft using self compacting concrete. The first concrete lorry was batched at 07:44 and we finished discharging at 10:00 therefore contravening clause KF10.3320b stating that the concrete should be compacted in its final position less than two hours after cement is added to the aggregate.
| 02SL - Stations (LUL) | Cxxx-NCR-001426 | NCR | Use of self compacting concrete not covered on ITP |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-06-20 | 2014-06-04 11:11 | -16 | 2014-05-08 14:21 | Civil - Civil Engineering General | 500 |  | Planning | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Lack of procedure | Completed |  | The use of self compacting concrete for the connection wall between the Level -1 and Level -2 capping beams was approved under Cxxx-FCD-000891. The use of self comapcting concrete was not added to the relevent ITP.
| 02SL - Stations (LUL) | Cxxx-NCR-001427 | NCR | SCL - Failure of Flexural Strength 28 Days (April) STW1 29 / PTW 74 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-07-18 | 2014-07-16 17:51 | -2 | 2014-05-08 18:06 | Tunnelling - Linings - Sprayed Concrete | 55000 |  | Material | Use As-Is | 2 (6-60k) | Complete | Material/Preservation Problems - Other | Completed |  | Failure of Flexural strength in accordance with KT20 rev18
| 02SL - Stations (LUL) | Cxxx-NCR-001429 | NCR | SMM - Pump Calibration Certificate |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-05-27 | 2014-05-15 11:27 | -12 | 2014-05-12 08:36 | Geotechnical Engineering - Compensation Grouting | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Refering to clause KC21.3212 c) the calibration certificate for the injection pump currently being used on site has recently expired.
| 02SL - Stations (LUL) | Cxxx-NCR-001430 | NCR | Damaged Cable in WTH Delivery Corridor. |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-07-25 | 2014-07-21 11:44 | -4 | 2014-05-13 14:42 | Surveying - Instrumentation and Monitoring | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | On the 04/04/2014 the power cable to the strain gauges on the gas main was cut, resulting in the strain gauges on the gas main and the tiltmeters on the retaining wall being damaged. The cut cable sent a surge of power to the data logger box which over loaded the equipment. This stopped logging data for the strain gauges and the tiltmeters on the west retaining wall. This meant that data was not recorded for several days while the equipment was re-cabled and tested. The strain gauges started to record data again on 16/04/2014 and the tiltmeters were back on 22/04/2014. Due to the power surge the cable was damaged in various places, this is visible due to the melted plastic casing of the cable. Due to the higher voltage passing through the tiltmeters, at around 15-19 volts, some of the tiltmeters were damaged. 3 tiltmeters overall were damaged beyond repair. Due to the data logger box being damaged __, the company who installed the data logger box, had to be called to come look at the system. __ had to send a representative from Austria, which contributed to the time it took to get the instrumentation fixed and gathering data.
| 02SL - Stations (LUL) | Cxxx-NCR-001431 | NCR | Honeycombing to Connection Wall |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-08-24 | 2014-07-30 17:52 | -25 | 2014-05-16 09:52 | Civil - Civil Engineering General | 1000 |  | Material | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | cast the connection wall (wall 26 and 33 junction) between the structural slab level of the Level -2 slab and the soffit of the Level -1 capping beam using self compacting concrete. On striking the shutters an area of honeycombing was identified. The attached documents show where on the connection wall it was identified and the extent of the honeycombing.
| 02SL - Stations (LUL) | Cxxx-NCR-001432 | NCR | WTH Level -2 base slabs I3 pour - Concrete Temperature Exceeding 60oC |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-06-06 | 2014-06-05 17:29 | -1 | 2014-05-16 15:49 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | installed thermocouples in the Level -2 base slab pour I3 to monitor the internal concrete temperature. The highest temperature recorded was 64.89 degrees celsius. Clause KF10.1302a states that the maximum temperature of placed concrete will not exceed 60 degree celsius. Similar NCR has been raised for SHW3 level -1 capping beam pour (Cxxx-NCR-001348) and WTH Level -2 base slabs I2a pour Curing agent and frost mats have been placed on completion and not removed to date. Cxxx will assess finish from the 16/05/14 See attached temperature data log and location of thermocouplers.
| 02SL - Stations (LUL) | Cxxx-NCR-001433 | NCR | Undersized Thrust Block at 16" to 4" Branch in St John Street |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-06-16 | 2014-06-10 15:52 | -6 | 2014-05-19 14:07 | Utilities Engineering - Water | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | As part of the requirements in the Works and Site Information Vol.2 Site Specific for the 16" water main in St John Street a thrust block as per the drawing A041-A1-21446 Typical Branch Connection Details is required for the 4"branch connection. The thrust block was cast on 23/04/2014 and on 24/04/2014 it was noticed when the shutters were removed that the thrust block was too small. The constraints of the thrust block location made for difficult shuttering conditions, this coupled with the time allowed for completing the works, led the subcontractors engineer to make the decision to cast the thrust block below the required volume of (0.30m3 and it should be 0.512m3 @1.22tn mass). In doing this the bearing area of the block was reduced which has meant less resistance is provided by transferring the thrust force to the surrounding ground. Mitigating circumstances underlying the decision taken by the subcontractors engineer were: The existence of a reinforced concrete thrust block previously cast 1.55m to the west and located central to a 1.0m DI puddle flange. This thrust block was designed to control the longitudinal separation caused by the unbalanced hydrostatic and hydrodynamic forces present within the mains. It also provides the necessary bearing restraint required as the pipe experiences considerable horizontal and /or vertical changes in direction. The concrete cast was a C32/C40 structural sulphate resistant mix and not the C20 dry lean mix as stated in the W&SI. The total volume of thrust restraint offered by both thrust blocks is 1.153m3 @ 2.76tn mass.
| 02SL - Stations (LUL) | Cxxx-NCR-001434 | NCR | SCL - PTE I14 - Missing 4 hour pull-out test |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-06-03 | 2014-05-28 10:43 | -6 | 2014-05-20 08:41 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate resources | Completed |  | No 4hr pull out tests recorded
| 02SL - Stations (LUL) | Cxxx-NCR-001435 | NCR | SCL - Fail to take 4/6/12 HR test from PTE advance 35 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-06-19 | 2014-05-28 10:44 | -22 | 2014-05-20 08:41 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Failure to take 4/6/12 hr tests on advance 35 in PTE
| 02SL - Stations (LUL) | Cxxx-NCR-001436 | NCR | SCL - Poor quality cores in PTW (TH1 - I141) |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-09-16 | 2014-09-09 12:04 | -7 | 2014-05-19 17:33 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Not Defined | Completed |  | Cores of Grade 4 or lower taken from the lining TH1,TH18(2no),B99,B123,TH113,TH116 (2No.) Updated 20/6/14 Cores with average =>2.5 TH01, B04, TH18, B99, TH113, TH116, B123, I138, TH141
| 02SL - Stations (LUL) | Cxxx-NCR-001437 | NCR | WTH SH-W2 Welding of Steel Reinforcement not in Accordance with Spec. & BFK Welding Management Plan |  | Contr | HYD | FAR - Farringdon Station (West) |  | 2014-06-27 | 2014-06-17 08:21 | -10 | 2014-05-20 16:18 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Lack of procedure | Completed |  | Welding of the earthing mat to the Level-8 basement slab of SH-W2 has been carried out in various locations without an approved WPS/ITP. Cxxx-SWN-C-RSP-M123-00004 Rev.6.0 Cl.KF 10.3235 ‘Welding of Steel Reinforcement’ details all Contractor requirements prior to any site welding taking place, which include: (a) the establishment of a satisfactory welding procedure which demonstrates that the strength of the parent metal is not reduced, (b) welder performance qualification tests, (c)no tack welding permitted unless in an exceptional circumstance and with prior agreement, etc. Additionally, the purpose of the Welding Management Plan (Cxxx--C-RGN-M123-51221 Rev.1.0) is ‘to control the quality of welding and steel fabrication works and provide assurance to Crossrail Projects’. Although the details of the earthing mat welds have been indicated on drawing Cxxx--E-DDD-M123_Z-25707 (P05) – thus adhering to Clause 2.10 (Welding of steel reinforcement’) of the Welding Management Plan - there is no documentation in place (WPS/ITP) to control the suitability and quality of the welds indicated on the drawing: 1. The ITP for the Level-8 RC works (Cxxx--C-ITP-M123-50186 Rev.2.0 items 18-20) only covers the inspection of the earthling system. 2. The aforementioned ITP in turn refers to the __ ITP (Cxxx-__-ITP-E-001) which again, only covers visual inspection that the earth mat connections are bonded as specified. The lack of a controlled process for the welding is further amplified by the fact that the welds which have been visually inspected in the western half of the Level -8 slab, are not in accordance with drawing Cxxx--E-DDD-M123_Z-25707 (P05), which states that minimum 100mm fillet welds are required. In most cases, the welds which have been completed are tack welds of a smaller length. Please refer to attached site photographs. CRL note that FCDs are being prepared by the Contractor to modify the existing design for welded earthing mat connections and to create a new earthing mat connection utilising clamps and copper tape. An approved WPS/ITP will also need to be implemented prior to any further welding of earth mat connections being carried out.
| 02SL - Stations (LUL) | Cxxx-NCR-001438 | NCR | SMM - Grout Injection Flow Rates |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-06-23 | 2014-06-09 11:01 | -14 | 2014-05-21 09:53 | Geotechnical Engineering - Compensation Grouting | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Relating to KC21.2104 Compensation Grouting proposals to date have, in error, been stating the maximum flow rate as 15l/min. This is contradicting the allowable 35 l/min allowable limit on the approved ITP.
| 02SL - Stations (LUL) | Cxxx-NCR-001439 | NCR | Wall 26 concrete placement |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-07-04 | 2014-06-30 12:13 | -4 | 2014-05-21 10:40 | Civil - Civil Engineering General | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | The final lorry load of concrete used to complete Wall 26 pour was placed outside the specification, namely clause KF10.3203h. This clause states that fresh concrete will not be placed against existing fresh concrete which has been in place for more than 60 minutes. The penultimate lorry finished discharging at 12:45pm with the final lorry did not begin discharging until 14:02pm, therefore 17 minutes over the sixty minute limit. The face of the existing concrete was kept live throughout this period. It has since come to light that similar NCRs have been raised on the same issue although the corrective actions were not known. did slow the discharge rate of penultimate lorry when in fact the discharge should have just ceased until the final lorry had arrived.
| 02SL - Stations (LUL) | Cxxx-NCR-001440 | NCR | SH-W2 L-8 Blinding Levels |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-06-13 | 2014-06-11 14:22 | -2 | 2014-05-22 19:58 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Other human error | Completed |  | Following surveying the blinding for the L-8 slabs some levels were out of tolerance. See attached sketch with levels. The tolerance from the ITP(Cxxx--C-ITP-M123-50200 Rev 1) is +0/-10.
| 02SL - Stations (LUL) | Cxxx-NCR-001441 | NCR | Waterproofing for walls in WTH SH-W2 Sump |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-06-06 | 2014-06-05 13:19 | -1 | 2014-05-23 07:53 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | During the pour of the Sump walls in SH-W2 it was noticed that small pieces of the plastic release liner on the GRACE __ tape had not been removed. This tape is used to connect two adjacent sheets of __. In accordance with the GRACE Product sheet included within the MCR for this material (Cxxx--C-LRC-M123-50216 Rev.2.0) the plastic release liner should be removed in order to form a continuous adhesive bond to the concrete poured against it.
| 02SL - Stations (LUL) | Cxxx-NCR-001443 | NCR | Damage to Cxxx-IM00002 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-07-04 | 2014-06-30 08:58 | -4 | 2014-05-27 10:34 | Surveying - Instrumentation and Monitoring | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The cause of this inclinometer being broken is due to the SCL tunnel excavation which clashed with inclinometer Cxxx-IM00002. This instrument is now broken and can no longer be read as per the specification Cxxx-OVE-C2-DDJ-CR001_Z-31531.
| 02SL - Stations (LUL) | Cxxx-NCR-001444 | NCR | ETH:Insufficient cover to nearface for Wall 23a |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2014-06-24 | 2014-06-13 12:35 | -11 | 2014-05-27 11:53 | Structural Engineering - Concrete Member | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Spot inspection on Wall 23a indicated an average cover of 43mm. all reinforcement came from cast-in starters
| 02SL - Stations (LUL) | Cxxx-NCR-001445 | NCR | ETH - lower sloping slab - increased concrete cover |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-06-13 | 2014-06-12 19:12 | -1 | 2014-05-28 16:44 | Civil - Civil Engineering General | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The blinding for the lower escalator slab has been installed low. Since the reinforcement cage has been installed with the 50mm cover as shown on Cxxx-ATK-S-DWG-M123_50112 there is an increased concrete cover of up to 120mm at the top of the lower escalator slab. Because of all the installed starter bars at L-3 and L-2 which would not allow the cage to be raised up proposes to leave the reinforcement cage at the current level and install an additional reinforcement mesh (A393 or similar) where required to avoid the negativ effects of an increased concrete cover. Concrete spacers will be used between mesh and reinforcement cage. Could Cxxx please confirm whether there are any objections to this proposal?
| 02SL - Stations (LUL) | Cxxx-NCR-001446 | NCR | WTH - SHW2 Earthing activities without approved drawing or FCD |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-06-11 | 2014-05-30 18:40 | -12 | 2014-05-28 19:03 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Lack of approval Code 1 procedures excessive | Completed |  | Detail 2 of Cxxx--E-DDD-M123_Z-25707 has not been followed in 6n locations. Due to the impossibility of meet the 100mm long weld as mentioned on the drawing, tack welds were carried out instead. As shown on details, there are 6n areas where tack welds were applied to structural reinforcement. Approximate location of welds as per attched sketch. A change to this detail has now been accepted via FCD-1295. The remaining installation of earthing on SHW2 proceeded without approved drawing or FCDs. FCD-1296, FCD-1301, FCD-1302 are all related to SHW2 earthing details. Even though all the details and changes have been discussed and agreed by Cxxx M&E designer (__), the FCDs have not been approved prior to works on site.
| 02SL - Stations (LUL) | Cxxx-NCR-001447 | NCR | SCL - Poor Quality Core from CP3A / CH1 thickening |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-08-15 | 2014-08-22 12:18 | 7 | 2014-06-02 16:39 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Core quality was greater than grade 3 in acordance with procedure Quality Core Grading Procedure Cxxx--O4-GPD-M123-50014
| 02SL - Stations (LUL) | Cxxx-NCR-001448 | NCR | SCL - Failure to achieve 28 Day compressive strength PTW B99 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-07-02 | 2014-06-28 10:54 | -4 | 2014-05-28 12:12 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Failure to achieve 28 Day compressive strength to KT20 requirements
| 02SL - Stations (LUL) | Cxxx-NCR-001449 | NCR | Early MEP Works - ETH Level-2 - Earth mat on sloping slab not installed |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-06-18 | 2014-05-30 16:08 | -19 | 2014-05-28 16:18 | Electrical - Electrical Engineering General | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Cxxx--E-DDD-M123_Z-25703 P02 showed earth mat extending through the escalator sloping slab area between gridlines B and C and north of grid lines 4 and 5. This section was not installed.
| 02SL - Stations (LUL) | Cxxx-NCR-001450 | NCR | WTH - ITP not revised on time |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-06-27 | 2014-06-27 13:20 | 0 | 2014-05-29 09:28 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | WTH Level -2 reinforced concrete works ITP, revision 3 covers the use of concrete mix SL6 (PFA) for level -2 base slabs. Cxxx proposed to alter the mix to SL6(GGBS) mix, through MCR Cxxx--C-LRC-M123-50344. This MCR has been approved by CRL (Code 1). Nonetheless all the details for the use of this mix have been approved, the ITP was not updated prior to start using this mix on site.
| 02SL - Stations (LUL) | Cxxx-NCR-001451 | NCR | ETH - SB L-2 W23A - reduced concrete cover at north construction joint |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-06-20 | 2014-06-20 13:16 | 0 | 2014-05-30 09:14 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The concrete cover on lining wall W23A at the construction joint at the north side is reduced. The minimum cover is 34mm. The concrete cover in lower section of the wall is alright as shown on Photo #1 and #2. The cover towards the top is reduced. (see photo #3)
| 02SL - Stations (LUL) | Cxxx-NCR-001452 | NCR | ETH Lining wall 21 'C’ – Procedural NCR – Outstanding FCD when casting area ‘C’ |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2014-07-04 | 2014-06-24 11:05 | -10 | 2014-05-30 17:52 | Civil - Civil Engineering General | 500 |  | Planning | Rework | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | installed shutters for lining wall 21 pour C on 23.05.14 and poured this area on the 24.05.14 with an outstanding FCD (Cxxx-FCD-001288) This issued was raised to during the pre- pour inspection on the 23.05.14 where at the moment of the inspection, the FDC was still outstanding and 1 hour later the shutters went up. FCD-001288 was raised on the 12.05.14 and reworked several times and finally sent back to CRL for approval on 22.05.14. construction team invited CRL Field Engineers to attend pre-pour inspections worksites when; a) the work was not in accordance with the accepted design has been advice as per the Cxxx-SCM-00013 and as per discussion during meeting that once the area is offered for inspection to CRL, the RFIS/FCDs and NCRs should be closed out and should be satisfied and should demonstrate that the works offered are ready and are compliant with the spec and design.
| 02SL - Stations (LUL) | Cxxx-NCR-001453 | NCR | ETH Lining wall 21’ C’ – Procedural NCR – Outstanding works found during pre-pour inspection by CRL |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2014-07-18 | 2014-07-17 19:05 | -1 | 2014-05-30 19:09 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | has invited CRL to undertake a pre-pour inspection for lining wall 21, area C on the 23.05.14. During the inspection it was found: 1. Hydrophilic strip installed over the area not cleaned at the lower left corner. The area was full of dust coming form the upper level drilling works 2. There were a number of links bars not tied at all and others loosely tied installed shutters for lining wall 21 pour C on 23.05.14 1hr after the inspection was done and this area was poured on the 24.05.14. No evidence that these issues were corrected was presented to CRL. This issued was raised to during the pre- pour inspection on the 23.05.14 This is a procedural NCR as construction team invited CRL Field Engineers to attend pre-pour inspections worksites when; a) the work is incomplete b) the work is not in accordance with the accepted design c) agreed design changes are not documented to check against d) inspection records have not been signed off verifying compliance has been advised as per the Cxxx-SCM-00013 and as per discussion during meetings that once the area is offered for inspection to CRL, that the works offered are ready and are compliant with the spec and design. To this end, when invited to attend a witness or hold point the Contractor shall demonstrate to CRL that work is compliant.
| 02SL - Stations (LUL) | Cxxx-NCR-001454 | NCR | WTH - Addition of preliminary TW reinforcement onto SHW2 base slab |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-06-30 | 2014-06-23 09:11 | -7 | 2014-05-31 12:45 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | Additional reinforcement for temporary works purpose has been installed on SHW2 level -8 slab without being approved. See attached preliminary sketch. This is to allow the contractor to carry out the thrust bore pipe works at later date. CRL designer have been contacted via email with not comments on the installation of these bars. Repairs to TOC of level -8 slab will be required.
| 02SL - Stations (LUL) | Cxxx-NCR-001455 | NCR | Lack of design drawing detail leading to construction errors |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2014-06-16 | 2014-06-13 12:47 | -3 | 2014-06-02 13:55 | Electrical - Electrical Engineering General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | This is a procedural NCR aiming at capturing a recurrent problem with regard to coordination between the design and construction teams on MEP issues, as well as producing enough design detail to allow the construction team to accurately reflect the design. The NCR is specifically referring to the missing earth mat connection at L-2 sloping slab and the missing detail capturing sloping in the slab.
| 02SL - Stations (LUL) | Cxxx-NCR-001456 | NCR | SCL - Missed Pull out tests at 4 /6 hr B/I 4 CP3B/CH1 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-06-30 | 2014-06-30 11:37 | 0 | 2014-06-02 16:15 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Other human error | Completed |  | Missed 4 / 6 hr test for early age strength
| 02SL - Stations (LUL) | Cxxx-NCR-001457 | NCR | Procedural NCR – ETH Excavation & Installation of Propping at South Basement out of sequence |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2014-09-19 | 2014-09-08 18:11 | -11 | 2014-06-02 17:55 | Civil - Civil Engineering General | 1500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | The escalator inclined area (slopping slab) has been excavated before the secondary raking props have been installed. This is not in accordance with the sequence shown on drawings Cxxx-SWN-S-DDB-M123_Z-27003 rev C04 & Cxxx-SWN-S-DDB-M123_Z-27004 rev C04. Although there have been discussions in different forums regarding the propping sequence at the ETH the alternative construction sequence proposed (Cxxx-RFI-001609), which included excavation of the inclined area prior to the installation of secondary raking props, was rejected.
| 02SL - Stations (LUL) | Cxxx-NCR-001458 | NCR | NCR - LSB - Use of sealant which is not listed on LU approved materials list |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-06-19 | 2014-06-12 19:21 | -7 | 2014-06-05 09:25 | Civil - Civil Engineering General | 1000 |  | Material | Rework | 4 (0.5-3k) | Complete | Supervision - Other | Completed |  | A fire rated silicone sealant (__ Sealant) that is not listed on the LU approved materials was used to seal off the horizontal shelf angle slot within the LU tunnel (adjacent to Pier 1/2N). Details of the material (__ Sealant) have been attached.
| 02SL - Stations (LUL) | Cxxx-NCR-001459 | NCR | SH-W2 Thermocouplers Pour 1 Level -8 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-06-23 | 2014-06-18 14:37 | -5 | 2014-06-09 18:49 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | One of the construction activities within the Reinforced Concrete Works for Sump and Level -8 Slab ITP (Cxxx--C-ITP-M123-50186 Rev 2) is the installation of thermocouplers. The check is that the thermocouplers are installed at the core and top face of concrete. This check was not completed, the thermocouplers were only installed in the core and not the cover with the result that the differential temperature could not be recorded.
| 02SL - Stations (LUL) | Cxxx-NCR-001460 | NCR | WTH SHW2 Buttress wall reinforcement fixed without C revision drawings approved |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-06-27 | 2014-06-11 16:41 | -16 | 2014-06-06 11:58 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | Drawing Cxxx-ATK-S-DWG-M123_Z-50243 Rev P05 has been used to order and fix the rebar for the buttress wall portion of Wall W9 in SHW2 as a C revision drawing accepted by CRL was not available at the time of fixing. Drawings Cxxx-ATK-S-DWG-M123_Z-50240, Cxxx-ATK-S-DWG-M123_Z-50241, Cxxx-ATK-S-DWG-M123_Z-50242, Cxxx-ATK-S-DWG-M123_Z-50243 P05 revision have been used to order and fix the starter bars in the -8 slab. Again, C revision drawings were not in place on time.
| 02SL - Stations (LUL) | Cxxx-NCR-001461 | NCR | ETH - Lower escalator ramp pour 1 - NCR not closed out prior to pour |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-06-26 | 2014-06-23 17:56 | -3 | 2014-06-10 17:07 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | Lower escalator ramp pour 1 was concreted on 09/06/2014 with NCR Cxxx-NCR-001445 not being closed out at the time of pour.
| 02SL - Stations (LUL) | Cxxx-NCR-001462 | NCR | SCL - Poor quality cores in CH1 enlargement |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-09-12 | 2014-09-09 12:37 | -3 | 2014-06-10 12:28 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Poor quality cores in CH1 enlargement. Adv TH13 / B108
| 02SL - Stations (LUL) | Cxxx-NCR-001463 | NCR | SCL - Poor core quality within PTE between Adv 1 - 105 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-08-29 | 2014-08-21 14:01 | -8 | 2014-06-23 15:19 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Inadequate/insufficient tooling. | Completed |  | Poor core quality found on advance TH45 / TH65 / B99 updated 20/6/14 Cores with an average =>2.5 I50,TH45, TH65, B67,B71,105
| 02SL - Stations (LUL) | Cxxx-NCR-001464 | NCR | ETH Trap Shaft Lining wall up-stand kicker not cast integrally with slab |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2014-08-06 | 2014-07-23 14:04 | -14 | 2014-06-11 13:35 | Civil - Civil Engineering General | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Up-stand kickers for ETH Trapezoidal shaft level 3 & 4 lining walls have not been cast integrally with the slab as specified in drawing Cxxx-SWN-S-DDD-M123_Z-0010.
| 02SL - Stations (LUL) | Cxxx-NCR-001465 | NCR | Anchorage to female piles for Beam 4 at Level -4 in the Shaft SHE3 at the Eastern Ticket Hall |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-09-19 | 2014-09-18 15:33 | -1 | 2014-06-12 10:10 | Civil - Civil Engineering General | 2000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | Due to shear link bars being scheduled with shorter vertical legs than required by the Euro Code, in order to function as a shear link, an alternative solution was required in order to provide the minimum shear area required in the rebar cage. The bar in question is bar mark 23 on drawing Cxxx-ATK-S-DWG-M123_5-50101 (see attached). A solution was developed by 's reinforcement detailer -__ which included the anchoring of rebar into both the female and male piles behind the beam. This solution which was fully implemented on site is recorded on Cxxx-RFI-001892. In response to RFI-001892, Cxxx raised concerns about the adequacy of the female piles to provide the required anchorage in order to make the solution on Cxxx-RFI-001892 compliant with Eurocodes. The slab at Level -4 was poured on Friday, the 6th of June along with Beam 4. Due to the fact that Cxxx were not fully satisfied with the proposal made on RFI-001892, thinks this is Non-Conformance to Works Information and hence the NCR.
| 02SL - Stations (LUL) | Cxxx-NCR-001466 | NCR | ETH - Insufficient concrete cover next to W23B south construction joint |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-07-04 | 2014-07-03 17:42 | -1 | 2014-06-12 15:26 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Affected by Cxxx-NCR-001451 there is limited area near the top corner of W23B construction joint where there is insufficient concrete cover. (see attached photos)
| 02SL - Stations (LUL) | Cxxx-NCR-001467 | NCR | WTH - Welding of TW to perimeter sheet piles |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-06-27 | 2014-06-17 16:10 | -10 | 2014-06-12 18:19 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Welding of temporary works to WTH perimeter sheet piles not as per KM10-Wedling as no welding procedure was in place.
| 02SL - Stations (LUL) | Cxxx-NCR-001468 | NCR | ETH - Lower escalator ramp - pour 1 - Concrete defects |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-07-11 | 2014-07-11 16:55 | 0 | 2014-06-16 08:58 | Civil - Civil Engineering General | 3000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The lower escalator ramp - pour 1 was poured on Monday 09/06/2014. Issues occured while pouring towards the top end of the pour near the hyrib stop end (see attached photos). Due to the position of the shutter and the pouring holes a number of areas were not properly concreted in, in some areas the reinforement steel is still exposed.
| 02SL - Stations (LUL) | Cxxx-NCR-001469 | NCR | WTH SHW2 level -8 sump base slab concrete strength |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-08-25 | 2014-08-21 10:42 | -4 | 2014-06-13 17:39 | Civil - Civil Engineering General | 1000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | WTH SHW2 level -8 sump base slab concrete mix is F3, C40/50 compressive strength at 28 days. Concrete strength has not been achieved at 28 days as per Cxxx-SWN-C-RSP-M123-00004, Table KF10-01, F3. Cube results at 28 days were 42.6N/mm2 and 42.9N/mm2 (see attached) Cube results at 45 and 56 days were 45.1N/mm2 (see attached) Also attached is the concrete site control sheet identifying the load were cubes were taken and its concrete delivery ticket. We have examined the test report for cubes cast on 15.05.14 for the WTH mix F3 and would comment as follows: 1. Reported cube densities are lower than those expected for this grade of concrete; 2. The gain from 28 day cubes to 56 days (2.5 N/mm2) is not typical for the concrete supplied; 3. Autographic records confirm the correct amount of materials being batched; Upon consultation with our concrete supplier, and even though the concrete strength has been constant from 45 to 56 days, from this F3 (GGBS) mix there is no reason to assume the concrete will not gain strength from 56 days onwards up to and including 128 days but it could not reach the full design strength of 50N/mm2
| 02SL - Stations (LUL) | Cxxx-NCR-001470 | NCR | WTH SHW2 Welding of earth bars to bottom mat reinforcement |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-06-30 | 2014-06-17 08:19 | -13 | 2014-06-16 09:29 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Earth bars have been tack welded (see attached photos) to the bottom mat of SHW2 level -8 pour 2 contradicting the approved FCD 1301. No FCD was written prior to work start. This has happen on Northern half of SHW2 level -8 base slab only. See attached sketch for locations.
| 02SL - Stations (LUL) | Cxxx-NCR-001471 | NCR | SCL - Thermometers used on site don't have calibration certificates |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-07-10 | 2014-07-09 18:05 | -1 | 2014-06-17 08:20 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Thermometers used on site did not have calibration certificates and they were not registered in the calibration register.
| 02SL - Stations (LUL) | Cxxx-NCR-001472 | NCR | WTH - SHW3 leaking secant piles |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-12-12 | 2014-12-08 15:07 | -4 | 2014-06-18 12:28 | Civil - Civil Engineering General | 2000 |  | Incomplete Works | Use As-Is | 4 (0.5-3k) | Complete | Previous Construction - Other | Completed |  | Clause KP10.1301 a) of the Civil & Structural Specification, could not be met. Secant pile walls are not free of from running or dripping water after exposing inside face. Following the guidelines of the Civil & Structural Specification and SPERW B1.9.1, Cxxx carried out an assessment, on the 16.07.14 am, of the watertightness of the SHW3 secant pile wall within the required weather conditions. See attached survey report. The assessment findings are as follows: •Generally the water ingress to the secant pile wall comes from the level -1 capping beam at the head of the piles. The waterproofing detail is unfinished at the moment as it will be closed out once the lining wall under the capping beam is constructed. The existing __ has been closed against the male piles but flies over the females (broken below blinding). This is at the moment providing a water path that flow down the secant piles. The project manager can note that from the survey, water is flowing down largely the females piles. This waterproofing detail will be closed out as per drawing Cxxx--C-DWG-M123-50064. Until then, the water ingress from the top of the piles is to be managed by the contractor so the remaining excavation and RC works are not compromised. •Areas of dampness not related with top water ingress do not exceed 1.0m2 so, as per the Civil & Structural Specification KP10.1301 a) no remedial works are required. Note that from the SPERW B1.9.1, no individual patch of dampness is to have an area in excess of 4m2.
| 02SL - Stations (LUL) | Cxxx-NCR-001473 | NCR | Early MEP Works - ETH Level-2 - Connections to lightning electrodes in Slab -2 not visible |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-07-01 | 2014-07-03 16:23 | 2 | 2014-06-17 14:46 | Electrical - Electrical Engineering General | 1000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The connections LE10 (U305), LE11 (U302), LE12 (T115), LE13 (T111) and grid line D - LE2 (T134), specified in drawing Cxxx--E-DDD-M123_Z-25706 X01 has not been implemented.
| 02SL - Stations (LUL) | Cxxx-NCR-001474 | NCR | SCL - Poor Core quality in STW1 Enlargement |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-09-12 | 2014-09-10 14:42 | -2 | 2014-06-20 12:20 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Poor quality cores in STW1 Enlargement Advances - TH4 - TH26 - I51
| 02SL - Stations (LUL) | Cxxx-NCR-001475 | NCR | ETH - South Basement - Lining wall 21D - Pouring with Blue tube installed |  | Crossrail | PDP | FAR - Farringdon Station (West) |  | 2014-07-25 | 2014-07-25 14:12 | 0 | 2014-06-17 16:42 | Civil - Civil Engineering General | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Verbal communication problem | Completed |  | Wall 21D was poured with a blue pipe installed to drain the water when it had expressly been agreed that this pipe was a temporary measure to keep the area dry and would be removed as the concrete was poured. The pipe remains in place and is not an approved permanent works detail.
| 02SL - Stations (LUL) | Cxxx-NCR-001476 | NCR | Concrete Temperature for W7 Concrete - SH-W2 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-10-03 | 2014-09-19 16:16 | -14 | 2014-06-19 10:46 | Civil - Civil Engineering General | 2000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | installed thermocouplers in buttress wall 7 and 9 to monitor the internal concrete temperatures. The highest temperature recorded for wall 7 was 68.36 and wall 9 was 74.69 degrees. Clause KF10.1302 and ITP Cxxx--C-ITP-M123-50209 Rev 2 states that the maximum temperature of placed concrete should not exceed 60 degrees. See attached log of temperature and location & level of thermocouplers. Curing agent has been placed on completion of pouring and frost blanket placed after the concrete moved to plastic state.
| 02SL - Stations (LUL) | Cxxx-NCR-001477 | NCR | WTH - SHW2 level -8 base slab drainage testing |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-07-03 | 2014-06-24 11:59 | -9 | 2014-06-19 17:22 | Civil - Drainage | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | Drainage testing not carried out as per ITP Cxxx--C-ITP-M123-50186 on SHW2 level -8 base slab, in one run of pour 2 (see attached in green). The hydraulic test could not be carried out on the drain runs shown on the attached drawing because the water level in the test pipe could not settle as per ITP (1.2mWG, constant for a period of not less than 30 min), even after all ends were inspected and re-inspected.
| 02SL - Stations (LUL) | Cxxx-NCR-001478 | NCR | ETH- Trap shaft - Level -3: Concrete repair prior to approved SAP |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-07-26 | 2014-07-23 15:00 | -3 | 2014-06-21 23:46 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Please find attached photograph showing a concrete repair that was done prior to approved SAP.
| 02SL - Stations (LUL) | Cxxx-NCR-001479 | NCR | SCL - Poor quality cores in PTW / CP3B thickening |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-09-18 | 2014-09-23 07:45 | 5 | 2014-06-23 15:16 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Core grade above 2.5 in accordance with procedure Cxxx--O4-GPD-M123-50014
| 02SL - Stations (LUL) | Cxxx-NCR-001480 | NCR | Maintenance of electrolevels on façade at 70-77 Cowcross street |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-07-14 | 2014-07-14 08:52 | 0 | 2014-06-23 08:47 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Two sensors of the electrolevel array (15 devices) installed on the façade at the 70-77 Cowcross have not been working properly and the reparation works have not been carried out within a reasonable time period.
| 02SL - Stations (LUL) | Cxxx-NCR-001481 | NCR | Missed couplers and incorrect downstand kicker position in Wall 6 at SH-E3 Trapezoidal Shaft Level -3 to -4 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-08-28 | 2014-08-20 15:02 | -8 | 2014-06-23 19:22 | Civil - Civil Engineering General | 1500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | have identified a 3m section of lining wall downstand kicker that has been incorrectly cast south of ES2 tunnel opening where the lining wall is locally thickened in between level -3 and level -4. The downstand kicker all along the west face at level -3 has been cast at an offset 1350 east of gridline A'. This ~3m section of lining wall downstand kicker should have been cast at an offset of 1650 east of gridline A' locally south of ES2 tunnel opening. Note, the position of the couplers facing upwards coming out of the top of the level -4 slab have been cast at the correct offset of 1650 east of gridline A'. The other issue is that the two lines of couplers (i.e. 56EF2 & 56EF4) have been installed in the level -4 slab but only one line of couplers (i.e. NF and FF) have been installed in the soffit of the level -3 slab as shown in the photo attached.
| 02SL - Stations (LUL) | Cxxx-NCR-001482 | NCR | ETH - Sourcing Rebar from different Rebar Suppliers without an approved MCR |  | Contr | BAM | FAR - Farringdon Station (West) |  | 2014-07-18 | 2014-07-08 10:56 | -10 | 2014-06-24 12:03 | Materials - Approval | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | Due to programme pressures and because BRC could not meet delivery deadlines to meet our programme for constructing the lining walls in between Level -2 to -3 inside the trapezoidal shaft, sourced the lining wall rebar from __ who could supply us the rebar in time on this occasion. Unfortunately, no one checked to see if an approved MCR was in place prior to fixing rebar until it was too late.
| 02SL - Stations (LUL) | Cxxx-NCR-001483 | NCR | SCL - Spraying rate over 18m3/hr |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-08-19 | 2014-08-15 11:53 | -4 | 2014-07-02 13:01 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 1. 12/06/14 – __ reported flow rates of 20m3/hr 2. 16/06/14 – __ reported flow rates of 23m3/hr 3. Putzmeister data presented on Tuesday 24/06/14 shows that on more than one or two occasions, we have been spraying at flow rates in excess of 18m3/hr
| 02SL - Stations (LUL) | Cxxx-NCR-001485 | NCR | WTH - Concrete mix used for SHW2 Western buttress wall |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-09-08 | 2014-09-01 09:43 | -7 | 2014-06-30 16:36 | Civil - Civil Engineering General | 1000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | W7 concrete mix Cxxx--C-LRC-M123-50349 (Approved Code 1) refers to 20mm aggregate. This mix has been supplied to site using 10mm aggregate without prior approval by the Project Manager. Concrete strength (60N/mm2) has been achieved from day 9 - See attached cube results.
| 02SL - Stations (LUL) | Cxxx-NCR-001486 | NCR | SH-W2 L-8 Slab Concrete Levels |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-07-16 | 2014-07-03 15:25 | -13 | 2014-07-02 16:22 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Other human error | Completed |  | Following the SH-W2 L-8 slab pours (the slab was split into 2 pours) carried out a survey of the concrete level and it was found that some levels in pour 1 were out of tolerance. The tolerances stated within the L-8 Concrete slab ITP (Cxxx--C-ITP-M123-50186 Rev 2) and Cxxx-SWN-S-DDL-M123_Z-00101 is +10/-0mm. A concrete screed will be cast on top of this slab in the future. See attached survey of levels and sketch.
| 02SL - Stations (LUL) | Cxxx-NCR-001487 | NCR | ETH - Trapezoidal Shaft - Hansons supplied concrete mix reference SL2 used in Level -4 |  | Contr | BAM | FAR - Farringdon Station (West) |  | 2014-07-17 | 2014-07-16 12:58 | -1 | 2014-07-01 20:33 | Materials - Approval | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | In accordance with Clause KF10.2202 (b) of the Civil & Structural Specification, the maximum cementitious content in any concrete design mix shall not exceed 450kg/cu.m. have poured Slab at Level -4 in the Trapezoidal Shaft at the Eastern Ticket Hall on 6th June 2014 using SL2 concrete mix supplied by . After the concrete was poured in the slab, it was spotted in the design data that the total cementitous content used in the concrete mix was 486kg/cu.m. instead of 450 kg/cu.m hence the reason for this NCR. understands that the fact that the reason for the maximum cementitous content in any concrete mix design is to limit the potential of thermal cracking caused due to faster heat of hydration. In order to record the in-situ temperature during curing period, used thermo-couplers in the concrete pour which recorded the maximum rise in temperature as 50 degrees centigrade (see attached graph for clarity) during curing period which is in compliance with the Clause KF10.3206 (j) of the Civil & Structural Specification which says that the maximum temperature of concrete during curing shall not exceed 70 degrees. Moreover, there is no visual sign of any thermal cracking on the surface of the slab anywhere. Based on the above facts, considers that the concrete has performed in a way it should have performed, had the cementitous content been 450kg/cu.m. in the first place. Therefore, would request CRL accept the proposal to use the cast concrete in Slab at Level -4 “As-Is” on this particular case and would also like to state that the total cementitious content will be particularly referenced in the Material Compliance records from now onwards to avoid similar issues.
| 02SL - Stations (LUL) | Cxxx-NCR-001488 | NCR | testing equipment |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-07-24 | 2014-07-24 17:16 | 0 | 2014-07-02 12:45 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Flow cones and tamping bars held in stores but not registered on testing equipment register to comply with the works information 20.4 Inspection and Testing and 20.8 measurmrnts
| 02SL - Stations (LUL) | Cxxx-NCR-001490 | NCR | SMM - Out of Spec heave at Butchers Ramp |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-07-22 | 2014-07-16 12:40 | -6 | 2014-07-02 10:19 | Geotechnical Engineering - Compensation Grouting | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | A compensation grouting post-jacking episode (Cxxx-GEO-S-11903-PoJPTE-020001) was carried out on 11/06/2014 and 12/06/2014 from Butcher’s Ramp Grout shaft to mitigate settlements above the alignment of Platform Tunnel East caused by CRL SCL and TBM tunnelling works. The grouting proposal was carried out and generated heave of up to 8-11mm across several monitoring points on the London Underground Running Lines (measured by Cxxx automatic prisms). This grouting proposal had been reviewed by Cxxx & CRL prior to starting.
| 02SL - Stations (LUL) | Cxxx-NCR-001492 | NCR | SCL - Re-filling accelerator IBC in accordance with procedure |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2014-08-08 | 2014-08-11 07:39 | 3 | 2014-07-02 12:22 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | Previous NCR (Cxxx-NCR-001321) proposed a limit on re-filling accelerator IBCs to no more than 5 times to preclude potential contamination of accelerator (linked to low early strength of the SCL). This proposed action was included in the Activity Plan for Spraying (Cxxx--C4-STP-M123-50284). Part of the procedure includes physically marking the IBCs so as not to exceed the limit. On 01/07/14 it was noticed that this has not been followed for at least 5 days. See attached photo.
| 02SL - Stations (LUL) | Cxxx-NCR-001493 | NCR | Unusable TAM in Butcher’s Ramp: TBU029 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-08-04 | 2014-07-24 12:44 | -11 | 2014-07-02 17:42 | Geotechnical Engineering - Compensation Grouting | 1000 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During maintenance works carried out at Butcher’s Ramp shaft, TaM TBU029 was being washing out with the high pressure pump (Rostor) when the nozzle got stuck inside this TAM pipe. Up until this point it has not been possible to retrieve the nozzle and line and therefore TaM TBU029 is currently unusable.
| 02SL - Stations (LUL) | Cxxx-NCR-001496 | NCR | SMM - No strength cylinders taken for April |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-08-04 | 2014-07-29 09:06 | -6 | 2014-07-03 08:59 | Geotechnical Engineering - Compensation Grouting | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | A set of cubes were taken on the 19/03/14 to test the strength of the grout mix. The next set of cubes for the same purpose was taken on the 08/05/14. This is longer than the stated ITP requirement of every month as tests for April were missed.
| 02SL - Stations (LUL) | Cxxx-NCR-001497 | NCR | Register and Issue Record had insufficient detail of 3D models |  | Crossrail | PDP | FAR - Farringdon Station (West) |  | 2014-08-07 | 2014-08-01 09:40 | -6 | 2014-07-03 10:24 | Mechanical - Mechanical Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | Register and Issue Record had insufficient detail of 3D models as identified in surveillance report QS435-11 resulting in reporting them in error as overdue.
| 02SL - Stations (LUL) | Cxxx-NCR-001498 | NCR | SMM - Unusable TaM in Butchers Ramp: TBU050 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-07-22 | 2014-07-16 12:36 | -6 | 2014-07-03 12:44 | Geotechnical Engineering - Compensation Grouting | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During maintenance works for CP2b & CP3b grouting, the double packer and the grout line became stuck inside TaM TBU050. There have been several attempts to unblock this TAM and recover the double packer but it has not been possible to do so up to this date and therefore TaM TBU050 is currently unusable.
| 02SL - Stations (LUL) | Cxxx-NCR-001499 | NCR | Sloping slab pour 3 reinforcement |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-08-08 | 2014-07-28 09:23 | -11 | 2014-07-03 16:38 | Civil - Civil Engineering General | 2500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | __ are currently constructing the top and last section (pour 3) of the sloping slab. During the steel fixing of beams East and West (see drawing attached) couplers for BM 02 and BM 04 were installed as per __ RFI-00051. Drawing Cxxx-ATK-S-DWG-M123_4-50112 C02 (attached) shows the number of couplers required for the connection between beams East and West and the sloping slab: 10No BM02 & 6No BM04 for top mat and 3No BM02 for bottom mat per beam. has exposed the couplers fixed into these beams and the number is less than what has been detailed in the above drawing: - East beam: 11No in total for BM02 and BM04 (top mat) and 0No for BM02 (bottom mat) - West beam: 12No in total for BM02 and BM04 (top mat) and 6No for BM02 (bottom mat) - Beam 5 (L-2) 56 out of 59 starter bars have been installed for top and bottom layer. proposes to drill and resin in the missing bars with __ Hit HY 200 as per attached RFI Cxxx--RFI-00344 and __ response. In the absence of the actual loading for the slab the embedment depth for the B25 bars was determined for the failure load of the B25 bar, this way assuming the worst case scenario. Due to the rebar congestion it was not possible to drill the holes to the required embedment depth everywhere. However, this embedment depth has not been derived with the actual loading but the failure load of the bar. The actual embedment depth is shown on the attached photos and has then been taken into account for the calculation. (see attached spreadsheet)
| 02SL - Stations (LUL) | Cxxx-NCR-001500 | NCR | ETH- Trap Shaft - Excess cover in lining wall steel |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-07-29 | 2014-07-28 19:45 | -1 | 2014-07-03 15:57 | Structural Engineering - Reinforcement | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | __ have identified a number of areas in Level -3 Lining Wall with excess cover, due to rebar congestion for wall starters. Please see attached drawing with locations of excess cover. propose to reduce cover by using A393 square mesh would this be acceptable. This was issued to __ and their response was as follow: "From a detailing perspective we have no adverse comments, however Cxxx will need to approve the use of mesh for crack control and the reduced lever arm of the starter bars." This issue might re-occur at other levels within the Trap shaft.
| 02SL - Stations (LUL) | Cxxx-NCR-001501 | NCR | ETH - MEP - Damage to cavity wall drainage |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2014-08-11 | 2014-08-05 10:56 | -6 | 2014-07-03 17:13 | Mechanical - Public Health Engineering | 5000 |  | Damaged | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the excavation from L-3 to L-4, the cavity wall drainage suspended from L-3 slab have been damaged/broken accross the perimeter of the level. the cavity wall drainage at L-3 is also not covered and wooden caps have all been taken off.
| 02SL - Stations (LUL) | Cxxx-NCR-001502 | NCR | WTH - Level -2 slab I1a 28 day concrete cube strength not achieved |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-08-15 | 2014-08-14 09:59 | -1 | 2014-07-04 16:15 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | 8 out of 24 samples from level -2 pour I1a failed in 28 day strength, although the results are very close to 50N/mm2.
| 02SL - Stations (LUL) | Cxxx-NCR-001503 | NCR | ETH - SB - Lower Escalator Ramp - Pour 1 - Insufficient waterproofing detail |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-05-05 | 2015-04-30 08:44 | -5 | 2014-07-04 16:48 | Civil - Civil Engineering General | 8000 |  | Design | Use As-Is | 2 (6-60k) | Complete | Design Problem - Other | Completed |  | The lower escalator ramp pour 1 was concreted with insufficient waterproofing details in place. The construction joint between Beam 3 (L-3) and the lower escalator ramp only had 2No vertical hydrophilic strips installed either side as per Cxxx--C-XKS-M123-50200 Rev C02. No confirmation from __ in place that the detail would suffice "Grade 3" waterproofing requirements.
| 02SL - Stations (LUL) | Cxxx-NCR-001504 | NCR | ETH- Hair Line Cracking around Level -1 Beam Box Outs |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-08-14 | 2014-08-13 15:49 | -1 | 2014-07-05 17:28 | Civil - Civil Engineering General | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Around the Box Outs for the Level -1 Beams in the lining wall W21 Section H of the Two Storey Basement ,hair line cracks have begun to form subsequent to pouring concrete during the curing period despite the application of concrete curing agent as is outlined in the methodology and despite installing the reinforcement as per detailed design. raised RFI-00295 to __ regarding the reinforcement detailing around the box out of the beams for which there was an accepted proposal and design detail. The detailed design however did not contain anti-crack bars at the vertices of these box outs. Please find attached Sketch Cxxx-SR-ETH-REBAR040 which is the proposal for RFI-00295 along with the informal agreement via email from __ and the formal RFI-00295 which will be responded to subsequently to reinforce the email correspondence.
| 02SL - Stations (LUL) | Cxxx-NCR-001512 | NCR | WTH SH-W3 Non-compliance with Method Statement |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-08-01 | 2014-07-31 13:06 | -1 | 2014-07-09 13:09 | Civil - Civil Engineering General | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | excavated a localised shallow trench at the splice plate location of the Southern waler. This allowed a welder to be able to see and weld underneath the splice plate. This was not covered in the Method Statement. In addition, are also planning on installing a scaffold access in a different corner of the shaft to that stated in the same document.
| 02SL - Stations (LUL) | Cxxx-NCR-001513 | NCR | SCL - Poor quality cores in PTE, TH116 and TH152 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-08-29 | 2014-08-21 11:36 | -8 | 2014-07-11 15:48 | Tunnelling - Linings - Sprayed Concrete | 2000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Inadequate/insufficient tooling. | Completed |  | Core grade > 2.5 average. TH 116 (1No. grade 4 and avg. 2.67) and TH152 (1No. grade 4 and avg. 3.33)
| 02SL - Stations (LUL) | Cxxx-NCR-001514 | NCR | SCL - Poor quality cores in PTW TH152 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-08-12 | 2014-09-06 08:01 | 25 | 2014-07-11 16:00 | Tunnelling - Linings - Sprayed Concrete | 2000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Poor core quality in PTW on TH152 TH152 (1 No. grade 4, avg. 3.33)
| 02SL - Stations (LUL) | Cxxx-NCR-001515 | NCR | SH-W2 Removal of S6 Steelwork |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-08-25 | 2014-08-22 16:51 | -3 | 2014-07-15 08:37 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | An 'L' shape waler was being lowered to the ground in SH-W2, its irregular shape caused it to become unstable and strike buttress wall 7 causing some damage. This activity formed part of the removal of the S6 steelwork. See attached photo of damage caused by waler on buttress wall 7.
| 02SL - Stations (LUL) | Cxxx-NCR-001516 | NCR | WTH SH-W2 Earthing Clamps |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-08-15 | 2014-08-14 08:26 | -1 | 2014-07-15 08:38 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | The acceptance of Cxxx-FCD-001296 allowed for the break out of concrete to pile R929, so that an L-Bar with a 100mm weld could be welded onto the vertical bar, as part of the earthing connection. The 100mm weld could not be achieved so instead additional concrete was broken out and earthing clamps were used (similar to the ones accepted in Cxxx-FCD-001295), however, this was done without an approved FCD. See attached picture. As
| 02SL - Stations (LUL) | Cxxx-NCR-001517 | NCR | WTH SHW2 Thrust Bore Pipe Enabling Works - Pile Breakout Method |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-08-08 | 2014-07-24 08:46 | -15 | 2014-07-16 07:45 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | During the female pile breakout works under MS Cxxx--C-GMS-M123-50324 for the Thrust Bore Pipe, a method of breakout (coring with diamond drill) was used that was not covered in the method statement. The method posed an increased risk to damage to steel in the adjacent male piles over the hand breakout method that had been agreed. No damage was caused to the steel in the pile, as was evident from inspection of the cores removed by Site Engineer (CL) and CRL Field Engineer (CC). Refer to the attached site photographs of cores removed. Therefore, as the core drilling did not have a detrimental effect on the works or cause any damage, no remedial works are necessary.
| 02SL - Stations (LUL) | Cxxx-NCR-001518 | NCR | SCL - Weekly Submission of Test Report Summary Sheets |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2014-08-01 | 2014-07-31 14:50 | -1 | 2014-07-16 10:21 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | SCL - test report summaries are not up to date and have not been issued via Sharepoint (as agreed in the Materials Meeting of Thursday 14.11.13) since 16.06.14. It was agreed at the same meeting that test report summaries would be issued weekly to CRL via Sharepoint. This has not been happening with the agreed frequency.
| 02SL - Stations (LUL) | Cxxx-NCR-001519 | NCR | ETH - Coupler cover in trapezoidal shaft level -3 wall 5 downstand kicker |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-09-10 | 2014-08-26 18:28 | -15 | 2014-07-16 13:57 | Civil - Civil Engineering General | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | In the ETH trapezoidal shaft level -3 slab soffit there are 7 or 8 couplers very close to the edge of the down stand kicker on wall 5 (South East corner of the shaft). The installed lining wall starter bars will have minimal or no cover (as shown in the attached document) and should have a cover of 50mm.
| 02SL - Stations (LUL) | Cxxx-NCR-001520 | NCR | WTH - SHW2 level -8 slab 28 day concrete cube strength |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-09-26 | 2014-09-12 16:39 | -14 | 2014-07-17 11:01 | Civil - Civil Engineering General | 1000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | WTH SHW2 level -8 slab 28 day concrete cube strength (C40/50) not achieved. See attached 28 day cube results for SHW2 level -8 slab pour 1 (31.05.14) and pour 2 (17/06.14). See also attached 56 day cube results for SHW2 level -8 slab pour 1 (31.05.14) and pour 2 (17/06.14).
| 02SL - Stations (LUL) | Cxxx-NCR-001521 | NCR | SMM - Malfunction of Tiltmeter in 94 Cowcross Street |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-08-17 | 2014-08-14 17:50 | -3 | 2014-07-18 17:24 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | Titlemeter Cxxx-TB00402, located in 94 Cowcross Street, was found to be malfunctioning from October 2013 until June 2014 when it was repaired. Initially, it had not been known that this tiltmeter had been malfunctioning as readings had been registered during the entire time. However, the readings were in fact the exact same values repeated over and over and were therefore erroneous (see attachment). The Contractor's automated system to detect of automated instruments break did not flag this up in this case as readings were being registered (broken instruments etc only flag up when no readings are registered).
| 02SL - Stations (LUL) | Cxxx-NCR-001522 | NCR | WTH - SHW3 temporary prop installation |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-08-07 | 2014-08-07 11:57 | 0 | 2014-07-22 13:31 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | The resin used to fix bolts into the secant piles (SH-W3) was not installed in accordance with manufacturer's instructions. Holes with a diameter of greater than 20mm are to be blown and cleaned out using compressed air which was not done, only a manual hand pump was used. This was realised and excavation work ceased.
| 02SL - Stations (LUL) | Cxxx-NCR-001523 | NCR | WTH SHW2 wall 17 coupled starter bars out of position |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-09-15 | 2014-09-15 17:34 | 0 | 2014-07-23 13:13 | Civil - Civil Engineering General | 1500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Other human error | Completed |  | The coupled starter bars in the -8 slab and Wall 7 were cast out of position. As such the matching couplers in Wall 17 are not aligned.
| 02SL - Stations (LUL) | Cxxx-NCR-001524 | NCR | WTH - Level -2 Slabs - I1B - Cover to reinforcement - Excess Cover |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-08-07 | 2014-08-07 11:48 | 0 | 2014-07-24 10:12 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Steel reinforcement cover on small section of slab I1B on Level -2 WTH has up to 20mm excess cover. Please see sketch attached
| 02SL - Stations (LUL) | Cxxx-NCR-001525 | NCR | SMM - Unusable TaM in Butcher's Ramp: TBU023 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-09-01 | 2014-08-20 16:21 | -12 | 2014-07-25 10:22 | Geotechnical Engineering - Compensation Grouting | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During maintenance works in TAM TBU023 using the __ drill to wash out this TAM, the rods of this machine broke when they were been retrieved at a distance of 11m from the shaft. The result is that only the first 11m of this TAM can be used for grouting because the remaining 54m of this TAM are blocked. Up to this point it has not been possible to recover the drill rods, and is unlikely to be in the future.
| 02SL - Stations (LUL) | Cxxx-NCR-001526 | NCR | Survey of internal wall couplers cast in slab -2 in the two storey basement |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-08-15 | 2014-08-13 11:54 | -2 | 2014-07-25 14:10 | Civil - Civil Engineering General | 3000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | In order to progress with the lining walls, a detailed survey has been carried out for walls W30, W31, W32 and W20 first (see attached drawing) and to identify the extend of the issues with the starter bars. The remaining wall will be addressed separately at a later stage. As shown on the survey the min concrete cover is 35mm where 50mm (e.g. W20, W31, W32) is required and 29mm where 30mm is required (e.g. W30). proposes to use as is in line with Cxxx comments where “a reduced cover to the outer bars of 30mm would be acceptable”. Excess concrete cover occurs in localised areas. proposes to carry out mitigation measures as discussed with __ (see response from __). - Between 50mm and 60mm concrete cover – this is within tolerance. - Between 60mm and 80mm concrete cover - proposes to use as is in order not to compromise the concrete cover by adding additional mesh particular in areas where lapping the mesh. - Over 80mm concrete cover - proposes to add A393 rebar mesh will be added in areas with exccess concrete cover over 80mm to avoid the increased risk of cracking.
| 02SL - Stations (LUL) | Cxxx-NCR-001527 | NCR | ETH - Trap shaft - Damaged pile shear links at level -5 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-09-19 | 2014-08-29 13:25 | -21 | 2014-07-28 19:33 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | During trimming of concrete to out of tolerance piles at level -5 to fix rebar with accordance to approved RC drawings to maintain the minimum lining wall thickness and/or beam lever arm, 12No. shear link were damaged. Consideration was taken to break back pile concrete cover in order to fit in rebar as detailed as noted in RFI Cxxx-RFI-001876 and Cxxx-RFI-001953 . Please note that in previous RFI-001876 and Cxxx-RFI-001953
| 02SL - Stations (LUL) | Cxxx-NCR-001528 | NCR | ETH - Trap Shaft - Honeycombing under side of Level -5 in main staircore |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-06-16 | 2015-02-16 10:18 | -120 | 2014-07-30 09:43 | Civil - Civil Engineering General | 2000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During excavation works for Level -6 have identified some honeycombing to the underside of Level -5 by north stair core. Photos attached still need to gain access to area and fully investigate the extent of honeycombing. Once this is done will propose actions/mitigation. NCR transferred to punchworks item Cxxx-PWK-00024 • to gain access at height to fully investigate the extent of honeycombing • will consult with grout company on required method to repair are • to discuss with CRL Field engineers on agreed method and to follow concrete repair SAP Cxxx--C-STP-M123-50227. • operatives or specialist sub-contractor to repair area • and CRL joint inspection to sign off works
| 02SL - Stations (LUL) | Cxxx-NCR-001529 | NCR | SMM - Data upload to the Crossrail UCIMS database |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-12-03 | 2014-12-03 16:13 | 0 | 2014-07-30 10:47 | Surveying - Instrumentation and Monitoring | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | have failed to upload a certain amount of Monitoring Data to the UCIMS database in accordance with Clause 1.1.2.12 of the Specification for the Control of Ground Movement. This clause requires that the Contractor incorporate all monitoring data obtained to the UCIMS database (note that the Clause also states that the database is operated by the Cxxx [Cxxx] contract). A number of areas and/or monitoring points have not been successfully uploaded in accordance with the Specification. These are: NR Track Prisms (manual readings) Extensometers (site-wide) Inclinometers (site-wide) Farringdon Road (Levelling studs and Prisms) In all cases, data files were being sent to the UCIMS database. However, the files were erroneous and were therefore not being incorporated. It should also be noted that the above-listed instrumentation account for only a small percentage of the total monitoring data being obtained by , the remainder of which is successfully and regularly uploaded to the UCIMS database in line with the Specification.
| 02SL - Stations (LUL) | Cxxx-NCR-001530 | NCR | ETH Two storey basement Lining wall W21 E Concrete cubes damaged |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-09-16 | 2014-09-08 18:46 | -8 | 2014-07-30 13:55 | Civil - Civil Engineering General | 1500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | poured lining wall W21 section E (concrete mix W2 S4) on 24/06/2014 in the Two Storey Basement. Test consult made 1No set of 4 concrete cubes on site and took them to the laboratory for testing. We have been told by __ that, during the initial curing period, all the cubes were damaged. They were left on an unstable surface and fell to the ground. Now, it is not possible to crush any concrete cubes. In order to know whether the concrete has reached the final design strength or not and how the concrete strength develops, propose to use a Schmidt hammer, take several readings off wall W21 E at 14 days and 28 days and compare the readings with the schimidt hammer results, at 14 days and 28 days, done on the cubes made for lining wall W21 G (18/07) and H (22/7) as the same concrete mix design were used. The test done on the cubes will be carried out prior to crushing and to get a reference to use when we test lining wall W21 E with the schimidt hammer. do not have currently a schimidt hammer on site. An order has been placed already. If it is not possible to do the test at 14 days (01/08/2014) it will be done as soon as the schimidt hammer is delivered on site. If the results are similar it will mean that the concrete poured on wall W21 E has reached the design strength and no further actions need to be taken. At this point, this NCR will get closed out.
| 02SL - Stations (LUL) | Cxxx-NCR-001531 | NCR | WTH - Level -2 integral kickers |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-08-22 | 2014-08-21 13:16 | -1 | 2014-07-30 13:14 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | When casting level -2 base slabs, no integral kicker has been cast on wall 33 and wall 37 as per typical waterproofing detail of Cxxx-SWN-S-DDD-M123_Z-00110 and notes of Cxxx-SWN-S-DDL-M123_Z-00101. Due to the size of the pours and the width of the walls (1500mm and 3038mm respectively), it was not possible to install the integral kicker. Both walls have a section cast against the perimeter sheet piles. See attached sketch of wall 33 detail. Nonetheless the typical detail could not be achieved, the existing waterproofing detail is more robust that the typical detail of Cxxx-SWN-S-DDD-M123_Z-00110. The current detail fully wraps level -2 slab, walls to level -1 and level 0 on a continuous __ membrane Prior to the construction of wall 33, a hydrophilic strip (ADCOR 500) will be placed continuously throughout the extent of the wall construction joint.
| 02SL - Stations (LUL) | Cxxx-NCR-001532 | NCR | SCL - PTE B263 - non compliant 4hr nail test |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-08-14 | 2014-08-04 09:45 | -10 | 2014-07-31 08:26 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | Failed 4hr nail test on PTE B263.
| 02SL - Stations (LUL) | Cxxx-NCR-001533 | NCR | SCL - PTW - TH300 - Non Compliant Pull Out Test |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-08-14 | 2014-08-06 07:49 | -8 | 2014-07-31 16:31 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Supervision - Other | Completed |  | The pull out test that was required to be carried out on PTW TH300 panel was not carried out as the panel was accidentally destroyed prior to testing.
| 02SL - Stations (LUL) | Cxxx-NCR-001534 | NCR | SCL - Non maintenance of supplier test results since Feb 2014 and not being able to demonstrate constituent material compliance for SCL concrete |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2014-10-10 | 2014-10-07 09:17 | -3 | 2014-07-31 09:30 | Civil - Tunnelling | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | During the Cxxx SCL primary lining surveillance dated 15th July 2014 a review was carried out on constituent materials testing against the requirements of KT20.1400 Materials, and ’s documented materials testing frequency tracker. KT20.1400 and the materials testing frequency tracker state requirements for carrying out testing, or obtaining supplier testing for the concrete constituent materials cement, micro silica, steel fibres, aggregates, accelerator and other admixtures on a weekly/ monthly frequency. It was highlighted during the surveillance that the last time supplier test results were obtained was February 2014; therefore could not demonstrate that the constituent materials used in concrete production from March 2014 onwards were compliant against the performance requirements detailed under KT20.1400. Works Information Vol 2B part 13.1 states “the provision and maintenance of records”. Additionally instructed their dedicated materials testing sub-contractor __ to carry out Particle Size Distribution (PSD) testing of the concrete aggregates at a frequency of one per week to demonstrate compliance. __ carry out the PSD testing to BS EN 933-1:2012 (Tests for Geometrical Properties of Aggregates Part 1: Determination of Particle Size Distribution – Sieving Method) and issue the report to . It was highlighted during the surveillance that on receipt of these results they are placed in the appropriate certification hand over folders as evidence against the frequency and performance requirements. On review of the test reports it was found that no specification had been placed against the PSD results, and as such there was no indication whether the aggregates received were compliant with BS EN 12620:2013 (Aggregates for Concrete). Additionally as no specification had been placed against the results, there was no way for the to monitor trending of the results against the specification, highlighting potential variability which could affect the performance of the batched concrete. Additionally as have received no results from the suppliers since February 2014 there is no way of determining whether the 2/6mm Limestone and 0/4mm Marine Sand are compliant with the defined specification grading curve obtained from BS EN 12620:2013.
| 02SL - Stations (LUL) | Cxxx-NCR-001535 | NCR | SCL – Flow testing not carried out in accordance with BS EN 12350-5 |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2014-08-28 | 2014-08-15 11:49 | -13 | 2014-07-31 09:37 | Civil - Tunnelling | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not trained for the work being performed | Completed |  | During the Cxxx SCL primary lining surveillance dated 15th July 2014 fresh concrete flow testing was witnessed being carried out by operative __ for PTW Bench 259. During the test the operative did not use a tamping bar as required by BS EN 12350-5:2009 clause 6 “Fill the mould with concrete in two equal layers using the scoop, levelling each layer by tamping lightly ten times with the compacting bar”. This was picked up by the Materials Technician who formed part of the site visit, and the operative was asked to redo the test. The tamping bar was subsequently used, however when carrying out the 15 drops as required by the procedure, the operative was seen to lift the table to such an extreme that caused the table to hit the upper stop and move the concrete, equating to 30 drops (15 drops, 15 bangs). BS EN 12350-5:2009 clause 6 further states “Slowly raise the table top till it reaches the upper stop in such a manner that the table top does not impact hard against the upper stop”. This was witnessed again by both the Contractors Materials Technician and Sub-Agent. On post surveillance review of the Contractors training records it was found that __ had been trained and signed off as competent to carry out flow testing to the defined British Standard.
| 02SL - Stations (LUL) | Cxxx-NCR-001536 | NCR | SCL – Traceability of records could not be provided for FAR 363 and 388 compressive strength samples |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2014-08-28 | 2014-09-05 11:29 | 8 | 2014-07-31 09:45 | Civil - Tunnelling | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | During the Cxxx SCL primary lining surveillance dated 15th July 2014 material results and document traceability was reviewed for compressive strength samples FAR 363 and 388. During the surveillance, the sample request form generated by the site team for these core samples could not be provided. On review of the laboratory test reports, the location, date sprayed and date sampled was detailed, however this could not be traced to the original sample request forms (FAR 363 and 388) as they could not be found and produced. A request was made in the surveillance exit note for the sample request forms to be provided within five days, however nothing was provided. Therefore it could not be determined that the information detailed on the __ reports were accurate and applicable. Works Information Vol 2B part 13.1 states “the provision and maintenance of records”. Additionally ISO 17025:2005 General Requirements for the Competence of Testing and Calibration Laboratories clause 5.7.1 states “The laboratory shall have procedures for recording relevant data and operations relating to sampling that forms part of the testing or calibration that is undertaken. These records shall include the sampling procedure used, the identification of the sampler, environmental conditions and diagrams or other equivalent means to identify the sampling location as necessary”. Additionally, on review of the compressive strength test report for FAR 388, it was identified that samples 3, 4 and 5 were missing from the report, with samples 6,7 and 8 being tested at approximately 37 days and 9,10 and 11 tested at approximately 41 days. Samples 1 and 2 were tested at 3 days. Nothing could be provided to indicate why samples 3, 4 and 5 were missing and why samples 6 through 11 were tested at ages 37 and 41 respectively with the samples taken on the same date. Furthermore, on review of the compressive strength summary, under FAR 388 there was no statement from providing information that the results reported under ’28 days’ related to testing carried out at 37 days.
| 02SL - Stations (LUL) | Cxxx-NCR-001538 | NCR | SCL - Failure of Flexural Beam test for June 2014 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-08-19 | 2014-08-15 11:52 | -4 | 2014-08-05 16:35 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | 5 No of 6. 28 days beams have passed 1No. 28 day beam has failed due to unload reload loop
| 02SL - Stations (LUL) | Cxxx-NCR-001539 | NCR | SCL - 28 Day compresive strength failed to reach the running mean |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-09-03 | 2014-08-26 12:59 | -8 | 2014-08-06 16:04 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Not Defined | Completed |  | The following 28 day Compressive strength results failed to reach the running mean. FAR - 248, FAR 253 FAR 255 FAR 259 FAR 263 FAR 304 FAR 308 FAR 313 FAR 316 FAR 318 FAR 321 FAR 322 FAR 326 FAR 330 FAR 336 FAR 337 FAR 343 FAR 345 FAR 346 FAR 350 FAR 354 FAR 357
| 02SL - Stations (LUL) | Cxxx-NCR-001541 | NCR | SCL - Poor quality core PTW I222 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-09-17 | 2014-09-05 07:22 | -12 | 2014-08-08 14:41 | Tunnelling - Linings - Sprayed Concrete | 2000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | Poor quality in PTW on I222. 1 no. core graded as 4.
| 02SL - Stations (LUL) | Cxxx-NCR-001542 | NCR | I&M - Starting works without an accpeted ITP |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2014-08-22 | 2014-08-29 16:42 | 7 | 2014-08-08 15:50 | Surveying - Instrumentation and Monitoring | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Failure to follow status stamp | Completed |  | The ITP for installation of water settlement cells (Cxxx--C-ITP-M123-50062) revision 1 was returned at Code 3 on 22/10/12. Revision 2 was submitted for acceptance on 18/07/14. Water settlement cells have been installed wihtout an accepted ITP.
| 02SL - Stations (LUL) | Cxxx-NCR-001546 | NCR | ETH - L-3 W4 Cover Issues |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-09-09 | 2014-08-26 17:08 | -14 | 2014-08-11 17:22 | Structural Engineering - Concrete Member | 800 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | have found that on W4 between L-2 & L-3 there is varying cover, from too little to too much. Please find attached a cover survey of the front face lacer with the number corresponding to the vertical slab starter bars. On the survey ‘0’ indicates correct 50mm cover. Also attached are photos of the area of too little cover. Both of these issues have been caused by congestion in the L-3 and wall starters being installed out of position.
| 02SL - Stations (LUL) | Cxxx-NCR-001548 | NCR | WTH - SHW2 - Incorrect placement of coupled starter bars for Wall 18 in Wall 8 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-08-15 | 2014-08-14 17:15 | -1 | 2014-08-12 18:44 | Civil - Structural Engineering | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | The group of 4 coupled starter bars, nearest to the lining wall 8, as indicated on the attached extract of Section 3-3 (BM 02, drawing Cxxx-ATK-S-DWG-M123_Z-50628) were placed incorrectly during the fixing of the level -8 base slab. Hence, the corresponding 4 threaded bars (BM 22) fell within the lining wall 8 as detailed in the attached photographs. The threaded bars were cast with the lining wall 8 and so only 4 x 2 coupled starters (BM 02) remain free for the steel fixing of wall 18, as detailed in the as built sketch, attached.
| 02SL - Stations (LUL) | Cxxx-NCR-001549 | NCR | SMM - Unsuccessful PTE concurrent grouting |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-09-01 | 2014-09-01 08:51 | 0 | 2014-08-13 14:27 | Geotechnical Engineering - Compensation Grouting | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During concurrent grouting works for PTE advances 332-335 a breach of the construction control alert occurred when only 20% of the planned volume was injected due to obstructions occurring within other TaMs in the proposal.
| 02SL - Stations (LUL) | Cxxx-NCR-001550 | NCR | SCL - PTW I318 - Mean over 2.5 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-09-24 | 2014-09-10 14:17 | -14 | 2014-08-15 12:36 | Tunnelling - Linings - Sprayed Concrete | 2000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 2no. cores from a set of 3 were graded as '3', the resulting mean is 2.67. 1No. grade 2
| 02SL - Stations (LUL) | Cxxx-NCR-001551 | NCR | WTH - SH-W2 Concrete Pre-Pour Inspections |  | Contr | HYD | FAR - Farringdon Station (West) |  | 2014-08-27 | 2014-08-18 15:42 | -9 | 2014-08-13 16:13 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | On Friday 8th August 2014 CRL were notified to attend the Pre-Pour Inspection for SH-W2 Wall 8(west) pour 2. The notification implies that all check items on the Cxxx Concrete Pre-Pour Checklist (doc.ref. Cxxx-SF-CON-0009) - included within the ITP for these works (doc.ref.Cxxx--C-ITP-M123-50209 Rev.2.0) – have been previously checked and corrected, where necessary, so as to comply with the Works Information. One of the check items that should be completed by Cxxx is ensuring that concrete cover is within the allowable limits (these limits have been stated in Cxxx-FCD-00974). During the CRL inspection it was noted that the concrete cover was outside the allowable limits of 45-60mm, with the areas at the far east and far west ends of Wall 8 having reduced cover of 35-45mm, and the central section having excess cover up to 85mm. It was found that the excess cover was caused in part by the 50mm spacer blocks being placed against the grout check at the top of the formwork, thus pushing the reinforcement further back away from the formwork face. This was corrected and the cover was brought to within the allowable limits prior to the pour commencing. For all future concrete pre-pour inspections, Cxxx are to ensure that all items on the Cxxx Concrete Pre-Pour Checklist have been satisfactorily completed, checked and verified, prior to inviting CRL to attend the inspections.
| 02SL - Stations (LUL) | Cxxx-NCR-001552 | NCR | WTH - SHW2 lining wall pour 8E1 concrete mix |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-09-12 | 2014-08-26 10:34 | -17 | 2014-08-14 12:18 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | WTH SHW2 pour 8E1 used W7 10mm aggregate without the approved FCD (FCD-001398). W7 10mm aggregate concrete mix MCR (Cxxx--C-LRC-M123-50380) is currently code 2 with minor comments.
| 02SL - Stations (LUL) | Cxxx-NCR-001553 | NCR | WTh - Level -1 - Slabs I1b - surface cracks |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-08-28 | 2014-08-26 08:39 | -2 | 2014-08-14 13:35 | Civil - Civil Engineering General | 1000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Surface cracking has been noted on RC Slab I1b on WTH Level -1. Cracks have appeared along the southern end of the pour as shown in skecth and photos attached. Cracks are 1.5mm in width. Cracks appear to be due to plastic settlement.
| 02SL - Stations (LUL) | Cxxx-NCR-001554 | NCR | No MCR for SCL reinforcement |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2014-09-04 | 2014-08-21 12:03 | -14 | 2014-08-14 17:10 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | an MCR for reinforcement for SCL thickening areas was not submitted and approved before use.
| 02SL - Stations (LUL) | Cxxx-NCR-001555 | NCR | ETH-Trap shaft - Pile trimming without agreement at level -5 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-09-30 | 2014-09-26 13:41 | -4 | 2014-08-17 16:31 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | carried out pile trimming to ETH Trapezoidal Shaft level -5 without specific agreement from Cxxx. Isolated damage to 12no pile shearlinks occurred during level -5 trimming and NCR1527 has been raised. This was a result of understanding that Cxxx requested to consider breaking out pile concrete cover in order to fit rebar as detailed which was mentioned previously in RFI-1876 & 1953 regarding specific piles in previous levels. RFIs will be raised only for piles that require pile concrete cover to be broken back to the rebar to accommodate lining wall and beams thickness.
| 02SL - Stations (LUL) | Cxxx-NCR-001556 | NCR | ETH - SB - L-3 sloping slab west side pile T121 - exposed reinforcement |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-09-12 | 2014-09-08 18:48 | -4 | 2014-08-18 13:31 | Civil - Civil Engineering General | 1000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | The secant piles either side of the lower sloping slab extend within the design position of the lining Wall 19 and W20 at Level L-3 (see attached survey). An invasive survey was supposed to be carried out to determine the position of the pile reinforcement. During the invasive survey on the west side of the sloping slab the reinforcement of corner pile T121 was exposed in an area of about 0.5m x 0.5m instead of just a 0.2m x 0.4m slot. We propose to use as is since the reinforcement got exposed in a localised area without damaging the reinforcement itself. The area of the exposed reinforcement will get included in the lining wall concrete pour in front of the pile. The reinforcement will be covered by the lining wall concrete.
| 02SL - Stations (LUL) | Cxxx-NCR-001557 | NCR | WTH SHW2 Honeycombing areas in Wall 8 East |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-09-01 | 2014-08-29 11:38 | -3 | 2014-08-18 16:42 | Civil - Civil Engineering General | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Following the striking of shutters for wall 8 east (bottom pour) honeycombing was identified. Areas affected are identified in the attached photos.
| 02SL - Stations (LUL) | Cxxx-NCR-001558 | NCR | SCL - Primary Lining Junction Thickening CH1/CP2 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-09-12 | 2014-09-09 12:39 | -3 | 2014-08-19 17:24 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | CH1/CP2 Thickening was sprayed with SFRC in areas where bar reinforcement was present.
| 02SL - Stations (LUL) | Cxxx-NCR-001560 | NCR | Missed Pullout tests in Tunnels PTW and PTE |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-09-17 | 2014-09-05 07:28 | -12 | 2014-09-03 11:42 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Not Defined | Completed |  | Engineers have missed pull out tests for advances I302 (12hr), TH305 (6&12hr) in PTE and TH324 (6hr), I330 (6&12) in PTW.
| 02SL - Stations (LUL) | Cxxx-NCR-001561 | NCR | WTH - Level -2 slab - Honey combing I1B pour |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-01-30 | 2015-01-28 10:45 | -2 | 2014-08-20 13:23 | Civil - Civil Engineering General | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Following the striking of shutters for I1B pour honeycombing was identified along the construction joint between I2a and I1b. Areas affected are identified in the attached photos.
| 02SL - Stations (LUL) | Cxxx-NCR-001562 | NCR | WTH SH-W3 Pile Starters |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-08-29 | 2014-08-28 09:05 | -1 | 2014-08-22 10:06 | Civil - Civil Engineering General | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Previous Construction - Problems based on previous construction errors | Completed |  | The pile cage in pile E808 in the South East corner of the SH-W3 shaft has been found to have rotated when it was installed. Only one line of couplers is visble, the other row is obscured by the adjacent female pile (E507) as seen in the attachment. As such we will not be able to install the threaded bar into these four hidden piles. propose to omit these four threaded bars, please confirm this is acceptable.
| 02SL - Stations (LUL) | Cxxx-NCR-001563 | NCR | WTH - Level -2 slab - I1B pour - Concrete temperature exceeding 60oC |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-09-19 | 2014-09-19 13:15 | 0 | 2014-08-26 17:47 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | installed thermocouples in the Level -2 base slab pour I1b to monitor the internal concrete temperature. The highest temperature recorded was 69.04 degrees celsius. This pour was one of the biggest of the WTH (approx.. 15000 Lx9000Wx3500H mm) Clause KF10.1302a states that the maximum temperature of placed concrete will not exceed 60 degree celsius. Similar NCR raised for I2B (Cxxx-NCR-001432) Minor surface cracks appeared on an isolated area of the slab and have been repaired and inspected as per closed NCR 1553. No other cracks found around pour faces.
| 02SL - Stations (LUL) | Cxxx-NCR-001564 | NCR | WTH - Level -2 slab - I1B pour - 28 day concrete cube strength not achieved |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-11-28 | 2014-11-18 09:02 | -10 | 2014-08-27 15:08 | Civil - Civil Engineering General | 3000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | WTH level -2 concrete pour I1b (location sketch attached) did not achieve 28day strength of 50N/mm2 as per Cxxx-SWN-C-RSP-M123-00004 Table KF10-01 and have not been compliant with BS EN 206:2013 criteria 1 and 2. Concrete mix used is SL6.1 (MCR-50344) I1b slab was cast on the 26/07/14. See attached results. As per BS EN 206:2013, no results have been disregarded due the difference between the two 28 day cube strengths divided by their mean as it is less than 15%.
| 02SL - Stations (LUL) | Cxxx-NCR-001565 | NCR | SCL - RESS not followed in PTW TH 396 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-09-10 | 2014-09-01 15:27 | -9 | 2014-08-27 16:56 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Other human error | Completed |  | RESS was not followed in Tunnel PTW advance TH396,
| 02SL - Stations (LUL) | Cxxx-NCR-001566 | NCR | WTH- SHW2 thermocouplers not installed as per current ITP |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-09-18 | 2014-09-17 17:33 | -1 | 2014-08-28 10:02 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | Thermocouplers not installed in all SHW2 lining walls and internal wall concrete pours as per ITP ref. number Cxxx--C-ITP-M 123-50209, item 15. See attached list of pours where thermocouplers were not installed.
| 02SL - Stations (LUL) | Cxxx-NCR-001567 | NCR | WTH - Concrete mix W7 20mm and W5 20mm not achieving 28d strength |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-01-19 | 2015-02-13 16:41 | 25 | 2014-10-01 14:39 | Civil - Civil Engineering General | 10000 |  | Material | Use As-Is | 2 (6-60k) | Complete | Material/Preservation Problems - Other | Completed |  | WTH SHW2 concrete pours where concrete mix W7 20mm (MCR-50349) and W5 20mm (MCR-50349) was used, did not achieve 28day strength of 60N/mm2 as per Cxxx-SWN-C-RSP-M123-00004 Table KF10-01 and have not been compliant with BS EN 206:2013 criteria 1 and 2. See attached results. As per BS EN 206:2013, no results have been disregarded due the difference between the two 28 day cube strengths divided by their mean as it is less than than 15%.
| 02SL - Stations (LUL) | Cxxx-NCR-001568 | NCR | WTH - SHW2 buttress wall 9 concrete temperature |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-10-27 | 2014-10-20 16:21 | -7 | 2014-10-06 18:08 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Cxxx installed thermocouples in WTH SHW2 buttress wall 9-2nd lift to monitor the internal concrete temperatures. The highest temperature recorded for wall 9 at core was 65.8 degrees. Location sketch attached. Clause KF10.1302 of Cxxx-SWN-C-RSP-M123-00004 states that the maximum temperature of placed concrete should not exceed 60 degrees. Curing regime as per ITP Cxxx--C-ITP-M123-50209 was in place. No visible surface cracks on face of buttress wall 9 central. Similar non-compliant temperature results of 1st lift of wall 9 have been captured on NCR-001476.
| 02SL - Stations (LUL) | Cxxx-NCR-001569 | NCR | WTH SHW2 connection starter bars missing between walls 7 and 17 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-09-08 | 2014-09-08 17:34 | 0 | 2014-08-28 14:42 | Civil - Civil Engineering General | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Previous Construction - Problems based on previous construction errors | Completed |  | The U-bars detailed on the elevation of Wall 17/Wall 7 were replaced by couplers bars, as agreed with Cxxx’s RC detailer via RFI. Cxxx-ATK-S-DWG-M123_Z-50627(C01) details 47no. U-bars from level -8 slab level to level -6 soffit level. In total only 37no. pairs of couplers and 3no. U-bars(at the top) have been installed, which translates to 7no. pairs of couplers missing from Wall 7 in this location. This is illustrated on the attached as-built version of this drawing. This is an installation error. The latest version of this drawing - Cxxx-ATK-S-DWG-M123_Z-50627(C03); yet to be submitted to CRL formally – has been amended to suit the late design change in the dimensions of the structural openings as per Cxxx’s requirements (refer to Cxxx-FCD-001366). This drawing version now details 46no. pairs of U-bars from level -8 slab level to level -6 soffit level at the elevation of Wall 17/Wall 7, which translates to 6no. pairs of couplers missing in this location. Again, this is illustrated on the attached as-built version of this drawing.
| 02SL - Stations (LUL) | Cxxx-NCR-001570 | NCR | I&M - Tiltmeters installed with ITP code 3 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-09-28 | 2014-09-11 14:28 | -17 | 2014-08-29 12:24 | Surveying - Instrumentation and Monitoring | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | I&M - Tiltmeters have been installed with the relevant ITP being code 3.
| 02SL - Stations (LUL) | Cxxx-NCR-001571 | NCR | SH-W2 Use of Cast Iron pipes as Cable Ducts in Sump Slab |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-10-10 | 2014-10-08 14:49 | -2 | 2014-09-01 19:32 | Civil - Civil Engineering General | 1000 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | used 4 no. cast iron pipes as cable ducts in SHW2 sump slab to accommodate electrical cables, see locations marked up on public health drawing attached. A conditional MCR (CRL-MCR-000021) was in place to use the cast iron pipe for certain areas but this did not include the sump.
| 02SL - Stations (LUL) | Cxxx-NCR-001575 | NCR | WTH Downstand Vertical Couplers in Level -1 Capping Beam |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-09-09 | 2014-09-08 12:44 | -1 | 2014-09-02 14:19 | Civil - Civil Engineering General | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | When fixing the downstand vertical couplers for the lining walls in the escalator shaft Level -1 capping beam, had great difficulty fixing the wall starters in the correct position. As the capping beam reinforcement was orientated perpendicularly to the ITH building this made it difficult to fix the downstand vertical couplers, with the wall reinforcement that was orientated perpendicularly to the site boundaries. As such the far face reinforcement on lining Walls 26 and 28 are not in the correct position to line up with the escalator shaft base slab starter bars. In the worst case the downstand coupler has 445mm of cover from the back face of the wall as shown on the attached sketch.
| 02SL - Stations (LUL) | Cxxx-NCR-001576 | NCR | Early MEP Works - ETH Levels -3/-4 Cavity Wall Drains |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-10-17 | 2014-10-02 14:26 | -15 | 2014-09-03 16:51 | Mechanical - Public Health Engineering | 5000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 1. 5 x CWD outlets are out-of-line with the lining wall, where the outlet flanges range from 20mm to 55mm inside the front face of the wall. 2. 5 x 100mm CWD from high level above drop out from the slab, are off-centre of the cavity and set back into the face of the lining wall where it would not be possible to fit an extension coupling and pipe to low level below.
| 02SL - Stations (LUL) | Cxxx-NCR-001577 | NCR | ETH: South Basement – Installation of waler and propping – Permit to load trestles - Hold Point Missed |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2014-10-10 | 2014-09-30 11:04 | -10 | 2014-09-06 15:45 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | issued 3No, Permits to Load for 3No, trestles. These permits to load were a Hold point for and Hold Point for CRL. As per Cxxx Project Quality Plan - Cxxx--O4-STP-M123-50001, section 8.5 Inspection & Testing: “... Records of checks, inspections and tests will be maintained in accordance with the ITP and sign off of hold points demonstrated before works can proceed further. These intervention points (Hold Points) were missed therefore QP, ITP and IRF were not followed. This is a procedural non conformance. Also, these permits to load were issued on the 29.08.14, 30.08.14 and 01.09.14, without having in place all the checks as per the ITP and manufacture specification. Bolts were lose and short. This is a workmanship and supervision non conformance and will be cover under another NCR
| 02SL - Stations (LUL) | Cxxx-NCR-001578 | NCR | ETH: South Basement – Installation of waler and propping – Trestles installation workmanship |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2014-10-10 | 2014-09-30 11:09 | -10 | 2014-09-08 17:41 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | were failing to identify that the works did not comply with the parameters of the ITP at their hold point and also the bolts were found not being installed correctly as per the TW drawings, design of the Mass 50 trestle tower. As per __, there was not torque requirement for the bolts connections but the bolts have to be tightened as much as possible using manual spanner. This was also confirmed by them on an email. CRL checked the trestles installation on the 02.09.14 and found that the 3no towers, # 3, #6 and #8, have loose bolts and a lot of them did not have the min threads required out of the nut as per standard. This is a workmanship and supervision non conformance. should spot those issues before issue each Permit to load IRF, Cxxx-ETH-TSB-SUB5-00012 rev 1.0, has been rejected. Actions given to There was also a procedural NCR to be raised (Cxxx-NCR-001577) and a RIVO as this is a safety issue.
| 02SL - Stations (LUL) | Cxxx-NCR-001579 | NCR | WTH SHW2 Cover on Wall 8(Level -8 to -6) |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-09-22 | 2014-09-15 18:13 | -7 | 2014-09-08 14:32 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Following erection of shutters on the internal face of wall 8 at the interface of wall 7, it was found that the cover was less than minimum specified in the reinforcement detailing drawings. The tolerance for cover (as per Cxxx-FCD-00974) for a 750mm thick lining wall is -5/+10 from the design cover of 50mm allowing a range of 45mm to 60mm, however cover ranged from 30mm to 45mm. See attached survey carried out on wall 8. (A similar NCR at ETH, Cxxx-NCR-001526 was accepted for reduced cover in local areas)
| 02SL - Stations (LUL) | Cxxx-NCR-001580 | NCR | SCL Early/Late Core Results January to July |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-09-24 | 2014-09-19 15:50 | -5 | 2014-09-10 15:26 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Insufficient work planning by the subcontractors | Completed |  | The following cores have been crushed late between January and July. The month indicates the date at which the concrete was sprayed. January FAR 236 – 1 Day Crushed at 3 Days FAR 243 - 1 Day Crushed at 3 Days FAR 246 - 1 Day Crushed at 3 Days FAR 246 – 28 Day Core Crushed at 30 Days February FAR 258 - 1 Day Crushed at 2 Days FAR 281 - 1 Day Crushed at 2 Days FAR 295 – 1 Day Crushed at 5 Days FAR 263 – 28 Day Core Crushed at 31 Days FAR 264 – 28 Day Core Crushed at 30 Days FAR 266 – 28 Day Core Crushed at 29 Days FAR 282 – 90 Day Core Crushed at 93 Days FAR 294 – 28 Day Core Crushed at 42 Days FAR 295 – 28 Day Core Crushed at 33 Days FAR 308 – 28 Day Core Crushed at 43 Days FAR 316 – 28 Day Core Crushed at 34 Days FAR 318 – 28 Day Core Crushed at 29 Days FAR 322 – 28 Day Core Crushed at 29 Days FAR 330 – 28 Day Core Crushed at 43 Days FAR 336 – 28 Day Core Crushed at 34 Days FAR 337 – 28 Day Core Crushed at 38 Days March FAR 313 - 1 Day Crushed at 2 Days FAR 336 - 1 Day Crushed at 2 Days April FAR 345 - 1 Day Crushed at 2 Days FAR 346 - 1 Day Crushed at 2 Days FAR 350 - 1 Day Crushed at 4 Days FAR 354 - 1 Day Crushed at 2 Days FAR 390 - 1 Day Crushed at 2 Days FAR 395 – 1 Day Crushed at 6 Days FAR 396 - 1 Day Crushed at 3 Days FAR 398 - 1 Day Crushed at 2 Days FAR 343 – 28 Day Core Crushed at 32 Days FAR 345 – 28 Day Core Crushed at 33 Days FAR 346 – 28 Day Core Crushed at 30 Days, 90 Day Core Crushed at 92 Days FAR 359 – 28 Day Core Crushed at 29 Days FAR 379 – 28 Day Core Crushed at 35 Days FAR 388 – 28 Day Core Crushed at 37 Days FAR 390 – 90 Day Core Crushed at 96 Days FAR 394 – 28 Day Core Crushed at 36 Days FAR 395 – 28 Day Core Crushed at 36 Days, 90 Day Core Crushed at 92 Days May FAR 416 – 1 Day Crushed at 5 Days FAR 423 - 1 Day Crushed at 2 Days FAR 441 - 1 Day Crushed at 2 Days FAR 421 – 28 Day Core Crushed at 26 Days FAR 429 – 28 Day Core Crushed at 33 Days FAR 451 – 28 Day Core Crushed at 29 Days June FAR 448 - 1 Day Crushed at 2 Days FAR 455 - 1 Day Crushed at 2 Days FAR 456 - 1 Day Crushed at 2 Days FAR 465 - 1 Day Crushed at 2 Days FAR 466 - 1 Day Crushed at 2 Days FAR 471 - 1 Day Crushed at 3 Days FAR 472 - 1 Day Crushed at 3 Days FAR 475 - 1 Day Crushed at 2 Days FAR 483 - 1 Day Crushed at 2 Days FAR 485 - 1 Day Crushed at 2 Days FAR 487 - 1 Day Crushed at 2 Days FAR 462 – 28 Day Core Crushed at 31 Days FAR 464 – 28 Day Core Crushed at 30 Days FAR 483 – 28 Day Core Crushed at 33 Days July FAR 492 - 1 Day Crushed at 2 Days FAR 493 - 1 Day Crushed at 2 Days FAR 494 - 1 Day Crushed at 2 Days FAR 496 - 1 Day Crushed at 2 Days FAR 500 - 1 Day Crushed at 2 Days FAR 503 – 1 Day Crushed at 4 Days FAR 504 - 1 Day Crushed at 2 Days FAR 492 – 28 Day Core Crushed at 30 Days FAR 500 – 28 Day Core Crushed at 34 Days FAR 522 – 28 Day Core Crushed at 33 Days FAR 529 – 28 Day Core Crushed at 36 Days
| 02SL - Stations (LUL) | Cxxx-NCR-001581 | NCR | WTH SHW2 Wall 8 Couplers not present for Wall 20 - Level -8 to -6 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-09-25 | 2014-09-18 12:57 | -7 | 2014-09-11 12:04 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following the pour to wall 8, level -8 to -6, it was found that 4 layers (16 No. couplers BMK 01 & 04 on Cxxx-ATK-S-DWG-M123_Z-50630) are missing, from a total of 39 layers.
| 02SL - Stations (LUL) | Cxxx-NCR-001582 | NCR | ETH - South Basement Wall 21 Misaligned Couplers |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-12-17 | 2014-12-15 15:36 | -2 | 2014-09-15 07:48 | Architectural - Walls | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | have surveyed Wall 21 starters bar couplers (please see attached GA). Couplers have been found to be out of position, by 45mm (survey attached). have informed __ of the issue and a formal Cxxx--RFI-00378 has been issued to __, propose to widen the lower section of Wall 21 in this specific location. Please see attached acceptance of Cxxx--RFI-00378
| 02SL - Stations (LUL) | Cxxx-NCR-001583 | NCR | WTH SHW2 Excess Cover for Lining and Internal Walls (Level -8 to -6) |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-10-10 | 2014-10-03 17:33 | -7 | 2014-09-12 18:17 | Civil - Civil Engineering General | 2000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | While fixing steel for the lining and internal walls for Level -8 to Level -6, it was found that some areas had excess cover(outside of the tolerances set by Cxxx-FCD-000974). In order to comply with the tolerance mesh was added in these areas. See attached plan location of walls and markups of mesh location at each affected wall. Also included on the drawings is the cover when the mesh was installed. Only 1 layer of mesh was installed at each location. (A solution similar to the above was accepted at ETH under Cxxx-NCR-001526)
| 02SL - Stations (LUL) | Cxxx-NCR-001584 | NCR | ETH - SB W21E - Schmidt-Hammer Test not carried out by UKAS accredited testing lab |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-10-17 | 2014-10-17 15:43 | 0 | 2014-09-15 16:34 | Civil - Civil Engineering General | 1000 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Insufficient surveillance of subcontractors | Completed |  | Following from NCR Cxxx-NCR-001530 non destructive concrete testing had to be carried out on lining wall W21E to prove the compressive strength of the concrete. According to KF10.2203 the testing laboratory is required to be UKAS accredited. The Schmidt-Hammer Test was carried out by __. It turned out later that __ was not UKAS accredited to carry out the Schmidt Hammer Test despite having confirmed this initial via email. See attached email.
| 02SL - Stations (LUL) | Cxxx-NCR-001585 | NCR | SMM - Missed Monitoring Points |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-10-17 | 2014-10-17 15:50 | 0 | 2014-09-15 17:29 | Surveying - Instrumentation and Monitoring | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | During the construction of CP2a, CP2b and CP3a there have been a number of points which have not been monitored in accordance with the specification (Cxxx-OVE-C2-DDJ-CR001_Z-31531). Whilst these cross passages were being constructed monitoring of sockets and levelling points should have been daily and crackmeters should have been twice per week.
| 02SL - Stations (LUL) | Cxxx-NCR-001586 | NCR | WTH Excess cover to top of SH-W3 base slab |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-10-17 | 2014-10-15 10:04 | -2 | 2014-09-17 10:06 | Civil - Civil Engineering General | 2000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | Prior to pouring the base slab to the SH-W3 base slab a cover survey was carried. It was found in certain areas that the cover exceeded the allowable +12.5mm meaning that the top mat reinforcement was low. A393 mesh was placed in these localised areas to reduce the cover to acceptable limits. In the South East corner of the slab photographs indicate that it was only one sheet of mesh rather than the two resulting in the cover being reduced from 73mm to 53mm as stated. In the South West corner two sheets of mesh were fixed, bottom sheet interlocked with the structural slab to reduce cover by 30mm. can ensure CRL that in no area of the slab the cover has been reduced to less than 50mm. New sketch showing areas where mesh was added is attached with photographs on first attachment. First photograph is SW corner and second is SE corner. Option to remove old attachments does not work so they are still attached.
| 02SL - Stations (LUL) | Cxxx-NCR-001587 | NCR | SCL - On-site welding |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2014-11-14 | 2014-11-07 15:04 | -7 | 2014-09-17 12:42 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | During the CRL surveillance on the management of on-site welding (03/09/14), it was noticed that 4" steel pipes have been welded on site. have a Welding Procedure Specification (WPS) for this type of weld yet none of their welders have the required Welding Approval Qualification Test Certificate (WQTC) and therefore should not be carrying out welding on pipes less than 6" in diameter.
| 02SL - Stations (LUL) | Cxxx-NCR-001588 | NCR | Incident Management of Property Damage |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-12-12 | 2014-12-12 12:30 | 0 | 2014-09-17 15:16 | Surveying - Instrumentation and Monitoring | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Lack of procedure | Completed |  | The contractor is not complying with Incident Management requirements outlined in the works information relating to “damage to or loss of, property” with respect to damage reported as a result of works.
| 02SL - Stations (LUL) | Cxxx-NCR-001589 | NCR | Incorrect reinforcement installed in PTW/CP2b top-heading thickening |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2014-11-07 | 2014-11-12 09:55 | 5 | 2014-09-19 14:13 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Reinforcement for PTW/CP2b thickening was installed to drawing Cxxx-MMD-C4-DDD-M123_5-00616 rather than Cxxx-MMD-C4-DDD-M123_5-00603. The section had been approved to spray, with spraying about to commence. CRL FE carried out a spot rebar inspection which identified the issue.
| 02SL - Stations (LUL) | Cxxx-NCR-001590 | NCR | WTH SHW2 startes bars for wall 12 damaged |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-10-06 | 2014-10-03 17:43 | -3 | 2014-09-22 08:29 | Civil - Civil Engineering General | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Personnel Error - Other human error | Completed |  | 8no 12mm coupled starter bars for wall 12 have been bent when a scissor lift drove over them. (See attached photos)
| 02SL - Stations (LUL) | Cxxx-NCR-001591 | NCR | SCL - Cxxx out of hours coverage - Farringdon |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-10-06 | 2014-09-27 10:36 | -9 | 2014-09-22 15:19 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Improper resource allocation | Completed |  | no Cxxx presence was on site for a) signing the RESS and b) agreeing response to breach of amber and red triggers on the in-tunnel monitoring. This was due to unexpected illness of Cxxx staff. This occured on 13/9/14
| 02SL - Stations (LUL) | Cxxx-NCR-001592 | NCR | ETH: Trapezoidal Shaft & South Basement – Failure of notification for witness point to CRL on concrete repairs |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2014-10-21 | 2014-10-17 15:45 | -4 | 2014-09-22 18:24 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Supervision - Other | Completed |  | failed to informed / notified Crossrail about the intervention point for concrete repairs as per the RC ITP (Cxxx--C-ITP-M123-50009 rev 6.0), Item 25. Concrete remedial works at the ETH (Trapezoidal Shaft & South Basement) have been carried out without formal notification for Inspection to Crossrail.
| 02SL - Stations (LUL) | Cxxx-NCR-001593 | NCR | SCL - Poor core quality in PTW TH441 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-10-31 | 2014-10-27 08:34 | -4 | 2014-09-23 12:50 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Quality cores for PTW TH441 failed on two counts a) a single grade 4 core and b) on the mean core grading (>2.5). The mean of the 5 No. cores taken is 2.8. If you disregard the grade 4 core, then the mean result is 2.5 (compliant).
| 02SL - Stations (LUL) | Cxxx-NCR-001594 | NCR | WTH SHW2 20mm chamfers not installed in the internal walls |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-10-10 | 2014-10-10 13:45 | 0 | 2014-09-26 15:45 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | Internal walls from levels -8 to -7/-6 in the SHW2 shaft have been cast without 20x20mm chamfers.
| 02SL - Stations (LUL) | Cxxx-NCR-001595 | NCR | SCL - No accpeted ITP for welding activities |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2014-10-21 | 2014-11-05 13:01 | 15 | 2014-09-23 13:38 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Welding activities have been taking place in the fabrication workshop in Caxton Basement without an accepted ITP.
| 02SL - Stations (LUL) | Cxxx-NCR-001596 | NCR | SCL:Temporary works inspections out of date |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2014-10-08 | 2014-10-02 14:35 | -6 | 2014-09-24 16:24 | Tunnelling - Tunnelling General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | Upon inspecting 's SCL Permit to Load folder, 17/21 listed active permits were outside their inspection frequency. An additional permit was in date but not listed in the inspection list.
| 02SL - Stations (LUL) | Cxxx-NCR-001597 | NCR | WTH - SH-W3 Non-conformance with waler removal method statement |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-10-10 | 2014-09-30 16:49 | -10 | 2014-09-25 10:18 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | The method statement for removing the walers from SH-W3 states that the East and West walers were to be cut at either end allowing the waler to be skated from position and lifted from the shaft. After completing the cuts at either end the waler was not sufficiently de-stressed to enable prop removal. An addition cut contrary to the method statement was made in the centre of the waler to enable it removal.
| 02SL - Stations (LUL) | Cxxx-NCR-001598 | NCR | WTH SHW2 wall 19 shutter misalignment |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-10-12 | 2014-10-09 10:08 | -3 | 2014-09-26 17:08 | Civil - Civil Engineering General | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The shutters for consecutive pours of wall 19 were misaligned resulting on a 11mm step on the concrete surface (see photos attached)
| 02SL - Stations (LUL) | Cxxx-NCR-001600 | NCR | Non compliance with SCL action plan |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2014-10-13 | 2014-10-10 09:51 | -3 | 2014-09-29 16:21 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | SCL Action plan Cxxx--C4-STP-M123-50001 (rev7) states in H.8 that two CPI silos will be available in the event of batching plant failure for emergency sealing. This is repeated in rev 8(draft). On 27/09/14, the silos were discharged to empty and were not refilled. The construction team confirmed there was no intention to refill the CPI silos.
| 02SL - Stations (LUL) | Cxxx-NCR-001601 | NCR | SMM:Temporary works inspections out of date |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2014-10-20 | 2014-10-14 16:24 | -6 | 2014-09-29 16:27 | Geotechnical Engineering - Compensation Grouting | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | 16/18 listed active permits were outside their inspection frequency. Cxxx grouting team offered that some checks are out of date as no works were being carried out, but the permit to load does not state this condition and the TW should be checked in the event of someone working in the area but not accessing the shaft. __ were unable to provide the missing sheets when requested.
| 02SL - Stations (LUL) | Cxxx-NCR-001602 | NCR | Early MEP Works - ETH Level-6 - CWD outlet repositioning |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-10-15 | 2014-10-03 15:41 | -12 | 2014-09-30 13:38 | Mechanical - Public Health Engineering | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | CWD outlet on ETH Level-6 at gridlines 7'/D' needs to be repositioned due to congested re-bar at the corner of the drop beam (see attached photo).
| 02SL - Stations (LUL) | Cxxx-NCR-001603 | NCR | WTH SHW2 wall 10 B40 lacers clash |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-10-14 | 2014-10-01 15:46 | -13 | 2014-09-30 16:59 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | 40mm lacers on wall 10 have been finished short of the steel columns as they are clashing with the vertical bars. (See attached sketch)
| 02SL - Stations (LUL) | Cxxx-NCR-001605 | NCR | ETH Two Sotrey Basement Reinforcement in Internal wall W20 from level -2 to -1 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-10-31 | 2014-10-30 18:53 | -1 | 2014-10-01 14:27 | Civil - Civil Engineering General | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Other human error | Completed |  | During the construction of internal wall W20 in the two storey basement from level -2 to -1 (see marked up area in blue in attached drawing Cxxx-ATK-S-DWG-M123_Z-50655 C01), at the south end of internal wall W20 (area highlighted in yellow in the above drawing), did not fix the reinforcement as detailed by __ to not compromise the cover. Also, in the same wall and outside of the concrete pour, at the south end of the void located between gridlines 4 and 5 there is a similar issue with the cover. raised RFI-00374 to __ (see attached all relevant attachements) where the above issues were highlighted. __ responded to the RFI and suggested a solution for each issue. __ also consider that their proposals need to be reviewed and accepted by Cxxx. Please review __ RFI-00374 responses and confirm that for: -South end of wall W20: it is acceptable to use it as it is. -South end of void between gridlines 4 and 5 in wall W20: __ has proposed a solution but carried out a survey (see attached) and propose to move the void 20mm to the north, fix vertical bars outside the B25 U-bars (same as at south end of wall W20) but fix in addition new B16 U-bars around the vertical bars leaving these inside. This solution avoids the need of cranking any bars as proposed by __. Also, this proposal would leave a as a minimum 36mm cover which is more than the minimum cover (30mm) stated by Cxxx in NCR-001526.
| 02SL - Stations (LUL) | Cxxx-NCR-001606 | NCR | SCL - Poor core quality in PTW, TH 432 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-10-30 | 2014-10-27 08:36 | -3 | 2014-10-01 17:00 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Cores failed to reach the required mean (=<2.5) total mean of 5No. corres is 2.6
| 02SL - Stations (LUL) | Cxxx-NCR-001607 | NCR | WTH Waterproofing Detail |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-10-17 | 2014-10-17 12:15 | 0 | 2014-10-02 12:28 | Civil - Civil Engineering General | 4000 |  | Damaged | Repair | 3 (3-6k) | Complete | Personnel Error - Other human error | Completed |  | The detail as provided by __ Construction between pile and slab soffit connection is detailed in drawing Cxxx--C-DWG-M123-50064 (attached - Section 2). When removing the __ 300R from the underside of the soffit it came apart at the soffit/pile connection leaving in some cases only approximately 10mm of __ exposed, see attached photograph. This is not in accordance with agreed detail. proposed an alternative solution to __ who have confirmed will work (email attached, references the use of two rows of hydrophilic as per expected response to Cxxx-FCD-001437). Bituthene LM is to be installed in the corner between the pile and soffit extending 75mm in both directions as shown on the attached sketch.
| 02SL - Stations (LUL) | Cxxx-NCR-001608 | NCR | SCL - Material placed in TBM backfill (PTE) without approved MCR |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-10-31 | 2014-10-18 08:06 | -13 | 2014-10-02 13:46 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | poured GROUT08 mix into the PTE TBM backfill yesterday with out an approved MCR
| 02SL - Stations (LUL) | Cxxx-NCR-001609 | NCR | SCL - Poor Core quality in PTW, TH 485 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-11-05 | 2014-10-27 08:39 | -9 | 2014-10-02 14:54 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Core quality failed to obtain a mean grade of <=2.5 in accordance with core grading procedure Cxxx--O4-GPD-M123-50014
| 02SL - Stations (LUL) | Cxxx-NCR-001610 | NCR | SCL - Poor core quality in CP4 (PTE side) TH30 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-11-02 | 2014-11-03 09:41 | 1 | 2014-10-02 17:15 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Core quality failed to obtain a mean grade of <=2.5 in accordance with core grading procedure Cxxx--O4-GPD-M123-50014
| 02SL - Stations (LUL) | Cxxx-NCR-001611 | NCR | SCL - Poor core quality in CP2 (PTW side) B/I 7 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-11-02 | 2014-11-03 09:39 | 1 | 2014-10-02 17:16 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Core quality failed to obtain a mean grade of <=2.5 in accordance with core grading procedure Cxxx--O4-GPD-M123-50014
| 02SL - Stations (LUL) | Cxxx-NCR-001612 | NCR | WTH SHW2 U Bar for Wall 10 Bent On Site (Level -8 to -6 Walls) |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-10-21 | 2014-10-16 11:56 | -5 | 2014-10-07 17:53 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | Following a site inspection it was found that a U Bar (BMK 05 on Cxxx-ATK-S-DWG-M123_Z-50626) previously cast in wall 6 was bent on site (see attached pictures). Cxxx-SWN-C-RSP-M123-00004 Clause KF10.3234 (a) its states that no item of reinforcement shall be bent, after it is embedded in concrete.
| 02SL - Stations (LUL) | Cxxx-NCR-001613 | NCR | WTH SHW2 Holes drilled in Wall 20 (Level -8 to -6 Walls) |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-10-24 | 2014-10-15 12:26 | -9 | 2014-10-10 15:05 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | Following a site inspection drill holes were found on wall 20 with dowel bars fixed into them. See attached pictures. The holes were used to fix the shutter for the upper section of Wall 20. This was not as per the temporary works design.
| 02SL - Stations (LUL) | Cxxx-NCR-001614 | NCR | ETH- Missing couplers in midlanding at 109.051 in internal wall W32 in the two storey basement |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-11-21 | 2014-11-21 11:11 | 0 | 2014-10-03 16:17 | Civil - Civil Engineering General | 1500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | has exposed the couplers of the midlanding at level 109.051 which were fixed during the construction of the internal wall W32. has compared the number of couplers fixed against the number of couplers detailed by __ (see attachment) and there is 1No coupler missing top and bottom. Find attached as built photo.
| 02SL - Stations (LUL) | Cxxx-NCR-001615 | NCR | ETH-Missing couplers in midlanding at 111.534 in internal wall W32 in the two storey basement |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-11-11 | 2014-11-10 19:09 | -1 | 2014-10-03 16:30 | Civil - Civil Engineering General | 1500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | During the construction of internal wall W32 up to underside of slab -1 (level 111.134) the couplers for the midlanding at level 111.534 were fixed using the information provided in RFI-001866 and __ RFI-00355 (attached). This information details the following: -2No Top and bottom coupled L bars to be fixed in the "nib" area -7No top and bottom coupled L bars be fixed in the "main midlanding" area -2No top and bottom coupled L bars to be fixed in the "recess" area. fixed the bars as follows: -1No Top and bottom coupled L bars fixed in the "nib" area -6No top and bottom coupled L bars fixed in the "main midlanding" area -2No top and bottom coupled L bars fixed in the "recess" area.
| 02SL - Stations (LUL) | Cxxx-NCR-001616 | NCR | ETH-Doorway opening in wall W32 in the two storey basement |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-01-30 | 2015-01-13 09:43 | -17 | 2014-10-03 16:36 | Civil - Civil Engineering General | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | has carried out an as built survey of the doorway located in the internal W32 between level -2 and level -1. Points 19 and 21 of the survey (attached) shows that the East top and bottom sides (point 19) are out 20mm towards the West and the West top and bottom sides (point 21) are out 30mm and 20mm respectively towards the West. Dimensions of the doorway are as per design and within the tolerance.
| 02SL - Stations (LUL) | Cxxx-NCR-001618 | NCR | SCL - Readiness Review Tracker Submission |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2014-10-21 | 2014-11-03 15:20 | 13 | 2014-10-07 17:06 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | The readiness review tracker for Phase 6 (Secondary Lining) was not formally submitted for the month of September. Furthermore, the weekly informal updated submissions have not happened.
| 02SL - Stations (LUL) | Cxxx-NCR-001619 | NCR | WTH SHW2 Misalignment of wall 18 South Face (Level -8 to -6) |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-11-07 | 2014-11-06 14:27 | -1 | 2014-10-13 15:30 | Civil - Civil Engineering General | 750 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Other human error | Completed |  | When setting out the shutter for slab -7 it was found that the alignment of wall 18 below was out of tolerance as per Cxxx-SWN-S-DDL-M123_Z-00101, see attached photo 1 showing maximum misalignment to be 27mm.
| 02SL - Stations (LUL) | Cxxx-NCR-001620 | NCR | ITP Witness Point 21 - Pre pour Inspections |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2014-10-30 | 2014-10-21 16:38 | -9 | 2014-10-09 16:39 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | ITP Witness Point 21 - requested a pre-pour inspection of ETH trap shaft L-5 wall 5A 07/10/14, it was noted during the inspection that a section of timber cast into the down stand kicker had not been removed. (Reinforced Concrete Works ETH - Cxxx--C-ITP-M 123-50009 - Rev 6)
| 02SL - Stations (LUL) | Cxxx-NCR-001621 | NCR | West Ticket Hall Retaining Wall Tiltmeters |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-10-28 | 2014-10-28 16:54 | 0 | 2014-10-10 17:44 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Not Defined | Completed |  | The west ticket hall retaining wall tiltmeters malfunctioned these instruments are still not working. As per the works information Cxxx-OVE-C2-DDA-CR001_Z-31532 'All instrumentation to be maintained throughout construction period and immediately replaced / reinstated if damaged/defective or unreadable.’
| 02SL - Stations (LUL) | Cxxx-NCR-001623 | NCR | SCL - No ITP submitted for Welding Activities |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2014-11-04 | 2014-11-03 10:50 | -1 | 2014-10-13 13:03 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Following Cxxx-NCR-001595 (raised on 23/09/14) regarding the lack of an accepted ITP for site welding operations, an ITP has yet to be submitted. The Contractor is continuing to weld in the workshop in Caxton basement without an ITP.
| 02SL - Stations (LUL) | Cxxx-NCR-001624 | NCR | ETH – Incorrect Downstand Kicker on Soffit of L-4 Slab W4 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-12-02 | 2014-11-26 08:45 | -6 | 2014-10-13 15:03 | Structural Engineering - Concrete Member | 1500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | The downstand kicker on the L-4 slab for Wall 4 has been cast in the correct position at the north end - but cast 128mm out of position towards the secant piles at the south end. The kicker has been cast on a straight line therefore the distance the downstand kicker is out of line is gradual over its length. The upstand kicker for Wall 4 on the L-5 slab has been cast in the correct position.
| 02SL - Stations (LUL) | Cxxx-NCR-001625 | NCR | ETH: South Basement – Slab -1 – Formwork Release agent used on site with no MCR in place |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2014-10-31 | 2014-10-30 12:28 | -1 | 2014-10-14 17:55 | Civil - Civil Engineering General | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | __ formwork release has been use in the South Basement works. It has been noticed that this material has been used over the falsework for the slab -1, however, there is no MCR in place for the use of this release agent at the FAR ETH
| 02SL - Stations (LUL) | Cxxx-NCR-001626 | NCR | ETH – Slab -1: Procedural non conformance for the installation on site of the __ Channels without the drawings being accepted by Crossrail |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2014-10-31 | 2014-10-28 16:59 | -3 | 2014-10-14 18:10 | Mechanical - Mechanical Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | A process for the CRL acceptance of the halfen channels’ drawings has been agreed between __/ & CRL (__). civils should have been followed the procedure but instead they have chosen to proceed with the installation of the channels without following the acceptance process and discussions during the engineering meeting on 07.10.14. The halfen channels were fixed without being submitted under Misc RIR as agreed between CRL & __/
| 02SL - Stations (LUL) | Cxxx-NCR-001627 | NCR | WTH - Concrete testing for Internal Wall 10 not carried out in accordance with National Standard. Equipment used for testing not calibrated as required by Works Information. |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2014-11-21 | 2014-11-20 18:09 | -1 | 2014-10-16 09:08 | Civil - Civil Engineering General | 500 |  | Testing and Commissioning | Repair | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | During a planned Crossrail surveillance dated 02nd October 2014, which witnessed the pouring of Internal Wall 10, the __ technician did not use a re-mixing tray and square mouthed shovel to remix the sample before manufacturing the cube samples. BS EN 12390-2:2009 testing Hardened Concrete Part 2: Making and Curing Specimens for Strength Tests clause 4 states “The sample shall be re-mixed, using the remixing container and square mouth shovel, before filling the moulds”. Additionally the thermometer used (serial number D12260681) for testing was overdue its calibration (last date 2012). Works Information Vol 2B Part 20.8 states “The Contractor shall maintain a schedule of all inspection, measuring and test equipment used for the works that includes records of the calibration of such equipment to nationally recognised standards.” The slump test equipment when reviewed during the surveillance had no form of identification mark present; therefore traceability to their respective equipment/ calibration records would be impossible. It was detailed that a system is in place however through wear and tear it had been removed. ISO 17025:2005 General Requirements for the Competence of Testing and Calibration Laboratories clause 5.5.5 states “Records shall be maintained of each item of equipment and its software significant to the tests and/or calibration performed. The records shall include at least the following; a-h” and clause 5.5.8 states “All equipment under the control of the laboratory and requiring calibration shall be labelled, coded or otherwise identified to indicate the status of calibration”.
| 02SL - Stations (LUL) | Cxxx-NCR-001628 | NCR | WTH SH-W2 Duct tape in Level -7 Slab Pour |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-10-30 | 2014-10-30 08:39 | 0 | 2014-10-16 13:51 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | Tie rods connecting the shutters together in the SH-W2 Level -7 slab are protected in plastic conduit. In some areas of the slab the joints in the conduit were joined by duct tape which is not an approved material. The accessible plastic conduit joints and duct tape at higher level either had the duct tape removed or were covered in an approved material (__ Tape - MCR number Cxxx--C-LRC-M123-50216) but there was no access to remove the duct tape from the lower level conduits. There were also isolated locations on L-bars at the base of the slab where duct tape had previously been used to hold protective ‘mushroom’ caps in place. It was also not possible to remove the duct tape from these areas before the pour.
| 02SL - Stations (LUL) | Cxxx-NCR-001630 | NCR | ETH Missing bars in level -1 slab Area A in Two Storey Basement |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-12-20 | 2014-12-08 14:13 | -12 | 2014-10-21 09:26 | Civil - Civil Engineering General | 750 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | has carried out a "Post pour inspection" of Area A at level -1 slab in the Two Storey Basement and has realized that some bars have not been fixed as per design. These bars have been highlighted in yellow in the Marked up drawings (see attached): - 2No B16 bars BM01 (top mat drawing) were meant to be fixed inside the slab (south face of internal wall W31 at Gridline 3). propose to omit them as these represent a small percentage of the total number of bars. -3No B16 bars BM33 & BM34 (bottom mat drawing) plus 3No B16 bars BM01 (top mat drawing) have been proposed to be drilled and fixed. __ to provide "drill and fix details" RFI-00416 (see attached) has been raised to __. Once this RFI has been responded, it will be attached to this NCR.
| 02SL - Stations (LUL) | Cxxx-NCR-001631 | NCR | WTH Excess cover on Level -7 slab kerbs |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-11-04 | 2014-11-03 16:46 | -1 | 2014-10-21 11:00 | Civil - Civil Engineering General | 1500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | After surveying the top of kerb reinforcement (adjacent to Walls 23 & 24) on the Level -7 slab, due to excess in some areas at the top side of the reinforcement, A393 mesh was laid to bring the cover within the tolerances stated in FAR-CRL-FCD-Cxxx-000974 (less than 1m in size -5/+10mm). As shown in the drawing attached mesh was placed on the majority of the Southern kerb to reduce the cover to 60mm and two isolated spots on the Northern kerb. In addition, on the external (inside) face of the Northern kerb formwork there were some areas of increased cover. B16 diameter bars were installed horizontally on the face of the kerb to reduce cover to within acceptable limits (-5/+10mm).
| 02SL - Stations (LUL) | Cxxx-NCR-001632 | NCR | SMM - Unusable TaM TN1054 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-11-10 | 2014-11-03 10:02 | -7 | 2014-10-21 14:28 | Geotechnical Engineering - Compensation Grouting | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | During maintenance works in TaM TN1054 using the rostor (high pressure pump) to wash out this TAM, the rostor line has become stuck. To date it has been unrecoverable. The result is that this TAM has become unusable for grouting works.
| 02SL - Stations (LUL) | Cxxx-NCR-001633 | NCR | SCL - Total suspended solids testing during depressurisation |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-12-04 | 2014-12-01 16:47 | -3 | 2014-10-22 13:20 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | KT22.3301 e) states that the measurement of Total Suspended Solids (TSS) contained within the water discharged from sub-surface levels must be taken daily with the total TSS content not exceeding 2.5ppm. have not recorded this information in accordance with the specification and an initial water sample has shown that the 2.5ppm limit has been exceeded resulting in non – conformance.
| 02SL - Stations (LUL) | Cxxx-NCR-001634 | NCR | WTH SHW2 Level -7 Slab Construction Drawings |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-11-05 | 2014-10-30 16:15 | -6 | 2014-10-22 15:45 | Structural Engineering - Concrete Member | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | WTH Level -7 Track Slab constructed with some of the drawings/bending schedules at ‘P’ revision, prior to issue and acceptance of ‘C’ revision documents, as required by clause 7.7.8.2 of the works information. It should be noted that RC drawings/schedules for bottom RC mat were at ‘C’ revision, and __ installation drawings had been accepted via Cxxx-FCD-001426. Concrete pours for this area were carried out on 16/10/2014 (track slab) and 18/10/2014 (track kerb). The following drawings and bar bending schedules were at ‘P’ revision at this time of the pour: Cxxx--P-DDA-M123_7-75211 (P05) Western Entrance, Platform Level -6, Public Health Services, Drainage & Cold Water Services Cxxx-ATK-S-DWG-M123_8-50126 (P08) Western Entrance, Rectangular Shaft (SH-W2), Level -7, RC Details of Slab - Top Reinforcement (Sheet 2 of 2) Cxxx-ATK-S-TSC-M123_8-50126 (P08) Western Entrance, Rectangular Shaft (SH-W2), Level -7, RC Details of Slab - Top Reinforcement (Sheet 2 of 2) Cxxx-ATK-S-DWG-M123_Z-50637 (P04) Western Entrance, Rectangular Shaft (SH-W2) Internal Wall Reinforcement Detail, Level -6 to Level -4, (Sheet 5 of 6) Cxxx-ATK-S-TSC-M123_Z-50637 (P04) Western Entrance, Rectangular Shaft (SH-W2) Internal Wall Reinforcement Detail, Level -6 to Level -4, (Sheet 5 of 6) -__
| 02SL - Stations (LUL) | Cxxx-NCR-001635 | NCR | SCL – Failure of Rolling Mean of Core Strengths in August and September 2014 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-11-10 | 2014-11-10 15:19 | 0 | 2014-10-23 11:39 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | For samples FAR597, FAR 598 and FAR 602, the rolling mean of the previous 15 results is less than the target strength based on the standard deviation of the previous 15 results as per Table 13 in EN 14487-1:2005.
| 02SL - Stations (LUL) | Cxxx-NCR-001636 | NCR | ETH SB Level L-2 Internal Wall W29 - missing starter bars |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-11-11 | 2014-11-10 19:21 | -1 | 2014-10-23 15:40 | Civil - Civil Engineering General | 2000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Due to rebar congestion in the Level L-2 slab in the South Basement at the interface between W20 and W29, not all wall starter bars for internal wall W29 could be installed. Instead of 142 couplers only 136 couplers could be installed.
| 02SL - Stations (LUL) | Cxxx-NCR-001638 | NCR | Out of specification heave at Moorgate Shaft 2 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-11-13 | 2014-11-12 09:57 | -1 | 2014-10-23 17:35 | Geotechnical Engineering - Compensation Grouting | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | A compensation grouting episode (Cxxx-GEO-S-11903-PoJM2-01005) was carried out on 28/09/2014 from Moorgate 2 Shaft to mitigate settlements caused by Westbound Cxxx TBM tunneling works and to prepare the buildings for anticipated movements from Platform Tunnel East Enlargement SCL tunneling works. The grouting proposal was carried out and generated 5.5mm on one __ and 6mm on a second __ as measured by daily readings of these instruments. The grouting proposal had been reviewed by CRL and Cxxx prior to starting.
| 02SL - Stations (LUL) | Cxxx-NCR-001639 | NCR | WTH - Level -2 slab - I1C - Cast in scaffold tube |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-11-25 | 2014-11-25 11:30 | 0 | 2014-10-26 17:39 | Civil - Structural Engineering | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | A scaffold tube was left on the inside of the shuttering for I1C during concrete operations, resulting in the tube being cast in. See attached phot and location sketch.
| 02SL - Stations (LUL) | Cxxx-NCR-001640 | NCR | WTH - Level -2 slab - I1C - Gap underneath timber shuttering and sheet pile |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-11-11 | 2014-11-11 08:43 | 0 | 2014-10-28 11:48 | Civil - Civil Engineering General | 2000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On completion of part of the level -1 base slab, I1C, a gap was found under the timber shutter installed against the sheet pile. The concrete has passed the line of the slab therefore all structural requirements have been met. The incomplete area is extra tolerance for sheet pile installation, a small area between the slab and waterproofing which has not been filled. This will form the underside of Level -1 slab to the north. Dimensions 165mm wide with a largest depth of 135mm. Photos attached.
| 02SL - Stations (LUL) | Cxxx-NCR-001641 | NCR | WTH-SHW2-Pour W10- Concrete Cubes storage conditions |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-12-03 | 2014-11-26 13:15 | -7 | 2014-10-28 10:52 | Structural Engineering - Testing | 500 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper storage of material | Completed |  | Following a Surveillance on __ for cube making procedures, the cube specimens done for wall 10 on the SHW2, were found being stored outside the lab containers with no temperature recorded devices available to control the storage temperature.This is a finding against BS-EN-12390-2 Clause 5.5 Curing of test specimens : “5.5.1 Leave the test specimens in the mould for at least 16 hours, but not longer than 3 days, protected against shock, vibration and dehydration at a temperature of (20 ±5) °C (or (25 ±5) °C in hot climates).
| 02SL - Stations (LUL) | Cxxx-NCR-001643 | NCR | WTH - Level -1 - Slab I1c - shutter failure |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-02-06 | 2015-02-04 11:16 | -2 | 2014-10-31 16:31 | Civil - Structural Engineering | 2000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | During the pour of Slab I1c on Level -1 WTH, one of the cast-in 20mm dywidag anchor bars restraining an A-Frame single sided shutter on the east face of the pour moved approximately 100mm. The shutter stopped moving and was strengthened during the pour. However, there is now a step in the concrete face of the wall which reaches a maximum dimension of 100mm at its base. Please refer to attached site photo and location sketch.
| 02SL - Stations (LUL) | Cxxx-NCR-001644 | NCR | ETH - Trap Shaft - ESS1 midlanding couplers cast wrong |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-11-21 | 2014-11-19 14:27 | -2 | 2014-10-27 04:39 | Civil - Civil Engineering General | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Personnel Error - Other human error | Completed |  | West mid-landing couplers for ESS1 stairs in wall 1 at level -3 and -4 were cast wrong due to an error in setting out. Drawing Cxxx-SWN-S-DDL-M123_Z-32001 (main landing) was used instead of Cxxx-SWN-S-DDL-M123_Z-32006 (mid landing). Please find attached sketch (SK-THM-NCR1644-01) for clarity.
| 02SL - Stations (LUL) | Cxxx-NCR-001645 | NCR | WTH SHW2 missing 4no couplers in wall 7 to connect to wall 24 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-11-04 | 2014-11-03 16:37 | -1 | 2014-10-28 15:20 | Civil - Civil Engineering General | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | 4no B25 coupled bars (BMK 73) bars are missing in wall 7 to connect to wall 24. (See attached sketch)
| 02SL - Stations (LUL) | Cxxx-NCR-001648 | NCR | WTH - Level -2 slab - Internal walls 31 35/36 - Concrete placement |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-11-25 | 2014-11-24 11:32 | -1 | 2014-10-31 18:05 | Civil - Civil Engineering General | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | Two of the concrete loads used on the WTH level -2 slab, internal walls 35 and 36, were placed outside the limits of the specification, namely KF10.3203 h). KF10.3203 h) states that fresh concrete shall not be placed against existing fresh in-situ concrete which has been in position for more than sixty minutes. Concrete load with ticket number 68213219 was placed 77 minutes after the previous load and concrete load with ticket number 68215406 80 was placed 80 minutes after the previous load. Similar NCR has been written for pours I2a (NCR 001384) and I2b (NCR-001419).
| 02SL - Stations (LUL) | Cxxx-NCR-001649 | NCR | SCL - Cores Crushed Late during August and September |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-11-17 | 2014-11-04 13:01 | -13 | 2014-10-31 11:28 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | The following cores have been crushed later than that which is required: FAR 565 - 28 Day Cores crushed at 36 Days FAR 569 - 28 Day Cores crushed at 29 Days FAR 589 - 1 Day Core crushed at 4 Days FAR 603 - 28 Day Cores crushed at 29 Days FAR 625 - 1 Day Cores crushed at 7 Days FAR 634 - 1 Day Cores missed
| 02SL - Stations (LUL) | Cxxx-NCR-001650 | NCR | SCL - On site Aggregate Gradings Missed in July 2014 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-11-21 | 2014-11-19 16:22 | -2 | 2014-11-03 10:07 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Between December 2013 and September 2014, a weekly grading for Marine Sand and Limestone was missed for the week ending 20/07/14. Note: All other gradings during this ten month period were taken weekly.
| 02SL - Stations (LUL) | Cxxx-NCR-001651 | NCR | SCL - Minimum concrete thickness not achieved in primary lining (PTE CH119-120 bench) |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-12-11 | 2014-11-23 13:21 | -18 | 2014-11-10 16:38 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | the lining in PTE between CH 119 - 120 was found not to have achieved the minimum lining thickness required for primary lining Cores showed 200mm of SCL instead of the required 400mm
| 02SL - Stations (LUL) | Cxxx-NCR-001653 | NCR | 91-93 Charterhouse Monitoring |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-11-21 | 2014-11-12 15:20 | -9 | 2014-11-03 15:17 | Surveying - Instrumentation and Monitoring | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | There are currently prisms and sockets on the facade of 91-93 Charterhouse Street that will not be read as per the sepcification which states daily during SCL Excavation.
| 02SL - Stations (LUL) | Cxxx-NCR-001654 | NCR | WTH - Level -1 - Slab I1c connection to 600mm suspended slab - Bottom mat reduced cover |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-12-04 | 2014-11-26 08:39 | -8 | 2014-11-04 18:49 | Civil - Structural Engineering | 2000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Personnel Error - Other human error | Completed |  | WTH – Level -1 – RC suspended slab The 600mm think suspended slab being currently built at Level -1 WTH anchors to the 3.45m thick OSD core slab. The OSD slab was previously cast. At locations A and B indicated in sketch attached, 32mm diameter couplers, cast into the OSD core slab to provide anchorage for the bottom steel of the suspended slab (BM C104), were incorrectly installed. The couplers were installed too low.
| 02SL - Stations (LUL) | Cxxx-NCR-001655 | NCR | ETH South Basement L-3 to L-2 Sloping Slab Concrete Strength |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-01-23 | 2015-01-12 07:36 | -11 | 2014-11-19 12:46 | Civil - Civil Engineering General | 1500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | After crushing cubes for the South Basement sloping Slab between L-3 and L-2 pour 3 (see section attached) it was found that the compressive strength did not reach the required strength as per Cxxx-SWN-C-RSP-M123-00004, Table KF10-01, F3 (C40/50) concrete (Cxxx--C-LRC-M123-50145) with 70% GGBS.
| 02SL - Stations (LUL) | Cxxx-NCR-001656 | NCR | SCL - Primary lining preparation (PTE) |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2014-11-24 | 2014-11-19 14:58 | -5 | 2014-11-06 11:47 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | During the pre-regulating inspection of PTE, a small section of primary lining (8 o'clock, TM120 to 125) was found to contain a layer of muck behind a thin layer of primary lining.
| 02SL - Stations (LUL) | Cxxx-NCR-001657 | NCR | ETH South Basement Level -1 Slab Cracks |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-01-23 | 2015-01-14 15:33 | -9 | 2014-11-24 12:47 | Civil - Civil Engineering General | 1000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | Following an investigation into the South basement Level -1 Pour 1 cracks the following items were found to be non-compliant: 1. Clause KF10.3225 a) & b) implies that a check should have been made to ensure that the concrete had gained sufficient concrete strength, cubes were broken but the calculations for self-weight and live load was carried after the false-work was struck. 2. KF10-08 was used for the striking time, this table applies to OPC (Ordinary Portland cement) concrete and the concrete used was a GGBS blend mix. 3. Clause KF10.3225 states that cubes stored under conditions that simulate field conditions should be used for in-situ strength; used cubes stored under laboratory conditions to determine the strength. 4. Back-propping was used for additional live loads and this was confirmed in writing to be sufficient for the extra loads. This was not captured in a Short Notice change to be approved by CRL. It must be noted that submitted an RFI (Cxxx-RFI-002219) to Cxxx requesting clarification on the striking period and the subsequent answer was not clear. The cracks remain under 0.3mm therefore are within specification.
| 02SL - Stations (LUL) | Cxxx-NCR-001658 | NCR | ETH - Concrete Cold Weather and Repair procedures not current at the time of a CRL planned surveillance |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2015-01-19 | 2015-01-19 16:00 | 0 | 2014-11-07 08:29 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | During a planned Crossrail surveillance of reinforced concrete works dated 17th October 2014 a review of the ‘Cold Weather Working Procedure’, Cxxx--O4-GPD-M123-50007 Rev 1 Decal Code 2, and ‘Concrete Repair Procedure’, Cxxx--C-STP-M123-50227 Rev 4 Decal Code 2 was carried out for acceptability and content. Following review, the cold weather and repair procedures were noted as being at a Code 2 Decal since October 2013 and August 2014 respectively, therefore not current. Works Information Vol 2B Part 14.7 Document Control and Management states “The Contractor shall follow the Project Manager’s document management procedures”. Under Crossrail Technical Directorate - Document Management Procedure Rev 2, CRL1-XRL-Z3-GPD-CR001-50001 clause 7.3 a Code 2 Decal stands for “Not Accepted. Revise and Resubmit. Work may proceed subject to the incorporation of changes indicated.” This NCR was raised to ensure the aforementioned documents are updated in line with the documented comments from review. It must be noted that the use of the cold weather procedure will be extremely prevalent as the works start to enter the colder winter months.
| 02SL - Stations (LUL) | Cxxx-NCR-001659 | NCR | ETH: Trapezoidal Shaft & South Basement - __ Failure to comply with specification KF10.2204 Strength Testing for Concrete Mixes |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2015-01-29 | 2015-01-22 13:41 | -7 | 2014-11-12 11:24 | Civil - Civil Engineering General | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Supervision - Other | Completed |  | __ have failed to provided adecuate strength testing for the Concrete works at the ETH (Trapezoidal Shaft & South Basement). Non conformance for no crushing at least two set of samples for testing at 28 days and provide analysis of the results to demonstrate compliance as per the Cxxx Farringdon Station - Civil & Structural Specification, BS and BS EN standards. __ is a UKAS certified company and likewise they are certified to undertake the compressive strength cubes test The following areas at the Trapezoidal Shaft & South Basement were found not to be compliant South Basement: Capping Beam Level 0 / F3 Concrete Mix Slab level -2 (Pour 1A and 1B) / F3 Concrete Mix Lining walls: • W21B / W2 Concrete Mix • W23A / W2 Concrete Mix • W21G / W2 Concrete Mix • W21H / W2 Concrete Mix • W21F / W2 Concrete Mix • W23A / W2 Concrete Mix Trapeziodal Shaft: Slab level -2 / SL2 Concrete Mix Slab level -3 / SL2 Concrete Mix Capping Beam -2 South: • H / F3 (S3) Concrete Mix • H2 / F3 (S3) Concrete Mix - Lower level • H2 Upper / F3 (S3) Concrete Mix Capping Beam -2 East: • J / F3 (S3) Concrete Mix • I Upper / F3 (S3) Concrete Mix
| 02SL - Stations (LUL) | Cxxx-NCR-001660 | NCR | WTH - Level -2 - Wall 33 north pour - time between concrete loads |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-11-28 | 2014-11-24 11:51 | -4 | 2014-11-12 18:45 | Civil - Structural Engineering | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | During concreting of Wall 33 north pour (40m3), one of the loads was placed 80 mins after the previous one, contravening clause KF10.3203 h) of the Civil and Structural Spec (please see attached concrete site control sheet) The pour could have been stopped half way, before this load was placed, but the concrete was assessed as being in good working condition and as such, the load was discharged.
| 02SL - Stations (LUL) | Cxxx-NCR-001661 | NCR | WTH SH-W2 Level -6 slab voids incorrectly positioned |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-12-11 | 2014-12-11 14:16 | 0 | 2014-11-13 11:44 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Two voids on the Level -6 slab (North) were incorrectly set out and cast. The two voids are adjacent to Wall 24 and in the worst instance 310mm too far east (see attached Cxxx-NCR-001661 Sh-W2 Level -6 Voids As-Built). Having discussed with __ in the MEP Co-ordination meeting (12/11/14) the holes appear to be redundant and therefore propose to use-as-is. Sketch Cxxx-NCR-001661 MEP Service Drawing (attached) showing the 3D model of the slab shows no services going through the voids.
| 02SL - Stations (LUL) | Cxxx-NCR-001662 | NCR | ETH - SB L-2 W23 lining wall exccess concrete cover |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-11-28 | 2014-11-27 13:27 | -1 | 2014-11-14 11:33 | Civil - Civil Engineering General | 1500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The starter bars for lining wall W23 at Level L-2 north of GL 3.5 have been cast in in the wrong position resulting in an excess concrete cover of the lining wall of 80mm to 100mm. Unfortunately the issue does not occur localy but over a longer stretch of the work. proposes to install additional B20 bars vertical bars at 150 center over the first 2m of lining wall (between 106.418 mATD and 108.418 mATD) to the correct cover. Above 108.418 the reinforcement will be pushed into the original design position resulting into 50mm concrete cover. Please confirm whether the proposal is acceptable or detail additional rebar requirements (i.e. sheets of A393 mesh)
| 02SL - Stations (LUL) | Cxxx-NCR-001663 | NCR | WTH - Level -2 slab - Internal walls 31 32 33 35/36 - Honeycombing |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-12-19 | 2014-12-19 11:50 | 0 | 2014-11-17 17:08 | Civil - Civil Engineering General | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Following the striking of shutters for the internal walls for level -2, small areas of honeycombing have been identified along the construction joint between the walls and the level -2 slab. Areas affected are identified in the attached photos.
| 02SL - Stations (LUL) | Cxxx-NCR-001664 | NCR | ETH L-7 - Use of Material without MCR |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2014-12-02 | 2014-11-28 13:28 | -4 | 2014-11-18 15:03 | Electrical - Electrical Engineering General | 0 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Failure to follow status stamp | Completed |  | During the installation of the earth mat connections at ETH L-7, the contractor used a conductive paste on the clamps without an MCR in place.
| 02SL - Stations (LUL) | Cxxx-NCR-001665 | NCR | WTH SHW2 Level -8 Earthing bars |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-12-22 | 2014-12-18 13:12 | -4 | 2014-11-24 09:16 | Civil - Civil Engineering General | 2000 |  | Planning | Repair | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | 2 No. earthing bars protruding out of Level -8 Slab cast in June 2014 were cut flush with top of concrete while installing shutters for wall 7 poured in June 2014. 2 No. earthing bars protruding out of Level -8 Slab cast in June 2014 were cut flush with top of concrete while installing shutters for wall 15/20/21 poured in Sept 2014.
| 02SL - Stations (LUL) | Cxxx-NCR-001666 | NCR | WTH - Level -2 slab - Not achieving F2 finish on voids inside I1C pour and internal walls walls on level -2 slab |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-12-19 | 2014-12-17 17:26 | -2 | 2014-11-19 17:47 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The level -1 slab consisted of a large 3.5m high pour named I1C. I1C contained large voids to be used as a lift pit. Following the striking of shutters for the voids a poor finish has been identified along the void walls. The North and South face of the largest void have been noted as needing to be repaired to reach an F2 finish. Additional repairs will be needed on the top 300mm of the East face and the south side of the west face. In addition small blow holes have been noted along the internal walls located on the level -2 slab. Please see attached sketches and photos for location.
| 02SL - Stations (LUL) | Cxxx-NCR-001667 | NCR | WTH - Level -2 slab - Missing chamfers on voids inside I1C pour and Internal walls 32 and 35/36 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-12-05 | 2014-12-01 08:43 | -4 | 2014-11-19 17:06 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Slab I1c on the WTH, which forms part of the level -1 slab, contains large voids for a lift pit. Internal walls 32 and 35/36 are located on the level -2 slab and contain box outs for services. During installation of the formwork for these voids and box outs, chamfers were not fitted on the exposed corners. A chamfer was also not installed on the North West corner of wall 36. The attached sketch and photos show the location of the exposed corners. The attached sketch and photos show the location of the exposed corner.
| 02SL - Stations (LUL) | Cxxx-NCR-001668 | NCR | SCL - No ITP for fabrication of KERN shutter |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-12-19 | 2014-12-11 16:03 | -8 | 2014-11-27 14:58 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | No CRL accepted ITP for the fabrication of the Secondary lining shutter.
| 02SL - Stations (LUL) | Cxxx-NCR-001669 | NCR | SCL - No ITP in place for fixing of invert shutters |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-12-20 | 2014-11-28 10:49 | -22 | 2014-11-19 14:47 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | No ITP in place prior to fixing the shutter for the invert concrete
| 02SL - Stations (LUL) | Cxxx-NCR-001671 | NCR | SCL - poor quality joints in waterbar (PTE TM12 to 25) |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2014-12-04 | 2014-12-03 15:31 | -1 | 2014-11-20 11:26 | Tunnelling - Linings - Sprayed Concrete | 4500 |  | Testing and Commissioning | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 3no. (of 6) t-piece junctions of the waterbar were observed to have defective joints as part of the hold point inspection of the invert waterproofing trial (between TM 12 and 25). These joints had been heat welded in accordance with manufacturer's instructions and were easily broken with very little pressure (see attached photo of joint at TM13 RHS).
| 02SL - Stations (LUL) | Cxxx-NCR-001672 | NCR | ETH - W21 Excess cover in lining wall |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-12-19 | 2014-12-17 12:54 | -2 | 2014-11-24 15:58 | Civil - Civil Engineering General | 1500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The starter bars for lining wall W21 along Capping Beam K North of GL 5.5 have been cast in in the wrong position resulting in excess concrete cover to the lining wall of 70mm to 85mm.
| 02SL - Stations (LUL) | Cxxx-NCR-001673 | NCR | ETH - L-6 W1B not poured to full height |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-12-08 | 2014-12-02 09:43 | -6 | 2014-11-24 15:36 | Civil - Civil Engineering General | 1000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | At Level -6 on Wall 1 the top lift pour of the western section of wall was poured short and did not reach the full height of the wall. This has left a small tapered section from 0mm to 90mm over a 2.8m length at the top of the wall. Please see attached photos of the area.
| 02SL - Stations (LUL) | Cxxx-NCR-001674 | NCR | SCL - Poor core quality in PTE TH557 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-12-25 | 2014-12-16 09:09 | -9 | 2014-11-24 16:46 | Tunnelling - Linings - Sprayed Concrete | 2000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Core Quality in TH557 failed to reach the >2.5 mean grade.
| 02SL - Stations (LUL) | Cxxx-NCR-001675 | NCR | ETH Documentation not compliant with reinforced concrete ITP (Cxxx-BFK-C-ITP-M123-50009) |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-02-03 | 2015-01-29 17:00 | -5 | 2014-12-16 13:46 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | Following the surveillance Cxxx--O4-XCS-M123-50068, it was found that the concrete testing company listed in the ITP was not the company that carries out the concrete testing.
| 02SL - Stations (LUL) | Cxxx-NCR-001676 | NCR | ETH Non compliance with specified ITP requirements - Prepour Inspections |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-01-13 | 2014-12-24 14:32 | -20 | 2014-12-16 13:47 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not trained for the work being performed | Completed |  | Following the surveillance it was found that the kicker and piles were not cleaned thoroughly before installing the hydrophilic strip. This was a hold point in the ITP.
| 02SL - Stations (LUL) | Cxxx-NCR-001677 | NCR | ETH Non conformance with slump values set out in ITP |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-02-03 | 2015-01-29 16:57 | -5 | 2014-12-16 13:48 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | The slump for Wall 22 Pour D on the 01/07/2014 was 160mm, which is outside of the parameters of 100-150mm as specified in Item 17.1 of the reinforced concrete ITP (Cxxx--C-ITP-M123-50009).
| 02SL - Stations (LUL) | Cxxx-NCR-001678 | NCR | WTH SHW3 Lining walls 1st lift concrete pour |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-01-23 | 2015-01-22 12:02 | -1 | 2014-11-26 16:30 | Structural Engineering - Concrete Member | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Clause KF10.3203h of the CRL specification states that fresh concrete will not be placed against existing fresh concrete which has been in place for more than 60 minutes. During the pouring of the 1st lift of the lining walls in SHW3 this was exceeded by 18 minutes.
| 02SL - Stations (LUL) | Cxxx-NCR-001679 | NCR | WTH -1 Suspended slab excess top cover in SE corner of slab |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-12-05 | 2014-12-03 13:09 | -2 | 2014-11-26 17:33 | Structural Engineering - Reinforcement | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Due to an accumulation of tolerances (falsework level, spacer blocks, deformed bar sizes) the top cover in 2 areas on the East half of the -1 Suspended slab is 12mm greater than the tolerance value. This gives a total top cover of 70mm in the worst case.
| 02SL - Stations (LUL) | Cxxx-NCR-001682 | NCR | WTH - Level -1 OSD Core Slab I1c - Concrete Strength at 28 days not achieved |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-03-21 | 2015-03-12 17:14 | -9 | 2014-12-02 16:16 | Civil - Civil Engineering General | 5000 |  | Material | Use As-Is | 3 (3-6k) | Complete | Material/Preservation Problems - Other | Completed |  | WTH level -1 concrete slab I1c (location sketch attached) did not achieve 28 day cube strength of 50N/mm2 as per Cxxx-SWN-C-RSP-M123-00004 Table KF10-01 and has not been fully compliant with BS EN 206:2013 criteria 1 and 2. These values where however achieved at 90 days. See attached results as well as batch records. Concrete mix used is SL6.2 (MCR-50398) I1c slab was cast on the 18/10/14. As per BS EN 206:2013, no results have been disregarded due the difference between the two 28 day cube strengths divided by their mean as it is less than 15%.
| 02SL - Stations (LUL) | Cxxx-NCR-001683 | NCR | SCL - In Situ Secondary Lining Concrete (BFK 29) Core Temperatures |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-01-16 | 2015-01-15 15:10 | -1 | 2014-12-08 12:32 | Tunnelling - Linings - In-situ Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | have poured the first of the secondary lining invert concrete. The first invert concrete pour was 850mm thick and reached a maximum temperature of 65.28 degrees based on thermocouple data. KF10.1302 states that "placed concrete during its early age heat cycle shall not exceed 60°C" when thicknesses exceed 500mm. In the case where thickness is less than 500mm, the maximum permissible temperature is 70°C.
| 02SL - Stations (LUL) | Cxxx-NCR-001684 | NCR | SMM - Incorrect Baseline for Shallow & Deep Datums |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-12-17 | 2014-12-12 12:32 | -5 | 2014-12-03 12:42 | Surveying - Instrumentation and Monitoring | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The baseline for all Shallow & Deep Datums was carried out by taking 6 readings spread evenly over at least 1 month. Drawing Cxxx-OVE-C2-DDJ-CR001_Z-31531 requires shallow datums to have baseline readings taken every 2 weeks for at least 3 months.
| 02SL - Stations (LUL) | Cxxx-NCR-001685 | NCR | SCL: Installing spiles without approved MCR |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2014-12-24 | 2014-12-17 16:41 | -7 | 2014-12-03 16:12 | Tunnelling - Tunnelling General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | GRP spiles have been installed without an accepted MCR
| 02SL - Stations (LUL) | Cxxx-NCR-001686 | NCR | Grouting within the exclusion zone |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-12-22 | 2014-12-16 09:02 | -6 | 2014-12-03 17:28 | Geotechnical Engineering - Compensation Grouting | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | As per clause 3.2.5.7 in the Cxxx Specification For Control of Ground Movements 'Concurrent grouting injections above SCL tunnels shall initially be scheduled outside the exclusion zone' Compensation grouting was done 1 metre insdie the exclusion zone for the safestop of PTE in order to avoid building damage due to the heave achieved from the chemical grouting and the settlements observed from CP6.
| 02SL - Stations (LUL) | Cxxx-NCR-001687 | NCR | WTH - Level -2 slab - Pour I1c - Incorrect location of recess |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-01-16 | 2015-01-13 11:13 | -3 | 2014-12-04 13:26 | Civil - Civil Engineering General | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Other human error | Completed |  | The level -1 slab within the west ticket hall contains a 60mm recess for cable trays. Slab I1C forms part of this slab. The recess within this area of the slab has been cast out of line and at the incorrect level. The south end of the recess on I1c was cast 25mm west of the correct line (increasing the recess width). Additionally, for a section 1m x 5m, the concrete outside of the recess is 30mm low (should be +106.430mAOD). The level within the recess is correct.
| 02SL - Stations (LUL) | Cxxx-NCR-001688 | NCR | WTH SH-W2: Post-fixed u-bars and verticals for wall 11 (level -6) |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-12-19 | 2014-12-16 08:57 | -3 | 2014-12-05 13:27 | Structural Engineering - Reinforcement | 750 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Personnel Error - Other human error | Completed |  | Four u-bars (BM 88 from drawing Cxxx-ATK-S-DWG-M123_Z-50633) were required to be cast into the Level-6 slab in wall 11 which would help form a void in the reinforcement. These bars were not installed due to engineers omission. On the same wall, four couplers have been installed out of position which meant 2No. BM 71 and 2No. BM 57 (BMs referenced from the above drawing) at the South end of the wall had insufficient cover when we installed them. Bars shown on attached sketch (Cxxx-NCR-001688 Wall 11 Drilled Bars). At the North, also on Wall 11, there were also 2No. BM 71 and 2No. BM 57 that had to be re-drilled as the couplers cast into the Level -6 slab to house them could not be located.
| 02SL - Stations (LUL) | Cxxx-NCR-001690 | NCR | WTH SH-W2 Leaks to Easternmost section of Wall 6 (Level -8 to -6) |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-04-24 | 2015-04-24 10:37 | 0 | 2014-12-05 18:37 | Civil - Civil Engineering General | 4000 |  | System Defect | Repair | 3 (3-6k) | Complete | Material/Preservation Problems - Not Defined | Completed |  | Water ingress has been observed at the Easternmost section of Wall 6 (between Walls 7 & 11 - see location sketch attached). This is occurring at the construction joint between the first and second lifts and the joint between Wall 6 and the underside of the Level -6 slab (see attached photographs). consulted their waterproofing supplier who has been to site to inspect the affected area. They have recommended using Betec Flex (Cxxx--C-LRC-M123-50222). Over the joint between the 1st and 2nd lift, will paint a 400mm band centrally over the length of the joint and at the wall/soffit connection, Betec Band 150 is used (covered under the same MCR) and a 200mm strip is painted on the horizontal face and a 200mm strip painted on the vertical face. A letter from __ is attached confirming this solution along with an email with further justification for use of the Betec Flex rather than the existing re-injectable grout tubes.
| 02SL - Stations (LUL) | Cxxx-NCR-001691 | NCR | WTH SH-W2 Honeycombing to Level -6 slab |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-01-30 | 2015-01-30 11:56 | 0 | 2014-12-05 14:04 | Civil - Civil Engineering General | 3000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | On striking the falsework to the Level -6 slab soffit two areas of honeycombing were discovered in the north-east corner of the shaft, between Walls 11 and 7. Attached sketch shows location of honeycombing. The worst affected area is approximately 1m long and 500mm wide and is located in the area shown on the attached sketch. Second area is approximately 500mm x 500mm. will repair the affected area based on the recommendations of a specialist sub-contractor, FOSROC.
| 02SL - Stations (LUL) | Cxxx-NCR-001692 | NCR | SCL - Failed waterproofing inspection (Invert pour #3 - TM47 to 72) |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2014-12-22 | 2014-12-11 09:51 | -11 | 2014-12-08 11:59 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | A waterproofing insepction was requested on Saturday 6th of Decmeber '14. Upon inspection, 6no. of the 8no. butt welds with the prefabricated junction T-pieces were found to be defective - the welded connection between the fins of the waterbar could be separated by hand with light pressure.
| 02SL - Stations (LUL) | Cxxx-NCR-001693 | NCR | SCL - Invert Concrete Pour 1 Curing Started Late |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-12-22 | 2014-12-17 11:39 | -5 | 2014-12-08 17:55 | Tunnelling - Linings - In-situ Concrete | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Not Defined | Completed |  | finished pouring the first secondary lining invert at 7.30pm but did not cover the pour with damp hessian until 2am. ITP Cxxx--C4-ITP-M123-50060 states that concrete pour should be covered 4-5 hours after the pour is completed.
| 02SL - Stations (LUL) | Cxxx-NCR-001694 | NCR | SCL - Crack at TM5 in CP4 crown found during hold point inspection |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2014-12-22 | 2014-12-17 11:43 | -5 | 2014-12-08 12:46 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Inspection points not adequate | Completed |  | During the hold point inspection of CP4 crown, a crack was found at TM5 (crown clock position 1 to 3 facing PTE). This crack had not been recorded on the crack log and therefore, it's width and stability could not be confirmed.
| 02SL - Stations (LUL) | Cxxx-NCR-001695 | NCR | ETH - Lining Wall W23 north of GL3.5 too wide |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-01-30 | 2015-01-23 07:47 | -7 | 2014-12-09 16:56 | Civil - Civil Engineering General | 1500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The position of the reinforcement of the wall was determined by the wall starter bars installed in the L-2 slab. Due to rebar congestion, the starter bars were installed with access cover to the front face of the wall. Because of the excess cover and the width of the reinforcement, the kicker of the lining wall W23 north of GL 3.5 lift 2 had to be made 100mm wider to the back of the wall compared to the design width of the wall in order to provide sufficient concrete cover to the reinforcement. Please find attached photos in this regards. proposes to keep the wall with the current alignment in order to provide sufficient cover to the reinforcement. This will only affect the back of the wall, the front of the lining wall is as per original design.
| 02SL - Stations (LUL) | Cxxx-NCR-001696 | NCR | ETH- ITP acceptance parameters and verifying documents not listed correctly at the time of surveillance |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2015-02-28 | 2015-02-27 15:51 | -1 | 2014-12-10 12:47 | Electrical - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | During a planned Crossrail surveillance of the earthing system installation dated 13th of November 2014 a review of the ITP (Cxxx--C-ITP-M123-50009-Rev 6, Code-1) was carried out. The review highlighted that the acceptance parameters for inspection number 14.3 and 14.6 were either inadequate or incorrect. It was also noted that the verifying document for inspection 14.6 carried the wrong document number. The Works Information Volume 2B Rev.2, part 20.8 states: “accepted ITPs shall stipulate the necessary level and frequency of test and inspections for each aspect of the works and also stipulate: • item(s) being inspected and tested; • the inspection and test activity; • acceptance criteria • certification/documentation/records to be generated in support of the inspection and test activities.” This NCR was raised to ensure that the ITP is updated to reflect the correct acceptance parameters and detail the correct verifying documents.
| 02SL - Stations (LUL) | Cxxx-NCR-001697 | NCR | ETH-Soil resistivity test results not provided with the correct unit of measure and therefore could not be determined as compliant |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2015-02-28 | 2015-02-10 11:49 | -18 | 2014-12-10 12:54 | Electrical - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | During a planned Crossrail surveillance of the earthing system installation dated 13th of November 2014 a review of the soil resistivity test results was undertaken. It was found that the unit of measure for the results was incorrectly listed as Ohms, rather than Ohm meters thus the result could not be verified as compliant as required by Crossrail’s Material and Workmanship specifications: JW51 Earthing and Bonding. JW51.1206 details this specific requirement for soil resistivity test results to be given in Ohm meters.
| 02SL - Stations (LUL) | Cxxx-NCR-001698 | NCR | SHW3 Lining Wall Concrete Slump Flow test tolerances |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-01-21 | 2015-01-15 13:10 | -6 | 2014-12-11 09:29 | Structural Engineering - Concrete Member | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | When pouring the 1st and 2nd lifts of the lining walls within SHW3, performed slump flow tests in accordance with the approved revision 3.0 of our ITP (Cxxx--C-ITP-M123-50217). This specified a target range of SF2, 660-750mm with a tolerance of +/-50mm. All the wagons were within this range. It has since been established that BS EN 206 (Table 21 P51) states the +/-50mm tolerance, initially thought to be applicable, does not apply when specifying a target slump-flow range for self-compacting concrete. As a result of this, 11 of the 33 wagons for the 1st lift and 13 of the 26 wagons for the second lift would of been classed as SF3 not SF2. Each wagon contains 7 cubic metres of concrete. The MCR states the mix is an SF2, hence the pouring of the 'SF3' wagons represents a non-conformance.
| 02SL - Stations (LUL) | Cxxx-NCR-001699 | NCR | WTH - Use of self-compacting concrete mixes without full initial tests |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-02-06 | 2015-01-15 13:24 | -22 | 2015-01-05 15:55 | Civil - Civil Engineering General | 1500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | Self compacting mixes W1 SCC Ad (MCR- 50423) and W7 SCC (MCR-50416) were used without initial tests carried out as per BS EN 206:2013 A.5 (5). Evidence of viscosity, passing ability and segregation resistance was not provided and included into the relevant MCRs prior to use of this mixes. Both MCRs are nonetheless code 1 documents. W1 SCC Ad was used on the SHW3 lining walls. W7 SCC was used on SHW2 lining wall 8, under and East of the South corbel.
| 02SL - Stations (LUL) | Cxxx-NCR-001700 | NCR | SCL: Failed fin welding for invert waterbar, TM71.755 |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2014-12-30 | 2014-12-16 12:31 | -14 | 2014-12-16 08:51 | Tunnelling - Linings - In-situ Concrete | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Personnel Error - Inadequate work environment | Completed |  | On inspection of the invert waterbar (LHS junction looking in-by - TM71.755), one of the butt welds between the fins of was split by hand with very little pressure.
| 02SL - Stations (LUL) | Cxxx-NCR-001701 | NCR | SCL - Wrong Admixture used in BFK 29 (Secondary Lining) Concrete Bays 1 and 2 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-02-03 | 2015-01-28 09:37 | -6 | 2014-12-16 13:54 | Tunnelling - Linings - In-situ Concrete | 4000 |  | Material | Use As-Is | 3 (3-6k) | Complete | Personnel Error - Other human error | Completed |  | have provided 29 with the wrong admixture in the mix. Viscaflow 1000 has been provided rather than Viscaflow 2000 which is dosed at 4.3 litres per cubic metre of concrete. This affects concrete within bays 1 and 2 cast on the 01/12/14 and 04/12/14 respectively.
| 02SL - Stations (LUL) | Cxxx-NCR-001702 | NCR | ETH - Upper Sloping Slab Misaligned Couplers |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-05-30 | 2015-04-27 16:04 | -33 | 2014-12-16 16:34 | Civil - Civil Engineering General | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The couplers within the capping beam at L-2 for the upper sloping slab have been cast incorrectly. BM09 and BM10 on Drawing Cxxx-ATK-S-DWG-M123_2-50102.
| 02SL - Stations (LUL) | Cxxx-NCR-001703 | NCR | WTH - Temporary Works Design Procedure Non-Compliance |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-02-06 | 2015-01-28 11:10 | -9 | 2014-12-16 17:15 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | There was no paper trial to show that the bolts that were selected for fixing the level -1 falsework props to the -2 slab had been reviewed by the engineering team. The accepted design drawing as per package (Cxxx--C-RGN-M123-51548 Rev 1.0) had specified the design loads required but not specified the bolts. Section 5.2 of the Temporary Works Management Plan (Cxxx--C-STP-M123-50009 Rev. 2.0) refers to on site designs and the need to communicate to the engineering team.
| 02SL - Stations (LUL) | Cxxx-NCR-001704 | NCR | SCL - Non butt weld used onsite to join T-Piece at CH 124.032 PTE invert |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2014-12-31 | 2014-12-19 13:17 | -12 | 2014-12-17 14:59 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | Lap joint was used instead of butt joint to weld T piece into position at CH 124.032 PTE invert
| 02SL - Stations (LUL) | Cxxx-NCR-001705 | NCR | SMM-I&M. Lack of installation of manual monitoring points |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-02-03 | 2015-01-28 13:51 | -6 | 2014-12-19 15:26 | Surveying - Instrumentation and Monitoring | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | Four number __ sockets were not installed by as per the design drawing Cxxx-OVE-C2-DDJ-CR001_Z_39700. This was due to the as found conditions of the building meaning installation was not possible (see attachments showing design locations and obstructions preventing installation). This is in contradiction to Specification for Control of Ground Movements clause 3.1.1.4 "The contractor shall install all instrumentation in accordance with the drawings and the materials and workmanship specifications." As a result of these points not being installed, 3 amber slope trigger breaches (as calculated using data from automatic prisms) between the northern and southern facades of the building were not identified or reported to when the breaches occurred.
| 02SL - Stations (LUL) | Cxxx-NCR-001708 | NCR | ETH-Trap Shaft - Level -6: Slabfolds shear links couplers |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-01-15 | 2015-01-09 16:55 | -6 | 2014-12-20 16:46 | Civil - Civil Engineering General | 7000 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Some shear links couplers were cast in the first pour of L-6 slab folds at 20-40mm higher than the underside of concrete. Photo (1) shows an area where some couplers are set to the correct level and others which need exposing due to being slighty higher.
| 02SL - Stations (LUL) | Cxxx-NCR-001709 | NCR | ETH SB the top of lining wall W19 between L-2 to L-3 out of tolerance |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-01-30 | 2015-01-16 07:47 | -14 | 2014-12-29 13:20 | Civil - Civil Engineering General | 750 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | During the as-built survey of the lining wall W19 L-2 to L-3 it was found that the top of the wall below the capping beam at Level L-2 is out of tolerance. See attached as built survey. Wall W19 (below Upper Escalator Ramp) is supposed to be 800mm offset from GLB' (as per drawing Cxxx-SWN-S-DDD-M123_3-29251 Detail 263) Only the top of the wall W19 below the capping beam is out of tolerance by max 31mm (tolerance +/-20mm). However, the top of wall is flush with the capping beam above. See attached photos of the wall and capping beam. In order not to compromise on the concrete cover to the reinforcement in W19, proposes to use as is.
| 02SL - Stations (LUL) | Cxxx-NCR-001710 | NCR | ETH - Trapezoidal Shaft - Level -7 Wall 11 MEP Opening out of alignment |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-02-11 | 2015-01-29 17:04 | -13 | 2014-12-29 15:41 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | After striking Wall 11 Level -7 Trapezoidal shaft aware that one of the MEP box out was out of alignment. Please see attached survey and photos.
| 02SL - Stations (LUL) | Cxxx-NCR-001711 | NCR | SCL - In Situ Concrete - Possible Bay 5 Cold Joints |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-02-25 | 2015-02-25 10:48 | 0 | 2015-01-05 16:30 | Tunnelling - Linings - In-situ Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Due to a delay between loads in the pouring of concrete for Bay 5 on the 21/12/2014, there is the possibility that a cold joint has formed in the pour.
| 02SL - Stations (LUL) | Cxxx-NCR-001712 | NCR | SCL - Invert Bays 2 to 5 Above Maximum Specification Temperature |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-02-03 | 2015-02-03 10:47 | 0 | 2015-01-06 12:48 | Tunnelling - Linings - In-situ Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | In a similar manner to NCR 001683, invert pours 2 to 5 have reached higher temperatures than allowed within the specification. KF10.1302 states that "placed concrete during its early age heat cycle shall not exceed 60°C" when thicknesses exceed 500mm. In the case where thickness is less than 500mm, the maximum permissible temperature is 70°C. All four invert pours reached up to 67 degrees and were greater than 500mm thick.
| 02SL - Stations (LUL) | Cxxx-NCR-001713 | NCR | ETH Cover on Level -6 North Slabfold |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-01-15 | 2015-01-15 14:40 | 0 | 2015-01-08 10:57 | Civil - Civil Engineering General | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | While fixing the steel for the north slab-fold, it was discovered that there was less cover than specified on the drawing (i.e. less than 45mm). See attached sketch showing cover at different locations across the north slab-fold. The cover on the south slab is within tolerance.
| 02SL - Stations (LUL) | Cxxx-NCR-001714 | NCR | SCL - Cores in December 2014 Missed/Late |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-01-23 | 2015-01-13 09:29 | -10 | 2015-01-07 17:15 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate resources | Completed |  | The following cores for sprayed concrete have either been missed or crushed late during December. PTE TH580 - 28 day core crushed at 29 days VA1 TH35 - 28 Day core crushed at 29 days CH2 TH32 - 1 Day Core Missed PTE B609 - 1 Day Core Missed
| 02SL - Stations (LUL) | Cxxx-NCR-001715 | NCR | ETH Two Storey basement concrete strength not achieved at 28 days in lining walls above sloping slab |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-01-30 | 2015-01-20 07:52 | -10 | 2015-01-08 11:50 | Civil - Civil Engineering General | 1000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | During the construction of Lining Walls W19 & W20 first and second pour, took concrete samples (W2 __) for testing. The results at 28 days (see attached reports from __) are as follows: -Lining wall W19 & W20 first pour: Concrete strength = 47.7 N/mm2 and 47.7 N/mm2 -Lining wall W19 & W20 second pour: Concrete strength = 50.3 N/mm2 and 48.8 N/mm2 According to MCR: Cxxx--C-LRC-M123-50424, W2 __ is a C40/50 concrete mix and therefore the mix must achieve at 28 days a characteristic compressive strength of at least 50 N/mm2
| 02SL - Stations (LUL) | Cxxx-NCR-001716 | NCR | WTH SHW3 Lining Walls honeycombing on North Wall |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-06-11 | 2015-02-05 10:52 | -126 | 2015-01-12 10:52 | Civil - Structural Engineering | 1000 |  | Material | Repair | 4 (0.5-3k) | Complete | Personnel Error - Other human error | Completed |  | There is a small area approximately 1m x 1m of honeycombing on W26 (North wall of the WTH escalator shaft). The attached photographs and marked-up dwg highlight where this area is located.
| 02SL - Stations (LUL) | Cxxx-NCR-001717 | NCR | WTH SHW3 lining walls water ingress |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-07-31 | 2015-07-21 11:27 | -10 | 2015-01-12 11:34 | Structural Engineering - Concrete Member | 7000 |  | Material | Repair | 2 (6-60k) | Complete | Material/Preservation Problems - Not Defined | Completed |  | After pouring Walls 26, 28 & 29 in SHW3 (the North, South & West lining walls of the WTH escalator shaft), water ingress has started occurring at the construction joints between lifts and also at other locations where cracks are present within the walls. have completed a post-pour inspection of all the areas of water ingress in accordance with B1.9.1 of "The ICE Specification for Piles and Embedded Retaining Walls" (SPERW). The report from this is attached. Despite no visible evidence of weeping of water, the damp patches beneath the cracks in the walls indicate that water has come through the cracks and run down the face of the wall, hence the ingress is best described with the definition of "weeping of water" from Section B1.9.1 of SPERW.
| 02SL - Stations (LUL) | Cxxx-NCR-001718 | NCR | SCL - Poor Core Quality CH2 TH32 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-01-30 | 2015-01-20 08:40 | -10 | 2015-01-12 17:11 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Core quality failed to obtain a mean grade of <=2.5 in accordance with core grading procedure Cxxx--O4-GPD-M123-50014
| 02SL - Stations (LUL) | Cxxx-NCR-001719 | NCR | ETH - Lower Sloping Slab Out of Tolerance |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-02-20 | 2015-02-17 14:48 | -3 | 2015-01-13 08:07 | Civil - Civil Engineering General | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | On completion of the as built survey it has been observed that the lower sloping slab is out of tolerance by up to 50mm too low, see attached as-built survey. The area for ventilation in this location has not been reduced and therefore proposes to use as-is.
| 02SL - Stations (LUL) | Cxxx-NCR-001720 | NCR | ETH - Trapezoidal Shaft - Level -5 Soffit Repair above Column C6 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-03-13 | 2015-03-02 17:02 | -11 | 2015-01-18 14:16 | Civil - Civil Engineering General | 2800 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | have identified an area of honeycombing on the soffit of Level -5 above Column C6 East. Photos attached.
| 02SL - Stations (LUL) | Cxxx-NCR-001721 | NCR | WTH SH-W2 Duct tape in Wall 6 (east) pour |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-02-02 | 2015-01-30 10:02 | -3 | 2015-01-19 16:44 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | After inviting the Crossrail Field Engineer to inspect a wall pour, it was found that duct tape had been used to tie the plastic cones to the dummy anchors within the pour. There is no MCR approved for duct tape. __ tape (approved under Cxxx--C-LRC-M123-50216) was wrapped around the duct tape.
| 02SL - Stations (LUL) | Cxxx-NCR-001722 | NCR | WTH - Failure to Sign Structural Concrete Site Control Sheet |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-02-02 | 2015-01-26 11:31 | -7 | 2015-01-19 17:58 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | The Structural Concrete Site Control Sheet, kept as a record of the details of individual loads of ready mixed concrete arriving on site and listed as a deliverable on reinforced concrete ITPs, was on occasion not signed at the end of the pour by the Engineer in attendance.
| 02SL - Stations (LUL) | Cxxx-NCR-001723 | NCR | SCL - Crack inducer in pour 2 PTE (CH38.955) wsa placed stagered |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-03-13 | 2015-03-16 11:45 | 3 | 2015-01-22 14:16 | Tunnelling - Linings - Sprayed Concrete | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | The crack inducer in bay 2 was placed staggered rather than at the specified single chainage (38.955) across the slab, parallel to the edge of the steel.
| 02SL - Stations (LUL) | Cxxx-NCR-001724 | NCR | SCL - Chamfer at construction joints not to design (PTE CH 23.755 / 47.755) |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-02-13 | 2015-02-10 12:43 | -3 | 2015-01-23 15:34 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | The first two construction joints on PTE invert slab (PTE CH 23.755 / 47.755) had no chamfer to the Cxxx design.
| 02SL - Stations (LUL) | Cxxx-NCR-001725 | NCR | SCL - Construction Joint Sketch not accepted / followed for PTE inverts (CH12-129.275) |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-04-20 | 2015-04-17 11:03 | -3 | 2015-01-22 15:07 | Tunnelling - Linings - Sprayed Concrete | 2500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Construction / contraction joint sketch was issued to CRL through RFI - 2311. Bay 5 pour in PTE was a combination of 2 pours, therefore a construction joint was now a crack inducer. The drawing was also not accepted by the PM prior to the pours commencing.
| 02SL - Stations (LUL) | Cxxx-NCR-001726 | NCR | WTH SH-W2 Wall 8 Couplers for Wall 20 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-02-05 | 2015-01-30 10:12 | -6 | 2015-01-22 17:11 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | On striking the shutters to Wall 8 we started scabbling the extent of Wall 20 to locate the couplers connecting the walls. On completion of the scabbling not all of the couplers had been located so drilled additional holes in an attempt to locate them. We have now been able to locate all the couplers but this has left a wall with lots of holes. These holes will be filled once Wall 20 is cast and so propose to use-as-is.
| 02SL - Stations (LUL) | Cxxx-NCR-001727 | NCR | SCL - Ventilation not to CRL accepted Design. |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-04-20 | 2015-04-17 17:01 | -3 | 2015-03-17 15:23 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Planning | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Not following approved ventilation design
| 02SL - Stations (LUL) | Cxxx-NCR-001728 | NCR | WTH SH-W2 Reduced cover to Wall 6 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-02-13 | 2015-02-06 08:11 | -7 | 2015-01-23 08:28 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Other human error | Completed |  | In the junction between Walls 6 and 11 we have a small area of reduced cover (see attached sketches), a minimum of 30mm. This pour is the top up above the North corbel. As there is only about 1m of exposed reinforcement above the wall it is impossible for us to move the reinforcement over generating more cover. Please can you confirm that in this instance this will be acceptable.
| 02SL - Stations (LUL) | Cxxx-NCR-001729 | NCR | WTH SHW2 Installation of steel reinforcement prior to the waterproofing installation |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-02-23 | 2015-02-23 13:59 | 0 | 2015-01-26 13:08 | Civil - Civil Engineering General | 1000 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | It has been noted that the installation of the steel reinforcement to several lining walls in the SHW2 shaft has commenced before the completion of the installation of the waterproofing systems. This contradicts item number 9 of the ITP Cxxx--C-ITP-M123-50226 that shows a hold point to check the installation of the waterproofing systems prior to the installation of the steel reinforcement.
| 02SL - Stations (LUL) | Cxxx-NCR-001730 | NCR | Early age strength testing frequency changes not added to ITP for Primary lining |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-02-16 | 2015-02-04 11:22 | -12 | 2015-01-26 15:45 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Early age strength testing frequency changed from every third advance to every 50m^3 via FCD 001399 on the 14/8/14. This change was not made on the ITP.
| 02SL - Stations (LUL) | Cxxx-NCR-001731 | NCR | SCL - Nozzleman Competency |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2015-02-10 | 2015-02-10 12:36 | 0 | 2015-01-27 09:39 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate resources | Completed |  | Nozzlemen__ and __ have been spraying unsupervised. They do not satisfy the competence criteria of KT20.2107 b).
| 02SL - Stations (LUL) | Cxxx-NCR-001732 | NCR | Excessive Heave caused by Compensation Grouting |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-02-23 | 2015-02-12 08:25 | -11 | 2015-01-28 15:43 | Geotechnical Engineering - Compensation Grouting | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | A compensation grouting episode (Cxxx-GEO-S-11903-PoJCP6&CH2-010054) was carried out on 26/01/2015 from Moorgate 2 Shaft to prevent slope triggers on structures caused by settlements anticipated to be observed due to CH2 enlargement SCL excavation. The grouting proposal was carried out and generated up to 11mm of heave on LU tracks as measured by Cxxx automatically read prisms. The grouting proposal adhered to the parameters of the proposal presented to the CTC on 21/01/15. The heave generated is contrary to clause 3.2.5.11 in the SCOGM stating: The maximum heave generated during a grout jacking episode shall be 5mm. The heave shall be determined as the reduction in settlement recorded at any monitoring location relative to the maximum settlement recorded at that point at any time prior to the start of the grout jacking episode.
| 02SL - Stations (LUL) | Cxxx-NCR-001733 | NCR | STW - __ not using calibrated instruments for onsite concrete testing on WTH- SHW2 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-03-16 | 2015-03-25 09:34 | 9 | 2015-02-06 10:53 | Structural Engineering - Testing | 1000 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | On the 26th Of January 2015, during a surveillance performed for WTH section of works for pre- pour inspection on Wall 9 - SHW2, it was noticed that __ was not using a calibrated Thermometer ( no register number was found please see photo attached) for concrete testing onsite during the very first load. this was pointed out to the lab technician at the time on site and he called the lab in order to get the right thermometer on site for the following concrete load. Please see attached second photo with the right instruments used ( Ref __ 007). Even though the use of this instrument was not compliant, this issue was sorted promptly. However as this is a re- current issue that was raised before on another NCR-1627 - by CRL , believes that corrective actions need to be put in place to prevent this non compliance from happening again.
| 02SL - Stations (LUL) | Cxxx-NCR-001734 | NCR | ETH Storage of site cured cubes for Level -6 trough slab |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-02-27 | 2015-02-20 17:41 | -7 | 2015-01-30 15:11 | Civil - Civil Engineering General | 800 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | Concrete cubes for level -6 trough slab which were due to be site cured, were not reliable for concrete strength.
| 02SL - Stations (LUL) | Cxxx-NCR-001735 | NCR | Missed readings of XR2 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-02-16 | 2015-02-16 16:52 | 0 | 2015-02-02 08:38 | Surveying - Instrumentation and Monitoring | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | During the construction of VA1 an extensometer located in the west ticket hall was not read as per the specificaiton.
| 02SL - Stations (LUL) | Cxxx-NCR-001737 | NCR | 66 Cowcross missed green trigger |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-03-06 | 2015-03-05 08:56 | -1 | 2015-02-02 09:03 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | A green trigger occured on 13-08-2014 on socket Cxxx-LB13967, this green was not notified to the SRG nor included in the trigger table.
| 02SL - Stations (LUL) | Cxxx-NCR-001738 | NCR | SCL - failed 4hr /12 hr Early age strength test - I35 CH2 enlargement |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-03-04 | 2015-02-12 15:10 | -20 | 2015-02-04 13:01 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | Failed 4hr and 12hr test nail test in advance I35 CH2 enlargement
| 02SL - Stations (LUL) | Cxxx-NCR-001739 | NCR | SCL - Poor core quality in PTE - TH 677 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-03-27 | 2015-03-25 16:45 | -2 | 2015-02-04 13:06 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 1no. Grade 4 core in PTE - TH 677
| 02SL - Stations (LUL) | Cxxx-NCR-001740 | NCR | ETH Two Storey Basement Midlanding at 111.534 in ESS5 Misaligned Couplers |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-02-19 | 2015-02-20 15:50 | 1 | 2015-02-05 12:08 | Civil - Civil Engineering General | 2500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Personnel Error - Other human error | Completed |  | has exposed the couplers of the midlanding in the Two Storey Basement at level 111.534 in ESS5 which were fixed during the construction of the Level -1 Slab Area A. 2 no. of the couplers have been installed at the incorrect level, BM48. The attached marked up drawing (Cxxx-ATK-S-DWG-M123_Z-50763 P02) shows, highlighted in yellow, the bars which have been installed at the wrong level. Also refer to photograph attached for clarity. Note that 20mm diameter bars were installed for BM 48 as opposed to the 12mm specified on the drawing due to availability during construction.
| 02SL - Stations (LUL) | Cxxx-NCR-001741 | NCR | ETH Two Storey Basement IP1 Misaligned Couplers |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-02-26 | 2015-02-26 14:01 | 0 | 2015-02-05 15:28 | Civil - Civil Engineering General | 2500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Other human error | Completed |  | The couplers within Capping Beam K for IP1 have been cast at the incorrect position and level.
| 02SL - Stations (LUL) | Cxxx-NCR-001742 | NCR | SCL - Missed 1 day Core - PTE B683 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-03-09 | 2015-03-09 11:55 | 0 | 2015-02-06 13:37 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | For Advance 683 in PTE, a 24 hour core was missed. All other E.A.S. tests were taken. The 12hr test achieved 10.63MPa, above the 24hr target.
| 02SL - Stations (LUL) | Cxxx-NCR-001743 | NCR | SCL - Damage to Waterproofing in invert PTE CH129.275 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-02-22 | 2015-02-19 12:22 | -3 | 2015-02-08 10:51 | Tunnelling - Linings - Sprayed Concrete | 4000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Invert waterproofing at CH 129.275 (PTE) was damaged, including the waterbar at the construction joint
| 02SL - Stations (LUL) | Cxxx-NCR-001744 | NCR | SMM - Inclinometer Readings Missed During Tunnel Construction |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-02-23 | 2015-02-21 13:37 | -2 | 2015-02-09 09:00 | Surveying - Instrumentation and Monitoring | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Cxxx-IE00006 was damaged due to the SCL excavation.
| 02SL - Stations (LUL) | Cxxx-NCR-001745 | NCR | WTH - SHW2 - Torque wrenches in use after calibration date has expired |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-02-23 | 2015-02-10 17:38 | -13 | 2015-02-09 11:58 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | • On the 29th January Crossrail site superintendent reported an observation in SHW2 of steelfixers using the faulty torque wrench for tightening coupled rebar connections, it reads: ‘It has been observed that the steel fixers were using a faulty coupler torque wrench there was no click noise to indicate that the correct torque is applied spoken to the steel fixer tried with another wrench and worked fine, the faulty wrench taken out of use and the serial number given to the Engineer to check the calibration status and also to be replaced’. After matching the serial numbers with calibration certificates of the faulty torque wrench and other wrenches in use, it was discovered that the calibrations certificates were out of date. • A further observation by the CRL PFE on 3rd February identified that steelfixers were over tightening couplers by having a wrong torque setting on wrenches. Refer also to CRL Observation Report CRL-OBS-00547.
| 02SL - Stations (LUL) | Cxxx-NCR-001746 | NCR | WTH SH-W2 excessive cover on Wall 20 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-02-24 | 2015-02-23 09:40 | -1 | 2015-02-10 16:24 | Civil - Civil Engineering General | 2500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Previous Construction - Problems based on previous construction errors | Completed |  | On inspecting the cover on Wall 20 (post shutter installation) it was observed that there appeared to be excessive cover in the South East corner of the wall (see attachment). Although an accurate measurement of the cover was not possible, as the shutters were already installed, it appeared to be greater than the maximum allowable tolerance of 60mm (50mm +10mm tolerance). The spacer block shown in the attached photograph is 50mm showing that the actual cover to the reinforcement is greater than 60mm. The cover is only an issue at the bottom of the shutter, the reinforcement at the top is within the allowable criteria. The spacer blocks on the West side of the wall are touching the shutter which means that the width of the cage is slightly too narrow as otherwise the spacers on the East side would also be touching. The majority of the starter bars forming wall 20 were cast in the South corbel by Cxxx and so our cage spacing was largely governed by the as-found condition (see attachment).
| 02SL - Stations (LUL) | Cxxx-NCR-001747 | NCR | SCL - Construction Management Plan |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2015-03-13 | 2015-03-09 11:55 | -4 | 2015-02-11 16:47 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | The SCL Construction Management Plan is currently not accepted Code 2 since 04/10/13. This document contains the details of those who occupy some of the key positions specified in Table KT20-05. A recent surveillance (Cxxx-XRL-O4-RGN-M123-50018) highlighted the fact that many of the personnel quoted in the document are no longer working on the project and the new personnel occupying these positions have not been formally accepted.
| 02SL - Stations (LUL) | Cxxx-NCR-001749 | NCR | SMM-Grout compressibility results |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-04-01 | 2015-03-31 14:08 | -1 | 2015-02-11 17:17 | Civil - Geotechnical Engineering | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Grout mix for compensation grouting: Cxxx--C-LRC-M123-50101 Rev 2.0 the compressibility ( youngs modulus ) of grout should be <2.5GPa. Recent mobthly testing has shown the compressibility of the grout to be greater than this sample 04/12/2014: 6.48GPa , sample 07/01/2015: 5.83GPa. It should be noted the compressibility results is not a critical parameter for goruting works as the grouting is dependent on hydrofracture of the surrounding clay.
| 02SL - Stations (LUL) | Cxxx-NCR-001750 | NCR | SCL - Bay 5 Cube Strength Failures at 56 Days |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-04-10 | 2015-03-31 17:28 | -10 | 2015-02-17 14:02 | Tunnelling - Linings - In-situ Concrete | 2500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Two sets of cubes out of four taken on Bay 5 (Poured 21st to 22nd of December 2014) in the Secondary Lining Cast In-Situ Concrete works have not achieved the minimum strength requirement of 56MPa requirement at 56 days. EX1077 - 44.7MPa EX1078 - 62.1MPa EX1079 - 49.3MPa EX1080 - 58.2MPa The minimum acceptable value is 56MPa in accordance with BS EN 206-1. See attached 29 Table for all results to date at Farringdon SCL. In Situ Cores have been taken from the lining and a corrected core strength in accordance with Concrete Guidance Note 47 give an average value of 60.4MPa from 4 results, above the 56MPa minimum strength, see attached calculations and test result EX1078.
| 02SL - Stations (LUL) | Cxxx-NCR-001751 | NCR | SCL - FAR 759 and FAR 760 1 Day Cores Crushed at 5 Days |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-03-10 | 2015-03-05 08:54 | -5 | 2015-02-17 12:44 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | FAR 759 and FAR 760 1 day cores were crushed at 5 days rather than the allowable 1-3 day period.
| 02SL - Stations (LUL) | Cxxx-NCR-001752 | NCR | WTH SH-W2 Damage to vertical hydrophilic strip |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-02-25 | 2015-02-20 17:28 | -5 | 2015-02-20 11:23 | Civil - Civil Engineering General | 3000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Personnel Error - Other human error | Completed |  | When casting the lining walls between Level -6 and Level -5 in the square shaft (SH-W2), Installed hydrophilic strip at all vertical construction joints. A lap length was left at the top of the wall to be tied into the slab soffit waterproofing system (horizontal construction joint). In three locations (see attachment) the lap length has been removed or damaged which prevents us from gaining the required overlap with the horizontal construction joint hydrophilic strip. proposed a detail to __ Construction (waterproofing supplier) with a remedial solution as attached. __ have confirmed at the three locations that the solution is acceptable (see attachment).
| 02SL - Stations (LUL) | Cxxx-NCR-001753 | NCR | ETH - PWP 2 Grout Loss to North Face |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-04-11 | 2015-04-07 07:20 | -4 | 2015-02-20 12:26 | Civil - Civil Engineering General | 2500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | After striking the top and sides of the formwork to PWP2 grout loss has been identified on the north face. See attached Photo. - PWP2_North Face 09.03.2015 Post striking of the soffit - an area of honeycombing was identified along the soffit at the join between the kicker and the remaining pour.
| 02SL - Stations (LUL) | Cxxx-NCR-001755 | NCR | Missing Instrumentation Installation and Baseline |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-03-20 | 2015-03-12 09:36 | -8 | 2015-02-23 08:35 | Surveying - Instrumentation and Monitoring | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | There are 3 number sockets that have not been installed as per the contract photomontage drawings and as a result the baseline has not been achieved.
| 02SL - Stations (LUL) | Cxxx-NCR-001756 | NCR | ETH-Trapezoidal Shaft- L-4 Wall 17, Downward facing Couplers at L-3 slab installed at incorrect location |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-03-12 | 2015-03-09 15:19 | -3 | 2015-02-23 14:46 | Civil - Civil Engineering General | 2500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | When fixing the L-3 slab a small area of wall 17 couplers for level -4 (see sketch L-4) were installed incorrectly. They were installed 100mm east of the correct position. Please see attached as built survey (Wall 17 As Built.pdf ) of cast in couplers.
| 02SL - Stations (LUL) | Cxxx-NCR-001757 | NCR | ETH -Trap Shaft: L-7 Grout loss at wall 7 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-03-24 | 2015-03-16 17:27 | -8 | 2015-03-05 01:40 | Civil - Civil Engineering General | 800 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | After stricking W7 shutter at L-7, grout loss was identified in the bottom right corner (looking east). See attached photograph.
| 02SL - Stations (LUL) | Cxxx-NCR-001758 | NCR | WTH SH-W2 - Void Propping end plate cover reduction |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-03-11 | 2015-03-11 08:30 | 0 | 2015-02-25 17:53 | Civil - Civil Engineering General | 3500 |  | Design | Repair | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | On Level -5 the void propping was installed in Opening 3 in accordance with the TW design drawing (Cxxx--C-DWG-M123-50455) and in Opening 2 8mm south due to constraints from the in-situ walls. The southern end plates for both the CHS props in 2 & 3 protrude into the slab pour. Opening 2 end plate is 30mm into the slab and Opening 3 end plate is 10mm into the slab. Refer to attached site photos. See attached sketches (Cxxx-NCR-001758 Opening 2 & 3) showing that these protrusions have occurred due to compound effects of tolerances on the wall and shutter positions. Note that although none of the tolerances for the in plan position of the concrete elements have been exceeded, the result is a reduction in cover on adjacent U bars to 20mm in Opening 2 and 35mm in Opening 3.
| 02SL - Stations (LUL) | Cxxx-NCR-001759 | NCR | ETH - Trap Shaft - L-7 Wall 7: Timber in concrete pour |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-03-20 | 2015-03-12 08:58 | -8 | 2015-02-27 13:16 | Civil - Civil Engineering General | 800 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | After stricking Wall 7 L-7 it was identified that 3 pieces of timber that were used for the stop end fell into the shutter prior to the concrete pour which left a indentation in the face of the wall (see photo-1759). Please note that the wall was inspected prior to putting up the shutter but it seems that an individual didn’t notify the engineer or supervisor that timber pieces dropped in the wall.
| 02SL - Stations (LUL) | Cxxx-NCR-001763 | NCR | SCL - Fixing rondels for waterproof membrane |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2015-04-30 | 2015-04-21 14:30 | -9 | 2015-02-26 12:24 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | The nails being used to fix the rubber rondels to the primary lining are not compliant with those submitted in MCR Cxxx--C-LRC-M123-50136 Rev 2. A sample of the rondel and nail taken from the tunnel on Thursday 26/02/15 shows that the washer that is currently being used is smaller than that specified in the MCR. Furthermore, the length of the nail is smaller than that specified in the MCR. Please see photos and attached MCR.
| 02SL - Stations (LUL) | Cxxx-NCR-001764 | NCR | WTH Level -1 to 0 Internal Walls - Wall 38 South pour concreting issues |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-03-30 | 2015-03-30 09:03 | 0 | 2015-03-02 17:50 | Civil - Structural Engineering | 3000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | poured the 1st lift (bottom 2.75m) of the Southern half of Wall 38 (level -1 to 0 internal wall) on Friday 02.03.15. After 2no. wagons had been poured (15m3), the next 2no. wagons were outside of the specified slump range and were sent away. The next (5th) wagon was slumped at 290mm (50mm out of specified range) - to mitigate the risk of a cold joint used this non-compliant concrete. At this point the time limit of 1hr to maintain a live concrete face had passed - the actual time was 1hr 50mins. Please see the attached structural concrete site control sheet which details this. took additional cubes from the non-compliant concrete. also periodically tested the 'liveness' of the concrete face by inserting the vibrating poker into the pour - the hole made by the poker disappeared upon removal of the poker, hence demonstrating the concrete was still live. have also carried out a post-pour inspection of the wall of which 2no. photos are attached. The first one demonstrates there is a very slight discolouration caused by the delay between concrete loads. The second image shows there is good quality concrete behind the line of slight discolouration and hence no cold joint.
| 02SL - Stations (LUL) | Cxxx-NCR-001765 | NCR | ETH - Trapezoidal Shaft - Further to Cxxx-FCD-001563 - Omission of A__ Horizontal Bars in Lining Wall above VA2 Tunnel Opening |  | Contr | BAM | FAR - Farringdon Station (West) |  | 2015-07-01 | 2015-06-10 07:18 | -21 | 2015-03-02 17:11 | Civil - Civil Engineering General | 2500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Following on from Cxxx-FCD-001563 and the ongoing discussions that are still occurring regarding reanalysis by Cxxx on whether or not the omission of the additional band of rebar is needed above VA2 opening in lining wall W1, please note the following: Design Intent drawing Cxxx-SWN-S-DDL-M123 Z-44000 C01 indicates the requirement for a band of B40 bars directly over the VA2 opening. These bars were not included as part of Cxxx’s initial detailing of ETH Lining Wall 1 (as covered on drawing Cxxx-ATK-S-DWG-M123_Z-50215 C03 at time of casting), and as such were not incorporated into the works on site. We would note that this drawing has been reviewed several times by CRL/Cxxx prior to the casting of this wall on site, and at no point was the omission of these bars identified during the reviewing process as part of the __ RIR process/comments, despite it being Cxxx’s responsibility to ensure design intent has been adequately transferred from their drawings. We would further note that this omission is an anomaly. Since the issue of this drawing in early 2014, we have further refined our checking procedures (adding an extra level of check and review) to avoid any repeats of this scenario. Note, it was agreed in the Engineering Meeting in between Cxxx/Cxxx/CRL that an FCD was going to be raised rather than an NCR hence why this NCR was not raised sooner on the assumption that the omission of the rebar was going to be accepted by Cxxx hence the FCD as agreed in between Cxxx/Cxxx.
| 02SL - Stations (LUL) | Cxxx-NCR-001766 | NCR | Section D not being completed on Checksheet SF-CON-210_01 (regulating layer) before installing sheet waterproof membrane |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2015-04-08 | 2015-03-31 17:29 | -8 | 2015-03-03 14:43 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | During a planned Crossrail surveillance on 16th February 2015 which looked a SCL Sheet Waterproof Membrane installation, it was highlighted on review of Checksheet SF-CON-210_01 (regulating layer) for PTE Bay 5 and 6, that Section D had not been completed for both bays which details post spray checks, such as regulating layer profile, visual checks for protruding steel fibres, roughness and cracks etc. These checks are Hold Points within documented ITP ‘Surface Preparation and Application of Regulating Layer’ Cxxx--C4-ITP-M123-50053 Rev 3 Code 1, which must be carried out before covering with sheet membrane. As the check sheets had not been completed by the site engineers, it could not be verified that the checks / inspections had been carried out before installing the sheet membrane system; as such this NCR was raised resulting from the surveillance visit.
| 02SL - Stations (LUL) | Cxxx-NCR-001767 | NCR | No control of access and tracking on installed sheet membrane with no protective layer down as defined in the MS |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2015-04-08 | 2015-03-31 17:30 | -8 | 2015-03-03 14:47 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | During a planned Crossrail surveillance on 16th February 2015 which looked a SCL Sheet Waterproof Membrane installation, it was highlighted during the site visit that there was no control of access and tracking over the PVC-P sheet membrane in Bay 6 which had no protective layer overlaid which is against the documented method statement 4.3.1 following geotextile installation: “From this point on, access to the invert area is to be restricted to personnel wearing protective cushioned overshoes to prevent damage to installed areas. A designated access point is to be installed where footwear is checked before entry Additionally, when the surveillance team visited Bay 6, no protective boots were offered before walking on the installed sheet membrane, as such this NCR was raised resulting from the surveillance.
| 02SL - Stations (LUL) | Cxxx-NCR-001768 | NCR | SCL - T-piece weld failed at CH 196.114 RHS (in-by) PTE |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-04-03 | 2015-04-02 14:56 | -1 | 2015-03-06 11:23 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Verification Problems - Not Defined | Completed |  | T-piece weld failed at CH 196.114 RHS (in-by) PTE
| 02SL - Stations (LUL) | Cxxx-NCR-001769 | NCR | ETH 2SB PWP1 Concrete Finish |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-03-30 | 2015-03-27 11:34 | -3 | 2015-03-09 18:21 | Civil - Civil Engineering General | 2000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | On striking the top face of formwork on PWP1 a sandy deposit was found on the surface of the concrete. An area of grout loss between the 1st and 2nd pouring hole from the base was noted. At each pouring hole and at the connection to the capping beam, concrete has entered into the area between the liner and the formwork causing an uneven surface. Please refer to attached photograph.
| 02SL - Stations (LUL) | Cxxx-NCR-001770 | NCR | ETH Lining wall W21 / W22 / W23 Level L-1 - Excess cover between GL1 and GL3.5 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-03-24 | 2015-03-25 09:32 | 1 | 2015-03-10 07:26 | Civil - Civil Engineering General | 2500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | At Level L-1 slab level the lining walls W21 / W22 / W23 have areas with excess concrete cover between GL1 and GL3.5. Please find attached as-built surveys. The values given in the surveys show the distance between the front face of lining wall and the vertical reinforcement (NF2) at kicker level. The required cover is 70mm (= 50 concrete cover + 20mm NF1 B20 horizontal lacer). The max excess cover is 25mm.
| 02SL - Stations (LUL) | Cxxx-NCR-001771 | NCR | ETH - Lining Wall W21 L-1 reduce concrete cover |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-03-24 | 2015-03-24 14:32 | 0 | 2015-03-10 07:46 | Civil - Civil Engineering General | 2500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | In a localised area on lining wall W21 at L-1 slab level between internal wall W32 and W30, the lining wall has reduced concrete cover. Min concrete cover is 25mm (45mm incl horizontal lacer). Please find attached as built survey. The values given in the survey show the measurement from the front face of the lining wall to the vertical bars (NF2) at kicker level. Therefore the required value should be 70mm (=50mm concrete cover + 20mm NF1 B20mm horizontal lacer). Further up the wall the concrete cover will be achieved by use of concrete spacer blocks.
| 02SL - Stations (LUL) | Cxxx-NCR-001773 | NCR | Repetitive lack of adherence to design drawings |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2015-04-09 | 2015-04-02 16:50 | -7 | 2015-03-10 10:48 | Mechanical - Piping | 2500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | The WTH construction team is repetitively not adhering to public health installation drawings and making changes without raising the necessary PTR requests. This is leaving the Project Manager with a position where the installation is already complete with no further change option without high cost/program implications. This instance specifically refers to WTH L-6 Public Health North Staircase The contractor is to investigate the lack of adherence to procedures and check implications of this installation on the architectural access panels layout.
| 02SL - Stations (LUL) | Cxxx-NCR-001774 | NCR | WTH – Level -1 Internal Walls – Torque Wrench Used On Site Without Calibration Certificate |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2015-03-31 | 2015-03-26 11:21 | -5 | 2015-03-10 11:49 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | On 3rd March Crossrail Field Engineer visited site during the construction of the internal walls on the -1 Level Slab and observed the steel fixers tightening coupled bars with a torque wrench that had no calibration certificate. The calibration number was recorded but could not be matched in the calibration register therefore meaning that it should not have been on site. NCR Cxxx-NCR-001745 stated one of the corrective actions was to remove all wrenches without a calibration certificates but it would appear that this action has not been completed and is a repeat NCR.
| 02SL - Stations (LUL) | Cxxx-NCR-001776 | NCR | SCL - Bays 6, 7 and 8 Temperatures over 60 Degrees |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-04-03 | 2015-03-31 14:09 | -3 | 2015-03-17 10:53 | Tunnelling - Linings - In-situ Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Bays 6, 7 and 8 invert pours reached a maximum core temperature of 61, 66 and 65 degrees celsius respectively. Specification KF10.1302 (a) only allows a maximum of 60 degrees for sections thicker than 500mm.
| 02SL - Stations (LUL) | Cxxx-NCR-001777 | NCR | WTH SH-W2 Dywidag bar repairs |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-04-01 | 2015-04-01 13:12 | 0 | 2015-03-11 15:31 | Civil - Civil Engineering General | 3500 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | Clause KF10:3222h of the Civil and Structural Specification states that all formwork ties used in the 50mm cover zone must be removable. 1) have installed dywidags through the walls which are not capable of being removed from the 50mm cover zone. These dywidag bars were additional to those shown on the temporary works drawings. 2) Furthermore and previously as per Cxxx-RFI-002438, when have come to remove them, we are only removing the dywidags to a depth of 30mm from the concrete surface before repairing them, and not the 50mm required. These two items have taken place on the walls between Level -8 & -6 and Level -6 & -5.
| 02SL - Stations (LUL) | Cxxx-NCR-001778 | NCR | WTH SH-W2 Timber cast in to soffit of Level -5 Slab |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-03-27 | 2015-03-25 10:32 | -2 | 2015-03-11 18:11 | Civil - Civil Engineering General | 3500 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Two small openings were made in the soffit falsework of the Level -5 slab in SH-W2 for electrical services to pass through, locations as shown on the attachment. These openings were ‘plugged’ by placing 18mm plywood over the top. This plywood was cast into the soffit of the slab. On striking the soffit falsework these two small pieces of plywood are now visible as seen on the attachment. One of the plywood pieces appears to be partly cast above Wall 25.
| 02SL - Stations (LUL) | Cxxx-NCR-001780 | NCR | WTH SH-W2 Wall 6/16 break back for L-6 void cover removal |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-03-28 | 2015-03-25 10:43 | -3 | 2015-03-14 03:45 | Civil - Civil Engineering General | 4000 |  | Design | Repair | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | During the void cover removal from the staircase opening on level -6 it was necessary to locally break back sections of wall 6 and wall 16 to enable their removal. Break out no more then 30mm deep. See attached file Cxxx-NCR-001780 showing location and photograph.
| 02SL - Stations (LUL) | Cxxx-NCR-001782 | NCR | ETH - Two Storey basement pipe cast in capping beam level 0 West |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-05-01 | 2015-04-29 10:18 | -2 | 2015-03-13 16:18 | Civil - Civil Engineering General | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | As part of the construction of capping beam level 0 West in the Two Storey Basement, 2No vertical pipes were cast in the capping beam as per drawing Cxxx--P-DDA-M123_1-25201 P05 (see highlighted in pink). These pipes stick down the underside of the capping beam approximately 220mm. During the construction of Lining wall W23 the southern pipe was damaged. The pipe has a crack which starts at the bottom end and goes, at least, up to the underside of the capping beam. Because of this, it is not possible to leave the undamaged pipe protruding 50mm from the soffit to install a coupling.
| 02SL - Stations (LUL) | Cxxx-NCR-001783 | NCR | STW-Tesconsult - Equipment/ Calibration Register not being maintained |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-04-27 | 2015-05-15 15:55 | 18 | 2015-03-16 09:21 | Structural Engineering - Testing | 1000 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | A follow up Surveillance to __ was carried out on 22nd of February as a result of 2 NCRs raised regarding __ lack of management of their Equipment / Calibration on site. ( Refer to NCR-1627 raised by CRL and NCR 1733 raised by . Both NCRs regarding non calibrated equipment being used on site. It was verified during this Surveillance that the Equipment / Calibration Register ( EB REF: - Cxxx--O4-RGN-M123-51224), is not being maintained by the laboratory in a suitable manner - calibration information is not being updated within; A few spot checks were made to check if the dates from the calibration certificates were consistent with dates from the register and in 3 occasions it was verified that the dates were not matching with the dates recorded on the certificates.
| 02SL - Stations (LUL) | Cxxx-NCR-001784 | NCR | ETH 2SB As Built Postion of PWP1 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-03-31 | 2015-03-24 07:10 | -7 | 2015-03-17 13:47 | Civil - Civil Engineering General | 2500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | On completion of the as built survey of PWP1 the as built differs from that raised in NCR-001741. The final as built position is as shown in Sketch Cxxx/SR/ETH/SB32. The change from NCR-001741 is that the angle of the prop is now 36.61 degrees from the vertical, the plan position is still as per NCR-001741. This brings it much closer in line with the original design angle of 36.52 as shown in Cxxx-SWN-S-DDD-M123_3-29251 but confirmation of this being acceptable is sought to close this out. Note that on reviewing the previously recieved information a discrepancy has been found within RFI-002072 and Detail 264 on DWG Cxxx-SWN-S-DDD-M123_3-29251. The angle in the drawing is 36.52 degrees from the vertical however in RFI-002072 it is calculated as 36.26 degrees from the vertical.
| 02SL - Stations (LUL) | Cxxx-NCR-001785 | NCR | SCL - Longitudinal crack above CP6 / PTE junction |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-04-24 | 2015-04-21 11:14 | -3 | 2015-03-16 10:17 | Tunnelling - Linings - Sprayed Concrete | 2500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Longitudinal crack above CP6 /PTE junction, Approx 14m in length (the entire length of the thickening) TM255 - 269
| 02SL - Stations (LUL) | Cxxx-NCR-001786 | NCR | Cxxx ETH Trapezoidal Shaft Level -7 Wall 1D 28 Day Cube Strength |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-05-12 | 2015-05-12 09:18 | 0 | 2015-03-16 15:01 | Civil - Civil Engineering General | 2500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Following the issue of the 28 day cube results for Level -7 Wall 1D it was found that the wall did not reach strength. The 28 day results were 47.4 N/mm2 and 46.7 N/mm2 respectively.
| 02SL - Stations (LUL) | Cxxx-NCR-001787 | NCR | ETH - Trap Shaft - W11 L-4: Honeycombing |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-04-07 | 2015-03-26 09:53 | -12 | 2015-03-18 10:33 | Civil - Civil Engineering General | 800 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | After striking W11 shutter at L-4, honeycombing was identified on the north and south face. Please find attached plan and relevant photographs showing the locations.
| 02SL - Stations (LUL) | Cxxx-NCR-001788 | NCR | ETH Trap Shaft - W11 L-4: Movement of shutter |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-04-01 | 2015-03-27 13:38 | -5 | 2015-03-18 09:47 | Civil - Civil Engineering General | 800 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During the concrete pour for W11 L-4, a timber shutter at the top of the wall moved. This caused an overspill of concrete as shown in attached photo.
| 02SL - Stations (LUL) | Cxxx-NCR-001789 | NCR | SCL - PTE - Failed crown waterproofing inspection (Bay 1 - TM76 to 88) |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2015-04-17 | 2015-04-17 16:55 | 0 | 2015-03-17 11:23 | Tunnelling - Linings - In-situ Concrete | 500 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Verification Problems - Inspection points not adequate | Completed |  | During the inpsection of the crown waterproofing in Bay 1 (TM76 to 88) the following observations were noted: 1) A plastic shim was protruding from the invert pour (see photo) 2) The cleanliness of the waterbar was not appropriate (see photo) 3) The reinjectible tubing attached to the waterbar was sagging and not secured tightly to the waterbar 4) A double seam weld on the LHS looking in by (labelled L1) did not have the pressure test marked and therefore it was not obvious whether or not this weld had been tested.
| 02SL - Stations (LUL) | Cxxx-NCR-001790 | NCR | SMM- No grout testing undertaken on the 16/10/14 Night shift |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-03-31 | 2015-03-31 15:00 | 0 | 2015-03-17 13:52 | Geotechnical Engineering - Compensation Grouting | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | On the 16/10/14 Nightshift there was no density,flow, bleed or viscosity tests were undertaken in accordance with KC21.3217 c)-original works information clause detailing tests to be undertaken Changed by FCD: Cxxx-FCD-000670 Test frequency is as follows : Density every 5th mix or 2m3 Flow every mix or 0.5m3 Bleed every 5th mix or 2m3 Viscosity every 5th mix or 2m3
| 02SL - Stations (LUL) | Cxxx-NCR-001791 | NCR | SCL – Pressure Gauge Being Used On Site Without Calibration Certificate Traceability |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2015-04-14 | 2015-04-14 16:51 | 0 | 2015-03-17 12:54 | Tunnelling - Tunnelling General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | During an ITP Validation exercise on Waterproofing Installation, Crossrail Field Engineer was examining some of the measuring equipment on site and noticed that the pressure gauge that is used on the pump for pressure testing of the double seam welds of the waterproofing membrane did not have a calibration number on it. This means it could not be traced to any of the calibration certificates in the Instrument Callibration Register.
| 02SL - Stations (LUL) | Cxxx-NCR-001792 | NCR | WTH SH-W2 Exposed reinforcement on Level -6 soffit |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-04-17 | 2015-04-17 15:36 | 0 | 2015-03-17 15:59 | Civil - Civil Engineering General | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | 1 - On striking the falsework for the Level -6 soffit, in a single location, where the slab changes between 750mm and 450mm depth (see attached sketch), a small section of reinforcing bar, approximately 50mm long was visible. This section of reinforcing bar only had approximately 5mm cover (see attached photograph). 2 - Further to CRL-OBS-00016 it was noticed that the reinforcement below -6 level (where the slab thickness changes from 750 to 450mm) had minimal cover, this area has been patched over by the concrete gang during the Level -8 to -6 snagging works. The repair they have carried out will need to be broken back to allow the NCR agreed remedial works to be carried out. Refer to attachment for before & after photos.
| 02SL - Stations (LUL) | Cxxx-NCR-001793 | NCR | SCL - Use of Damaged ETC Flow Table on PTE Crown Pour CH 100 to 112 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-04-30 | 2015-04-22 10:05 | -8 | 2015-03-20 12:34 | Tunnelling - Linings - In-situ Concrete | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Inspection points not adequate | Completed |  | On 19/03/15, __ performed a flow table test with a damaged flow table for the first load of a crown pour, PTE CH100-112. This concrete was then placed into the shutter before the damage was identified. The flow was measured as 640mm. The damaged flow table was replaced in time for the second load of the pour, therefore the rest of the concrete was correctly tested.
| 02SL - Stations (LUL) | Cxxx-NCR-001794 | NCR | SCL- Use of non-calibrated test equipment |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2015-04-22 | 2015-04-22 10:02 | 0 | 2015-03-23 10:56 | Tunnelling - Linings - Sprayed Concrete | 500 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | It was discovered during an informal review of a draft internal surviellance report that some of the equipemnt used to carry out flow testing fo the SCL works had not been calibrated. The report Cxxx--O4-RGN-M123-51222, detailing a surviellance of testing equipment and calibration register undertaken 25/02/2015, failed to identify the non-conformance and incorrectly reported the following equipment as having been calibrated; Flow table, cone and tamping bar ref. FT5 Flow table, cone and tamping bar ref. FT4 The equipment register also incorrectly records this equipment as having been calibrated.
| 02SL - Stations (LUL) | Cxxx-NCR-001795 | NCR | WTH SH-W2 Level -5 to -4 Wall 7(Pour 2) Pre-Pour Inspection |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2015-05-20 | 2015-05-21 11:12 | 1 | 2015-03-23 15:21 | Civil - Civil Engineering General | 3000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | CRL FE was invited to attend Pre-Pour Inspection for WTH SH-W2 Wall 7(Pour 2) on 23/03/2015. All checks were confirmed as having been previously completed by (refer to attached Pre-Pour Inspection Checksheet). During the inspection CRL FE noticed that the horizontal waterproofing detail at the southern construction joint was not in accordance with the design details (refer to __ waterproofing detail on Cxxx--C-DWG-M123-50058 Rev.C01) or manufacturer's installation details (refer to MCR for __ - Cxxx--C-LRC-M123-50004 Rev.1.0), as the 2no. __ strips stopped at the hy-rib stop-end, and did not pass through it a minimum of 100mm to allow for a lap with the horizontal waterproofing for the next adjacent wall pour (Wall 7/8 Pour 2). An alternative detail will now need to be agreed and implemented prior to the adjacent wall pour. The non-conformance is summarised and photos are also provided on attachment Cxxx-NCR-001795 NCR Details.
| 02SL - Stations (LUL) | Cxxx-NCR-001796 | NCR | SCL - Top Heading 3 - Out of Specification Load |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-05-01 | 2015-04-22 11:11 | -9 | 2015-03-23 15:56 | Tunnelling - Linings - In-situ Concrete | 2500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Inspection points not adequate | Completed |  | During the pouring of PTE Crown Bay 3, Chainage 100-112, a non compliant load was added to the Kern Shutter on night shift. The load was ticket number 1974755203 batched at 19:41 on 19/03/15, the 7th load of the night. The flow of the load was measured as an average of 510mm.
| 02SL - Stations (LUL) | Cxxx-NCR-001797 | NCR | SCL - Crown Casting - Non encapsulation of waterbar at crown (Trial Pour - Pour 1) |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-06-18 | 2015-06-17 11:48 | -1 | 2015-03-31 16:40 | Tunnelling - Linings - In-situ Concrete | 2500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Training Deficiency - Insufficient practice or hands -on experience | Completed |  | Full encapsulation of the waterbar was not achieved in the radial installation on Trial Pour - Pour 1. The effected area was in the crown at chainage 76.432, whereby a small void was left on the stop end.
| 02SL - Stations (LUL) | Cxxx-NCR-001798 | NCR | SCL - Crown Casting - Injectable hose displacement from the invert waterbar |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-05-22 | 2015-05-15 14:50 | -7 | 2015-03-27 17:37 | Tunnelling - Linings - In-situ Concrete | 2500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | Following a pre-pour inspection, it was noticed that a small section of the injectable hose had come loose from the waterbar rib in the invert. The hoses are held within the rib by a loop of membrane at regular centres. The shutter was set in place for pouring and therefore access was not available. Location Details: (see picture) - PTE Bay 3 ( TM100.232 - TM112.132) - RHS invert joint looking towards PL3 - Area effected approx 500mm from TM100.732 - TM101.232
| 02SL - Stations (LUL) | Cxxx-NCR-001799 | NCR | WTH - Strength of the concrete spacers blocks used on the SHW2 walls |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-04-08 | 2015-03-31 11:40 | -8 | 2015-03-25 14:32 | Civil - Civil Engineering General | 2500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | The strength of the concrete spacers blocks used on the SHW2 walls (MCR – Cxxx--C-LRC-M123-50147 Rev.1.0) is lower than the strength class specified for the concrete used in the walls. Concrete spacers strength is stated as being greater than 40N/mm2 and the concrete strength class for the walls is C50/60
| 02SL - Stations (LUL) | Cxxx-NCR-001801 | NCR | SCL - Poor aplication of curing agent on Crown pour Bay 4 CH 112.132-124.032 (PTE) |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-06-12 | 2015-05-29 13:56 | -14 | 2015-03-25 15:15 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Insufficient quantity of material to do the job | Completed |  | Poor application of curing agent onto Crown pour Bay 4 CH 112.132-124.032 (PTE) - Procedural NCR
| 02SL - Stations (LUL) | Cxxx-NCR-001802 | NCR | ETH Level 0 Slab Coupler Issues W21 and W22 Interface |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-08-20 | 2015-07-13 08:50 | -38 | 2015-03-26 14:35 | Civil - Civil Engineering General | 2500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | have carried out a survey of the couplers for the Level 0 slab. A few areas require a remedial solution as the couplers have not been installed at the correct level. Are the following proposals acceptable? A. W21 1) In areas along the top of the slab where the top mat couplers have been installed too low a non-contact lap is proposed. A starter bar of appropriate length will threaded into the coupler and spliced to the main slab reinforcement to create the non-contact lap. Refer to attached PDF - Cxxx-SR-ETH-SB33 which shows the areas in question. The maximum gap in these areas is 40mm. The starter bar will be a minimum 1000mm in length. 2) Between GL4 and GL5. The B2 layer has been installed too low. They are in the cover zone between 19mm and 30mm from the soffit. It is proposed to install cranked bars. This will result in an area of reduced cover over a length of approximately 200mm. Refer to Cxxx-SR-ETH-SB33. Is this proposal acceptable including accepting the area of reduced cover? If it is not acceptable propose to apply a cementitious coating product to provide additional cover once poured. Product used in LSB (Cxxx--C-LRC-M123-50244). Product provides up to an additional 100mm of concrete cover. 3) Between B3C and approximately Gridline 2.5 the B2 layer has been installed too low. It is approximately in B1. propose to install cranked bars to bring the bars back into B2 layer. This will mean that the first three bars in the perpendicular B1 layer adjacent to W21 will be positioned in B2 to accommodate this. B. W22 1) Between the capping beam and GLC the starter bars for the top mat have been installed too low. The distance from top of slab to the bars is 180mm. A non-contact lap is proposed in this location with a 1100mm starter bar. 2) For the remainder of the W22 the bars have been installed too low for the T1 layer and too high for the B1 layer. The maximum distance from the slab face to the rebar, in these areas, is 95mm. A non-contact lap is proposed with a 1100mm starter bar splicing to the main reinforcement. The same length as used in Point 1 is proposed to prevent incorrect installation on site. The proposals for W21 and W22 are detailed in full in the attached sketch, Cxxx-SR-ETH-SB33. In areas that have not been scabbled (as indicated in the sketch) the same solutions as suggested above would be adopted if found to be necessary. C. Missing bars 1) On the survey there are areas that show bars to be missing in localised areas. Further scabbling will be carried out to confirm that the bars are in fact missing. If that is the case the preferred option is to place the reinforcement up to the face of the capping beam and not drill and fix – is this acceptable? If that is not acceptable, propose to drill and fix in these locations. The embedment depth will be in line with the manufacturer’s recommendations. The sheet has been attached to this NCR. ( See __ Post Installed Rebars). A good bond condition is assumed and in this case a 240mm depth of embedment will be carried out.
| 02SL - Stations (LUL) | Cxxx-NCR-001803 | NCR | WTH - Level -1 Internal Walls - Concrete strength of cover spacer blocks used in walls 38, 40, 41, 42 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-04-17 | 2015-04-10 17:22 | -7 | 2015-03-26 15:00 | Civil - Civil Engineering General | 2500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | The strength of the concrete spacers blocks used for the internal walls 38, 40, 41, 42 (MCR – Cxxx--C-LRC-M123-50147 Rev.1.0) is lower than the strength class specified for the concrete used in the walls. Concrete spacers strength is stated as being greater than 40N/mm2 and the according to General Notes Drawing (Cxxx-SWN-S-DDL-M123_Z-00101) concrete strength class for the walls is C50/60. Clarification as agreed in engineering meeting on 31/03/2015: Concrete spacers are double cover type 50x40x20 (20mm thick). Spacers have been fixed on external faces of walls in 1m x 1m grid.
| 02SL - Stations (LUL) | Cxxx-NCR-001804 | NCR | ETH Two Storey Basement Missing couplers in internal wall W20 from level -2 to level -1 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-04-21 | 2015-04-22 14:18 | 1 | 2015-03-30 11:24 | Civil - Civil Engineering General | 2500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | On the internal wall W20 from L-2 to level -1 between GL4 and GL5.5 there are two areas with missing couplers. Please find attached marked up drawings. There are 2 areas with starter bars or couplers missing: Area 1 – north end at W20 GL5.5 3No B32 couplers of starter bars are missing in the NF and FF of W20 at GL5.5 (north end of the wall). The starter bars could not be installed because of rebar congestion. The area in question is the meeting point between the capping beam (east side sloping slab / south side trap shaft) and the beam coming from the north. For that reason does not propose a drill and fix solution but to substitute the couplers with 3No B32 UBars. 73 out of 76 bars have been installed (=96%) anyway. Area 2 – Construction joint at GL4 4No B25 couplers are missing in the NF and FF of W20. proposes to drill and fix the outstanding 4No B25mm bars instead. We managed to achieve 400mm embedment. The embedment length for __ Hit 200 for the failure of a B25mm bar is 624mm (see rebar check calculation). achieved 15No bars with full embedment (installed as per design) and 4No bars with reduced embedment (400mm). This equates to 92.4% of the design requirement. Please find attached "Cxxx--RFI-00527" to __ and __ informal response "__ response to RFI-00527" confirming that the above proposal is acceptable.
| 02SL - Stations (LUL) | Cxxx-NCR-001805 | NCR | SCL - Secondary Lining Surface Finish Bays 1 - 8 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-06-12 | 2015-06-10 10:39 | -2 | 2015-03-31 16:41 | Tunnelling - Linings - In-situ Concrete | 2500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The first 84m section of crown concrete castings in PTE, "Bay 1 - Bay 8", located between chainage CH76.432 - CH160.414 has small localised areas where a class F2 finish has not been achieved. All of these areas are below tunnel axis. The rework for this NCR is unlikely to be completed in a suitable time for package handover, hence Cxxx-PWK-00104 has been opened to capture all outstanding works in bays 1 -8 and going forward.
| 02SL - Stations (LUL) | Cxxx-NCR-001807 | NCR | ETH-Two storey basement Grout loss on Lining wall W22 intersection between section E and G |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-04-20 | 2015-04-02 12:26 | -18 | 2015-03-30 15:52 | Civil - Civil Engineering General | 800 |  | Planning | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | After the striking of lining wall W22 section G formwork, a post pour check was done whereby it was discovered that there was an area of grout loss at the intersection between section G and section E. The length of the area of the intersection requiring repair is 12.5m and height of no more than 100mm (see photos attached).
| 02SL - Stations (LUL) | Cxxx-NCR-001808 | NCR | SCL - failed inspection PTE invert waterbar TM320 (RHS and LHS) |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2015-04-20 | 2015-04-15 11:10 | -5 | 2015-03-30 18:34 | Tunnelling - Linings - In-situ Concrete | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the inspection of the waterbar between TM320 and 340 it was noted that the arrangement of the waterbar junction at TM320 was not crrectly orientated. Please see the attached photo.
| 02SL - Stations (LUL) | Cxxx-NCR-001809 | NCR | ETH-SB Two Storey Basement Missing couplers in drop down beams at L0 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-08-20 | 2015-07-09 19:08 | -42 | 2015-03-31 18:37 | Civil - Civil Engineering General | 2500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | After scabbling work was done on L0, discovered that there are couplers missing in the drop down beams that interface with the capping beam. There are five couplers missing in L0 capping beam (see photos attached in Cxxx-SR-ETH-SB35 and plan in RC Detail of beams drawing) 1. Beam B3A • 1 No B25 coupler missing TOP • 1 No B25 coupler missing BOTTOM 2. Beam B3C • 2 No B25 Couplers missing BOTTOM 3. Beam B1 • 1 No B25 coupler missing TOP propose a solution to drill and fix 5 No B25 starter bars at the postions where the couplers are missing. The steel reinforcement will be drilled and fixed at an embedment depth of 354 mm in line with the manufacturer’s instructions (see attached __ information)
| 02SL - Stations (LUL) | Cxxx-NCR-001811 | NCR | SCL - PTE TH Bay 9 - TM160 to 172 - Failed waterproofing inspection |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2015-04-20 | 2015-04-20 11:12 | 0 | 2015-04-02 09:39 | Tunnelling - Linings - In-situ Concrete | 500 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | During the inspection of the waterproofing of Bay 9 PTE TH (TM160 to 172) the following was noted: 1) CP4 junction - the t-piece on the RHS (looking from PTE towards PTW through CP4) where the collar will be installed was found to have 3no. defective fins (please see photo) 2) The construction joint between the invert and crown of CP4 had not been scabbled.
| 02SL - Stations (LUL) | Cxxx-NCR-001812 | NCR | SCL - RTE2 Pre-regulating - Failed Inspection |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2015-04-30 | 2015-04-30 17:26 | 0 | 2015-04-02 09:49 | Tunnelling - Linings - In-situ Concrete | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During the inspection of the primary lining for pre-regulating purposes, it was noticed that 2no. core holes at TM10 LHS 9 o'clock were not sufficiently grouted creating a potential waterpath.
| 02SL - Stations (LUL) | Cxxx-NCR-001813 | NCR | SCL - Incorrect mix used in CP4 kicker CH |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-08-07 | 2015-08-05 15:37 | -2 | 2015-04-02 12:53 | Tunnelling - Linings - Sprayed Concrete | 20000 |  | Workmanship | Rework | 2 (6-60k) | Complete | Personnel Error - Inattention to detail | Completed |  | The CP4 secondary lining invert kickers between CH -0.776 - 8.782 were poured using 20 (regulating mix) instead of 29. Attached sketches show the affected area. In sketch FCD001569SKC2 Amended the area shown as "pour 2" is the affected area
| 02SL - Stations (LUL) | Cxxx-NCR-001814 | NCR | WTH - Level -1 - Suspended slab soffit - post-pour inspection and tie wire mark on concrete |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-06-19 | 2015-06-18 10:52 | -1 | 2015-04-09 08:09 | Civil - Civil Engineering General | 3500 |  | Workmanship | Repair | 3 (3-6k) | Complete | Personnel Error - Inattention to detail | Completed |  | At WTH level -1 suspended slab, tie wire stains, grout loss and minor honeycombing have been noted on the soffit. The structure had already been inspected after pour and handed over to CRL prior to these defects being noted. There are therefore two failings: 1) concrete finish not achieved and not repaired within 24 hours of discovery 2) post-pour inspection not noting that concrete finish was not achieved
| 02SL - Stations (LUL) | Cxxx-NCR-001815 | NCR | WTH SH-W2 Level -5 to -4 Wall 15 Kicker Pre-Pour Inspection |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2015-04-22 | 2015-04-17 12:48 | -5 | 2015-04-08 14:31 | Civil - Civil Engineering General | 750 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | The CRL FE was invited to attend Pre-Pour Inspection for WTH SH-W2 Level -5 to -4 Wall 25 and Wall 15 (kicker only) on 08/04/2015. All checks were confirmed as having been previously completed by with no issues identified (as recorded by on the Pre-Pour Inspection Checksheet). No issues were noted by CRL following the inspection to Wall 25. However, during the inspection of the Wall 15 kicker the CRL FE noticed that the cover on the southernmost 500mm length of the west face of the kicker was approximately 70mm, and the cover on the equivalent length on the east face of the wall was less than 40mm. Refer to attached site photographs. Both of these values are outside the permitted limits accepted under Cxxx-FC D-00974 (where the design cover is stated as 50mm, 45-60mm cover is allowed for sections of thickness less than 1000mm - Wall 15 is 500mm thick).
| 02SL - Stations (LUL) | Cxxx-NCR-001816 | NCR | SCL Crack Width in PTE Bay 6 Crown Pour Exceeds 0.3mm |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-08-28 | 2015-08-18 08:22 | -10 | 2015-04-09 14:06 | Tunnelling - Linings - In-situ Concrete | 2500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | A crack has been identified in bay 6 crown PTE cast Secondary Lining which is greater than 0.3mm. The crack is located on the following chainages CH137.8 to CH140.42, measuring 2.625m long and 0.38mm wide and is situated directly at the top of the crown of the pour. Bay 6 is the only bay for which the leading edge crack is greater than 0.3mm, other bays have developed similar cracks but all have been less than 0.3mm.
| 02SL - Stations (LUL) | Cxxx-NCR-001817 | NCR | WTH SH-W2 Level -5 Void 7 Covers |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-04-23 | 2015-04-14 12:51 | -9 | 2015-04-09 15:54 | Civil - Civil Engineering General | 750 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | The steel void covers for Level -5 opening 7 have been fabricated to the wrong size. The covers have been fabricated to a length of 4390mm (+/- 2/3mm) instead of the design length of 4370mm.
| 02SL - Stations (LUL) | Cxxx-NCR-001818 | NCR | ETH South Basement - Lining Wall W21 Pour J - localised grout loss |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-04-23 | 2015-04-24 12:42 | 1 | 2015-04-09 18:04 | Civil - Civil Engineering General | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | After striking the shutters for lining wall W21 Pour J it was found that there had been some localised grout loss in the area below the pouring hole.
| 02SL - Stations (LUL) | Cxxx-NCR-001819 | NCR | WTH SH-W2 Level -5 - Wall 6 East lower - reduced cover |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-04-27 | 2015-04-16 08:12 | -11 | 2015-04-13 19:16 | Civil - Civil Engineering General | 750 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | In SHW2, Wall 6 East 1st 2.2m pour from the -5 slab, the bottom 1m of the wall has reduced cover of 35mm and the 0.5m above has 40mm cover between walls 11 and 15. The bars cannot be moved in anymore due to the rigidity of the vertical bars cast into the wall below. See attached (Cxxx-NCR-001819 Wall 6 reduced cover area) location of reduced cover in plan and elevation.
| 02SL - Stations (LUL) | Cxxx-NCR-001820 | NCR | WTH - SHW3 Water ingress issues through secant pile wall |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-06-05 | 2015-06-02 12:43 | -3 | 2015-04-10 10:52 | Shafts - Shafts General | 6000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A inspection of the remaining exposed sections of the SHW3 secant pile wall has shown that 3no. areas of water ingress have developed beyond that of what is acceptable under the Cxxx specification (KP10.1301 Section B9.4.5 a)). Water was observed dripping down the inside face of the piles at a rate of approximately 1 drip/10 seconds. The piles in question are E506 (Area 1), E508 (Area 2) and E530 (Area 3). These are shown in the attached 'Water Ingress Report' - please also see the attached marked-up drawing which provides a location key. note this inspection was carried out in accordance with SPERW Section B1.9.1 'Inspections', with the correct weather conditions observed. The 3no. areas are at the joint between the soffit of the capping beams and the top of female piles – this falls outside the guidance of SPERW (see Section B1.9.2, highlighted extract attached) which states “responsibilities for the management and/or repair of these types of leaks shall, where appropriate, be identified in the Project Specification”. In the absence of any guidance in the Cxxx Specification, propose to use the crack injection method to inject a hydrophobic injection grout/resin behind the crown of the piles in accordance with guidance from the Technical Manager of __, ’s specialist waterproofing supplier. The datasheet for the proposed injection resin and a pdf of __’s (__ Construction Technical Manager) email which recommends its use are both attached. An MCR will be submitted for the resin.
| 02SL - Stations (LUL) | Cxxx-NCR-001821 | NCR | SCL - PTE Waterproofing and pre-pour inspections (Crown: Bay 9; Invert: Bay 10 & 13) - Incomplete IRFs presented |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2015-04-30 | 2015-04-27 12:25 | -3 | 2015-04-10 13:17 | Tunnelling - Linings - In-situ Concrete | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Inspector not familiar with inspection methods | Completed |  | IRFs were presented for the pre-pour inspection of PTE crown Bay 9 and waterproofing inspections of PTE inverts Bay 10 and 13. The following issues were found: Bay 9 Crown Pre-pour - Check sheet SF-CON-212_01: 1) Substrate inspection not completed and signed. 2) Rebar inspection not signed for. Bay 10 Invert Waterproofing - Check Sheet SF-CON-214_00: 1) Number of fixing discs not recorded for the installation of the geotextile as per the check sheet Bay 13 Invert Waterproofing - Check Sheet SF-CON-214_00 1) Number of fixing discs not recorded for the installation of the geotextile as per the check sheet 2) Re-injectible hose installation marked as complete with sub-contractor signature with a contradictary note stating that installation had not yet been completed.
| 02SL - Stations (LUL) | Cxxx-NCR-001822 | NCR | SCL - Failed Waterproofing Inspection - PTE Bay 13 Invert TM296 to 320 |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2015-05-21 | 2015-05-18 13:42 | -3 | 2015-04-10 17:02 | Tunnelling - Linings - In-situ Concrete | 1000 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | During the inspection of the invert waterproofing for PTE Bay 13 TM296 to 320 the following was found to be non-compliant: 1) TM307 T-pieces on the RHS and LHS were found to be defective (3no. LHS and 3no. RHS) 2) TM296 T-pieces on the RHS and LHS were found to be defective (1no. LHS and 2no. RHS) 3) TM315 Repair patch not tested just left of centre Sides indicated looking towards PL3.
| 02SL - Stations (LUL) | Cxxx-NCR-001823 | NCR | ETH - Trapezoidal Shaft - Level -3 - ES2 second lift incomplete pour |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-05-04 | 2015-05-05 09:52 | 1 | 2015-04-13 07:16 | Civil - Civil Engineering General | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following the removal of shutters on ES2 second lift, became aware that the pour was not completed. Please see attached photo.
| 02SL - Stations (LUL) | Cxxx-NCR-001824 | NCR | Barbican Station Piling Platform |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-04-27 | 2015-04-24 16:10 | -3 | 2015-04-13 10:58 | Civil - Civil Engineering General | 750 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | The material compaction record sheets (Cxxx-SF-CON-0047_00) for the piling mat installation are not available from our Sub-contractor. The check sheets are a deliverable under the ITP for the works and are to be included in the handover package.
| 02SL - Stations (LUL) | Cxxx-NCR-001825 | NCR | WTH SHW3 Damage to hydrophilic strip laps at vertical joints of lining walls |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-05-14 | 2015-05-14 11:31 | 0 | 2015-04-14 11:03 | Civil - Civil Engineering General | 4000 |  | Damaged | Repair | 3 (3-6k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | At the vertical construction joints in the WTH escalator shaft lining walls, left the 100mm lap of __ 500S hydrophilic strip protruding from the concrete as per the approved lap detail, in anticipation of the follow-on pours. This was protected by a timber box. Unfortunately the 100mm lap has been destroyed by the SCL team at both the midlevel CJ and on the kicker of the North and South lining walls (Walls 26 & 28). NOTE: please ignore pdf attachment 'hydrophilic lap remedial works', this has been superseded by SK-MP-03.
| 02SL - Stations (LUL) | Cxxx-NCR-001826 | NCR | WTH SH-W2 Wall 16 Kicker Concrete Quality |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-04-28 | 2015-04-23 11:43 | -5 | 2015-04-14 15:54 | Civil - Civil Engineering General | 750 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The 200mm high kicker for wall 16, that was previously cast with the -5 slab, required beyond the usual amount of scabbling due to a localised section of pour quality concrete with little visible aggregate. The area covered approx. 0.5m long and was scabbled down a maximum of 100mm.
| 02SL - Stations (LUL) | Cxxx-NCR-001827 | NCR | SCL - Honey Combing on Crown pour Bay 9 (Ch160.414 - Ch172.314) |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-08-14 | 2015-08-03 11:41 | -11 | 2015-04-16 08:56 | Tunnelling - Linings - In-situ Concrete | 3500 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | There are areas of honey combing located at the PTE/CP4 secondary lining junction pour. Location is RHS (looking towards CP6) two areas at approximately CH 166 (1.5m above invert level) and CH 162 (2m above invert level) See attached pictures
| 02SL - Stations (LUL) | Cxxx-NCR-001828 | NCR | SCL - BFK 29 Concrete - Shorter Steel Reinforcement Fibres |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-05-19 | 2015-05-12 13:55 | -7 | 2015-04-16 10:29 | Tunnelling - Linings - In-situ Concrete | 2500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | KF10.1409 (a) (iii) states that steel fibres for insitu concrete "shall have a minimum length of 50mm". 29 mix uses LH35/0.7 __ Fibres which are 35mm in length. This is detailed in MCR Cxxx--C4-LRC-M123-50124. Fibre size and dosage is the same as per the primary lining mix ( 17.2) as flexural requirements are the same. See attached test results from December 2014 monthly testing which show that use of the shorter fibres has no adverse effects on drying shrinkage nor compressive strength as well as exceed the flexural strength requirements of the lining. 29 mix is compliant with all performance requirements as required in KF10. This concrete has been poured for the secondary lining works to date (~2500m3). Specific Locations are: - PTE CH12-CH354 Inverts PTE CH76-CH208 Crowns CP4 Invert and Collar
| 02SL - Stations (LUL) | Cxxx-NCR-001829 | NCR | WTH - SHW2 Re-injecto grout tube ports unaccessible (Level -8 to -6) |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-02-17 | 2016-02-11 16:30 | -6 | 2016-01-20 17:06 | Civil - Civil Engineering General | 3500 |  | Incorrect Installation | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 5no reinjecto tube ports (potentially 4no loops) on wall 7 between levels -8 and -6 cannot be located. (see attached survey)
| 02SL - Stations (LUL) | Cxxx-NCR-001830 | NCR | SCL - Deviations from EUREKA Curve during BFK 21 Fire Testing |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-05-28 | 2015-05-15 14:54 | -13 | 2015-04-16 13:43 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | __ have tested 21 for compliance to the fire proofing requirement as given in KT24. __ encountered several non conformances which are listed in pages 27 to 29 of the revised __ report, 135323-1 . Specifically, these are related to adherance to the EUREKA curve as detailed in Figure KT24-01. 1. The furnace temperature between 0 and 6 minutes was outside of the specification limits. 2. The time when sample reached 1200 degrees celsius ± 20% to the cooling phase was 54 minutes rather than the 55 minutes given in the specification. 3. The time between 60 and 170 minutes, the cooling phase falls below the minimum temperatures given in the specification. Energy consumption was not achieved during this period. 4. The test used an open furnace rather than an enclosed furnace.
| 02SL - Stations (LUL) | Cxxx-NCR-001831 | NCR | ETH - Trapezoidal shaft: L-3 W11a missing couplers |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-05-06 | 2015-05-05 13:26 | -1 | 2015-04-16 14:33 | Civil - Civil Engineering General | 2500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | It was identified that 18No couplers are missing from L-2 soffit located on top of Wall11a opening as shown in sketch SK-THM-544-01. propose to install 8No U-bars to lap onto the existing BM54 and 16No additional 32mm bars 8EF @300mm c/c to bridge over the opening as shown on sketch SK-THM-544-02. We want to avoid drill and fix solution into L-2 slab, due to the location of the geothermal pipes which could be damaged. Please note from a detailing point of view __ have no objection regarding our proposal.
| 02SL - Stations (LUL) | Cxxx-NCR-001833 | NCR | ETH - Trapezoidal shaft: L-3 W11a wrong starter bars diameter |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-05-06 | 2015-05-05 07:31 | -1 | 2015-04-16 16:21 | Civil - Civil Engineering General | 2500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | During the construction of L-3 slab drawing Cxxx-ATK-S-DWG-M123_4-50110 C07 was used to install walls starter bars for W11a. This drawing detailed the starter bars as 25mm diameter which is incorrect and should have been 32mm. Drawing Cxxx-ATK-S-DWG-M123_Z-50600 C03 shows the correct vertical bars of 32mm, which we propose to fix onto the existing 25mm starter bars.
| 02SL - Stations (LUL) | Cxxx-NCR-001834 | NCR | SCL - Failed Waterproofing Inspection - PTE TM 172 to 184 - Crown |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2015-05-21 | 2015-05-06 17:07 | -15 | 2015-04-21 09:49 | Tunnelling - Linings - In-situ Concrete | 500 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | During the inspection of the crown waterproofing in PTE between TM172 and 184 on Saturday 18/04/15, the following was noted: 1) the sheet membrane had not been adequately cleaned 2) Hardened concrete had not been removed from the waterbar; the waterbar had not been sufficiently cleaned Please see the attached photos (please note the title of the photos is misleading - please see date and time stamp on same).
| 02SL - Stations (LUL) | Cxxx-NCR-001835 | NCR | SCL - Failed waterproofing inspection - PTE TM 196 to 208 - Crown |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2015-05-15 | 2015-05-08 13:45 | -7 | 2015-04-21 10:02 | Tunnelling - Linings - In-situ Concrete | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | During the crown waterproofing inspection of PTE TM 196 to 208 a hole was found through a fin in the waerbar T-piece on the RHS at TM208 - please see the attached photo. The hole was repaired during the inspection.
| 02SL - Stations (LUL) | Cxxx-NCR-001836 | NCR | SCL - Failed waterproofing inspection - PTE crown - TM296 to 320 |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2015-05-14 | 2015-05-09 16:35 | -5 | 2015-04-23 09:28 | Tunnelling - Linings - In-situ Concrete | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | During the waterproofing inspection of the crown between TM296 and 320 in PTE one area of the waterbar at ~10 o'clock (facing STW2) TM320 failed the hook test. Please see attached photos.
| 02SL - Stations (LUL) | Cxxx-NCR-001837 | NCR | ETH Two Storey Basement - Missing CWD at level -1 midlanding 111.534 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-05-14 | 2015-05-14 13:20 | 0 | 2015-04-23 18:29 | Civil - Civil Engineering General | 1500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Personnel Error - Verbal communication problem | Completed |  | During the construction of the ESS5 midlanding at 111.534 in the Two Storey Basement, did not realise that a CWD had to be installed in the landing as shown on Cxxx--P-DDA-M123_2-25203 P06 (see attached "Missing CWD at level -1 midlanding").
| 02SL - Stations (LUL) | Cxxx-NCR-001838 | NCR | Reinforcement at PTE/CP4 Crown Secondary installed 200mm short of contraction joint |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-05-29 | 2015-05-18 16:43 | -11 | 2015-04-23 12:38 | Tunnelling - Linings - In-situ Concrete | 2500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | The secondary lining reinforcement on the PTE/CP4 junction should have protruded from the construction joint between PTE TH bay 9 and TH bay 10 (Chainage 172.314) into the TH bay 10 by 356mm (crack inducer location is at chainage 172.770). However on the RHS (facing the headwall) the far face reinforcement from approx 3 o'clock down to the TH/Invert construction joint was 100mm short, protruding approximatly 250mm only from the Bay9/Bay10 construction joint.
| 02SL - Stations (LUL) | Cxxx-NCR-001839 | NCR | SCL - Non Approved Junction Boxes Installed in PTE Crown Pour CH196-208 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-06-26 | 2015-06-15 21:58 | -11 | 2015-04-24 14:15 | Tunnelling - Linings - In-situ Concrete | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | Plastic junction boxes were cast into the PTE Crown Pour, Bay 12 Chainage 196 to 208. These boxes are not approved materials as they are not LU compliant, nor do they have an approved MCR.
| 02SL - Stations (LUL) | Cxxx-NCR-001842 | NCR | ETH - Trapezoidal Shaft Level -3 - Wall 11 - Not Enough Cover on Chamfer |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-05-14 | 2015-05-14 15:44 | 0 | 2015-04-23 17:44 | Civil - Civil Engineering General | 2000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Having struck the shutter on the chamfer of Wall 11 Level -3 (South West face) have found a number of exposed reinforcement bars. have then conducted an as built survey on the face of the concrete which has clearly shown the shutter has not been installed in the correct position, please see attached as built survey. The shutter is effectively leaning into the wall, from the correct position at the bottom of the wall to the worst instance at the top where the cover has been reduced by 27mm.
| 02SL - Stations (LUL) | Cxxx-NCR-001843 | NCR | SCL - CP1/PL2 Foam Concrete Backfill Struck Without Permit to Strike |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-05-08 | 2015-05-01 13:27 | -7 | 2015-04-24 08:43 | Tunnelling - Linings - In-situ Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Verbal communication problem | Completed |  | The formwork for the foam concrete backfill for CP1/PL2 was struck before the permit to strike had been issued. Pour finished on 21/04/2015 at 4pm, shutters were being struck at 8am on 22/04/2015. Foam concrete strike cube was not crushed until 10:30am and permit to strike was signed off at midday on the 22nd. This is a four hour gap.
| 02SL - Stations (LUL) | Cxxx-NCR-001844 | NCR | WTH-SHW3 Lining Walls - Concrete repairs |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-07-31 | 2015-07-31 10:57 | 0 | 2015-04-24 16:35 | Shafts - Linings | 5000 |  | Damaged | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | Upon handover of SHW3 from the tunnelling team to the WTH civils team it is apparent there are several areas of the lining walls which have been damaged and will require concrete repairs. This NCR will be updated once access is available to complete a full survey of the lining walls.
| 02SL - Stations (LUL) | Cxxx-NCR-001845 | NCR | WTH External vibrators being used on outside of formwork |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-05-29 | 2015-05-13 14:09 | -16 | 2015-04-28 15:58 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | During a surveillance on the 15/4/15 it was observed that external vibrators were being used on the wall shutters. KF 10.3204 states that c) External vibrators shall only be used when set out in the Method Statements. No reference to their use could be found in the method statement for these works Cxxx--C-GMS-M123-50330
| 02SL - Stations (LUL) | Cxxx-NCR-001849 | NCR | WTH SH-W2 Timber cast into Level -7 Soffit |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-07-03 | 2015-06-30 17:50 | -3 | 2015-04-29 07:56 | Civil - Civil Engineering General | 1500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Similarly to Cxxx-NCR-001778, it has since been noticed that two small pieces of plywood are visible in the underside of the Level -7 soffit between Walls 7 & 15(see attached photograph). These are present due to services coming through the Level -7 slab until it was poured at which point they were blocked up by placing plywood on top of the hole.
| 02SL - Stations (LUL) | Cxxx-NCR-001850 | NCR | ETH Two Storey Basement misaligned as built couplers in capping beam L0 West |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-05-19 | 2015-05-19 13:49 | 0 | 2015-05-01 15:07 | Civil - Civil Engineering General | 3500 |  | Incorrect Installation | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | has scabbled the underside of Capping beam Level 0 West to expose the couplers fixed from GL3 to the end of capping beam heading northwards. These couplers are required for the construction of Lining Wall W23 from level -1 to level 0. A total number of 11 couplers at the Near Face of this capping beam have been fixed incorrectly over a length of 1900mm. As these couplers are B20, have drilled 11No 25mm diameter holes through the underside of the capping beam and achieved an embedment of 500mm apart from one hole which has a depth of 250mm due to the congestion of the steel. See attached marked up drawings.
| 02SL - Stations (LUL) | Cxxx-NCR-001851 | NCR | SCL - BFK 21 - Pre-Stressing of Concrete not in Accordance with KT24 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-05-25 | 2015-05-15 15:03 | -10 | 2015-05-11 09:46 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Other | Completed |  | In testing 21 for fire loading, __ only loaded the cast section of the secondary lining and not the sprayed. Please see attached drawing showing where the loading occured and a picture of the test set up. KT24.2214 (i) states that "The test samples shall be subject to an external applied uni-axial stress of 5MPa for the duration of the test."
| 02SL - Stations (LUL) | Cxxx-NCR-001852 | NCR | SCL - ES1 primary lining transition profile incorrect |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-07-31 | 2015-07-21 08:41 | -10 | 2015-05-05 18:07 | Tunnelling - Linings - Sprayed Concrete | 30000 |  | Software | Repair | 2 (6-60k) | Complete | Verification Problems - Other | Completed |  | ES1 has been constructed with a profile that is out of tolerance. Between approximate chainages Ch.11.8 & 15.8 the crown of the tunnel has been constructed approximately 1m higher than the design. Minimum thickness has been achieved. Between approximate chainages Ch.15.8 and 19.5 the crown of the tunnel has been constructed approximately 250mm lower than the design. The minimum thickness has been achieved. Please also see attached sketch001 showing as built against design spray profile for more information.
| 02SL - Stations (LUL) | Cxxx-NCR-001853 | NCR | SMM - Reporting Of 10mm Alert In All Directions |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-07-22 | 2015-07-21 09:43 | -1 | 2015-05-05 16:44 | Surveying - Instrumentation and Monitoring | 2500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | As per The Project Managers request this non-conformance is being raised as document Cxxx-OVE-C2-RGN-M123-50013 Cection 6.2 Alert Values for Construction Control was not conformed to as per the project managers expectations. 'The alerts will be investigated and, where the movement is shown to be in accord with the predicted assessment, the alert will be re-set to a higher default alert value for subsequent stages of work, subject to the approval of the Project Manager.' The Contractor showed the 10mm alert through the graphs in the SRG but did not note them in the minutes.
| 02SL - Stations (LUL) | Cxxx-NCR-001854 | NCR | ETH Use of Incorrect Formula for Vertical Shutter Striking |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-06-05 | 2015-05-19 14:51 | -17 | 2015-05-08 10:25 | Civil - Civil Engineering General | 850 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | The incorrect formula (300/t+10) was used on a permit to strike for a lining wall. The formula used was for a concrete made with 100% OPC and not a concrete made with a blended GGBS/cement which was used.
| 02SL - Stations (LUL) | Cxxx-NCR-001855 | NCR | WTH SH-W2 Concrete Placement between Walls 10 & 11 at Level -5 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-02-02 | 2015-11-06 10:02 | -88 | 2015-05-21 13:07 | Civil - Civil Engineering General | 2500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | When the second lift formwork of Wall 6 West between Levels -5 & -4 was struck, there was evidence of layers in the pour. The wall was jetwashed (to receive __ waterproofing at a later date) and the layers remained. Further investigation is required at the affected locations. These will be locally scabbled back to determine to what depth the layers persist. If the layers continue past 40mm (from concrete face) scabbling will stop to ensure the reinforcement is not exposed.
| 02SL - Stations (LUL) | Cxxx-NCR-001856 | NCR | SCL - Junction Boxes Not Approved Before Use in Secondary Lining |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-05-25 | 2015-05-12 14:00 | -13 | 2015-05-06 16:44 | Tunnelling - Grouting | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | The aluminium junction boxes being used in all secondary lining pours to date are currently not approved through the MCR procedure. Although the junction boxes are on the LU approved register, they have not been formally submitted for Crossrail approval.
| 02SL - Stations (LUL) | Cxxx-NCR-001857 | NCR | ETH - Trapezoidal Shaft - Level -3 - Wall 7 honeycombing |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-09-04 | 2015-08-17 16:09 | -18 | 2015-05-07 12:26 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following striking of Wall 7 Level -3 a small section has been identified to have honeycombing. Currently do not have access to this section works so an accurate survey still needs to be conducted.
| 02SL - Stations (LUL) | Cxxx-NCR-001858 | NCR | ETH - Trapezoidal Shaft - Level -4 - Mining hole missing bars |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-05-21 | 2015-05-13 07:17 | -8 | 2015-05-07 17:46 | Civil - Civil Engineering General | 2500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | After exposing mining hole starter couplers for Level -4 Mining Hole, became aware of 7No couplers in the South West corner that could not be found. Please see attached photo and sketch for location. propose to use as is. The 7No couplers missing from the west side result in 94% of bars installed meeting the RC intent on this side only.
| 02SL - Stations (LUL) | Cxxx-NCR-001860 | NCR | WTH SH-W2 Level -4 – Opening 1 short void prop |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-09-28 | 2015-08-26 10:35 | -33 | 2015-05-08 19:21 | Civil - Civil Engineering General | 2000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Regarding the void propping installed in Opening 1 in the Level -4 slab the southern end plate is short of the construction line for wall 16 by 14mm. As such the wall (part of the -4 slab pour) has been cast up to this end plate which will leave a projection of concrete out of the wall line once the prop is removed. See attached site photos.
| 02SL - Stations (LUL) | Cxxx-NCR-001861 | NCR | SCL - Failed Waterproofing Inspection - CP4 TM18.3 to 26.5 |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2015-06-12 | 2015-06-09 10:30 | -3 | 2015-05-11 08:51 | Tunnelling - Linings - In-situ Concrete | 500 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During the inspection of the waterproofing in CPR between TM18.3 and 26.5 damage to a fin of the waterbar at TM18.3 (RHS looking towards PTW). The waterbar had not been sufficiently cleaned of hardened concrete from the previous pour.
| 02SL - Stations (LUL) | Cxxx-NCR-001862 | NCR | WTH SH-W2 Level -4 wall 6 finish (between wall 10 and 11) |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-08-18 | 2015-08-18 17:45 | 0 | 2015-05-13 12:39 | Civil - Civil Engineering General | 1000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A section of Wall 6 was poured as part of the level -4 slab in the lift shaft void. After striking the slab shutters between walls 10 and 11, some foam has been found cast within the concrete cover zone (see attached photo). The foam is located halfway between walls 10 and 11, at the construction joint with wall 6 below (see attached sketch). Additionally, there is a 20mm step in wall 6 approximately 265mm from wall 11 (see attached photo).
| 02SL - Stations (LUL) | Cxxx-NCR-001866 | NCR | WTH - Level -1 Internal Walls 40, 41, 42 concrete finish below F2 standard |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-09-25 | 2015-09-25 15:10 | 0 | 2015-05-12 09:02 | Civil - Civil Engineering General | 3000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | After removal of formwork from walls 40, 41 & 42 the concrete finish was discovered to be below F2 standard. The face contains sporadic 5-20mm blow holes, discoloration and honeycomb in a single location immediately above the kicker line of wall 42 south face.
| 02SL - Stations (LUL) | Cxxx-NCR-001867 | NCR | SMM- Blocked TaM CHS TCS201 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-05-28 | 2015-05-15 12:49 | -13 | 2015-05-12 18:26 | Geotechnical Engineering - Compensation Grouting | 2500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Whilst dipping the TaMs in Charterhouse grout shaft (06.05.15), as part of the maintenance works. The double packer got stuck within TAM TCS021 at a depth of 2.75m. A number of attempts have been made to try and remove the line, but with no avail. As a result TAM TCS021 is now non-operational, the cause of the blockage is possible harden grout lodging the packer in place. The adjacent TaMs 20 & 22 is still available for compensation grouting.
| 02SL - Stations (LUL) | Cxxx-NCR-001869 | NCR | ETH - SB L-2 Internal Wall W19 - missing starter bars |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-05-27 | 2015-05-22 11:07 | -5 | 2015-05-13 15:50 | Civil - Civil Engineering General | 2500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | After removal of thrust blocks and exposure of starter bars on Level L-2 it became apparent that there are 6no B16 starter bars BM 82 (Cxxx-ATK-S-DWG-M123_3-50116) missing per face in the capping beam / top of L-2 slab for internal wall W19. It appears that the couplers are missing either side of the thrust blocks used for the Temporary Secondary Props.
| 02SL - Stations (LUL) | Cxxx-NCR-001870 | NCR | ETH - SB Internal Wall W30 - excess concrete cover |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-07-17 | 2015-07-08 16:46 | -9 | 2015-05-14 13:38 | Civil - Civil Engineering General | 2500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | There is an excess concrete cover at internal wall W30 at the underside of the L0 slab. The access cover was caused by the vertical reinforcement being tied together at the top during the concrete pour. The bars were not released directly after the pour. The design concrete cover is supposed to be 30mm below the L0 slab. Currently it can only be measured between the vertical bars (BM67 and BM68) and the edge of the wall. The measurement needs to be reduce by 16mm to allow for the horizontal lacer in NF1 / FF1 (BM16 and BM17). The worst case measured is locally 85mm in the SE corner of the wall which results in an excess cover of 39mm (85mm - B16 bar = 69mm - 30mm = 39mm excess cover). On average 65mm to 75mm can be measured which results in an excess cover of 19mm to 29mm.
| 02SL - Stations (LUL) | Cxxx-NCR-001871 | NCR | WTH SHW3 - honeycombing in stage 2 lining wall pour 1st lift |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-07-31 | 2015-07-27 15:51 | -4 | 2015-05-14 17:43 | Civil - Structural Engineering | 3000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Following the striking of the shutters & void formers for the 1st lift of the SHW3 lining walls stage 2 pour, multiple areas of honeycombing have been identified. Please see the attached photos - each photo is titled with a description of it's location.
| 02SL - Stations (LUL) | Cxxx-NCR-001872 | NCR | Misalignment of Couplers in capping beam for Level 0 along W23 interface |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-08-21 | 2015-07-09 19:13 | -43 | 2015-05-15 17:19 | Civil - Civil Engineering General | 2500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | have carried out a survey of the couplers for the Level O Slab along W23 Interface. A few areas require a remedial solution as the couplers have not been installed to the correct alignment similar to issues described in NCR-1802. proposal is based on the proposed solution for NCR-1802.
| 02SL - Stations (LUL) | Cxxx-NCR-001873 | NCR | SCL - Crack in Primary Lining - In PTW/CP4 junction |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-06-12 | 2015-06-12 10:34 | 0 | 2015-05-15 15:04 | Tunnelling - Linings - Sprayed Concrete | 2500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | Longitudinal crack has appeared in PTW crown next to CP4 junction. Chainages 203.1 to 193.9. The crack varies in width from 1.2mm to 2.5mm and is stable. Please find attached an extract of the crack register to this NCR with the crack L1 highlighted.
| 02SL - Stations (LUL) | Cxxx-NCR-001874 | NCR | WTH SH-W2 Level -5 – Opening 1 concrete repairs |  | Contr | 201068 | FAR - Farringdon Station (West) |  | 2015-08-07 | 2015-07-01 17:22 | -37 | 2015-05-20 15:26 | Civil - Civil Engineering General | 3000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | When the void propping and angles for the void covers were removed from void 1 level -5 a number of concrete repairs were identified as required. See attachment showing locations and photos of the various areas requiring repair. Types of repair are: • Misaligned surfaces • Foam removal (foam cast into wall)
| 02SL - Stations (LUL) | Cxxx-NCR-001876 | NCR | SCL - Secondary Lining Crown Bay 16 [TM320.067-331.722] out of finish tolerance |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-07-30 | 2015-07-05 13:56 | -25 | 2015-05-26 10:57 | Tunnelling - Linings - In-situ Concrete | 2500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Secondary lining Crown Bay pour 16, TM320.067-331.722 is out of the specified finish tolerance. The magnitude of the error is approximately +45 mm on train side, -30mm on platform side. Attached for further details: - Sketch showing locations and set-out position - As-built surveys of the bay - As-built comparison of before and after surveys to demonstrate minimum thickness
| 02SL - Stations (LUL) | Cxxx-NCR-001877 | NCR | ETH-Two Storey Basement Internal wall W31 step in on concrete finish |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-06-30 | 2015-06-12 12:05 | -18 | 2015-05-29 10:10 | Civil - Civil Engineering General | 1500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | After striking the formwork on internal wall W31, a post pour check was done whereby it was discovered that there was area where the concrete steps 17mm in on the wall finish see attached photo 'W31 concrete finish photo'. Following the reinforced concrete ITP Cxxx--C-ITP-M123-50009 Rev 7.0 parameters concerning formwork erection section 20.4 see attached page 'Concrete ITP formwork erection', this comprises the cover on the wall finish.
| 02SL - Stations (LUL) | Cxxx-NCR-001878 | NCR | WTH SH-W2 Shear links being fixed to NF2 bars |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-06-12 | 2015-06-01 16:24 | -11 | 2015-05-29 14:26 | Civil - Civil Engineering General | 2500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | On striking the Wall 8 West 1st lift shutters it has been noticed that the first horizontal lacer for the 2nd lift has been cast slightly into the 1st pour. This has come about as the grout check which they were pouring to was installed incorrectly. The shear links should be fixed to the NF1 (lacer) bars. As this bar is slightly cast into the 1st pour it is not possible to install the shear links to the NF1 bar. Photographs and location sketch attached.
| 02SL - Stations (LUL) | Cxxx-NCR-001879 | NCR | WTH SH-W2 Insufficient cover to Wall 13 starter bars |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-06-09 | 2015-06-03 17:45 | -6 | 2015-06-02 16:25 | Civil - Civil Engineering General | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | Wall 13 in SH-W2 has been poured to a level of +86.760m. Two vertical reinforcement bars at this level in the NE corner of the wall (sketch attached) have insufficient cover. The cover should be 40mm whereas these bars have between 15 and 20mm cover (see photos attached).
| 02SL - Stations (LUL) | Cxxx-NCR-001880 | NCR | SCL - Secondary Lining Surface Finish PTE CH319.822 - CH331.722 BAY 16 Triple Junction Crown Pour |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-10-06 | 2015-10-02 15:41 | -4 | 2015-06-03 13:11 | Tunnelling - Linings - In-situ Concrete | 1500 |  | Material | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Following the striking of PTE CH319.822 - CH331.722 secondary lining BAY 16 triple junction crown pour, minor honey combing to the LHS (down chainage toward ETH) was visible and therefore not compliant with the F2 finish required. The location is approximately at axis level and predominantly over the length of the 11.9m bay casting.
| 02SL - Stations (LUL) | Cxxx-NCR-001881 | NCR | SCL - Secondary Lining Crown Pour BAY 19 PTE CH319.822 - 307.922 Missing Junction Box |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-11-13 | 2015-10-29 10:08 | -15 | 2015-06-04 14:19 | Tunnelling - Linings - In-situ Concrete | 2500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Following the striking of the Secondary Lining Crown Pour BAY 19 PTE CH319.822 - 307.922, it was noticed that junction boxes for the reinjectable hoses were missing from the rear of the shutter. The location is at chainage 319.322. The hoses were fed through a hole in the shutter instead of going into the junction box as per the waterproofing system design. This therefore does not conform with the design via incorrect installation.
| 02SL - Stations (LUL) | Cxxx-NCR-001882 | NCR | WTH - SHW3 Lining walls concrete pour 1hr time limit exceeded |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-07-31 | 2015-07-15 17:21 | -16 | 2015-06-05 10:57 | Civil - Structural Engineering | 3000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | During the concrete pour for the 2nd lift of the remaining sections of the lining walls in SHW3 the 1hr time limit for placement of in-situ concrete was exceeded. The 3rd wagon finished being placed at 14:00 and the 4th wagon started placing concrete at 15:52 (1hr 52mins between loads). It should be noted minimised the time between placing of concrete as much as reasonably possible by placing the 3rd wagon of concrete very slowly but could not slow it down enough to prevent the 1hr 52min time between wagons - this was caused by external factors beyond the control of . Please see attached 'honeycombing' photo showing potential cold joint region.
| 02SL - Stations (LUL) | Cxxx-NCR-001883 | NCR | WTH SH-W2 Level -4 to -3 Wall 6 Construction Joint Not Cast Horizontally |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-06-19 | 2015-06-19 10:11 | 0 | 2015-06-05 16:52 | Civil - Civil Engineering General | 1000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Insufficient quantity of material to do the job | Completed |  | The lining walls in SH-W2 are being poured in two lifts. The first lift of Wall 6 West on the Level -4 slab was being poured when it was discovered we were approximately 1.5m3 short of concrete to finish and were unable to get further concrete. At the Western end of the pour there is a small slope, approximately 1.5m long on Wall 6 and a metre long on the Wall 9 return, where we had to finish the pour and so we are unable to form a horizontal construction joint (see Photo 1 atached).
| 02SL - Stations (LUL) | Cxxx-NCR-001884 | NCR | WTH - SHW3 Lining walls 2nd lift void in pour |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-06-29 | 2015-06-29 10:23 | 0 | 2015-06-08 09:59 | Civil - Structural Engineering | 3500 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Management Problem - Inadequate supervision | Completed |  | poured the second lift of the remaining sections of lining walls in SHW3 on 03.06.15. Please see the marked-up sketch in the appendix showing the pour area. Striking the formwork has revealed a void at the joint between the top of the lining walls and the capping beam soffit in the East Wall (Wall 27). The void is 2.5m wide, a maximum of 250mm deep and is the full depth of the lining wall (i.e. back to the face of the piles). Please see the photo attached to this NCR.
| 02SL - Stations (LUL) | Cxxx-NCR-001885 | NCR | ETH- Trapezoidal Shaft L-3 W9 not poured to full height |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-07-07 | 2015-07-06 16:16 | -1 | 2015-06-23 09:58 | Civil - Civil Engineering General | 1200 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate resources | Completed |  | At Level-3 on Wall 9 , the concrete pour did not reach the full height of the wall In the North Section of the wall ,this has left voids of varying heights along the wall from 120mm to 220mm for an over length of 2220mm . In the Southern End of the Wall , there is a taper varying from 15mm to 130mm over a distance of 850mm . Please see photo and sketch attached .
| 02SL - Stations (LUL) | Cxxx-NCR-001886 | NCR | SCL - Damage to Waterproofing CP8/PL3 Junction |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-08-31 | 2015-08-24 16:50 | -7 | 2015-06-09 11:51 | Tunnelling - Tunnelling General | 20000 |  | Damaged | Repair | 2 (6-60k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | After casting the PL3 junction, the void former in CP8 was removed. When stitch drilling the void former, the waterproofing behind was damaged due to the waste being produced by the coring rig. The damage is between 2 and 8 o clock and the waterproofing has been damaged back to the construction joint between the void former and the cast secondary lining. This does not provide adequate overlap for the waterproofing system as it currently stands.
| 02SL - Stations (LUL) | Cxxx-NCR-001887 | NCR | SCL - Damage to Waterproofing CP9/PL3 Junction |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-08-31 | 2015-08-03 13:44 | -28 | 2015-06-09 11:40 | Tunnelling - Tunnelling General | 20000 |  | Damaged | Repair | 2 (6-60k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | After casting the PL3 junction, the void former in CP9 was removed. In doing this, a 5 tonne excavator was used to remove the bottom pieces of the void former and doing so damaged the waterproofing. The damage is between 4 and 8 o clock and the waterproofing has been damaged back to the construction joint between the void former and the cast secondary lining. This does not provide adequate overlap for the waterproofing system as it currently stands.
| 02SL - Stations (LUL) | Cxxx-NCR-001888 | NCR | ETH - Two Storey Basement - Internal wall W19 dywidag anchor bar installed without sleeve |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-07-07 | 2015-07-03 12:40 | -4 | 2015-06-23 13:13 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | Dywidag anchor bar installed without a sleeve during the construction of internal wall W19 GL 4-5. After striking the double sided formwork, it was discovered by that the dywidag bar was cast in the concrete without a sleeve and could not be removed without damaging the finished concrete (see attached photo).
| 02SL - Stations (LUL) | Cxxx-NCR-001889 | NCR | SCL - sheet waterproof membrane - no I.D. number on gauge for pressure testing equipment |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2015-07-01 | 2015-06-17 17:20 | -14 | 2015-06-10 09:14 | Tunnelling - Linings - In-situ Concrete | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | The equipment for pressure testing double seam welds in the sheet waterproof membrane was found to have an unidentified pressure gauge. The gauge could not be traced to the calibration register. The gauge was removed from site.
| 02SL - Stations (LUL) | Cxxx-NCR-001890 | NCR | SCL - Underspraying of eyes of CP6 junctions with CH2 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-07-10 | 2015-07-09 09:32 | -1 | 2015-06-10 15:35 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | have undersprayed the eyes in CP6a and CP6b at the junction with CH2. The underspraying of the eyes varies between 297mm under thickness in the crown down to 50mm under thickness in the invert. Additional monitoring points were installed in this area in order to show that ground movements were not above the allowable trigger levels.
| 02SL - Stations (LUL) | Cxxx-NCR-001891 | NCR | ETH South Basement W2 Concrete Strength |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-08-31 | 2015-09-03 14:14 | 3 | 2015-06-11 16:15 | Civil - Civil Engineering General | 2500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Following the issue of a number of 28 day cube results for lining wall pours it was found that the some did not reach design strength. See attached Concrete Strengths showing the list. Analysis has been carried out using the 56 and 90 day results and the concrete strengths acheived are compliant with Table B.1. BS EN 206:2013, Criterion 1 & 2. See attachment W2 Low Concrete Strength showing justification.
| 02SL - Stations (LUL) | Cxxx-NCR-001892 | NCR | WTH - PMI229 - ARCH 8 CONCRETE TIMES |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-07-10 | 2015-07-10 15:49 | 0 | 2015-06-22 08:32 | Civil - Civil Engineering General | 800 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | During pour of Arch 8, as part of PMI 229 temporary works arch infill, one concrete wagon remained on site for a period exceeding two hours from batching (ticket number 69585731 finished pouring this wagon 2 hours 25 minutes after batching). Furthermore the driver, without consent from , added a small amount of water to the very last half skip from this load and this concrete was discharged into the arch. Additionally the subsequent wagon was poured start 1 hour 35 minutes after the previous wagon was finished (ticket number 69589180). At the end of the first wagon the concrete was still workable despite having been batched 2 hours 25 minutes previously. Prior to start of second wagon concrete was visibly workable inside the arch despite the 1 hour 35 minutes elapsed to the previous wagon.
| 02SL - Stations (LUL) | Cxxx-NCR-001893 | NCR | Level -1 Slab Over SHW3 - Excess Cover |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-06-29 | 2015-06-16 12:56 | -13 | 2015-06-15 13:04 | Civil - Structural Engineering | 3000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Following completion of steel fixing for the level -1 slab over the SHW3 shaft a T1 mat level survey was carried out when it was found the T1 bars would have excess cover. Where the cover to the T1 bars falls outside of the applicable tolerance (+10/-5) as set out in FAR-CRL-FCD-Cxxx-00974, propose to fix A393 mesh directly onto the T1 layer or packed with suitable diameter spacer bars where the level of exess cover requires. The A393 mesh will be fixed accordingly to provide the desired amount of cover. Please confirm this is acceptable.
| 02SL - Stations (LUL) | Cxxx-NCR-001894 | NCR | ETH Two Storey Basement sleeves cast in capping beam level 0 East |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-08-07 | 2015-08-04 09:42 | -3 | 2015-06-17 13:08 | Civil - Civil Engineering General | 1500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the construction of capping beam level 0 East installed 4No sleeves as per RFI-00148 (see attached). This RFI includes setting out information, type of sleeve and number of sleeves to install. Currently is installing the falsework for level 0 slab at the location of the sleeves. An as built survey has been carried out and the issues are as follows: 1- The 4No sleeves are out of position by 237mm northwards (pipe 1, north ), 207mm northwards (pipe 2), 217mm northwards (pipe 3) and 213mm northwards (pipe 4, south) 2- The 4 No sleeves are not at the correct level (top of sleeves to be at 116.200). Sleeves are too high and some of them are encroaching the underside of slab at level 0 (116.250mm). From level 116.250 m: Pipe 1 is 8mm above soffit, pipe 2 is 12mm below soffit, pipe 3 is 10mm below soffit and pipe 4 is 8mm above soffit. See attached "location of sleeves", RFI-00148, "as built survey pipes" and photos
| 02SL - Stations (LUL) | Cxxx-NCR-001895 | NCR | SMM- Jack location 2/3 & 3/4 pair no. 7 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-07-16 | 2015-07-03 17:27 | -13 | 2015-06-18 11:10 | Civil - Structural Engineering | 3500 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Due to site constraints when installing the jacks, in particular the existing stool positions. Jack pair no. 7 (jacks closet to the ETH) on pier ¾ and pier 2/3 where not located within their original design position (see attached sketch). As a result additional load is currently being taken by these jacks, therefore 2 pairs of additional jacks are to be installed near the end of lintel. The installation of additional jacks will be covered under a short notice change to the design statement: Cxxx--C2-CCN-M123-50998 - Short Notice Change – Additional Jacks in Lindsey Street Bridge
| 02SL - Stations (LUL) | Cxxx-NCR-001896 | NCR | ETH - Trapezoidal shaft - Wrong installation of lift 9 call button recess |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-03-31 | 2015-11-27 14:37 | -125 | 2015-06-18 14:08 | Civil - Civil Engineering General | 1250 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the construction of wall 8 in the lift shaft at L-6 to L-5, the lift call button recess was cast in the wrong side of the wall due to a confusion when reading the drawing and setting it out on site. In addition the recess button was missed at L-3 W11a. Note: The architecture drawing was used to set out the recess and drawing Cxxx-SWN-S-DDC-M123_Z-31003 [C07] was issued after the completion of these walls. Attached sketch highlights the as-built location in W8 L-6 & L-5.
| 02SL - Stations (LUL) | Cxxx-NCR-001897 | NCR | ETH - Wall 17 missing couplers |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-08-04 | 2015-08-03 09:42 | -1 | 2015-07-07 12:18 | Civil - Civil Engineering General | 2950 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During the construction of L-3 slab and due to reinforcement congestion in the area located between beam 4 and the capping beam “beam 3” (attached photo 1), 4 out of 6 wall “17” starters where installed very close together as shown in the attached photo 2. In addition and during the construction of W20, 2No of the starters were snapped after an operative tried to bend them in order to fit the shutter see attached photo 3. So currently we have 2 couplers within 450mm spacing. please find attached sketch (SK-THM-01) showing our proposed solution because drill and fix solution will not be possible due to steel congestion.
| 02SL - Stations (LUL) | Cxxx-NCR-001898 | NCR | ETH Two Storey Basement - Starter bars reinforced concrete walls W28 and W32 at level 0 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-11-27 | 2015-09-17 09:20 | -71 | 2015-06-18 15:13 | Civil - Civil Engineering General | 2500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Prior to the construction of reinforced concrete walls W28 and W32 above level 0 has carried out an as built survey of the couplers cast in capping beam level 0 East. has raised RFI-00606 to __ detailing the issues found and proposing a solution for each one. Any cover issue will be sorted out from level 0 to level +1 and will not affect the cover from level +1 upwards. One of the issues explained in the RFI is related to PMI-431 where drawing Cxxx-SWN-S-DDA-M123_1-30002 was up revved to C07 changing the dimensions of south end of wall W28. Despite of this can not be classified as a NCR, included it in RFI-00606. Please refer to "__ RFI-00606 not responded", and all the attachments related to it : "as built survey of couplers W28 and W32 level 0", "marked up drawings" showing the location and the proposals "W28 level 0" and "W28 - W32" level 0.
| 02SL - Stations (LUL) | Cxxx-NCR-001899 | NCR | SMM-Blocked TaM TN2002 ( MS2) |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-07-10 | 2015-07-03 17:42 | -7 | 2015-06-19 09:33 | Geotechnical Engineering - Compensation Grouting | 3300 |  | Damaged | Use As-Is | 3 (3-6k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | Prior to excavation commencing for ES2 (from ETH) TaMs TN2001, TN2002 and TN2003 were required to be partially backfilled to allow the ES2 tunnel to pass through. TaMs TN2001 and TN2003 were successfully backfilled and rostored out to allow partial use of the TaMs nearest to the shaft. However, TN2002 was blocked a number of attempts were made to unblock it with the Rostor, __ drill but with no avail. As a result TaM TN2002 is no longer available for grouting.
| 02SL - Stations (LUL) | Cxxx-NCR-001900 | NCR | SCL - Secondary Lining Crown Pour Bay 22 PTE CH64.532 - CH76.432 - Grout loss |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-08-14 | 2015-07-23 16:34 | -22 | 2015-06-19 16:47 | Tunnelling - Linings - In-situ Concrete | 2500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the secondary lining crown pour (Bay 22) located in PTE CH64.532 - CH76.432, leaks occurred in two locations. Firstly through the overlap ring and also centrally between the underside of the forms and bearing timbers causing grout loss in these locations.
| 02SL - Stations (LUL) | Cxxx-NCR-001901 | NCR | ETH - Level L-2 Internal Wall W29 Opening moved while concreting |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-08-31 | 2015-08-06 12:14 | -25 | 2015-06-23 14:26 | Civil - Civil Engineering General | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | During concreting of the internal wall W29 between L-2 and L-1 the bottom corner of opening on the north side of the wall moved by about 25mm. See attached photo and marked up drawing. The south side and the top of the opening has not moved.
| 02SL - Stations (LUL) | Cxxx-NCR-001902 | NCR | Kwikastrip section moved from its position at CP4 location |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-07-22 | 2015-07-17 09:58 | -5 | 2015-06-23 17:34 | Civil - Civil Engineering General | 3000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | After the shutter removal from a section in Cross passage 4 that was poured, It was revealed that a section of kwikastrip that was installed along the cross passage moved from its set position during the pour. Please see photo attached
| 02SL - Stations (LUL) | Cxxx-NCR-001903 | NCR | SCL - Cross Passage 4 Poor Secondary Lining Finish |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-10-30 | 2015-10-29 10:05 | -1 | 2015-06-24 14:36 | Tunnelling - Linings - In-situ Concrete | 2500 |  | Material | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The concrete surface finish in cross passage 4 ch. 0.064m to 25.412m is unsatisfactory in relation to the required F2 finish. Concrete joints and concrete edges are visible from the various poured bays.
| 02SL - Stations (LUL) | Cxxx-NCR-001904 | NCR | SCL - Failed pre pour inspection - CP2a/PTE junction |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2015-07-31 | 2015-07-23 08:38 | -8 | 2015-06-26 09:12 | Tunnelling - Linings - In-situ Concrete | 500 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | During the pre-pour inspection of Bay 25 (junction of CP2a and PTE), it was noted that the spacing of the L-Bars (BM 02; Cxxx-MMD-C4-DDD-M123_5-00623 C02) was not as per the drawing (200mm c/c) in the knee area around the collar. Please see photos.
| 02SL - Stations (LUL) | Cxxx-NCR-001905 | NCR | WTH - Level -1 - South East Slabs - __ damage |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-07-31 | 2015-07-23 18:39 | -8 | 2015-06-26 09:25 | Civil - Civil Engineering General | 3000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Historical __ waterproof membrane installed under capping beam for SH-W3 that will lap onto __ under L-1 South East (SE) slabs was found to be damaged afetr excavation for SE SLabs. This historical membrane from the capping beam was buried for about 18 months until the area was excavated for L-1 SE slab construction. This membrane had to be lapped with new __ membrane laid for construction of L-1 SE slabs. As it was found damaged, the standard detail (Cxxx--C-DWG-M123-50045) of overlap and __ tape would not be achievable.
| 02SL - Stations (LUL) | Cxxx-NCR-001906 | NCR | ETH 2SB Level 0 GL3.5 towards GL5 along W21 Misaligned Couplers |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-08-21 | 2015-08-17 12:39 | -4 | 2015-06-29 11:46 | Civil - Civil Engineering General | 3500 |  | Incorrect Installation | Use As-Is | 3 (3-6k) | Complete | Supervision - Insufficient supervision | Completed |  | Misaligned couplers in the bottom mat have been located between approximately GL 3.5 and GL5 for Level 0 within the capping beam along W21 compromising the cover required. This is further to NCR-001802, NCR-001872 and NCR-001809 raised for coupler misalignment in the Level 0 Slab in the South Basement.
| 02SL - Stations (LUL) | Cxxx-NCR-001907 | NCR | ETH - Lining wall W23 - rebar layers |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-07-06 | 2015-07-01 15:17 | -5 | 2015-06-29 10:50 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Withing Lining Wall W23 Level L-1 there is a 0.7m wide area where the reinforcement of the far face could not be installed as per design requirement (FF1 = horizontal bar, FF2 = vertical bar) between L-1 slab und L 0 slab. The reinforcement has been installed as FF1 = vertical bars, FF2 = horizontal bars. Sketch Cxxx-SR-ETH-REBAR063 shows an overview of the location. The near face reinforcement is not affected by the issue.
| 02SL - Stations (LUL) | Cxxx-NCR-001908 | NCR | ETH - Trapezoidal Shaft - Level -3 - Wall 17 honeycombing |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-07-13 | 2015-07-13 10:13 | 0 | 2015-06-29 16:55 | Civil - Civil Engineering General | 1250 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | ETH - Trapezoidal Shaft - Level -3. Following removal of shutters for Wall 17 a small section of honeycombing was identified. Photos attached.
| 02SL - Stations (LUL) | Cxxx-NCR-001909 | NCR | ETH - SB - Internal Wall pour W20 L-2 - Break during placement of concrete |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-07-31 | 2015-06-30 10:27 | -31 | 2015-06-29 17:31 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate resources | Completed |  | During placing the concrete for Internal Wall W20 L-2 GL4 to GL5.5 a break of 80min between the 1st and 2nd lorry occurred. The 1st lorry finished discharging at 13.50 and the 2nd lorry started discharging only at 15.10. According to KF10.3203 the max break while placing concrete is 60min.
| 02SL - Stations (LUL) | Cxxx-NCR-001910 | NCR | SCL - Cp2a Kicker Steel Out of Tolerance |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-08-21 | 2015-08-04 09:23 | -17 | 2015-07-01 11:25 | Tunnelling - Linings - In-situ Concrete | 2500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The Cp2a kicker between CH1 and LP1 has been cast with over 200mm of cover to the near face steel reinforcement. Please see attached pictures. The steel passed the pre pour inspection and the correct cover is maintained throughout the kicker, except for at the stop end where the cover is as shown.
| 02SL - Stations (LUL) | Cxxx-NCR-001911 | NCR | SCL - Damage to Waterproofing PTE/CP2a with Repair |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-07-16 | 2015-07-16 09:02 | 0 | 2015-06-30 13:21 | Tunnelling - Linings - In-situ Concrete | 1500 |  | Material | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In PTE/CP2a, Bay 26, CH25.136 to CH37.036, the waterproofing was damaged the full length of the bay when removing the sand backfill around the bench. Although the damage was minor at each location, the extent of damage was over the length of a bay and therefore merited a large repair.
| 02SL - Stations (LUL) | Cxxx-NCR-001912 | NCR | WTH SH-W2 Superseded Revision Public Health drawings being used on site |  | Contr | 201068 | FAR - Farringdon Station (West) |  | 2015-07-23 | 2015-07-13 16:03 | -10 | 2015-07-09 13:54 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | For the -3 slab construction a ‘P03’ revision drawing was used on site to set out the cast in cavity wall drainage. However during this time a 'P04' revision was available. Drawing No: Cxxx--P-DDA-M123_3-75205.
| 02SL - Stations (LUL) | Cxxx-NCR-001913 | NCR | WTH - Level -1 South East Slabs - Pile breakdown - bent bars |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-07-31 | 2015-07-23 11:26 | -8 | 2015-06-30 15:34 | Civil - Civil Engineering General | 2500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During pile breakdown of bearing piles on the South East area of the WTH, some steel reinforcement bars of piles U215, S219, S221 and S222 were slightly bent and on Pile S220 the piles were more affected. Please refer to photos attached It is noted RFI Cxxx-RFI-000965 allowed for 6 bars to be cut from bearing piles, and only 1 has been cut on pile S220.
| 02SL - Stations (LUL) | Cxxx-NCR-001914 | NCR | SCL - Concrete Tickets Not Checked on Pour - CP4 Bay 8 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-07-17 | 2015-07-13 11:19 | -4 | 2015-07-03 08:50 | Tunnelling - Linings - In-situ Concrete | 800 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | s ITP for casting concrete, Cxxx--C4-ITP-M123-50060, gives a inspection number 3.9 for checking the correct concrete has been delivered. During a surveillance on CP4 Crown Bay 8, CH22.4-CH25.6, it was seen that the only check on the concrete was by the ganger in the delivery corridor. No check was performed on the ticket by the shift engineer that the correct mix had been delivered to site.
| 02SL - Stations (LUL) | Cxxx-NCR-001915 | NCR | SCL - ETC Technician Using Wrong Flow Range for CP4 Bay 8 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-07-17 | 2015-07-10 12:04 | -7 | 2015-07-03 13:12 | Tunnelling - Linings - In-situ Concrete | 800 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | During the pouring of CP4, Crown Bay 8, CH 22.4 - 25.4 on 16/06/15, a technician was found to be using the wrong flow limits when undertaking the test. The operative understood the limit to be 540mm to 640mm whereas the ITP states that that the flow range is 530mm to 660mm.
| 02SL - Stations (LUL) | Cxxx-NCR-001916 | NCR | SCL - Retesting of Concrete After One Hour on CP4 Crown Bay 8 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-07-17 | 2015-07-10 12:02 | -7 | 2015-07-03 14:34 | Tunnelling - Linings - In-situ Concrete | 800 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | During the pouring of CP4, Crown Bay 8, CH22.4-25.6 cast on 16/06/15, a wagon was found to be on the pump for longer than an hour during a Crossrail surveillnace. The __ technician was asked whether he had retested the concrete in the wagon and incorrectly stated that it was due 2 hours after batch time. The ITP states that the wagon should be tested every hour after arrival. The technician was also unaware of the ITP requirement to retest the concrete evey half an hour once the flow went below 550mm.
| 02SL - Stations (LUL) | Cxxx-NCR-001917 | NCR | WTH - Level -1 - South East Slabs - Pile breakdown - overbreak of piles |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-07-31 | 2015-07-20 10:52 | -11 | 2015-07-06 16:55 | Civil - Civil Engineering General | 2500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During pile breakdown of pile U215 on the south east slabs of Level -1 WTH, the jack-hammer accidentally locally broke the pile below cut off level. Please see photos attached In the same area, pile S220 had to be locally broken 100mm below cut off level around a geothermal loop to repair the pipe. This however was in the cover zone of the pile, leaving the pile edge trimmed to correct cut off level, where the waterproof bituthene seal was installed correctly.
| 02SL - Stations (LUL) | Cxxx-NCR-001920 | NCR | ETH-Two Storey basement cover issue on level 0 slab cantiliver section over wall W23 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-07-21 | 2015-07-15 12:57 | -6 | 2015-07-07 19:14 | Civil - Civil Engineering General | 1500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | have installed the temporary works required to build the cantilever section of level 0 slab over W23. When constructed capping beam level 0 West, 12No couplers (6No T2 and 6No B2) were fixed as per drawing Cxxx-ATK-S-DWG-M123_1-50103 C04 (see attached "marked up drawing Cxxx-ATK-S-DWG-M123_1-50103") to connect these couplers to the bars of level 0 slab located in this cantilever section area. has carried out an as built survey: 1) The distance from the underside of B2 couplers to the soffit of slab level 0 varies between 30mm and 35mm. 2) The distance between top of capping beam (top of slab) and T2 couplers cast in the capping beam is 90mm
| 02SL - Stations (LUL) | Cxxx-NCR-001921 | NCR | SCL - Pressure Gauges Being Kept On Site without in Date Calibration |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2015-07-24 | 2015-07-22 10:40 | -2 | 2015-07-08 12:12 | Tunnelling - Tunnelling General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | During a CRL Surveillance it was noted that there were 2 no. 25kN pressure gauges (FAR 62 & FAR 69) that were on site and were available to be used past their calibration dates. This was confirmed by ’s Site Engineer. This means that any results obtained after the expiration dates have been invalidated.
| 02SL - Stations (LUL) | Cxxx-NCR-001922 | NCR | STW - Non Submittal of Readiness Review Trackers |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2015-07-31 | 2015-07-29 18:00 | -2 | 2015-07-08 13:10 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | It was noted during a CRL Surveillance that investigated over time line of 6 periods, that each section of have missed the periodic submission of Readiness Review Trackers. From examination of the CARs register, the non-submission of Readiness Review Trackers has occurred several times and the last CAR with regards to this was on 09/12/2014. need to manage better their periodic submissions.
| 02SL - Stations (LUL) | Cxxx-NCR-001923 | NCR | ETH - Barbican Station Piles 22 & 23 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-07-31 | 2015-07-20 13:14 | -11 | 2015-07-10 16:09 | Civil - Civil Engineering General | 1500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The bore depth of piles 22 and 23 short by 250mm and 190mm respectively. The pile reinforcement has been set 270 and 170mm above the desired level.
| 02SL - Stations (LUL) | Cxxx-NCR-001924 | NCR | SCL - CP3a Bay 4 Poor Secondary Lining Finish |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-08-06 | 2015-07-31 14:28 | -6 | 2015-07-17 13:34 | Tunnelling - Linings - In-situ Concrete | 2500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not qualified | Completed |  | The secondary lining concrete for bay 4, CH8.970 to 12.215, in CP3a has been cast with a lip between the kicker concrete and the crown concrete. This lip is greater than is permissible for an F2 finish and repair work will be required to make good.
| 02SL - Stations (LUL) | Cxxx-NCR-001925 | NCR | WTH - Further water ingress issues in lining walls of SHW3 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-11-13 | 2015-11-06 15:11 | -7 | 2015-07-21 17:15 | Civil - Civil Engineering General | 20000 |  | Material | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Further to previous NCRs raised in relation to water ingress issues in SHW3 (NCRs 001717, 001820 and 001844), there have since been another 4no. areas of water ingress that have become visible. The attached location plan show the locations of these areas. __, the Technical Manager for __ Construction, attended site on 15/7/15 to inspect the areas of water ingress. His report, containing his proposed remedial measures, is attached to this NCR. Please note 'Leak 1' in the report refers to 'Area 1' on the location plan, etc.
| 02SL - Stations (LUL) | Cxxx-NCR-001926 | NCR | WTH SH-W2 Use of unapproved HDK anchors to fix cavity wall pipes |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-09-30 | 2015-09-25 11:23 | -5 | 2015-07-16 13:14 | Civil - Civil Engineering General | 1000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | has used HDK anchors to fix the cavity wall drainage pipes to the lining walls on level -8 of the SHW2 shaft. The MCR (CRL-MCR-001335) for these anchors was not approved at the time of the installation and was later rejected by CRL.
| 02SL - Stations (LUL) | Cxxx-NCR-001927 | NCR | SCL - Removal of Piles at RTE2/SH-E3 Connection |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-08-28 | 2015-08-14 12:09 | -14 | 2015-07-16 10:09 | Tunnelling - Tunnelling General | 6000 |  | Supervision/Management | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | , in breaking through between RTE2 and SH-E3, broke down the piles of SH-E3 below the level indicated in drawing Cxxx-MMD-C4-DDD-M123_Z-00106 Detail 2. The piles have been broken down to the same level as the primary lining rather than to the level of the -6 slab, see attached pictures and marked up extract of Cxxx-ATK-S-DWG-M123_Z-50225.
| 02SL - Stations (LUL) | Cxxx-NCR-001928 | NCR | ETH - Trap Shaft Handback package 37 - Level -1 to Level 0 Lining walls Missing documentation |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-08-25 | 2017-07-03 13:09 | -53 | 2016-09-22 15:08 | Civil - Civil Engineering General | 750 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | This package is missing completed earthing connection check sheets produced by __ for Wall 33 and Wall 23 DC16, DC17, DC18 and DC19
| 02SL - Stations (LUL) | Cxxx-NCR-001930 | NCR | ETH - Barbican Station Pile Reinforcement Cages |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-08-03 | 2015-07-20 13:20 | -14 | 2015-07-17 12:42 | Civil - Civil Engineering General | 1500 |  | Manufacturing Defect | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A number of the bottom sections for the pile cages delivered to site on 15/07/2015 have been fabricated approximately 100mm short of the required length. In addition one of the top sections was missing the skid spacers. The issues were highlighted following the onsite checks for the reinforcement cages but was not picked up at the off site fabrication facility.
| 02SL - Stations (LUL) | Cxxx-NCR-001932 | NCR | ETH - Barbican Station - Missing Feet on Pile 7 Reincorcement Cage |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-04-29 | 2016-03-08 11:46 | -52 | 2015-07-21 15:29 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Insufficient quantity of material to do the job | Completed |  | The feet providing minimum 75mm bottom cover were not installed for pile 7. The pile cage was suspended from the temporary drill casing during the concrete pour. Once the pour was complete, the cage, now held in situ by the concrete, was released from the casing support. the minimum 75mm bottom cover and the correct pile cut-off (107.503m) were maintained, despite this non-conformance.
| 02SL - Stations (LUL) | Cxxx-NCR-001933 | NCR | WTH Level -1 – Blocked Geothermal Loop – Pile U220 |  | Contr | 201068 | FAR - Farringdon Station (West) |  | 2015-09-04 | 2015-09-03 09:19 | -1 | 2015-07-22 15:43 | Civil - Civil Engineering General | 3500 |  | Damaged | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | 2 of the geothermal loops in Pile U220 (see drawing Cxxx--C-DWG-M123-50060) in the south east of the WTH footprint have become blocked. Pipes were flushed, tested and sealed 2 weeks prior to connecting up to bring out of the pour shutter and were all clear at the time. To date, a total of 7 geothermal loops have become unusable.
| 02SL - Stations (LUL) | Cxxx-NCR-001934 | NCR | WTH SH-W2 - Level -3 - column RC1 - starter bars misaligned |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-08-07 | 2015-08-07 17:15 | 0 | 2015-07-24 10:22 | Civil - Civil Engineering General | 2750 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Starter bars for the column RC1 were cast into the level -3 slab within SHW2. Upon commencing to fix the links in the column it became apparent that the starter bars have been cast to a larger area than the designed column therefore the links do not fit around the outside of the starter bars.
| 02SL - Stations (LUL) | Cxxx-NCR-001935 | NCR | SCL - Delayed testing of BFK 17.2 Drying Shrinkage and Water Penetration for June 2015 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-09-02 | 2015-08-28 08:51 | -5 | 2015-07-24 11:51 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Repair | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | The samples sent to the __ laboratory for monthly testing in June 2015 have been delayed by 28 days. The samples were cast on 16/06/2015 and sent from the site laboratory to Warringdton on the 21/06/2015, but were only registered by the laboratory on the 15th July for testing. The tests will therefore be performed on the following dates: - 28 Day Dry Shrinkage - 19/08/2015 90 Day Dry Shrinkage - 20/10/2015 28 Day Water Penetration - 12/08/2015
| 02SL - Stations (LUL) | Cxxx-NCR-001936 | NCR | ETH - Barbican Station Pile Reinforcement - Wire Rope Clamps |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-08-10 | 2015-08-04 12:09 | -6 | 2015-07-24 17:07 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | Wire rope clamps have been used to fix the adjustable feet to the bottom of the pile reinforcement cages for piling works at Barbican Station. The clamps are not structural but form part of the permanent works as they are cast into the base of the piles. No MCR was submitted for the clamps before use.
| 02SL - Stations (LUL) | Cxxx-NCR-001937 | NCR | WTH Level -1 – South East Slab – Excess cover |  | Contr | 201068 | FAR - Farringdon Station (West) |  | 2015-08-07 | 2015-08-05 11:36 | -2 | 2015-07-24 16:59 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | There is excess cover of 70mm on limited sections of the level -1 south east slab. See attachment for location details.
| 02SL - Stations (LUL) | Cxxx-NCR-001938 | NCR | ETH - Area A L0 Slab 3 no. misaligned box outs |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-08-14 | 2015-08-04 09:53 | -10 | 2015-07-31 17:36 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | On completion of as built surveys of the Level 0 Slab Area A between GL 1 and 3 , 3 no. box outs have been found to be out of position by 200mm. Refer to attached sketch Cxxx-SR-ETH-SB42 showing the misalignment and as built position.
| 02SL - Stations (LUL) | Cxxx-NCR-001939 | NCR | WTH SH-W2 – Post fixing dywidag bars for supporting formwork for Wall 7 Second Lift (Level -4 to -3) |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-12-01 | 2015-10-20 09:11 | -42 | 2015-07-28 09:20 | Civil - Civil Engineering General | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | Wall 7 second lift (between Levels -4 & -3) was poured over its full length including small returns on Wall 6 and 8 (see attached sketch). These small returns were fixed in position by post fixing dywidag bars into previously cast walls , see attached.
| 02SL - Stations (LUL) | Cxxx-NCR-001940 | NCR | WTH SH-W2 Level -3 to -1 Wall 25 Wall Failed Pre-Pour Inspection |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2015-08-11 | 2015-08-11 17:39 | 0 | 2015-07-28 16:32 | Civil - Civil Engineering General | 750 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | The CRL FE was invited to attend Pre-Pour Inspection for WTH SH-W2 Level -3 to -1 Wall 25 on 28/07/2015. All checks were confirmed as having been previously completed by (refer to attached Pre-Pour Inspection Checksheet), but no cover survey was attached to the checksheet, as per usual. During the inspection the CRL FE noticed that the cover along the west face of the wall was between 20-30mm; the design cover for this wall is 50mm, with the allowable tolerance limits for a wall of this size being 45-72.5mm (as per Cxxx-FCD-000974). Refer to attached site photos. The following was also observed: a) Hazard tape wrapped around one of the vertical bars in the north-west corner of the pour, b) Several off-cuts of tying wire at the base of the pour, c) Several of the vertical bars had not been tied to the uppermost lacer, resulting in some bars having a spacing of approximately 50mm, whilst other had a spacing of approximately 250mm (design spacing is 150mm). CRL note that all of the above issues were addressed prior to the pour commencing. Previous NCRs raised regarding failed pre-pour inspections in SH-W2 (Cxxx-NCR-001551, Cxxx-NCR-001795 & Cxxx-NCR-001895) have focused the corrective actions on the engineers carrying out more thorough checks, prior to inviting CRL for formal inspections. Further to this, CRL note that, overall, the quality of the SH-W2 pre-pour inspection packs over the last 5-6 months have generally been of a good standard, with all checks signed off and all necessary supplementary surveys attached. However, CRL suggest that more onus is now also placed on the workforce, namely the steel fixers and the carpenters, as the above are basic issues which should have been picked up and corrected during the construction phase, and prior to formal CRL inspection.
| 02SL - Stations (LUL) | Cxxx-NCR-001941 | NCR | SCL None compliance with book 1Vol 1.12 Annex period 14 day reply to coded document |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-09-04 | 2015-08-27 14:36 | -8 | 2015-07-29 13:24 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Rev 2 of Testing Procedure is Code 3 (PMC received on 09/07/15). And rev 1 was Code 2 (PMC received On 15/12/2014) this is against Book 1Vol 1.12 Annex 2 Period of reply is 14 days
| 02SL - Stations (LUL) | Cxxx-NCR-001942 | NCR | SCL Misssing spare flow tables and steel rules |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-09-04 | 2015-08-25 14:21 | -10 | 2015-07-29 13:42 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Inadequate/insufficient tooling. | Completed |  | Flow tables held in stores does not comply with testin procedure. Only 1 spare table and 1 steel rule
| 02SL - Stations (LUL) | Cxxx-NCR-001943 | NCR | WTH - SHW2 - Midlanding 94.68m - broken lintel |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-08-28 | 2015-08-27 09:51 | -1 | 2015-08-06 10:40 | Civil - Civil Engineering General | 3000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Coupled starter bars have been installed into walls 16 and 6 during previous pours, ready to connect into the midlanding slab. The starter bars for the level -5 midlanding (+94.680m) have been installed. On the eastern landing the correct number of bars have been installed of incorrect spacing, but over a distance that is approximately 600mm larger than designed. On the south side of the western landing the correct number of bars, at the incorrect spacing, have been installed over a distance of approximately 250mm larger than designed. To ensure the correct number of bars have been installed within the landing area, post drilled bars into the existing walls. However, when drilling these bottom mat bars part of the concrete above the lintel within wall 16 broke, exposing a couple of the cast-in couplers. The deepest section of broken concrete is approximately 60mm deep. See attached drawings and photos for details
| 02SL - Stations (LUL) | Cxxx-NCR-001944 | NCR | WTH SH-W2 Damaged hydrophilic strip at Wall 6/Level -2 slab connection |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-08-10 | 2015-08-07 17:38 | -3 | 2015-07-31 13:55 | Civil - Civil Engineering General | 3000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Wall 6 was poured in two halves creating two vertical construction joints. At both locations, the lap of the hydrophilic strip was left protruding from the top of the wall and protected. Once work started in this area both laps were damaged meaning it is not possible to get the 100mm overlap required (see attached sketch and photos). Two strips of hydrophilic strip will be installed across the top of wall 6 as per standard waterproofing details. Where there is no connection will carry out the same remedial measure used in Cxxx-NCR-001752 (see attachment ‘Cxxx-NCR-001752 Proposed Solution’). __, our waterproofing specialists, were satisfied that this solution was acceptable.
| 02SL - Stations (LUL) | Cxxx-NCR-001945 | NCR | ETH 2SB Level 0 Soffit Damage during box out striking |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-09-09 | 2015-09-08 15:35 | -1 | 2015-08-12 12:02 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Whilst striking one of the box outs within the L0 slab the soffit in the surrounding area was damaged. See attached photograph.
| 02SL - Stations (LUL) | Cxxx-NCR-001946 | NCR | WTH Level -2 – Insufficient __ lap at construction joint |  | Contr | 201068 | FAR - Farringdon Station (West) |  | 2015-08-21 | 2015-08-10 08:43 | -11 | 2015-07-31 18:25 | Civil - Civil Engineering General | 5000 |  | Damaged | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | At the level -2 construction joint for the tie in with SH-W2 north of wall 6, __ left from a previous pour has been damaged or not enough was left to lap onto to comply with the technical data sheet. A minimum of 50mm lap is currently available.
| 02SL - Stations (LUL) | Cxxx-NCR-001948 | NCR | WTH Slump test not carried out in accordance with BS |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-08-31 | 2015-08-25 15:41 | -6 | 2015-08-03 15:28 | Structural Engineering - Concrete Member | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | When doing the slump test on 31/07/2015 in WTH (ES1 and SHW3 stepped ramp) __ did not re-mix the samples using the remixing container.
| 02SL - Stations (LUL) | Cxxx-NCR-001949 | NCR | WTH SH-W2 Level -2 Pile Starter Bar Projections |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-08-09 | 2015-08-07 17:04 | -2 | 2015-08-04 13:16 | Civil - Civil Engineering General | 2500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Male piles R949 - R962 of the square shaft are cast in the level -2 pilecap. 1) Cxxx-RFI-002841 specified that the bars should project 1100mm out of the piles. In several of the piles (R949 – R951 & R953 – R957) the bars only project at worst 1000mm (see attached mark-up). 2) Furthermore, on the same RFI the bar spacings were specified as being 212mm. On pile R962, due to reinforcement congestion in that corner, two of the bars do not meet the required dimension.
| 02SL - Stations (LUL) | Cxxx-NCR-001955 | NCR | Reinforcement of Lining wall W23 (far face L-1 to L0) |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-08-24 | 2015-08-18 09:43 | -6 | 2015-08-05 13:17 | Structural Engineering - Reinforcement | 3000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Previous Construction - Interfacing issues | Completed |  | In a localised area, the far face of lining wall W23 could not be installed as per the design requirement (FF1 - horizontal bars and FF2 - vertical bars) between the slabs at levels L-1 and L0. See attached marked drawing Cxxx-SR-CTH-REBAR-065. The reinforcement has instead been installed as FF1 for vertical bars and FF2 for horizontal bars. The near face of the lining wall is not affected by this issue and is therefore installed as per the design.
| 02SL - Stations (LUL) | Cxxx-NCR-001958 | NCR | ETH - Barbican Station Pile Cap Blinding Level |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-08-19 | 2015-08-17 17:22 | -2 | 2015-08-05 16:52 | Civil - Civil Engineering General | 1500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | The excavation for the high level pile caps at Barbican Station was not excavated to the required depth and the blinding concrete installed too high. The excavation should have been reduced to a level of 108.955 and a 50mm thick layer of blinding concrete installed with a tolerance of +0/-10mm.
| 02SL - Stations (LUL) | Cxxx-NCR-001959 | NCR | ETH - ESS2 stairs 3rd flight misalgnment |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-09-17 | 2015-09-16 12:06 | -1 | 2015-08-12 16:20 | Civil - Civil Engineering General | 3000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Verbal communication problem | Completed |  | After the construction of the 3rd flight between L-7 and L-6 it was identified that the stairs were constructed slightly incorrect by 40mm starting correctly at the bottom steps and tapering in. Please find attached sketch showing the error (redline indicates the as-built location).
| 02SL - Stations (LUL) | Cxxx-NCR-001960 | NCR | WTH Level -1 – Damaged/missing __ at construction joint |  | Contr | 201068 | FAR - Farringdon Station (West) |  | 2015-09-11 | 2015-09-04 11:12 | -7 | 2015-08-14 11:36 | Civil - Civil Engineering General | 4000 |  | Damaged | Repair | 3 (3-6k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | At the level -1 construction joint on the east SH-W3 capping slab (area shown on attachment - East slab waterproofing damage), __ left from a previous pour has been damaged or not enough was left to lap onto to comply with the technical data sheet. The __ has been damaged at both the concrete construction joint and sheet piles as shown in the pictures. Additionally the adcor strip left to lap onto from the previous level -2 pour doesn't have sufficient length to lap onto.
| 02SL - Stations (LUL) | Cxxx-NCR-001961 | NCR | ETH Two Storey Basement Clash between box out at level 0 and starter bars W20 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-08-28 | 2015-08-19 20:34 | -9 | 2015-08-14 15:06 | Civil - Civil Engineering General | 2500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | is currently constructing level 0 slab in area B. Mark up drawing Cxxx-SWN-S-DDA-M123_1-30002 C07 shows the location of the box out which is clashing with 13No B32 L bars BM50 highlighted in yellow in mark up drawing Cxxx-ATK-S-DWG-M123_Z-50655 C03. Refer to mark up photos for position of box out in relation of BM50.
| 02SL - Stations (LUL) | Cxxx-NCR-001962 | NCR | WTH Level -1 - Wall 6 side face bars starters out of position |  | Contr | 201068 | FAR - Farringdon Station (West) |  | 2015-08-28 | 2015-08-17 10:22 | -11 | 2015-08-14 18:15 | Civil - Civil Engineering General | 750 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | At the north doorway in wall 6 on level -1 couplers where previously cast in for side face bars to be fixed. However, the couplers were positioned not allowing for a lacer to be placed on the outside of them, this would have resulted in out of spec cover to the face of the wall (around 30mm). Rebar drawing is Cxxx-ATK-S-DWG-M123_3-50140, bar mark 47.
| 02SL - Stations (LUL) | Cxxx-NCR-001964 | NCR | ETH - No MCR in place for shutter oil used |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-09-08 | 2015-09-03 14:53 | -5 | 2015-08-25 13:51 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Lack or improper material identification and traceability | Completed |  | __ mould release oil was used for the side shutters of the level L 0 slab area B without having a valid MCR in place for the product.
| 02SL - Stations (LUL) | Cxxx-NCR-001965 | NCR | WTH SH-W2 Level -1 Incorrect Pile Starter Bar Spacings & Edge Distances(East Side of SH-W2) |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-09-02 | 2015-09-01 15:44 | -1 | 2015-08-19 17:57 | Civil - Civil Engineering General | 2500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Previous Construction - Interfacing issues | Completed |  | Male piles R901 – R912, along the Eastern edge of the square shaft are cast in to the Level -1 pilecaps. Cxxx-RFI-002841 specified that the bar spacings were to be 212mm and edge distances to be a minimum of 160mm. Please see below a list of non-conformances: R901 1 dowel has 130mm edge distance. R902 3 dowels have 150mm edge distance. R904 1 dowel spacing is 185mm. R907 3 dowels have 130-150mm edge distance. 1 dowel spacing is 195mm. R908 1 dowel spacing is 200mm. R909 1 dowel spacing is 200mm.
| 02SL - Stations (LUL) | Cxxx-NCR-001966 | NCR | Platforms works - A quantity of Water present in Remixer at the start of pour |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-09-30 | 2015-09-29 14:25 | -1 | 2015-08-20 11:40 | Civil - Kerbs | 2500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Supervision - Other | Completed |  | A quantity of water was left in the Remixer and mixed with the first load used for the pour of the platform kerb (13/08/15)between bay 1 and bay 2, wrongly the supervisor didnt stop the activity, The location of this incident was approximately between chainage 7039 and chainage 7056 .
| 02SL - Stations (LUL) | Cxxx-NCR-001967 | NCR | WTH SH-W2 Package F Concrete Repairs |  | Contr | 201068 | FAR - Farringdon Station (West) |  | 2016-01-22 | 2016-01-21 13:35 | -1 | 2015-08-26 14:51 | Civil - Civil Engineering General | 5000 |  | Workmanship | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Concrete repairs which are classified as defects required for package F (level -4 to -3 walls and -3 slab) are listed in the attached PDF.
| 02SL - Stations (LUL) | Cxxx-NCR-001968 | NCR | SCL Crack Width in PTE Bay 28 Crown Pour Exceeds 0.3mm |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-09-11 | 2015-09-11 08:55 | 0 | 2015-08-21 15:48 | Tunnelling - Linings - In-situ Concrete | 2500 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | A crack has been identified in PTE cast Secondary Lining crown (bay 28) which is greater than 0.3mm. The crack is located in the crown from the leading edge chainage CH2.746. Crack survey details are as follows; Start: CH 2.767 m Hz-off 0.1795 m Ver-off 4.7430 m Deviation 0.0214 m Derolement 0.1787 m Width 0.6mm Finish: CH 13.979 m Hz-off -0.0568 m Ver-off 4.7583 m Deviation 0.033 m Derolement -0.0563 m Width 0.6mm Photographs have been attached
| 02SL - Stations (LUL) | Cxxx-NCR-001969 | NCR | SCL Crack Width in PTE Bay 20 Crown Pour Exceeds 0.3mm |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-09-11 | 2015-09-11 08:51 | 0 | 2015-08-21 16:04 | Tunnelling - Linings - In-situ Concrete | 2500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | A crack has been identified in PTE cast Secondary Lining crown (Bay 20) which is greater than 0.3mm. The crack is located from the leading edge chainage CH296.022. Crack surveyed as 2.6m long from the leading edge at 1-2 o'clock clock position (shoulder position cross passage side) and is 1mm wide.
| 02SL - Stations (LUL) | Cxxx-NCR-001970 | NCR | SCL - Failed waterproofing inspection - CP6a kickers |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2015-09-10 | 2015-09-07 08:54 | -3 | 2015-08-24 09:41 | Tunnelling - Linings - In-situ Concrete | 500 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | During the pre-pour inspection of CP6a kickers, the waterproof membrane was not of an acceptable standard to release the hold point - failed inspection.
| 02SL - Stations (LUL) | Cxxx-NCR-001971 | NCR | SCL - Failed inspection CP3b invert waterproofing |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2015-09-10 | 2015-09-07 08:55 | -3 | 2015-08-24 09:49 | Tunnelling - Linings - In-situ Concrete | 500 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | During the pre-pour inspection of the CP3b invert, the sheet waterproof membrane was found not to be in an appropriate condition with respect to cleanliness - failed inspection.
| 02SL - Stations (LUL) | Cxxx-NCR-001972 | NCR | SCL - Damage to drainage pipe in sump 1 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-09-30 | 2015-09-11 15:34 | -19 | 2015-08-24 10:01 | Tunnelling - Linings - Sprayed Concrete | 1500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The drainage pipe shown in drawing Cxxx-MMD-C4-DDB-M123_5-00250 has been damaged. The last pipe section has been removed to allow construction of the sump
| 02SL - Stations (LUL) | Cxxx-NCR-001973 | NCR | SCL - Incomplete check sheets for waterproofing and secondary lining |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-10-16 | 2015-10-12 13:28 | -4 | 2015-08-27 11:15 | Civil - Tunnelling | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Personnel Error - Not Defined | Completed |  | SCL Check sheets Cxxx-SF-CON-230 Sprayed Concrete Secondary Lining and Cxxx-SF-CON-231 Pre-waterproofing Check not fully completed during spraying of waterproofing and secondary lining in ES1. Sprayed Concrete Secondary Lining is missing curing times. Pre-waterproofing Check is missing Engineer approval signature sheet missing
| 02SL - Stations (LUL) | Cxxx-NCR-001974 | NCR | WTH - Level -1 - Perimeter Walls 44 and 43 (east) - Concrete placed more than 2 hours after batching |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-09-25 | 2015-09-17 10:32 | -8 | 2015-09-01 15:09 | Civil - Civil Engineering General | 2500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Due to mis-communication between and __ (LC), 3 concrete wagons were sent to site too early and without enough time between them for the early-start Saturday pour of WTH Level -1 Walls 43 (east) and 44. This resulted in one load being used after 2h had elapsed from batching. Please see attached Concrete Control Sheet.
| 02SL - Stations (LUL) | Cxxx-NCR-001975 | NCR | SCL - Regulating layer inspection by Project Manager |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-09-30 | 2015-09-28 15:57 | -2 | 2015-09-01 15:34 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Verification Problems - Inspection points not adequate | Completed |  | ITP specifies check for regulating layer only as a witness point for CRL what is against requirements in KW20.
| 02SL - Stations (LUL) | Cxxx-NCR-001976 | NCR | SCL - ES1 Damage to Sprayed Waterproofing at Joint |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-09-30 | 2015-09-28 17:11 | -2 | 2015-09-04 09:14 | Tunnelling - Linings - Sprayed Concrete | 2800 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | have damaged the sprayed waterproofing in Escalator Shaft 1, Chainage 14.9 to CH20.9, on the RHS of the tunnel and CH16.3 to 20.2 on the LHS of the tunnel. The damage is at the joint between the invert and the far face concrete at a level of 85.300. The damage is in an area 200mm in width. The damage was caused by the removal of rebound at the sprayed joint. As there is no access behind the already sprayed concrete, there is not sufficient lap available for repairing the TamSeal.
| 02SL - Stations (LUL) | Cxxx-NCR-001977 | NCR | WTH - Level -1 Perimeter Walls - Wall 45 east stop end damaged __ water bar |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-10-02 | 2015-10-02 10:07 | 0 | 2015-09-18 16:51 | Civil - Civil Engineering General | 1000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | During the striking of the east stopend formwork on wall 45 the water bar has been damaged (squashed). See picture attached. The outside water bar remains attached to the cast part but has lost the shape and integrity.
| 02SL - Stations (LUL) | Cxxx-NCR-001978 | NCR | WTH - Level -1 Perimeter Walls - Wall 43 damaged __ Water Bar |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-10-02 | 2015-10-02 10:05 | 0 | 2015-09-18 16:59 | Civil - Civil Engineering General | 1000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | During the striking of the formwork on wall 43 east opening the water bar has been damaged (truncated). See picture attached. The outside water bar remains attached to the cast part with circa 10% of the cross section.
| 02SL - Stations (LUL) | Cxxx-NCR-001979 | NCR | SCL - Hollow test on CH1/CP3 invert thickening |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-10-01 | 2015-09-30 10:09 | -1 | 2015-09-04 16:39 | Tunnelling - Linings - Sprayed Concrete | 6000 |  | Workmanship | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | At the junction between CH1 and CP3B invert thickening hollow sounds have been found in the areas marked on the attached sketch. Following discussions with Cxxx, the understanding is that the second layer of the thickening has parcially debonded from the first layer. Please find attached western side of the thickening hollow area in addition to the sketch submitted originally.(CH55.4 to CH57.6 at CH1 Horizontal offset 2.3m (on the Northern side of CH1), approximatly 1 metre wide)
| 02SL - Stations (LUL) | Cxxx-NCR-001980 | NCR | WTH SH-W2 Level -1 Eastern Pilecap Excess Cover |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-09-22 | 2015-09-22 08:27 | 0 | 2015-09-08 08:13 | Civil - Civil Engineering General | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | Cxxx-FCD-000974 states that concrete members greater than 2m in depth can have cover up to +72.5mm (assuming 50mm cover). The Level -1 Eastern pilecap to SH-W2 is 2.5m in depth. In some areas we had cover of up to 90mm. In these areas A393 mesh was added to reduce the cover to allowable limits. See attached drawings showing the location of the mesh.
| 02SL - Stations (LUL) | Cxxx-NCR-001983 | NCR | SCL - ES2 top heading advance - tight profile and reduced steel cover |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-10-01 | 2015-09-25 08:53 | -6 | 2015-09-08 18:07 | Tunnelling - Linings - Sprayed Concrete | 2500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The kwikastrip on the right hand side of top heading advance no. 34 (looking downhill) has been installed in the incorrect location. This has resulted in the steel being installed with reduced cover of min. 20mm and the sprayed profile being approx. 40mm tight in some sections within the affected area. (Please see attached marked up photograph showing said location).
| 02SL - Stations (LUL) | Cxxx-NCR-001984 | NCR | SCL - Waterproofing detail around ETH piles on the CP9 connection |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-09-22 | 2015-09-17 11:34 | -5 | 2015-09-08 22:38 | Tunnelling - Linings - In-situ Concrete | 2500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Waterproofing detail drawing Cxxx-MMD-C4-DDD-M123_Z-00060 "SCL Box Connection Detail Cross Passage CP9" note number 10 states the following "Double layer of fleece applied around full connection perimeter". Waterproofing on Box to CP9 connection has been already installed at the bottom of the opening and on the sides up to level 85.300, where only 1 layer of geotextile has been applied around the connection perimetre.
| 02SL - Stations (LUL) | Cxxx-NCR-001985 | NCR | ETH-Trapezoidal Shaft - Level -2 - Lining Wall 1 Groutloss in Wall Pour |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-10-02 | 2015-10-05 14:46 | 3 | 2015-09-18 08:55 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | After striking lining wall 1 shutter at L-2, grout loss was identified at the base of the pour (area around lining wall and beam connection). Please find attached plan and relevant photographs showing the locations. The honeycombing is a result of grout loss at the connection between the Doka panel and concrete beam.
| 02SL - Stations (LUL) | Cxxx-NCR-001986 | NCR | ARC - Starting GRC Cladding prototype works & testing without accepted ITP |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-11-27 | 2015-11-19 09:53 | -8 | 2015-09-14 08:17 | Architectural - General | 2500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | Starting GRC Cladding prototype works & testing without accepted ITP.
| 02SL - Stations (LUL) | Cxxx-NCR-001988 | NCR | Decal 2 & 3 documents overdue for resubmission |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2015-10-13 | 2015-10-12 16:48 | -1 | 2015-09-15 08:12 | Architectural - Finishes | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | Documents overdue for resubmission as listed: Cxxx--A-RGN-M123-50048 rev 1, Cxxx--A-RGN-M123-50048 rev 1 , Cxxx--A-RGN-M123-50047 rev 1 , Cxxx--A-RGN-M123-50045 rev 1 and Cxxx--K1-RGN-M123-50002 rev 2. Part 14.1 of works information volume 2B requires resubmission within the period of reply ( 14 days) some of the above are overdue by 8 months
| 02SL - Stations (LUL) | Cxxx-NCR-001989 | NCR | WTH Level -1 – Unnecessary scabbling on construction joint with SH-W3 capping beam |  | Contr | 201068 | FAR - Farringdon Station (West) |  | 2016-01-29 | 2016-01-20 16:42 | -9 | 2015-09-15 12:17 | Civil - Civil Engineering General | 750 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | At the level -1 construction joint on the east capping slab (area shown on sketch attached), a section of the previous construction joint was unnecessarily scabbled where there is actually a box out in the slab.
| 02SL - Stations (LUL) | Cxxx-NCR-001990 | NCR | WTH Level -1 – Poor concrete finish on the eastern capping slab pour, Wall 28 & Wall 7 |  | Contr | 201068 | FAR - Farringdon Station (West) |  | 2016-01-29 | 2016-01-29 15:14 | 0 | 2015-09-16 11:47 | Civil - Civil Engineering General | 4000 |  | Workmanship | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | For the SH-W2 eastern capping slab pour the following defects have occurred with regards to the concrete finish: 1. The finish at the base of the box out is uneven and not flush with design level and numerous concrete spacers are exposed where they had been supporting the timber box out 2. Large blow holes on the north (central) face of wall 28 3. Blow holes on north (western-most) face of wall 28 4. Blow holes and pour line visible on Wall 7 5. A misaligned surface on the face of wall 7 combined with grout runs 6. Where column holding down bolts have been installed for column SC6 the concrete hasn’t achieved the level to the underside of the timber template holding the bolts in place 7. Missed chamfer on external corner, north side of wall 28 The numbers above relate to the attached sketch (Cxxx-NCR-001990-east-slab-finish).
| 02SL - Stations (LUL) | Cxxx-NCR-001991 | NCR | UTX's out from theoretical position |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-10-30 | 2015-10-12 15:22 | -18 | 2015-09-15 17:10 | Electrical - General | 2500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Not Defined | Completed |  | the UTX in the chainages between Chainage 7104.906 to 7129.906 and Chainage 7129.906 to 7152.906 were installed out of the theoretical position by 3 metres towards the east The Following UTX ducts were installed 3 metres EAST from their theoretical position : • Located in bay 5 ( Chainage 7104.906 to 7129.906) 2 No . UTX type 3 2No. UTX type 2 • Located in bay 6 Chainage 7129.906 to 7152.906 2No. type 1 find attached the drawing Cxxx--DDA-M123_8-50244 MARKED UP that it is an extract of the FCD: Cxxx-FCD-001726 Platform - Cxxx UTX Ducts Omission showing the theoretical location of the UTX’s
| 02SL - Stations (LUL) | Cxxx-NCR-001992 | NCR | WTH Excessive cover to SH-W2 Level -1 Western Pilecap |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-09-30 | 2015-09-28 14:03 | -2 | 2015-09-16 08:08 | Civil - Civil Engineering General | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Previous Construction - Problems based on previous construction errors | Completed |  | Cxxx-FCD-000974 states that concrete members of 2m in depth can have cover up to +72.5mm (assuming 50mm cover). The Level -1 Western pilecap to SH-W2 is 2m in depth. In some areas we had cover of up to 80mm. In these areas A393 mesh was added to reduce the cover to allowable limits. See attached drawings showing the location of the mesh and cover measurements post-mesh installation. Note this section of capping beam was poured on 11/09/2015.
| 02SL - Stations (LUL) | Cxxx-NCR-001993 | NCR | SCL - Insufficient Curing of STW3 Invert |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-10-09 | 2015-10-01 16:04 | -8 | 2015-09-21 12:50 | Tunnelling - Linings - In-situ Concrete | 2500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | After the casting STW3 invert, the invert was not cured in accordance with specification. Damp hessian was not applied for the curing phase, contrary to ITP Cxxx--C4-ITP-M123-50060 Item 3.27.
| 02SL - Stations (LUL) | Cxxx-NCR-001994 | NCR | SCL - CP6a Cast Secondary Lining Finish not F2 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-06-17 | 2016-05-18 10:12 | -30 | 2015-09-22 14:14 | Tunnelling - Linings - In-situ Concrete | 2500 |  | Material | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The secondary lining finish of CP6a bays 1 and 2 is below the F2 standard required by the Works Information. There is significant grout loss from bay 2 onto bay 1.
| 02SL - Stations (LUL) | Cxxx-NCR-001995 | NCR | WTH SH-W2 Wall 11 Level -3 to -1 Excess Cover |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-10-05 | 2015-10-05 09:00 | 0 | 2015-09-21 09:48 | Civil - Civil Engineering General | 2000 |  | Planning | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Cxxx-FCD-000974 states that concrete members less than 1m in width can have cover between 45mm and 60mm. (assuming 50mm cover). The Northern 800mm of wall 11 (both east and west faces between Level -3 and -1) had between 70-80mm of cover over its full height. Additional 20mm bars were added in that region to reduce cover to acceptable limits. Please see attached documents showing the affected areas and the photos before and after the 20mm bars were installed.
| 02SL - Stations (LUL) | Cxxx-NCR-001996 | NCR | ETH - 2SB- Upper escalator slab / W19 - Cast in couplers |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-10-07 | 2015-10-02 12:12 | -5 | 2015-09-23 08:31 | Civil - Civil Engineering General | 2500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | have installed the temporary works required to build the upper escalator ramp (falsework and soffit) and currently steelfixers are fixing the reinforcement. On scabbling Wall W19/W5 at L-3 (see attached mark up drawing), 2 issues were found with Bar mark 61 and 48 on drawing Cxxx-ATK-S-DWG-M123_2-50102. See below issues found: 1) has exposed the couplers on wall W19 where it steps out and the B2 couplers (BM48) are too low. The distance from the underside of B2 couplers to the soffit is approximately 30mm. 2) The couplers were not shown on drawing Cxxx-ATK-S-DWG-M123_2-50102 rev C02 which was current at the time of casting W19/W5. raised C453-RFI-00454 which agreed 4No couplers (2No. T2 and 2No. B2) see attached. Drawing Cxxx-ATK-S-DWG-M123_2-50102 rev C03 however now shows 6No couplers (3No T2 and 3No B2).
| 02SL - Stations (LUL) | Cxxx-NCR-001997 | NCR | SCL - Voids in CP9 ETH Connection Pour |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-10-30 | 2015-10-12 15:03 | -18 | 2015-09-22 14:01 | Tunnelling - Linings - In-situ Concrete | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In striking the CP9 Headwall, found voids in the crown of the pour. There is no steel reinforcement in the area of these voids. See attached pictures for location.
| 02SL - Stations (LUL) | Cxxx-NCR-001998 | NCR | WTH - South East Slab - Non compliance with BS EN 206 Criterion 2 |  | Contr | 201068 | FAR - Farringdon Station (West) |  | 2015-10-30 | 2015-10-07 12:40 | -23 | 2015-09-23 11:27 | Civil - Civil Engineering General | 2500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | From the cube results obtained from the Level -1 south east slab pour one set of cubes failed BS EN 206 Criterion 2, where the average of the 56 day results are more than 4N/mm2 away from the characteristic strength. Note the use of 56 day strength was accepted in Cxxx-FCD-001677 for the SL6.1A mix (Cxxx--C-LRC-M123-50530). It should be noted however that the non-compliance was by only 0.1N/mm2. See attached the concrete compliance summary sheet.
| 02SL - Stations (LUL) | Cxxx-NCR-001999 | NCR | ETH - Barbican Station Pile Caps - Pile Head to Pile Cap Detail |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-10-07 | 2015-09-24 14:58 | -13 | 2015-09-23 09:58 | Civil - Civil Engineering General | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | The L-bars that extend from the pile head into the pile caps were delivered at a length shorter than was required. The bars were not checked before they were installed and the minimum 40xdiameter anchorage length specified on drawing number Cxxx--S-DDB-M123_Z-41003 was not achieved. The issue was highlighted in the pre-pour check.
| 02SL - Stations (LUL) | Cxxx-NCR-002000 | NCR | FSC Platforms concrete results not achieving 56-day compressive strength required |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-12-15 | 2015-12-02 12:42 | -13 | 2015-10-22 14:52 | Materials - General | 2500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Not Defined | Completed |  | has received the results after 56 days for the section of bay 4 showing a average compressive strength of 43 Mpa that is below the strength requirement EX1933 - 43.0 Mpa EX1934 - 43.7 Mpa The minimum acceptable value is 46 MPa in accordance with BS EN 206-1. See attached platform concrete table for the results to date . Following the specification c136-SWN-C-RSP-M123-00004 clause KF10.2207 f). took cores for the area affected in different locations (total of 4 cores bay 4) on the 5th of October 2015, the 56th day was on 2nd of October Applying a reduction of 0.69N/mm2 per week of age in excess of 28 days the result should have a strength of 40.74 Mpa taking into account the average of the result of the cores. The cores where crushed give the results as follows: 43.9 MPa, 42.4 MPa ,43.5 Mpa and 44.2 Mpa. Also refer to Cxxx-FCD-001661 - Relaxtion of long term compressive strength from 28 to 56 days
| 02SL - Stations (LUL) | Cxxx-NCR-002001 | NCR | SCL - Breakthrough into RTE2 Tunnel when Excavating ES2 Primary Lining |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-11-05 | 2015-10-21 14:49 | -15 | 2015-09-25 17:57 | Tunnelling - Linings - Sprayed Concrete | 4000 |  | Damaged | Repair | 3 (3-6k) | Complete | Personnel Error - Not Defined | Completed |  | During the excavation of ES2 Invert 52, whilst excavating, the equipment broke into RTE2 tunnel which lies directly below this invert advance. The first picture shows the extent of the breakthrough. The damage occured at Chainage 18.5 on the RHS invert of ES2 and at Chainage 15.7 on the LHS crown in RTE2.
| 02SL - Stations (LUL) | Cxxx-NCR-002002 | NCR | ETH 2SB Surfaces Cracks in Level 0 Slab Area A |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-10-08 | 2015-10-05 15:31 | -3 | 2015-09-24 11:26 | Civil - Civil Engineering General | 2500 |  | Material | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | 7 no. surface cracks to the top of the Level 0 slab were identified in Area A (see attached sketch Cxxx/SB/SR/ETH/SB58 - showing location). These cracks exceed the limit of 0.3mm permitted within the specification. Cracks have been monitored since the 15/07/2015 to date. Records attached. The cracks are not increasing in size and final size is as recorded below. Crack 1 - 0.7mm Crack 2 - 0.7mm Crack 3 - 0.6mm Crack 4 - 0.3mm Crack 5 - 0.3mm Crack 6 - 0.6mm Crack 7 - 0.65mm Photographs off Cracks 1 to 7 are attached for reference.
| 02SL - Stations (LUL) | Cxxx-NCR-002003 | NCR | ETH - Trapezoidal Shaft - Level -2 Internal Wall W24 - Cast in Wall Starter Alignment Clashing with Threaded Lacers in Capping Beam and Geothermal Pipes |  | Contr | BAM | FAR - Farringdon Station (West) |  | 2015-10-09 | 2015-09-30 12:54 | -9 | 2015-09-25 13:12 | Civil - Civil Engineering General | 3000 |  | Design | Repair | 4 (0.5-3k) | Complete | Previous Construction - Problems based on previous construction errors | Completed |  | are currently installing wall W24 reinforcement in between level -2 to -1 in the vicinity of the geothermal pipes in the level -2 slab where we cast in the wall starter couplers into the slab and the east capping beam on the 18/11/13. Note, all __ redlines, __ RFIs (Cxxx-BKF-RFI-00054 and 00755), Cxxx RC intent drawings and CRL PTRs (Cxxx-RFI-001954) have been referenced or attached below. Currently the __ drawing (marked up and attached below) shows 2No B40 front and back to be drilled and fixed into the capping beam. However, site has cast in B32 couplers within the capping beam to accommodate threaded bars even though these are the wrong size coupler. The couplers however cannot all be used as some of the bars once threaded into the couplers will clash with the existing cast-in wall starter couplers and the existing cast in geothermal pipes. I have attached the Cxxx--RFI-00755 confirming __ position on ’s proposal to drill and fix nearer to the centre of the wall rather then EF3. Please confirm that this will be acceptable.
| 02SL - Stations (LUL) | Cxxx-NCR-002005 | NCR | SCL - August 2015 Cast Flexural Beam Failures |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-12-28 | 2015-10-15 11:11 | -74 | 2015-09-29 18:08 | Tunnelling - Linings - In-situ Concrete | 2500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Two of the three cast beams for flexural strength tests for August 2015 for 29 have failed the D3S1.4 criteria at 28 days. See attached files. One is a rebound loop, the second is a crack through the beam from when the notch is formed.
| 02SL - Stations (LUL) | Cxxx-NCR-002006 | NCR | ETH- Omission of Angle Fillet from Wall 9 Doorwway on Level-2 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-10-14 | 2015-10-13 13:38 | -1 | 2015-09-30 08:02 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | After striking the doorway shutters of Wall 9 at L-2, it was identified that the angle fillet that should have been positioned in the vertex of the North Eastern edge of the doorway was missing. This left a sharp edge in the doorway and it does not match the other edge surfaces of the dorway. Please find attached plan and relevant photographs showing the locations.
| 02SL - Stations (LUL) | Cxxx-NCR-002007 | NCR | ETH- Unnecessary Preparation of Concrete Surface for Cavity Wall Upstand on ESS2 Midlanding at 89.840 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-10-14 | 2015-10-13 13:37 | -1 | 2015-09-30 08:12 | Civil - Civil Engineering General | 1000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | In the ESS 2 staircore on the midlanding situated at the height of 89.840, the area on the floor along the capping beam adjacent to wall 5, was unecessarily scabbled and prepared for a cavity wall upstand.
| 02SL - Stations (LUL) | Cxxx-NCR-002008 | NCR | WTH SHW2 Small Parallelogram Void_ Level -1 Suspended Slab |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-10-01 | 2015-10-01 13:23 | 0 | 2015-09-30 13:20 | Civil - Civil Engineering General | 2500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | A single U-shaped reinforcement bar (BM N281), South of the small parallelogram void, on the southern part of the SH-W2 Level -1 suspended slab, was cast incorrectly into the Southern pilecap (see attached photo). An additional U-bar was drilled into the existing Southern pilecap as a replacement (see photo).
| 02SL - Stations (LUL) | Cxxx-NCR-002009 | NCR | WTH SH-W2 Level -1 Slab Tie-in Aborted Pour |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-10-01 | 2015-09-30 17:02 | -1 | 2015-09-30 15:16 | Civil - Civil Engineering General | 5000 |  | Incomplete Works | Rework | 3 (3-6k) | Complete | Material/Preservation Problems - Insufficient quantity of material to do the job | Completed |  | Clause KF10.3203(c) states that concreting of any unit or section of the works shall be carried out in one continuous operation. Additionally, clause KF10.3203(h) states that there can be no more than 1 hour between fresh concrete being placed on top of existing in-situ fresh concrete. commenced the Level -1 slab pour (see attachment for pour area). After the first lorry had completed discharging there was a gap of over 2 hours before the second lorry arrived. This load subsequently failed the slump test and was rejected and it was not possible to recover the existing concrete. At this point it was decided to abort the pour.
| 02SL - Stations (LUL) | Cxxx-NCR-002010 | NCR | ETH - Upper Escalator Slab Excess Cover Pour 1 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-10-15 | 2015-10-01 13:35 | -14 | 2015-10-01 09:41 | Civil - Civil Engineering General | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During installation of the T1 bars for the Upper Escalator an area of excess cover was identified. (See attached cover survey) Cover requirement according to drawing Cxxx-ATK-S-DWG-M123_2-50102 is 40mm with a tolerance of +10/-5 in accordance with FCD-00974.
| 02SL - Stations (LUL) | Cxxx-NCR-002011 | NCR | PLT - Not following procedure identified in FCD for testing concrete from onsite batching plant |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-11-30 | 2015-11-06 13:02 | -24 | 2015-10-05 09:59 | Civil - Tunnelling | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | Platform slab construction bay 6 FCD Cxxx-FCD-OO1810 states that the first 5 batches produced from the onsite batching plant will be tested and if results fall within the range of 500-630mm the next 5 can be visually inspected and the 6th tested if any fall outside the tolerances they will all be tested until confidence has returned. Testing check sheet from __ for the platfrom slab pour on the 1/10/15 shows that only the first 3 pours had been tested before visual testing carried out on the next five does not following the process within the FCD
| 02SL - Stations (LUL) | Cxxx-NCR-002012 | NCR | SCL - Quality cores procedure |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-11-12 | 2015-10-14 11:25 | -29 | 2015-10-06 12:51 | Tunnelling - Tunnelling General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Not Defined | Completed |  | did not follow its grading procedure. Because of that, CP8, CP9 have no core reports (no grades and no pictures) and ES1 cores were only graded buy shift managers.
| 02SL - Stations (LUL) | Cxxx-NCR-002013 | NCR | WTH SH-W2 Walls 10 & 16 Level -3 to Level -1 – Exceeding concrete placement time |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-10-19 | 2015-10-07 09:01 | -12 | 2015-10-05 12:41 | Civil - Civil Engineering General | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Clause KF10.3203h states that there can be no more than 1 hour between fresh concrete being placed on top of existing in-situ fresh concrete. When pouring Walls 10 & 16 between Level -3 and Level -1 on 15/09/2015 it was observed that a lorry finished discharging at 12:15pm and the next lorry did not start discharging until 13:30pm which contravenes the specification.
| 02SL - Stations (LUL) | Cxxx-NCR-002014 | NCR | WTH - Honeycombing on Wall 50 1st lift |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-11-15 | 2015-11-13 17:17 | -2 | 2015-10-19 15:36 | Structural Engineering - Finishes | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | There were 2no. small areas of honeycombing at the base of the 1st lift pour of Wall 50. These were caused by poor compaction in these very small areas.
| 02SL - Stations (LUL) | Cxxx-NCR-002015 | NCR | WTH - ES1/SHW3 mass fill stepped ramp concrete finishes |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-11-20 | 2015-11-20 11:31 | 0 | 2015-10-05 16:46 | Structural Engineering - Finishes | 3000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Clause KF10.3222 l) of the Civil & Structural Specification states that all exposed arises of concrete should be chamfered. The edges of the steps on the mass fill ramp of SHW3/ES1 have not been chamfered. Please see the attached photo highlighting an example section of the concrete edge breaking away due to the missing chamfer. Cxxx-RFI-002822 accepts an F2 finish for the top of the stepped ramp in SHW3/ES1. Pitting on the top of the steps caused by trapped air in the lidded shutter in multiple locations mean the F2 finish has not been achieved. Please see attached photo highlighting example areas of pitting.
| 02SL - Stations (LUL) | Cxxx-NCR-002016 | NCR | Uncontrolled loading of slab |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-11-02 | 2015-10-30 12:21 | -3 | 2015-10-06 14:08 | Tunnelling - Linings - In-situ Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Supervision - Other | Completed |  | While moving mesh in tunnel, an additional bundle of mesh was loaded onto the slab which exceeded the signage of 120kg/m3. Currently have signage on the hoarding of the platform nosing showing 120kg/m3. This equates to 2 x bundles of mesh, or 24 sheets of mesh. The excavator driver loaded an additional bundle onto the platform. He was found within 30mins and the bundle removed.
| 02SL - Stations (LUL) | Cxxx-NCR-002017 | NCR | ETH - Level L-1 slab reduced size of MEP opening infront of wall W23 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-10-29 | 2015-10-28 10:43 | -1 | 2015-10-08 11:17 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | The cavity wall upstand in front of lining wall W23 encroaches with a MEP opening in front of W23 and reduces the width from 200mm by about 15mm (see attached marked up drawing and photo). The kicker and the opening were installed within the tolerance given in the concrete ITP Cxxx--C-ITP-M123-50009 (see attached as build survey of the kicker for wall W23 and the opening).
| 02SL - Stations (LUL) | Cxxx-NCR-002018 | NCR | ETH - SB L-2 drainage opening clash with lining wall W21 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-11-06 | 2015-11-03 12:09 | -3 | 2015-10-13 07:53 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | One opening of the cavity wall drainage at Level L-2 in front of wall W21 clashes by about 10mm with the face of lining wall W21 (see attached photo).
| 02SL - Stations (LUL) | Cxxx-NCR-002019 | NCR | ETH - Trapezoidal Shaft - Level -6 Slab Over-coring Mass Fill Void & Damaging L-6 Slab |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-10-23 | 2015-10-20 14:10 | -3 | 2015-10-09 08:58 | Civil - Civil Engineering General | 2950 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | During the construction of the level -6 slab 4nr voids were mass filled, in accordance with Cxxx-SWN-S-DDA-M123_7-40650 C02. have now removed the concrete mass fill using a 100mm core drill. During the coring operation, the coring rig was positioned incorrectly in three locations on the South East void and subsequently cored 40mm, 30mm and 25mm respectively out of the L-6 slab. A single reinforcement bar has been damaged during this coring. See attached photos.
| 02SL - Stations (LUL) | Cxxx-NCR-002021 | NCR | ETH - Trapezoidal Shaft - Level-4 - Damaged couplers for UPE |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-12-18 | 2015-12-09 12:48 | -9 | 2015-10-13 23:23 | Civil - Civil Engineering General | 2500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | During the construction of ES2 the SCL team required level -4 to mine from. As heavy machinery was required to operate on the slab, the ETH team opted to cast 150mm of blinding over the slab to protect already cast couplers for UPE. During the removal of 150mm blinding a number of couplers were damaged. Please see attached photos as well as marked up drawing of damaged couplers.
| 02SL - Stations (LUL) | Cxxx-NCR-002022 | NCR | ETH - Procedural NCR - Concrete pour Upper Escalator Ramp |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-10-24 | 2015-10-20 11:50 | -4 | 2015-10-10 13:30 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Reject | 4 (0.5-3k) | Complete | Procedure Problem - Lack of procedure | Completed |  | As part of the concrete pour of the upper escalator ramp on 08/10/2015 __ delivered the wrong concrete mix with the first waggon. __ delivered a SL4 mix instead of the required SL2 mix for the upper escalator ramp. This was discovered during the slum test. Furthermore it was witnessed that the driver added water to the concrete. The concrete was rejected, none of the concrete from this load was used for the concrete pour.
| 02SL - Stations (LUL) | Cxxx-NCR-002023 | NCR | ETH - Cavity Wall Drainage |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-10-23 | 2015-10-20 14:56 | -3 | 2015-10-09 13:58 | Civil - Drainage | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | commenced installation of cavity wall drainage at Level -7 without approved construction drawings in place. __ issued a sketch to but this had not been through the correct approval process.
| 02SL - Stations (LUL) | Cxxx-NCR-002024 | NCR | WTH - Level -1 Perimeter Walls 44 & 43 holding down bolts for SC12 columns out of positional tolerance |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-11-20 | 2015-11-19 16:22 | -1 | 2015-10-12 16:04 | Structural Engineering - Steel Member | 3000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Other human error | Completed |  | Bolt clusters for columns SC12 baseplates adjacent to GL's- G, H,1,2 (__ ref.: G+5m/1+4m and G+9m/1+5m Cxxx--S-DDD-M123_Z-70107) ( __ Ref.: C09 & C10 Cxxx--X-DWG-M123-50086) on walls 43 and 44 have been set out and cast out of positional tolerance. Cardboard cones could not be used due to bolts being only 100mm apart; therefore bolts are now fully encased in concrete to the baseplate level. Please refer to survey drawings attached.
| 02SL - Stations (LUL) | Cxxx-NCR-002026 | NCR | ETH - reduced concrete cover on Wall W20 Level L 0 GL4 to GL5.5 east side |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-12-11 | 2015-11-24 09:22 | -17 | 2015-10-13 17:18 | Civil - Civil Engineering General | 2500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | The line of the concrete kicker of wall W20 between GL4 to GL5.5 east side needed to be corrected due to the type of shutter to be used for Wall W20 Level L0 to +3. As the result there is reduced cover on the east side. Please find attached cover survey. The values shown in the survey state the distance measured between the front face of the kicker and the vertical reinforcement. A reading is taken every 3rd bar which means measurements were taken at about 0.5m centres. The smallest cover is between reading 13 and 14 which would currently result in 24mm (40mm - 16mm bar) of concrete cover over a very localised area. reckons that within 1m from the kicker the design cover is established. Everywhere else we have at least 30mm concrete cover
| 02SL - Stations (LUL) | Cxxx-NCR-002027 | NCR | SCL - Cracks in Secondary Lining Invert of VA1 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-03-18 | 2016-02-03 12:46 | -44 | 2015-10-12 13:47 | Tunnelling - Linings - In-situ Concrete | 2500 |  | Material | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | There are two cracks in VA1 Secondary Lining Invert, at Chainage 15 and Chainage 22, both of which have an average initial crack width of 1.0mm. The cracks span the full width of the invert and are full depth. They have both been placed on the crack register.
| 02SL - Stations (LUL) | Cxxx-NCR-002028 | NCR | STW - Welding of 22mm shear studs to 25mm plate without a correct WPQR / WPS |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-11-16 | 2015-11-13 11:18 | -3 | 2015-10-12 17:20 | Structural Engineering - Welding | 2500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | __, 's steelwork subcontractor, are fabricating the cast-in plates for both the ETH & WTH superstructures. A number of these plates (which have already been fabricated) have 22mm shear studs welded onto 25mm thick plate. Previously, __'s Responsible Welding Co-ordinator (RWC) verbally advised that the plate thickness did not matter for shear stud welds, hence it was believed the WPS & WPQR BS/WP/237 provided on the __ Welding Competencies Document (Cxxx--X-LRC-M123-50001) qualified these welds. The __ RWC has since been advised by their independent welding testing house that this is not the case - hence these welds have taken place without a qualifying WPS / WPQR. Please see attached NCR 001 (ETH) and NCR 002 (WTH) documents raised by __ which provide further details.
| 02SL - Stations (LUL) | Cxxx-NCR-002029 | NCR | WTH Concrete Column Nib at GL C4 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-10-19 | 2015-10-19 15:42 | 0 | 2015-10-13 14:05 | Civil - Civil Engineering General | 3000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | The concrete nib (GL C/4) shown in the attached sketches has been set out incorrectly and as a result the reinforcement has been fixed incorrectly to these marks. The reinforcement bars are approximately 100mm to far South. As moving the bars would be a very large undertaking now that the majority of T1 bars and shear links are fixed, are proposing to extend the nib and cast it approximately 100mm further South (nib to be cast to provide 50mm cover to outer most bar) of the theoretical position. The column anchor bolts and 245mm wide upstand will not change position only the concrete nib will be approximately 100mm larger. Please see attached documentation. Cxxx--RFI-00779 has been raised to __ to determine whether there is any architectural conflicts.
| 02SL - Stations (LUL) | Cxxx-NCR-002030 | NCR | SCL - Void in PTE Crown/VA2 Junction Pour |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-12-18 | 2015-12-11 10:59 | -7 | 2015-10-20 12:07 | Tunnelling - Linings - In-situ Concrete | 4000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A void has been found in PTE Crown/VA2 Junction, Chainage 296-308, Crown Bay 20 pour. The size of the void is seven metres by 300mm high by up to 2.5 metres back, see the sketch and photo attached for clarity. The void is situated between the stop end of Crown Bay 19 (the previous pour) and the opening of VA2. It was found during the removal of the polystyrene void former used for casting VA2.
| 02SL - Stations (LUL) | Cxxx-NCR-002031 | NCR | ETH - Upper Sloping Slab Incomplete Pour 2 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-06-09 | 2017-05-24 14:29 | -16 | 2015-10-21 11:55 | Civil - Civil Engineering General | 3000 |  | Incomplete Works | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Upper Concrete Slab Pour 2 was carried out 17/10/2015. Several non-conformances occurred which are summarized below: 1. The fourth concrete load was batched at 09:51 (Ticket 70477369). It was slump tested and found to be within the S4 specification, 180mm. Placing of the concrete started at approximately 14:00 and therefore time between batching and placing exceeds the limit specified in FCD-001173. (3 hours for mix W5/W7). Approximately 2m3 of concrete was used from this wagon before the concrete was returned as it was out of specification. 2. A fifth wagon was utilised but the placement time between the fourth and fifth wagon was approximately 1.5hours. ( 14:45 – 16:15) which is outside of the 1 hour specification allowance. 3. The pour was not completed to the planned pour level as no further concrete was available resulting in the pour being three steps short and creating two localized valleys in the 9th Step. Remedial works will be required prior to subsequent pour for construction joint. 4. On striking the shutter for the sloped side an area of voids has been identified ( Refer to Photograph Ref: NCR- UER Pour 2 Sloped Side). The out of specification concrete contributed to these voids (mentioned in Point 1).
| 02SL - Stations (LUL) | Cxxx-NCR-002033 | NCR | ETH - Trapezoidal Shaft - Wall 14 - Low Cover |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-11-26 | 2015-11-18 14:42 | -8 | 2015-10-22 13:32 | Civil - Civil Engineering General | 2500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following the installation of reinforcement of Wall 14 At Level -6 ETH Trapezoidal Shaft. identified that the cover is below the required 30mm. Note following Cxxx-FCD-00974 range of tolerance is between 25mm-40mm. Areas are very localized as seen in attached cover survey.
| 02SL - Stations (LUL) | Cxxx-NCR-002034 | NCR | ETH - Welding Procedure for Butt Welds to C4 and C5 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-11-27 | 2015-11-19 09:34 | -8 | 2015-10-30 13:42 | Civil - Civil Engineering General | 6500 |  | Supervision/Management | Rework | 2 (6-60k) | Complete | Management Problem - Inadequate supervision | Completed |  | During the fabrication of the Columns C4 ( C7001) and C5 ( C7002) for ETH by __ (BSL) the following non conformance occurred: Both plates have 150mm thick base plates. Originally the thickness of the base plates was not picked up and a Welding Procedure Qualification Record (WPQR) was not arranged. It was agreed to run the WPQR and the as run data from the preliminary Weld Procedure Specification (pWPS) was then used to weld the columns whilst the WPQR was at the test house. This strategy developed into two issues. 1. The pWPS was not followed by production which led to inclusions in the welds which then failed testing. 2. The WPQR failed due to a low impact reading on the 150mm test plate. The WPQR has been rerun, passed and is attached. ( Reference: Welding Competency Records for Baseplate Welds C4 and C5)
| 02SL - Stations (LUL) | Cxxx-NCR-002035 | NCR | SCL - Low Density Result for CP6a Kickers |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-11-09 | 2015-10-29 11:42 | -11 | 2015-10-26 08:29 | Tunnelling - Linings - In-situ Concrete | 2500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | The 56 day cube density result for CP6a Kickers is an average of 2290kg/m3 (EX 2013), this is lower than the specification requirement of 2300kg/m3.
| 02SL - Stations (LUL) | Cxxx-NCR-002036 | NCR | WTH Wall 39 Kicker Recessed to Accommodate Cast-In Gully Locations |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-11-27 | 2015-11-27 16:14 | 0 | 2015-10-22 14:48 | Civil - Civil Engineering General | 3000 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | The two gullies as identified in drawings Cxxx--P-DDA-M123_2-75401 (C01) and Cxxx--P-DDA-M123_2-75403 (C01) have been installed into the Western pilecap of SH-W2. When casting the wall 39 kicker (western perimeter wall) to the L-1 slab it was found that the two gullies protrude into the kicker by up to 30mm and so the kicker was notched out to accommodate them, see attached photographs. By notching out the kicker we have reduced the cover in these two isolated areas. The Northern-most gully has been notched out by approximately 30mm leaving cover to the coupler of 20mm. The Southern-most gully has been notched out by approximately 20mm reducing the cover to the coupler to 30mm.
| 02SL - Stations (LUL) | Cxxx-NCR-002037 | NCR | WTH - Mesh on top of C1A Slab to reduce cover |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-11-05 | 2015-11-04 11:49 | -1 | 2015-10-22 15:09 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | A cover survey of the top mat reinforcement (C1A Slab) was carried out as part of the pre-pour inspection. It was identified that the cover exceeded the limits stated in Cxxx-FCD-000974. Two metre deep slabs are allowed cover up to 72.5mm which had been exceeded. A393 mesh was added to the top of the slab to bring this value within the allowable tolerances. See attached sketches.
| 02SL - Stations (LUL) | Cxxx-NCR-002039 | NCR | WTH SH-W2 Foam cast into Level -4 upstand along Walls 6, 7 & 8 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-11-06 | 2015-11-06 10:59 | 0 | 2015-10-23 17:02 | Civil - Civil Engineering General | 2000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Concrete upstands as part of the cavity wall channel construction was cast at Level -4 in the corner between Walls 7 & 8 adjacent to a slab opening in the south and between Walls 6 and 7 adjacent to a slab opening in the north. See sketch attached highlighting the extent of this non-conformance. Prior to the pour, expanding foam was observed as being used to seal the joint between the upstand and the Level -4 slab. No access was available to remove the foam and so the upstand was poured. On striking the formwork the expanding foam was visible.
| 02SL - Stations (LUL) | Cxxx-NCR-002040 | NCR | WTH Level -1 Southern Pilecap to SH-W2 – Water added to concrete delivery on site |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-11-25 | 2015-11-25 17:20 | 0 | 2015-10-28 14:07 | Civil - Base Course | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | BS EN 206 (2013) Clause 7.5 (as part of CRL1-XRL-C-GPD-CR001-50001) states that no water can be added to a concrete delivery once it arrives on site. During the pouring of the Southern Pilecap it was observed that water was added to a concrete delivery that had arrived on site. This concrete was discharged into the pour.
| 02SL - Stations (LUL) | Cxxx-NCR-002041 | NCR | PLT - StaxoTemporary works checks |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-11-11 | 2015-11-06 09:44 | -5 | 2015-10-28 20:01 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Personnel Error - Not Defined | Completed |  | Although permit to load has been in used before the pour of the platform slabs, It has been highlighted that a permit to load should be used and in place once the formwork has been moved into position this to ensure that compliance with temporary works before any works are taking place on top of the slab
| 02SL - Stations (LUL) | Cxxx-NCR-002043 | NCR | ETH Two Storey Basement RC Walls W20, W28, W30 and W32 Level 0 to Level +1 Concrete finish |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-11-16 | 2015-11-12 10:39 | -4 | 2015-11-02 09:07 | Civil - Civil Engineering General | 1500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | has struck the formwork panels for Walls W20, W28, W30 and W32 from level 0 to level +1 in the Two Storey Basement. A post pour inspection has been carried out on the concrete finish of the walls (in both F3 and F4 areas) and there are a number of areas with small blow holes (see photos attached).
| 02SL - Stations (LUL) | Cxxx-NCR-002044 | NCR | WTH - Damaged __ for Level -1 Slab E2 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-11-27 | 2015-11-24 10:44 | -3 | 2015-11-04 09:57 | Civil - Civil Engineering General | 3000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | During excavation for the Level -1 Slab E2, historical __ laid and cast with Wall 33 to the West extent and the SHW3 capping beam to the South extent was damaged or the sections of __ protruding from the cast members were pulled away.
| 02SL - Stations (LUL) | Cxxx-NCR-002045 | NCR | SCL - PTW Bay 15 CH142.500-137.500 Tight |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-12-18 | 2015-11-30 09:09 | -18 | 2015-11-05 14:57 | Tunnelling - Linings - In-situ Concrete | 2500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | When striking the PTW shutter, it was clear that there was a large lip between Bay 14 and Bay 15 Crown pours in PTW. Further investigation found that the profile between chainage 137.500 and 142.500 on Bay 15 was tight by up to 20mm, please find attached the profiles for Bay 15 in the effected area. Bay 14 (CH143.5) is within tolerance but the overall effect is a 32mm step in the lining at this point.
| 02SL - Stations (LUL) | Cxxx-NCR-002046 | NCR | SCL - RTE2 Secondary Lining Tight CH 9.777-17.377 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-12-18 | 2015-11-17 09:17 | -31 | 2015-11-05 16:33 | Tunnelling - Linings - In-situ Concrete | 2500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The secondary lining in RTE2 between Chainage 9.777 and 17.377 is tighter than allowed within the Cxxx drawings. The worst location is 43mm tighter than is permitted (Chainage 13.939m), the profiles for these locations are attached.
| 02SL - Stations (LUL) | Cxxx-NCR-002047 | NCR | ETH - ESS2 Concrete Strength - Pour 6 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-12-04 | 2015-11-17 15:37 | -17 | 2015-11-06 17:24 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | Following the issue of a number of 28 day cube results for pour 6 of the ESS2 landing it was found that the W3 concrete design strength was not reached. The average 28 day strength was 45.7 N/mm2. The 56 day results show a compressive strength of 49.95 N/mm2 which again is below the design strength. 2 No. cubes are due to be crushed on 26/11/15 and are satisfied that design strength will be reached due to the 56 day being so close.
| 02SL - Stations (LUL) | Cxxx-NCR-002048 | NCR | SCL - RTE2 Bay 16 not an F2 finish |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-12-18 | 2015-12-18 10:59 | 0 | 2015-11-05 17:37 | Tunnelling - Linings - In-situ Concrete | 3000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Upon striking Bay 16 of RTE2, it became apparant that the finish for this bay was less than the required F2 finish. The location is between chainages 40.377 and 43.377. The areas which are not F2 are below axis. Between the turnaround of Bay 15 and Bay 16, there was no cleaning of the RTE2 shutter. This lack of cleaning led to the poor finish to the lining.
| 02SL - Stations (LUL) | Cxxx-NCR-002049 | NCR | SCL - Longitudinal Crack in PTE Crown between CP4 and CP6 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-09-16 | 2016-09-14 12:18 | -2 | 2015-11-05 17:54 | Tunnelling - Linings - In-situ Concrete | 2500 |  | Design | Repair | 4 (0.5-3k) | Complete | External Phenomenon - Not Defined | Completed |  | have found longitudinal cracks, situated in the crown of PTE platform tunnel. The chainages for the crack locations are below: - Chainage 119.849 to Chainage 146.856 - Crack Width 0.38mm Contact grouting has already occurred in all of these locations
| 02SL - Stations (LUL) | Cxxx-NCR-002050 | NCR | SCL - Cold Joint in VA2 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-04-15 | 2016-03-31 11:27 | -15 | 2015-11-06 13:47 | Tunnelling - Linings - In-situ Concrete | 2500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A horizontal cold joint has been found running through the concrete in the PTE/VA2 junction at approximately chainage 350. See attached pictures showing where the exact location.
| 02SL - Stations (LUL) | Cxxx-NCR-002051 | NCR | ETH - Trapezoidal Shaft Level -6 Wall 14 Poor concrete finish |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-11-20 | 2015-11-17 16:50 | -3 | 2015-11-06 17:32 | Civil - Civil Engineering General | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | After striking the shutters on Wall 14 Level -6, discovered several small areas of honeycombing on the North and South faces of the wall. The honeycombing is located aroud the box outs and where the wall sits on the L-6 slab. As well as the grout loss and a small recess created at the joint between L-6 slab and wall 14. This was casued by excessive foam being used between the underside of the shutter and L-6 slab. The recess extends 10mm into the face of the wall as seen in attached photos.
| 02SL - Stations (LUL) | Cxxx-NCR-002052 | NCR | WTH – SH-W2 Level -5 to Level -4 Wall Defects |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-11-10 | 2015-11-09 17:50 | -1 | 2015-11-06 17:07 | Civil - Civil Engineering General | 4000 |  | Workmanship | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following post-pour inspections of all walls cast between L-5 to L-4, the following defects were identified: 1) A 20 x 20mm chamfer was missed from the external corner of Walls 10 & 16 2) A 10mm step between a previously cast column kicker and the remainder of the column (RC15-2). 3) Wall misalignment – adjacent panels were not flush with one another so a small step greater than 4mm was created on the Southern side of Wall 25. 4) Wall misalignment – as No. 3 but on Wall 9 South 5) 6) 7) Surface repairs where minor grout loss has occurred, Wall 9m, Wall 19 (West) and Wall 19 (East). Attached sketch indicates the locations of all these defects with a sign off sheet confirming the defects were rectified.
| 02SL - Stations (LUL) | Cxxx-NCR-002053 | NCR | ETH - Trapezoidal Shaft - Missing couplers North Hanging Wall Escalator Pit |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-02-12 | 2016-02-11 10:43 | -1 | 2015-11-17 11:58 | Civil - Civil Engineering General | 2950 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Please see attached photo. Following scabbling works on soffit of Level -3 slab have identified a small area where couplers were not cast for North Hanging Wall Escalator Pit. and total number of 20 couplers are missing
| 02SL - Stations (LUL) | Cxxx-NCR-002054 | NCR | WTH - Level -1 Slab E2 Damage to Historical __ 500S Hydrophilic Strip |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-11-27 | 2015-11-27 16:32 | 0 | 2015-11-09 11:25 | Civil - Civil Engineering General | 2500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | During the waterproofing of the SHW3 capping beam, lengths of __ 500S hydrophilic strip were left protruding through the shutter marking the CJ with the Level -1 base slab E2, to be cast in the future. These lengths of __ 500S were left to allow a lap detail to be used as installation of __ continued during waterproofing of the slab E2. Due to the length of time these sections of __ have been left unprotected in backfill material and the nature of the excavation of the area for the slab E2, the "lap lengths" of the historical __ protruding from the previously cast SHW3 capping beam have been damaged and pulled away. The locations of the damaged __ 500S are indicated on the attached sketch "Location Sketch".
| 02SL - Stations (LUL) | Cxxx-NCR-002055 | NCR | WTH - Wall 50, 51 & 54 second lift pour concrete placement non-conformances |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-11-27 | 2015-11-25 17:01 | -2 | 2015-11-09 13:23 | Civil - Structural Engineering | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | poured the 2nd lift of Wall 50, 51 & 54 from level +111.150m to +118.230m on Thursday 4-11-15. Due to very inconsistent concrete supply there were the following non-conformances (please see attached structural control sheet for wagon references): 1. The time gap for the placement of concrete onto existing fresh concrete was greater than 1 hour between wagons 1 & 2 (1hr 40 mins) and 2 & 3 (2hrs 2 mins), 2. The time from batching to placing & compaction of concrete exceeded 2 hours for wagon 5 (2hrs 15 mins) The concrete mix used for the walls was W1(10)AD.
| 02SL - Stations (LUL) | Cxxx-NCR-002056 | NCR | SCL - PL4/RTE2 Headwall Cast Out of Tolerance |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-04-29 | 2016-04-13 13:15 | -16 | 2015-11-10 09:06 | Tunnelling - Linings - In-situ Concrete | 2500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | The PL4/RTE2 Headwall, chainage -1.72 from RTE2, has been cast out of tolerance. Please see attached sketch which shows the extent of the issue where the headwall has been cast up to 130 millimetres tight from chainage -1.72 of RTE2. As can be seen by the elevation on the sketch, the only issue is at the top of the first headwall pour, where the headwall meets the tunnel profile the headwall is as per design.
| 02SL - Stations (LUL) | Cxxx-NCR-002057 | NCR | ETH - Internal wall W30 Level L0 - grout loss at doorway |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-11-30 | 2015-11-24 09:43 | -6 | 2015-11-16 17:27 | Civil - Civil Engineering General | 1000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | When striking the formwork on the west side of the door opening in wall W30 Level L0 areas of grout loss could be seen.
| 02SL - Stations (LUL) | Cxxx-NCR-002058 | NCR | WTH - Level -1 - Wall 45 west kicker poured without a chamfer |  | Contr | 201068 | FAR - Farringdon Station (West) |  | 2015-11-27 | 2015-11-18 11:53 | -9 | 2015-11-13 15:58 | Civil - Civil Engineering General | 1000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | The wall 45 west kicker (approx between gridlines B and R1) was poured without chamfer on the column external edges.
| 02SL - Stations (LUL) | Cxxx-NCR-002059 | NCR | WTH SH-W2 Staircase Misaligned Couplers at 105.24 |  | Contr | 201068 | FAR - Farringdon Station (West) |  | 2016-02-07 | 2016-01-20 15:55 | -18 | 2015-12-09 17:26 | Civil - Civil Engineering General | 3500 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the Wall 6/10/16 Level -3 to -1 wall construction couplers were fixed into the wall above the doorway for the future construction of the stair landing at 105.24m. As shown on the attached sketch a section of couplers were fixed in the wrong position for the mats that they are supposed to line up with. (This section of Wall 6 was poured in two sections).
| 02SL - Stations (LUL) | Cxxx-NCR-002060 | NCR | WTH – SH-W2 Level -4 Soffit Defects |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-11-27 | 2015-11-27 16:20 | 0 | 2015-11-13 18:41 | Civil - Civil Engineering General | 4000 |  | Workmanship | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Concrete repairs which are classified as defects required for package E (Level -4 soffit) are listed in the attached PDF. Survey undertaken on the cracks on the soffit to check whether they are above 0.3mm or not. Also WTH SH-W2 Level -4 Slab Opening 1 Concrete Repairs: Scabbling and concrete repairs observed occurring in Level -4 Opening 1 at interface between top of walls and bottom of slab pour. Refer to the attached photos.
| 02SL - Stations (LUL) | Cxxx-NCR-002061 | NCR | WTH SH-W2 Precast Stair Flight F3 Fabricated Incorrectly |  | Contr | 201068 | FAR - Farringdon Station (West) |  | 2016-02-03 | 2015-12-16 08:53 | -49 | 2015-12-05 15:12 | Structural Engineering - Pre-cast | 15000 |  | Design | Rework | 2 (6-60k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | WTH MNS4-F3 flight on Cxxx--Y-DWG-M123-53000 P06, with a lower landing of 2170mm was manufactured 200mm short from the in-situ landing indicated on drawing Cxxx-SWN-S-DDA-M123_Z-82001 C05 where the landing is 1970mm.
| 02SL - Stations (LUL) | Cxxx-NCR-002062 | NCR | ETH - Trapezoidal Shaft - Wall 16 & Wall 17 concrete finish |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-12-01 | 2015-11-27 14:05 | -4 | 2015-11-17 12:05 | Architectural - Finishes | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Follow striking Wall 16 and 17 on level -4. A number of concrete defects were identified, please see attached photos. Defects will be rectified under ETH Concrete Repair Site Activity Plan Cxxx--C-STP-M123-50227.
| 02SL - Stations (LUL) | Cxxx-NCR-002063 | NCR | ETH - Cover for Wall 16 at Level -4 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-12-01 | 2015-11-27 13:30 | -4 | 2015-11-17 17:01 | Civil - Civil Engineering General | 750 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following the cover survey on W16 at Level -4 prior to the concrete pour it was found that the cover was less than specified in the drawings. The shutter was moved outwards locally (within tolerance) to provide sufficient cover to the reinforcement. will conduct a cover survey of the wall to verify the wall has adequate cover.
| 02SL - Stations (LUL) | Cxxx-NCR-002064 | NCR | ETH - L-6 Wall 5 water ingress |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-01-10 | 2016-01-06 10:35 | -4 | 2015-11-17 17:15 | Civil - Civil Engineering General | 3500 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | It was identified that water is still leaking at the top joint in Wall 5 L-6 after using the injectable __ tube with __ injektocem. The approved water proofing detail was followed with 2 lines of hydrophyllic strip were installed.
| 02SL - Stations (LUL) | Cxxx-NCR-002066 | NCR | ETH - L-2 along Wall W23 - clash between the CWD and the upstand |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-12-18 | 2015-11-26 10:12 | -22 | 2015-11-18 12:42 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The cavity wall drainage in L-2 along wall W23 between GL3 and GL4 clashed with the cavity wall upstand by 35mm.
| 02SL - Stations (LUL) | Cxxx-NCR-002067 | NCR | ETH - Level L-2 - wrong drainage cover |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-03-31 | 2016-02-29 17:03 | -31 | 2015-12-01 13:22 | Civil - Civil Engineering General | 1000 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | A wrong drainage gully has been installed near Wall W21 in Level L-2 between GL2 and GL3. See attached marked up drawing for the exact location.
| 02SL - Stations (LUL) | Cxxx-NCR-002068 | NCR | Platforms CP4 Wrong Pre-Post Pour check sheet used |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-12-31 | 2015-12-18 17:23 | -13 | 2015-11-20 09:24 | Civil - Tunnelling | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Personnel Error - Not Defined | Completed |  | Wrong check sheet used for the checks on CP4 Cxxx-SF-CON 0226 used for the installation of First Stage Concrete sheet Cxxx-SF-CON-237 should have been used as noted in the ITP Cxxx--C4-ITP-M123-50069
| 02SL - Stations (LUL) | Cxxx-NCR-002069 | NCR | WTH – Level -1 Wall 39 Damaged Waterproofing |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-12-07 | 2015-12-04 09:48 | -3 | 2015-11-23 17:50 | Civil - Civil Engineering General | 1500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Two rows of hydrophilic strip were installed between the Level -1 slab (C1A) and the kicker for Wall 39 (see attached sketches). A tail was left protruding and protected from the slab/kicker interface for future connection to the rest of Wall 39. The tail got damaged beyond use.
| 02SL - Stations (LUL) | Cxxx-NCR-002070 | NCR | Upper sloping slab pour 5 - Incomplete step |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-12-16 | 2015-12-10 16:55 | -6 | 2015-11-27 14:37 | Civil - Civil Engineering General | 1000 |  | Incomplete Works | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On striking the formwork for pour 5 on the upper sloping slab, one step was found to be incomplete (See attached photo Cxxx/SR/ETH/SB62)
| 02SL - Stations (LUL) | Cxxx-NCR-002071 | NCR | ETH-Trapezoidal Shaft Level -2, Wall 24, 23mm step at construction joint between Pour 1 and Pour 2 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-12-10 | 2015-12-10 12:19 | 0 | 2015-11-26 13:13 | Civil - Civil Engineering General | 1200 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | When striking shutters for the south of wall 24 it became apparent that there was a step between pour 1 and pour 2 tapering from 0mm at 106.418 to 20mm at 109.450. Please see attached photos for clarification. Further to the step in the concrete, there is a small area of concrete that has broken off the face due to grout seeping into the dywidag bar sleeve. Please see attached photo.
| 02SL - Stations (LUL) | Cxxx-NCR-002072 | NCR | WTH – Level -1/Wall 43 Lightning Protection Interface |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-12-10 | 2015-12-08 15:22 | -2 | 2015-11-26 18:41 | Civil - Civil Engineering General | 2500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Drawing Cxxx--E-DDD_M123_Z-75101 (C01) shows three piles requiring lightning protection, LE5, LE6 and LE7 (see attachment). A reinforcing bar was required from a dedicated pile to protrude within the wall to the roof. have installed these away from the intended column and also in accordance with detail 2 on drawing Cxxx--E-DDD-M123_Z-75107 (C01) which is a pile to steel column connection rather than detail 3 from the same drawing which is a pile to concrete column connection.
| 02SL - Stations (LUL) | Cxxx-NCR-002073 | NCR | SCL - Procedural NCR - Suspected improper curing in VA1 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-12-11 | 2015-12-01 10:39 | -10 | 2015-11-27 16:37 | Tunnelling - Linings - Sprayed Concrete | 2500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | See attached photos. In VA1 between chainage 14.5 and chainage 36.0 it has been noticed several very fine longitudinal cracks in the sprayed lining. The cracks are only visible when the concrete is dampened. Consulting the document "Concrete Society TR22" the most likely cause is suggested to be plastic shrinkage. The most likely cause of this is insufficient curing. The concrete was cured in accordance with the accepted MS however for the particular ambient conditions of this structure at the time of spraying this may not have been sufficient.
| 02SL - Stations (LUL) | Cxxx-NCR-002074 | NCR | MEP - Use of Materials prior to Approval |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-01-31 | 2016-01-29 13:59 | -2 | 2015-11-30 13:12 | Electrical - Cable Management | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | __ have procured Uni-Strut end caps, Stud Caps, and 'NordLock' washers for installation without submittal of MCRs for these materials. The end caps were excluded from a data sheet submitted for uni-strut materials (CRL-MCR-002074). The washers were not as originally specified when obtained, however provide a better solution to the original material. The Stud Caps were overlooked for inclusion and an MCR since submitted.
| 02SL - Stations (LUL) | Cxxx-NCR-002075 | NCR | WTH - Walls 50, 51 & 54 3rd lift concrete pour concrete placement time exceeded |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-12-18 | 2015-12-04 11:39 | -14 | 2015-12-01 13:32 | Civil - Structural Engineering | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | Walls 50, 51 & 54 were cast from +118.230m to +121.190m on 25-11-15. The 1st wagon was batched at 0707 and finished pouring at 0953 so 46 minutes over the 2hr hour time limit stated in Clause KF10.3202 c) of Cxxx C&S specification. The 2nd wagon was batched 0755 and finished pouring at 1130 so 1hr 35mins over the 2hr time limit.
| 02SL - Stations (LUL) | Cxxx-NCR-002076 | NCR | WTH SH-W1 Waterproofing - Historic damage to Level -7 waterbar |  | Contr | 201068 | FAR - Farringdon Station (West) |  | 2016-02-05 | 2016-01-13 11:27 | -23 | 2015-12-07 18:59 | Civil - Civil Engineering General | 3500 |  | Damaged | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The __ tricosol metal waterbar installed by Cxxx in the level -7 slab has become damaged. Refer to attached photos.
| 02SL - Stations (LUL) | Cxxx-NCR-002077 | NCR | WTH – SH-W2 Level -3 downpipe clash with blockwork wall |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-04-04 | 2016-02-08 15:35 | -56 | 2015-12-03 15:42 | Civil - Civil Engineering General | 750 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Drawing Cxxx--P-DDA-M123_3-75205 (C01) shows a downpipe installed adjacent to Wall 9 (see attached sketch). The pipe was cast in and it has since been discovered that the downpipe collar will clash with the blockwork wall at high level by approximately 25mm.
| 02SL - Stations (LUL) | Cxxx-NCR-002078 | NCR | SCL - Defective single weld in LP1 invert waterproofing |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2015-12-18 | 2015-12-15 14:49 | -3 | 2015-12-04 10:05 | Tunnelling - Linings - In-situ Concrete | 2000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During a routine pre-inspection inspection a defective weld was identified in the invert of LP1 by engineers. The defect was detected due to water seeping through. See attached photo, there is significant charring on the leaking area. The area in question was on a single welded patch repair. The defective patch was repaired in accordance with procedures.
| 02SL - Stations (LUL) | Cxxx-NCR-002079 | NCR | SCL - STE1 & STE2 - Damage to primary lining during removal of TBM by Cxxx |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2016-02-26 | 2016-02-16 15:41 | -10 | 2015-12-04 13:36 | Tunnelling - Linings - Sprayed Concrete | 2500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Cxxx used oxy-a__ylene torches during the removal of the TBM shields in STE1 and STE2. Scorch marks are evident on the primary lining (shoulder level either side) as a result of the cutting operations. Given the temperature produced during oxy-a__ylene cutting (~3500 degrees), it can be assumed that the operation has caused a detrimental impact on the integrity of the lining.
| 02SL - Stations (LUL) | Cxxx-NCR-002080 | NCR | SCL - L-bars cut out in VA2 collar |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-01-08 | 2016-01-07 16:31 | -1 | 2015-12-04 15:31 | Tunnelling - Linings - Sprayed Concrete | 4000 |  | Supervision/Management | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | The front face connection L-bars between VA2 and PL3 were mistakenly cut back too far not allowing sufficient splice to re-connect the bars later. The bars were re-connected using approved shear bolt couplers as agreed on site
| 02SL - Stations (LUL) | Cxxx-NCR-002081 | NCR | ETH - South Basement - Cold joint line Wall W20 Pour3 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-01-22 | 2016-01-07 12:50 | -15 | 2015-12-04 15:17 | Civil - Civil Engineering General | 1000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Insufficient quantity of material to do the job | Completed |  | Pour 3 of Wall W20 between Level L0 and L+1 had to be abandoned 600 to 800mm below the top of the Level L+1 slab (123.65mATD). The joint is in an area which was supposed to have a F4 concrete finish
| 02SL - Stations (LUL) | Cxxx-NCR-002082 | NCR | SCL - VA2 shadowing on reinforcement |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-01-29 | 2016-01-08 11:20 | -21 | 2015-12-04 16:11 | Tunnelling - Linings - Sprayed Concrete | 3400 |  | Workmanship | Rework | 3 (3-6k) | Complete | Personnel Error - Inattention to detail | Completed |  | VA2 - at the location of the collar connection into PL3, the first layer spray has resulted in some minor shadowing behind some of the re-inforcement bars
| 02SL - Stations (LUL) | Cxxx-NCR-002083 | NCR | ETH - SB Drilling into F3 Finish Wall 20 at L+1 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-03-31 | 2016-03-24 15:13 | -7 | 2016-01-06 10:59 | Civil - Civil Engineering General | 1000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | During the installation of the access scaffold on W20 Level L+1 the scaffold was tied back into wall W20. 3 no 20mm holes were drilled in an area with a F3 concrete finish just below the coffer ceiling in Level L+1 during night shift.
| 02SL - Stations (LUL) | Cxxx-NCR-002085 | NCR | ETH - SB - W23 Kicker Strength |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-01-20 | 2015-12-16 13:52 | -35 | 2015-12-16 08:38 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Following the issue of 28 day strength results for Lining wall 23 column kicker at GL5 it was found that required strength (50N/mm2) was not achieved. Average 28 day strength was 35.25N/mm2. The strength was monitored and the 90 day strength reached 51.6 N/mm2. See attached EX1962 showing results. Please confirm this is acceptable. See attachment titled ‘location mark-up’ for location.
| 02SL - Stations (LUL) | Cxxx-NCR-002086 | NCR | WTH SH-W2 wall 7/PL2 Waterproofing damaged |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-07-18 | 2016-05-26 15:11 | -53 | 2015-12-09 14:05 | Civil - Civil Engineering General | 4500 |  | Damaged | Repair | 3 (3-6k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | After the SCL break through into the SHW2 shaft, several non-compliances have been identified affecting the waterproofing to Wall 7 : 1.- 1no __ Hydrophilic strip and 1no re-injecto has been lost due to a concrete overpour that leaked through a hy-rib stop end. 2.- Re-injecto tube port cannot be located 3 , 4, 5, 6 & 7 – Exposed __ Hydrophilic strip tails have either been removed or sprayed over. (See attached sketch)
| 02SL - Stations (LUL) | Cxxx-NCR-002087 | NCR | WTH - Structural steelwork - insufficient HD bolt protrusion for column D/7 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-01-30 | 2016-01-29 11:58 | -1 | 2015-12-16 10:06 | Structural Engineering - Steel Member | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | The holding down bolts cast in the -1 slab of the WTH for Column D/7 are 56mm low (see attached marked-up __ drawing Cxxx--S-DDD-M123_Z-70108 C02). The current bolt length protruding from the -1 slab does not allow the column to be fixed in position. note that the required embedment depth of the HD bolts was correct.
| 02SL - Stations (LUL) | Cxxx-NCR-002088 | NCR | SCL - Drainage channel on STW1 Secondary Lining Headwall pour 1 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-02-19 | 2016-02-09 13:18 | -10 | 2015-12-14 19:14 | Tunnelling - Linings - In-situ Concrete | 3000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | STW1 Secondary Lining Headwall pour 1 void former (See drainage channel Cxxx-SWN-S-DDB-M123_Z-50102) was installed 70mm south of its actual position. The pour extends from the edge of the last TBM ring to the face of the headwall.
| 02SL - Stations (LUL) | Cxxx-NCR-002089 | NCR | WTH – Wall 39 perimeter wall pour between Level -1 and 0 exceeding placement times |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-01-23 | 2016-01-20 12:25 | -3 | 2015-12-14 18:00 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Error by manufacturer in shipping or marking | Completed |  | The third pour of Wall 39 was cast between GL4 minus 3m to GL6 minus 1.5m. During this pour both the clauses stated below were exceeded. Clause KF10.3202c from the Civil and Structural Specification (Cxxx-SWN-C-RSP-M123-00004) states that concrete is to be placed and compaction within 2 hours of the addition of water. Clause KF10.3203h states that fresh concrete must not be placed against fresh in-situ concrete that has been in position for more than sixty minutes.
| 02SL - Stations (LUL) | Cxxx-NCR-002090 | NCR | SCL - Damage to walls in SHW2 level -6 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-06-17 | 2016-05-25 13:23 | -23 | 2015-12-15 09:34 | Architectural - Walls | 4000 |  | Damaged | Rework | 3 (3-6k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Some of the walls in SH-W2 level -6 have been damaged. This was caused accidentally whilst the area was being used for the passage of heavy tunnelling machinery. Please see attached photos Additionally some small areas of -7 track slab have been damaged also. This damage was most likely caused during removal of spoil from ST-W3.
| 02SL - Stations (LUL) | Cxxx-NCR-002091 | NCR | SCL - VA1 Minimum radius not achieved |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-03-18 | 2016-02-19 11:41 | -28 | 2015-12-15 17:51 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Surveillance Cxxx--O4-RGN-M123-51342 has reported that there are small isolated areas in VA1 where the minimum radius has not been achieved. Mostly this is very small spots of 1-8mm. Worst case is an area of appox 750mm that is 18mm inside the minimum radius.
| 02SL - Stations (LUL) | Cxxx-NCR-002092 | NCR | ETH-SB L-2 W26 - Missing starter bars |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-04-29 | 2016-04-13 12:52 | -16 | 2016-01-05 17:57 | Civil - Civil Engineering General | 2500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | An as built survey of the internal wall W26 was starter bars (B16 bar marks 31 and 32) has been carried out. These bars were fixed during the construction of the L-2 slab. The as built survey shows that two starter bars are missing, one on near face and one on the far face.
| 02SL - Stations (LUL) | Cxxx-NCR-002093 | NCR | SCL - ES2 Transition B12 bars not cast in transition |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-01-15 | 2015-12-18 11:17 | -28 | 2015-12-17 08:56 | Tunnelling - Linings - In-situ Concrete | 2500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | See atached sketches "Invert transition 1 Missing bars". The first 2.8m of ES2 invert has been cast without the transverse bars on the top face of the invert.
| 02SL - Stations (LUL) | Cxxx-NCR-002094 | NCR | PLT - CP9 Wall Steel installation |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-02-29 | 2016-02-17 11:50 | -12 | 2015-12-17 14:14 | Tunnelling - Linings - In-situ Concrete | 2500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | This NCR is raised because the general arrangement drawings had been revised without the steel detail being revised. As a result, the steel installed and cast to the Z-50683 C01 revision drawing reflected the old arrangement. This was identified when Cxxx wen to make comments on the C01 issue of the old detail. Please see attached comments titled "CP9 Wall 2.msg" relating to technical aspects of the design.
| 02SL - Stations (LUL) | Cxxx-NCR-002095 | NCR | WTH - Level -1 Base Slab E2 Concrete Timings |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-01-14 | 2016-01-06 10:33 | -8 | 2015-12-17 18:42 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Error by manufacturer in shipping or marking | Completed |  | 1) Specification clause KF10.3202 c) states "concrete shall, under normal circumstances, be placed and compacted within two hours of addition of water, unless other agreed measures are taken and detailed in the appropriate Method Statement.". During the concrete pour for the level -1 base slab E2 the placement and compaction of concrete wagons 2,3,6,7,8 and 9 as recorded on the attached structural concrete site control sheet did not take place within 2 hours of batching. This was due to a combination of a breakdown of the concrete pump and the time taken to replace the pump and also the time taken for concrete wagons to reach site during peak traffic times. 2) Specification clause KF10.3203 h) states "Fresh concrete shall not be placed against existing fresh in-situ concrete which has been in position for more than sixty minutes.". The time between placement of wagon 9 and wagon 10 as recorded on the attached structural concrete site control sheet exceeded 60 minutes. This gap in placement of concrete was due to poor supply by 's concrete suppliers.
| 02SL - Stations (LUL) | Cxxx-NCR-002096 | NCR | WTH SHW1 Level -7 slab pour. Haki stair standards cast into slab. |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-03-31 | 2016-03-11 09:50 | -20 | 2015-12-18 15:11 | Civil - Civil Engineering General | 1500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | Haki stairs are installed as primary access from level-2 to base slab at level -7. To allow continued access during the pour the haki stair standards were intentionally left in the base slab.
| 02SL - Stations (LUL) | Cxxx-NCR-002097 | NCR | WTH - ITH - Sealing of ITH hoarding without sufficient detail within the ITP |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-01-19 | 2016-01-07 09:19 | -12 | 2015-12-23 12:43 | Fire - Compartmentation | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | On the weekend of 19/20th December 2015, completed the fireproofing to the ITH hoarding. The main element of these works was the removal of the pedestrian doors (1 double door at concourse level and 1 single door at platform level) and the sealing of these openings. had an approved ITP in place for the hoarding works (Cxxx--C-ITP-M123-50282) but there was not a line item included for the sealing of the doors.
| 02SL - Stations (LUL) | Cxxx-NCR-002098 | NCR | ETH-SB L0 to L+1 Concrete Pour 3 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-02-05 | 2016-02-05 17:01 | 0 | 2016-01-05 18:12 | Civil - Civil Engineering General | 1000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | After striking the formwork on internal wall W20 L0 to L+1 following the concrete pour 3, found that there are localised areas of concrete that were not compacted very well leading to honey combing and holes in the concrete finish where some bars are exposed. Two are to the south of the cast in plate 3315 (BCEL MK A731) and one at the front face of column C5. See site photos attached.
| 02SL - Stations (LUL) | Cxxx-NCR-002099 | NCR | ETH - South Basement - Wall 19 L-2 to L-1 Damage |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-03-25 | 2016-03-01 10:40 | -24 | 2016-01-06 18:05 | Civil - Civil Engineering General | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Damage to the finish of Wall 19 during installation of post drilled ties for scaffold anchor bars between L-2 to L-1. On wall 19 L-2 to L-1 no sleeves were left in the wall to allow the installation of the scaffold anchors. The anchors were drilled and fixed damaging the finish of the wall as shown in the attached photo (Cxxx-SR-ETH-SB64).
| 02SL - Stations (LUL) | Cxxx-NCR-002100 | NCR | WTH - SH-W2 - Wall 25/11 Pour from +2 to +3 - Concrete Timings |  | Contr | 201068 | FAR - Farringdon Station (West) |  | 2016-02-05 | 2016-01-13 14:24 | -23 | 2016-01-08 14:38 | Civil - Civil Engineering General | 750 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Error by manufacturer in shipping or marking | Completed |  | During the concrete pour for walls 25/11 on 05/01/16 from +2 to +3 a number of instances occurred where the concrete went outside the specification requirements with regards to timings. 1) Clause KF10.3202 c) relating to placement within 2 hours of batching: Placement of wagons 1 and 3 did not take place within 2 hours of batching. This was due to the time taken for concrete wagons to reach site during peak traffic times and 2 wagons being batched only 20 minutes apart. 2) Clause KF10.3203 h) relating to a maximum gap of 60 minutes between placing concrete onto the live pour face: The time between placement of wagons 1 and 2 was 95 minutes. This gap in placement of concrete was due to poor supply by __ (batching the first 2 wagons 2hrs 35mins apart). All of the above is recorded on the attached structural concrete site control sheet.
| 02SL - Stations (LUL) | Cxxx-NCR-002101 | NCR | ETH - Trapezoidal Shaft - Wall 6 Level -6 incorrect position of downstand kicker |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-02-26 | 2016-02-24 09:25 | -2 | 2016-01-09 12:07 | Civil - Civil Engineering General | 4500 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following the construction of Wall 6 Level -6 identified a previously cast down stand kicker was cast incorrectly, please see attached photo. Approx kicker is 40mm away from required. Note Lining Wall has been cast correctly. failed to identify the difference of line between cast downstand kicker and lining wall position. Additional information: Based on the results of the As-built survey and the cover survey, the reinforcement cover for the down stand kicker as well as the Lining Wall (Wall 6) are both within tolerance and conform to the 40mm reinforcement cover as specified in Reinforcement Drawing Cxxx-ATK-S-DWG-M123_Z-50224. It appears that the entire excavation for the down stand kicker was poorly positioned and not only the front shutter of the down stand kicker ,hence why the As-Built survey shows poor alignment of the down stand kicker and the cover survey shows adequate reinforcement cover.
| 02SL - Stations (LUL) | Cxxx-NCR-002102 | NCR | ETH - Trapezoidal Shaft - Escalator pit hanging wall concrete step between slab kicker |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-03-11 | 2016-03-11 14:02 | 0 | 2016-01-09 12:03 | Civil - Civil Engineering General | 1000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | Following striking North Hanging Wall in Escalator Pit Level -3.5, a small step was identified between slab kicker and hanging wall. Approx 20mm
| 02SL - Stations (LUL) | Cxxx-NCR-002103 | NCR | ETH-SB 28 L+1 to L+2 Dywidag hole damage on concrete finish |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-01-22 | 2016-01-20 17:34 | -2 | 2016-01-08 09:06 | Civil - Civil Engineering General | 1000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Dywidag anchor bar installed with a short sleeve in wall W28 during the construction of ESS5 walls L+1 to L+2. The sleeve was not covering the whole width of the wall, therefore during the striking of the formwork there was damage to the concrete finish around the dywidag hole on the west face of wall W28 see attached site photo.
| 02SL - Stations (LUL) | Cxxx-NCR-002104 | NCR | SCL - December 2015 Polypropelyne Fresh Fibre count lower than target |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-01-29 | 2016-01-19 08:25 | -10 | 2016-01-08 12:00 | Tunnelling - Linings - In-situ Concrete | 2500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | The fresh fibre test result for polypropelyne fibres in 29 for the week between 08/12/15 and 17/12/15 gave an average result of 1.4kg/m3 against a minimum allowable of 1.6kg/m3.
| 02SL - Stations (LUL) | Cxxx-NCR-002105 | NCR | ETH - Hayne Street Shaft, Insufficent Cover to Jacking Collar Reinforcement |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-01-29 | 2016-01-15 12:20 | -14 | 2016-01-15 09:55 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | The minimum concrete cover to the top mat of steel reinforcement has been measured as 28mm and is not in accordance with the design drawing and will be out of tollerance.
| 02SL - Stations (LUL) | Cxxx-NCR-002106 | NCR | ETH - Hayne Street Shaft Verticality |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-02-12 | 2016-01-28 14:16 | -15 | 2016-01-15 09:54 | Civil - Civil Engineering General | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | The verticality of the segmental section of the shaft is not in line with the tolerances set out in the ITP and the BTS Specification for Tunnelling. The as built survey shows that the as installed verticallity is approximately 1 in 126. A sketch showing the position of the top and bottom rings is attached.
| 02SL - Stations (LUL) | Cxxx-NCR-002107 | NCR | ETH – Trapezoidal Shaft - Starting Blockwork on Level -4 Without Lining Wall Sign off |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2016-01-25 | 2016-01-25 14:43 | 0 | 2016-01-11 17:04 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | Blockwork construction commenced on Level -4 without lining walls being accepted and signed off as free of snags and repairs. Blockwork commenced on Walls 2, 5 & 6 up a height of 1.5m and it was noticed that there were still some outstanding snags on the exposed faces of the lining walls.
| 02SL - Stations (LUL) | Cxxx-NCR-002108 | NCR | WTH - SH-W2 – Precast Stairs – Unapproved Concrete Mix Used |  | Contr | 201068 | FAR - Farringdon Station (West) |  | 2016-03-15 | 2016-03-14 07:55 | -1 | 2016-01-19 15:49 | Structural Engineering - Pre-cast | 2000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | During the fabrication of the precast stairs for SH-W2 (ESS1/INS1) the concrete mix used was changed by the Sub-Contractor (__) without notifying . The initial 7 flights were cast using the pre-approved mix and the remaining flights were cast with the new __ in-house mix prior to MCR approval. See attached sketch showing which flights were cast with which mix.
| 02SL - Stations (LUL) | Cxxx-NCR-002109 | NCR | WTH - SH-W2 – Defect on walls from level -3 to -1 and level -1 slab soffit |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-04-22 | 2016-04-22 11:04 | 0 | 2016-01-13 14:19 | Civil - Civil Engineering General | 3000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Concrete repairs which are classified as defects required for walls between level -3 and level -1 and Level -1 slab soffit are listed in the attached PDF
| 02SL - Stations (LUL) | Cxxx-NCR-002110 | NCR | ETH - Lack of Damp proof membrane at L-7 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-04-08 | 2016-04-05 07:57 | -3 | 2016-01-16 14:07 | Architectural - Brickworks/Blockworks | 6000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | During the construction of blockwork walls at L-7, Damp proof membrane was not installed within the internal wall.
| 02SL - Stations (LUL) | Cxxx-NCR-002111 | NCR | Lining wall W23 level -2 to -1 connection with capping beam at GL7 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-01-27 | 2016-01-21 14:03 | -6 | 2016-01-13 09:43 | Civil - Civil Engineering General | 3000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | is constructing lining wall W23 from -2 to -1. This wall connects to a capping at GL 7 as shown in the mark up drawing attached. The couplers on the capping beam have been exposed and the NF1 (East side) was fixed incorrectly and couplers are inside the wall.
| 02SL - Stations (LUL) | Cxxx-NCR-002112 | NCR | WTH – Section of Wall 10 not poured to full height between Levels -7 and -6 in SH-W2 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-02-26 | 2016-02-25 10:57 | -1 | 2016-01-13 15:01 | Civil - Civil Engineering General | 4000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Drawing Cxxx-SWN-S-DDC-M123_Z-81024 (C09) shows Wall 10 between Walls 6 and 13 being cast from the midlanding at +84.120m to the soffit of the mid landing at +86.760m. only cast the wall to the SSL of Level -6 approximately 560mm too low. See attached for further details and photographs.
| 02SL - Stations (LUL) | Cxxx-NCR-002113 | NCR | SCL - Part of ES2 Invert Case Outside of Waterbar Fins |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-03-18 | 2016-02-06 17:32 | -41 | 2016-01-13 17:36 | Tunnelling - Linings - In-situ Concrete | 2500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | have cast part of the ES2 invert outside of the waterbar fins. The construction joint outside of the fins is between the invert and kickers at chainage 3-5 on the left hand side facing up ES2, see the attached Sketch and Picture for further information of the location
| 02SL - Stations (LUL) | Cxxx-NCR-002114 | NCR | SCL - Void in CP1 kickers CH 19.5 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-03-11 | 2016-02-25 10:19 | -15 | 2016-01-15 17:57 | Tunnelling - Linings - In-situ Concrete | 2500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The kicker pour of CP1 has an area at approximately CH19.5 where the concrete has not fully filled the formwork. Please see attached photos the area in question is approx 1000mm x 200mm x 100mm deep
| 02SL - Stations (LUL) | Cxxx-NCR-002115 | NCR | ETH - Incorrect wall tie installion at L-1 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-01-30 | 2016-01-19 14:32 | -11 | 2016-01-16 14:25 | Architectural - Brickworks/Blockworks | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | It was identified that SDV wall ties was used in a small area within L-1 South basement area rather than SDB which is specified on the drawing. Please note that the wall ties used have been approved through an MCR and the only difference is that SDV tie allows some vertical adjustment, see attached sketch for clarity.
| 02SL - Stations (LUL) | Cxxx-NCR-002116 | NCR | Early MEP Works - Non Conformance with the INR procedure |  | Contr | __ | FAR - Farringdon Station (West) |  | 2016-02-11 | 2016-01-29 18:09 | -13 | 2016-01-21 12:19 | Electrical - General | 0 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | A formal Inspection Notification Request was not issued prior to the Earthing Test and Under Platform Benchmark sign offs been carried on installed works. Earthing Test Due to the hasty coordination between CRL / __ and in getting a __ attendant present for the test the test date and time where agreed by all parties at a pre testing meeting with __. A further email invitation was then issued to all parties which was accpeted by all required to witness the test. Under Platform Benchmark The Benchmark sign off exercise was coordinated and agreed with the interested parties (, CRL FE and CEG) at site level.
| 02SL - Stations (LUL) | Cxxx-NCR-002117 | NCR | Non- compiliance of ETH and WTH for not following the BFK Disign Management Plan for using drawings not approved for construction |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-02-19 | 2016-02-17 14:40 | -2 | 2016-01-21 14:43 | Civil - Civil Engineering General | 2000 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | In some cases ETH and WTH have not been following requirement below from Design Management Plan Cxxx--Z-STP-M123-50001 Rev 6 from 25/09/15 (when rev 6 was accepted). “Situations are arising where late change instructed by CRL is requiring changes to IFC drawings, but there is insufficient time to change the drawings, carryout a Gate Impact Assessment and produce new IFC drawings. There may also be situations where the designs have not yet been through Gate and have been reviewed by CRL, but are needed for construction. In both these situations will agree with CRL that the P status drawings can be used for construction and this shall be recorded on a FCD. The related drawings shall be referenced in the FCD and if only part of a drawing can be constructed or is relevant to the FCD then this shall be marked on the drawing and signed by both CRL and with reference to the FCD prior to being issued to site for construction as part of the FCD. If any comments received from CRL as part of the review process relate to the area of design to be included in the FCD shall agree with CRL how these are to be dealt with and this shall be recorded in the FCD.” has been using P status drawings on site without FCD. It has been agreed unofficially with CRL that to avoid countless FCDs being raised to approve ‘P’ status drawings for construction, ‘Minimum Assurance Matrix’ will be used to enable to provide the necessary assurance that ‘P’ status drawings are acceptable for construction purposes.
| 02SL - Stations (LUL) | Cxxx-NCR-002118 | NCR | Level -1 slab soffit, section of pile S101 inner cason cut below specified level |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-02-03 | 2016-02-01 15:28 | -2 | 2016-01-20 11:23 | Civil - Excavation | 2750 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | During excavation works pile S101 inner casing was cut off 35mm below the level specified in Cxxx-SWN-S-DDA-M123_Z-76018. Please refer to the photo attached.
| 02SL - Stations (LUL) | Cxxx-NCR-002119 | NCR | STW - Compressive strength cubes for PES |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-03-18 | 2016-03-02 13:53 | -16 | 2016-01-21 09:18 | Architectural - General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | For the Prototype and MCR compressive strength cubes were sampled and cured by __ not accredited laboratory.
| 02SL - Stations (LUL) | Cxxx-NCR-002120 | NCR | SCL - Honeycoming in STW3 Wall pour 1 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-06-24 | 2016-05-17 17:18 | -38 | 2016-01-21 15:01 | Tunnelling - Linings - In-situ Concrete | 2500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The stopend of SWT3 wall pour 1 has been struck and there is visible honeycombing on the surface of the concrete. See attached photos of the extent of the honeycombing. On the south wall the affected area is around 5m long x 1m high, on the north wall it is smaller mainly affecting the stopend. Investigation on site (22/01/16) has shown the concrete is effected to a depth of between 30-100mm. Upon inspection it is clear that the honey-combed concrete has had nearly all of the binder washed out from it. Suspected cause is that there was water in the formwork that was not removed prior to pouring.
| 02SL - Stations (LUL) | Cxxx-NCR-002121 | NCR | SCL - CH2/ES2 transition pour grout spillage over waterbar |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-02-04 | 2016-02-02 17:20 | -2 | 2016-01-21 15:48 | Tunnelling - Linings - In-situ Concrete | 2500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Personnel Error - Not Defined | Completed |  | During the pour of a temporary slab on the CH2/ES2 transition, a leakage on the shutters caused a spillage of grout over the PVC and waterbar on the sides of the CH2/ES2 transition Secondary Lining invert. The grout was not cleaned inmediatly and went off. As a result it was introduced risk of damaging the waterproofing when breaking the grout.
| 02SL - Stations (LUL) | Cxxx-NCR-002122 | NCR | ETH -Trap Shaft - Wall 33 shutter movement |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-09-01 | 2016-08-11 13:33 | -21 | 2016-01-26 17:50 | Civil - Civil Engineering General | 35000 |  | Supervision/Management | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | ETH – While monitoring a concrete pour to W33/35 at level -1 it was noticed that one of shutters by column section had moved during concrete operations. Upon noticing this, the pour was immediately stopped and the shutter was monitored for further movement of which none occurred. Please see attached sketch with as-built position of column.
| 02SL - Stations (LUL) | Cxxx-NCR-002123 | NCR | PLT-As builts Surveys bay 3 Ch 7057.298 to bay 9 Ch 7224.024 and Bay 11 Ch 7251.079 to bay 13 Ch 7317.698 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-06-07 | 2016-06-02 15:30 | -5 | 2016-01-25 17:41 | Surveying - Surveying General | 2500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | has done the As-builts from bay 3 Ch 7057.298 to bay 9 Ch 7152.521 and Bay 11 Ch 7251.079 to bay 13 Ch 7317.698 Please find attached the PDF's corresponded to each bay these PDF's include a summary in the first page Bay 3 Ch 7057.298 to Ch 7075.516 Bay 4 Ch 7081.552 to Ch 7102.625 bay 5 Ch 7105.479 to Ch 7126.457 bay 6 Ch 7129.107 to Ch 7152.521 bay 7 Ch 7155.521 to Ch 7176.524 Bay 11 Ch 7251.079 to Ch 7266.115 Bay 12 Ch 7269.104 to Ch 7296.265 Bay 13 Ch 7299.172 to Ch 7317.698 On the surveys that has done and as the records show the ID points 1-16 in bays 3, 4, 5, 6, and ID points 1-16 in bays 11,12, 13 there are some points that are out of tolerance. Track slab points ( 3,5 and 6) from Bay 7 Ch 7158.503 to bay 9 Ch 7224.024: ID points 3, 5 and 6 present levels between +16 and 30mm, in regards these points and to avoid recurrence extra monitoring during the jet wash at the end of the pour will be reinforced.
| 02SL - Stations (LUL) | Cxxx-NCR-002124 | NCR | ETH - Trapezoidal Shaft - Water damage to Internal Wall |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-05-19 | 2016-02-18 08:46 | -91 | 2016-01-28 18:14 | Civil - Civil Engineering General | 1000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Supervision - Other | Completed |  | After the construction of Wall 13 from Form Level -7 to -6 have identified a small wall section has become damaged by rain water seeping through openings in. See photo attached
| 02SL - Stations (LUL) | Cxxx-NCR-002125 | NCR | STW - Precast elements by __ – Non UKAS accredited operatives sampling concrete |  | Contr | 201068 | FAR - Farringdon Station (West) |  | 2016-03-12 | 2016-02-18 10:08 | -23 | 2016-02-02 12:02 | Civil - Civil Engineering General | 1250 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | During a surveillance at __’s fabrication factory in November 2015 it was observed that the concrete sampling (flow testing and cube making) was being undertaken by trained __ operatives but who were not accredited by UKAS. Cubes that were made were given to a UKAS accredited lab for crushing.
| 02SL - Stations (LUL) | Cxxx-NCR-002126 | NCR | MEP - Not carrying out pull-out tests in line with ITP |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-02-19 | 2016-02-18 17:56 | -1 | 2016-01-26 15:40 | Electrical - Cable Management | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Not carrying out pull-out tests prior to installing wall mounted brackets into concrete, as stated in ITP. Initial Tests only covered the initial 50M of the installation, leaving 100M untested before bracketry was installed. At the time of installation the necessary test equipment was not available on site, as the initial testing was carried out by __ as part of fixings training. Tests were then completed on the remaining installation, once test equipment available and after the works had been carried out.
| 02SL - Stations (LUL) | Cxxx-NCR-002127 | NCR | ETH /WTH - CPI Mortar onsite Testing (M4 and Wi Mortars) not in compliance with BS 5628-1 A.3 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-02-26 | 2016-02-25 16:10 | -1 | 2016-02-02 14:37 | Architectural - Brickworks/Blockworks | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The CPI Mortar on site testing (M4 and Wi Mortars) carried out for the Level -7, ETH block work was not in compliance with BS 5628-1 2005 A.3. Spot checks carried out on the block work between gridlines C-6, Level -7 at the ETH during surveillance (Cxxx--O4-RGN-M123-51347) revealed that the number and age of samples tested were not in compliance. For the M4 Mortar, 2 cubes (S1411846) were taken on 14-11-15 and tested on the 7th and 28th day; 2 cubes (S1411848) were taken on 27-11-15 and tested on the 7th and 31st day (see attached). For the Wi Mortar, 2 cubes (14118487) were taken on 14-11-15 and tested on the 7th and 28th day; 2 cubes (S1457503) were taken on 27-11-15 and tested on the 8th and 31st day (see attached)
| 02SL - Stations (LUL) | Cxxx-NCR-002128 | NCR | WTH - Level -1 Perimeter Wall 45 - Fixing reinforcement to P revision of rebar drawing Cxxx-ATK-S-DWG-M123_Z-50287 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-02-16 | 2016-02-16 11:24 | 0 | 2016-02-02 13:49 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | WTH - Level -1 Perimeter Wall 45 - Rebar drawing Cxxx-ATK-S-DWG-M123_Z-50287 has not been approved in time for construction. Therefore site team had installed reinforcement at risk to P revision of this drawing. Issue was raised previously on an Cxxx-FCD-001791 "WTH - Level -1 - Wall 43, 44 and 45 - Approval of drawings".
| 02SL - Stations (LUL) | Cxxx-NCR-002129 | NCR | WTH – Leaks to Walls 6 and 9 in the stairwell of SH-W2 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-03-30 | 2016-03-17 12:01 | -13 | 2016-02-03 15:17 | Civil - Civil Engineering General | 5000 |  | System Defect | Repair | 3 (3-6k) | Complete | Previous Construction - Other | Completed |  | have to provide a watertight station upon completion of the works. A few minor leaks have appeared to the perimeter walls within the stairwell in the NW corner of SH-W2. The location of each leak is detailed on the attached sketch. In all instances, apart from one location, the leaks have occurred at horizontal construction joints. There is no seepage visible and the affected area has not increased in size since it was initially spotted.
| 02SL - Stations (LUL) | Cxxx-NCR-002130 | NCR | WTH – Honeycombing in L-1 Slab I1C |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-02-17 | 2016-02-16 08:22 | -1 | 2016-02-03 17:19 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | After burning sheet piles that formed the formwork for L-1 slab I1C from L-1 TOC (106.430m ATD) down to formation level (104.430m ATD) for the construction of L-1 slab C1B, an area of honeycombing was identified. Please see attached photo of initial findings. This area of honeycombing is in the vertical face of L-1 slab I1C that will form a construction joint for slab C1B.
| 02SL - Stations (LUL) | Cxxx-NCR-002131 | NCR | WTH – L-1 Slab C1B Waterproofing – Construction Joint with Slab I1C |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-02-17 | 2016-02-12 12:05 | -5 | 2016-02-03 17:25 | Civil - Civil Engineering General | 3000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 1) Sheet piles were used as formwork to form the north and west extents of L-1 Slab I1C. These sheet piles were burnt down to formation level during the construction of L-1 Slab C1B (104.430m ATD). Once the sheet piles were burnt down it exposed the waterproofing membrane that was left after construction of Slab I1C, of which 75mm is required to lap onto Slab C1B waterproofing. Areas of the waterproofing membrane have been damaged or have less then 75mm of material to lap onto. See attached images of affected areas. 2) __ strip has been damaged from previous pour L-1 Slab C1A. There is not sufficient length of material present that is required to lap onto. See attached image of affected area. See attached overview of Slab C1B waterproofing showing locations of damage.
| 02SL - Stations (LUL) | Cxxx-NCR-002132 | NCR | WTH – Wall 39 South (From SOP1-4 to 800mm South Grid Line 6) |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-04-15 | 2016-04-15 11:03 | 0 | 2016-02-03 18:24 | Civil - Civil Engineering General | 1750 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Concrete repairs which are classified as defects required for wall 39 are listed in the attached PDF.
| 02SL - Stations (LUL) | Cxxx-NCR-002133 | NCR | WTH - Level -1 Perimeter Walls, end of wall 45 1st pour concrete timing. |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-02-18 | 2016-02-18 11:45 | 0 | 2016-02-04 09:24 | Civil - Civil Engineering General | 500 |  | Manufacturing Defect | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Error by manufacturer in shipping or marking | Completed |  | During the concrete pour for wall 45 end section 1st lift on 03/02/16 the concrete went outside the specification requirements with regards to timings. 1) Clause KF10.3202 c) relating to placement within 2 hours of batching: Placement of concrete did not take place within 2 hours of batching. This was due to the following factors: - the pour was originally planned to start 1100, but __ batcher sent the wrong mix. W1(10) instead of the requested W1(10) AD. The mix was missing the waterproofing admixture. Hence the wagon was rejected and the planned craneage slot was lost. - The second wagon, with the correct mix, arrived at 1300 ( 45 mins atfter it was batched) and at this time the tower crane movements were restricted by __ installing the beam close to tower crane mast. Beam was suspended of 750t crane close to position when concrete arrived. - A further delay was caused by HTC setting the tower crane lifting capacity restriction back to 75%. - The pour did not commence untill 1330 - Because end of wall 45 is out of reach of the tower crane, had to use an additional crane (spider crane) to complete the pour so every concrete skip had to double handled by both cranes. The above is recorded on the attached structural concrete site control sheet.
| 02SL - Stations (LUL) | Cxxx-NCR-002134 | NCR | WTH – SS – Beam 2126 delivered to site with end plates welded to wrong ends of beam |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-05-20 | 2016-04-20 08:08 | -30 | 2016-02-04 09:39 | Structural Engineering - Steel Member | 3500 |  | Manufacturing Defect | Rework | 3 (3-6k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | On 29/01/16 Beam 2126 (Beam B19 shown on attached marked-up Cxxx GA drawing) was delivered to site. The end plates of the beam were welded at the wrong ends of the beam.
| 02SL - Stations (LUL) | Cxxx-NCR-002135 | NCR | MEP - WTH Level -8 - Installation of Spare Earthing Electrode in HV Switchroom |  | Contr | __ | FAR - Farringdon Station (West) |  | 2016-02-26 | 2016-02-23 15:00 | -3 | 2016-02-05 08:59 | Electrical - Power Distribution | 3000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | 2no spare Earthing Electrode installed to the HV Switchroom in Level -7 WTH. These electrodes are connected to the Earth mat located at the Level -7 basement slab. As part of the Stage E design these electrodes were design to be installed within the HV switchroom however the Stage F design indicates a revised location on the corridors. Confirmation has been received from Cxxx that they may remain within the room. The connection from the 2 electrodes are made using a 25x3mm copper tape and installed through the wall upstand. The tapes will be capped off and left for future use. These spare additions will be incorporated in the as builts drawings.
| 02SL - Stations (LUL) | Cxxx-NCR-002136 | NCR | WTH - SS - steel members incorrectly painted due to error in paint demarcation drawings |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-09-30 | 2016-09-16 15:04 | -14 | 2016-02-08 08:24 | Structural Engineering - Steel Member | 4000 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Multiple beams in Areas 2 and 3 were shown on __’s paint demarcation drawings as fully painted (paint code AS) whereas the drawing should have shown them as having no paint on the top flange (paint code AF). This is because the top flange of these beams will have shear studs welded to it and these welds cannot be completed onto painted steelwork. These beams are labelled on the attached site photographs. They have also been highlighted on the relevant marked-up __ GA drawings and the paint demarcation drawings. Column C2008 should have been part painted but was annotated as ‘blast only’ (unpainted).
| 02SL - Stations (LUL) | Cxxx-NCR-002138 | NCR | WTH - Lack of Protection of waterproofing on perimeter walls as per ITP |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-04-30 | 2016-04-28 08:29 | -2 | 2016-02-08 12:51 | Civil - Civil Engineering General | 3000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | have installed waterproofing for the perimeter walls. As part of the Perimeter Walls ITP, all protruding lengths for future connections are supposed to be protected. This has regularly not been the case.
| 02SL - Stations (LUL) | Cxxx-NCR-002139 | NCR | WTH - Wall 50 ledge at level +3 omitted |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-08-05 | 2016-06-14 07:35 | -52 | 2016-02-09 10:34 | Civil - Civil Engineering General | 3450 |  | Design | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | raised Cxxx-RFI-002948 in July 2015 proposing to create a ledge at the Western end of Wall 50 at level +3. This was to allow Beam 5.1 (running North-South) to have a steel-to-steel connection with Beam 5.1 running along GL 9. Beam 5.1 along GL 9 would then have a connection to an encast plate on the vertical face of the ledge detail. This is shown on __ Wall Elevation drawing Cxxx--Y-DWG-M123-51873 P03 (referenced below). This was accepted by Cxxx but not passed onto the site team or __ ( RC detailers) to redetail the reinforcement within the wall - hence Wall 50 has been built in accordance with the original design (i.e. full height with no ledge). The original __ design showed CiP WTH-9507 on the western edge of Wall 50 so this has been installed. There is no CiP on the South elevation of Wall 50 to take Beam 5.1 (in the North-South orientation).
| 02SL - Stations (LUL) | Cxxx-NCR-002140 | NCR | ETH - Trapezoidal Shaft - Level -2 Capping Beam along Wall 15 cast incorrectly |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-07-01 | 2016-04-21 09:31 | -71 | 2016-02-10 09:51 | Civil - Civil Engineering General | 1700 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Following the construction of Wall 15 Level -2. conducted a as-built survey of capping beam at at Level -2. became aware capping beam was cast incorrectly. Please see attached survey and photos.
| 02SL - Stations (LUL) | Cxxx-NCR-002141 | NCR | WTH_SHW2 Stairwell blockwork at level +82.305m |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-02-25 | 2016-02-11 16:41 | -14 | 2016-02-11 16:00 | Architectural - Brickworks/Blockworks | 750 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | __ started building blockwork on level 82.305m in the stairwell without the area being signed off previously, as required by Cxxx--C-ITP-M123-50277Rev.1.0 Activity 4.1.
| 02SL - Stations (LUL) | Cxxx-NCR-002142 | NCR | SCL - Failed Waterproofing Inspection - CH1 Bay 2 Crown |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2016-04-15 | 2016-04-13 10:18 | -2 | 2016-02-10 18:43 | Tunnelling - Linings - In-situ Concrete | 500 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | During the CRL inspection of the waterproofing in CH1 bay 2 crown, carried out on Wednesday 10/02/16 at around 2pm, it was found that testing to ensure enough cover between rebar and waterproofing (min. 35mm) had not been carried out by near to the crown, where it appeared that rebar was touching the waterproofing (see photo). It may be the case that there was the required distance behind the sagging membrane, but as there ware no spacer blocks nearby to prove this and the distance had not been checked, the inspection was failed.
| 02SL - Stations (LUL) | Cxxx-NCR-002143 | NCR | WTH - SS - TOC level in Wall 39 pocket connections 6242, 6201, 6203, 6204 too high |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-04-18 | 2016-04-07 11:11 | -11 | 2016-02-11 13:03 | Civil - Civil Engineering General | 3500 |  | Design | Repair | 3 (3-6k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | constructed Wall 39 pocket connections 6242, 6201, 6203, 6204 in accordance with the KPS drawings appended to the KPS design package accepted by Cxxx (relevant marked-up drawing attached and design package referenced below). This drawing shows the connecting beams sitting directly on a bed of grout. When completing the fabrication drawings, __ added a 70mm steel packer to the underside of these beams to help with load spread. This differentiation between __’s fabrication drawings and the KPS pocket connection drawings was not identified during the drawing review process hence the beams have been delivered to site with the 70mm spreader plate welded to the underside of the beam.
| 02SL - Stations (LUL) | Cxxx-NCR-002144 | NCR | ETH SB W23 Lift 2 (Level L-2) Grout loss and Dywi bar repair |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-07-29 | 2016-07-29 07:27 | 0 | 2016-02-12 10:25 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | After striking the shutters for wall W23 2nd lift (L-2) between GL5 and GL7 a small area with grout loss was observed on the bottom of the west side of the wall. In order to fix the formwork a dywi bar was fixed into the previous pour of wall W23 on the back of the wall (west side). The dywi bar has been cut flush with the wall after striking the shutter for H+S reasons. Both areas require concrete repair.
| 02SL - Stations (LUL) | Cxxx-NCR-002145 | NCR | WTH - SS - Concrete level of perimeter wall 43 low beneath columns |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-03-21 | 2016-03-21 18:16 | 0 | 2016-02-11 17:44 | Civil - Civil Engineering General | 2500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | The concrete beneath the columns highlighted on the attached Cxxx structural steelwork GA drawing has been cast too low. Drawing Cxxx--S-DDD-M123_Z-70107 C02 shows the design concrete level as +111.325m. The attached surveys show the as-built levels of the concrete. In the worst case, the concrete level is 98mm lower than design.
| 02SL - Stations (LUL) | Cxxx-NCR-002146 | NCR | SCL - Honeycombing on Stop End of CP1 Crown Bay 7 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-03-11 | 2016-03-09 12:20 | -2 | 2016-02-15 15:19 | Tunnelling - Linings - In-situ Concrete | 2500 |  | Material | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | When striking the formwork of Crown Bay 7 in Cross Passage 1, the construction joint at chainage 20.886 appeared honeycombed. The area of honeycombing was between 2 and 4 o clock and 8 and 10 o clock. These areas of honeycombing were investgated and chipped back to sound concrete. The depth of honeycombing was 200mm from the waterproof membrane between 8 and 10 o clock when facing towards PTE and so extends beyond the waterbar at this construction joint. See attached photo. Between 2 and 4 o clock, the honeycombing was a couple of centimetres deep over 100mm of the lining. This did not compromise the waterbar encapsulation.
| 02SL - Stations (LUL) | Cxxx-NCR-002147 | NCR | SCL - Wrong location of waterbar at CP2A TH Construction Joint between bay 3 and bay 4 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-03-02 | 2016-02-22 19:00 | -9 | 2016-02-17 12:28 | Tunnelling - Linings - In-situ Concrete | 2500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | The waterbar for the Construction Joint between CP2A TH BAY 3 and BAY 4 was installed with a 0.000m off set from the LP1 axis, 633mm away from where the actual location of this Construction Joint is (633mm off set from LP1 axis towards CH1). An hydrophilic strip and a grout hose was installed at that Construction Joint instead.
| 02SL - Stations (LUL) | Cxxx-NCR-002148 | NCR | WTH – SH-W2 Downpipe clash with blockwork wall in stairwell at Landing +99.960m |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-04-15 | 2016-04-15 09:09 | 0 | 2016-02-15 18:14 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Previous Construction - Problems based on previous construction errors | Completed |  | Drawing Cxxx--P-DDA-M123_5-75208 (P06) shows a downpipe installed adjacent to Wall 9 (see attached sketch). The pipe was cast in and it has since been discovered that the downpipe collar will clash with the blockwork wall at high level by approximately 20mm.
| 02SL - Stations (LUL) | Cxxx-NCR-002149 | NCR | SCL - Honeycombing on CH1 Crown Bay 3 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-04-19 | 2016-03-19 15:16 | -31 | 2016-02-23 14:18 | Tunnelling - Linings - In-situ Concrete | 2500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Supervision - Other | Completed |  | Upon striking CH1 Crown Bay 3, Chainage 23.057 to 31.057, it was apparant that there was honeycombing at the joint between the invert and crown. The extent of the honeycombing was from chainage 23 to 27.
| 02SL - Stations (LUL) | Cxxx-NCR-002150 | NCR | SCL - Error in Reading Drawing for ES1 Connection |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-03-03 | 2016-02-21 18:37 | -11 | 2016-02-18 10:42 | Tunnelling - Linings - Sprayed Concrete | 2500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Not Defined | Completed |  | The drawing for ES1 Box Connection - Cxxx-MMD-C4-DDD-M123_Z-00064 section D-D - details a 2 layer waterproofing application over the first 5 metres of the tunnel, i.e. a double thickness of waterproofing system being applied in this area. read this note as 2 layers of waterproofing membrane, i.e. normal spraying conditions. The ITP for sprayed waterproofing states that each layer of sprayed waterproofing is 4mm wet thickness and 3mm dry thickness. A double layer, as detailed in the drawing above, would correspond to an 8mm wet thickness and a 6mm dry thickness. See attached summary which shows that in the invert of ES1 between chainage 0 and 22, a minimum wet thickness of 5mm was applied. This corresponds to a dry thickness of 4mm. Therefore have not adhered to the ITP requirement of each layer being 3mm dry thickness as per the ITP.
| 02SL - Stations (LUL) | Cxxx-NCR-002151 | NCR | SCL - Insufficient Curing Records of ES1 and VA2 Sprayed Secondary Concrete Linings |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-03-03 | 2016-02-24 09:09 | -8 | 2016-02-18 15:19 | Tunnelling - Linings - Sprayed Concrete | 2500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Other human error | Completed |  | There are no records for the curing of the secondary lining in ES1 and VA2 in accordance with the Works Information requirements. Although the work took place, there are no records of such activity occuring. Therefore the minimum curing which has occured is the curing in a tunnel environment in a similar manner to the primary lining.
| 02SL - Stations (LUL) | Cxxx-NCR-002152 | NCR | MEP - Relocation of Level -7 Earthing Electrode to Corridor |  | Contr | __ | FAR - Farringdon Station (West) |  | 2016-03-04 | 2016-02-29 09:46 | -4 | 2016-02-19 15:49 | Electrical - General | 1000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | The Electrical Design illustrates all Earthing Electrodes within the ETH Level -7 installed at lockable cupboards along the corridor wall as per (Cxxx--E-DD-M123_Z-25701). However, one of the 4 electrodes to be connected to EB1B (Spare) is installed at the HV Switchroom. This electrode is required to be connected to EB1B so it is proposed herewith in accordance with Cxxx--E-DDD-M123_Z-25707 that a minimum of 20mm rebar is welded to the rebar in the HV Swtichroom to extend the rebar to the corridor point where the earth bar will be installed.
| 02SL - Stations (LUL) | Cxxx-NCR-002154 | NCR | MEP - pull out tests for anchor bolts by non-UKAS accredited company |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-03-30 | 2016-03-23 15:53 | -7 | 2016-02-19 13:27 | Electrical - Cable Management | 1500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | Pull out Tests in the soffit and walls for cable trayanchor bolts underside of platforms was done by non-UKAS accredited company.
| 02SL - Stations (LUL) | Cxxx-NCR-002155 | NCR | MEP - HDG Cable tray |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-03-21 | 2016-03-23 16:02 | 2 | 2016-02-22 11:54 | Electrical - Cable Management | 2000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | The designer has detailed ‘HDG’ for cable tray on the accepted drawings. The construction team has interpreted this as ‘Hot Dip Galvanised’ whereas the designer asserts that this means ‘Heavy Duty Gauge’. The Medium Duty tray has been installed in the under platform areas and offered and accepted as benchmark. Note that Medium Duty Gauge complies with the wording in JY63.1302 (b) JY63.1302 Cable tray and ladder a Cable tray shall be sized to provide 25% capacity b. The cable tray shall have a standard return flange of minimum 25mm
| 02SL - Stations (LUL) | Cxxx-NCR-002156 | NCR | WTH – SHW2 Landing +105.240m nib incorrectly installed |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-03-21 | 2016-03-18 14:27 | -3 | 2016-02-22 16:18 | Civil - Civil Engineering General | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The eastern nib on the SH-W2 staircase landing at +105.240m was cast to the incorrect length, 200mm rather than 80mm.
| 02SL - Stations (LUL) | Cxxx-NCR-002157 | NCR | ETH - Trapezoidal Shaft - Level -2 to Level -1 Wall 7 - Reinforcement Bars moved |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-04-07 | 2016-03-31 11:41 | -7 | 2016-02-25 14:24 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | ETH - Trapezoidal Shaft - Level -2 to Level -1 Wall 7 - Reinforcement Bars Moved During concrete pour on 23/02/16 concrete finishes displaced a number of reinforcement bars to enable the concrete to be poured via pump pipe. As shown in attached photo bars where not replaced and have been concreted at an angle.
| 02SL - Stations (LUL) | Cxxx-NCR-002159 | NCR | ETH-SB cast in plate ETH-4403 installed at incorrect level |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-05-13 | 2016-04-27 12:27 | -16 | 2016-02-29 08:30 | Civil - Civil Engineering General | 2900 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | carried out an as built survey of the cast in plate ETH-4403 on wall W30 at L+2. The level at the top of the cast in plate was found to be 15mm lower than the design level as shown on drawing Cxxx--S-DWG-M123-52027 C02. As built level is 127.455m AOD and the design level is 127.470m ATD, therefore site work detail 16 as required by drawing Cxxx--Y-DWG-M123-51866 P4.0 and shown drawing Cxxx--X-DWG-M123-50288 P01 cannot be carried out due to insufficient depth to carry out a full penetration outer fillet weld across the top of the top flange.
| 02SL - Stations (LUL) | Cxxx-NCR-002161 | NCR | STW - Subcontractor started manufacturing PES before ITP was accepted by CRL |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-03-11 | 2016-03-10 08:28 | -1 | 2016-02-26 13:19 | Architectural - General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Insufficient work planning by the subcontractors | Completed |  | PES subcontractor started manufacturing steel products and precast panels without CRL accepted ITP. was not aware that manufacturing had started.
| 02SL - Stations (LUL) | Cxxx-NCR-002162 | NCR | SCL - Missing Dry Shrinkage Result for BFK 29 December 2015 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-03-28 | 2016-03-08 12:10 | -20 | 2016-02-29 12:50 | Tunnelling - Linings - In-situ Concrete | 2500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Other human error | Completed |  | __ have lost the 28 day dry shrinkage result for 29 (Cast in situ lining mix). This means there is no dry shrinkage result for the month of December in 2015. See attached table which shows previous dry shrinkage results to date, all within specification.
| 02SL - Stations (LUL) | Cxxx-NCR-002163 | NCR | STW –Incorrect making and storage of mortar cubes |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-03-14 | 2016-03-14 16:55 | 0 | 2016-02-29 13:26 | Civil - Civil Engineering General | 1000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | Clause JZ21.1301ai) of Cxxx--A-RSP-M123-50057 Rev 10.0 (Architectural Specification) refers to BS 5628-1 Annex A with regards to mortar testing. It requires 6No. prisms to be taken per 150m2 of wall constructed. __ (blockwork subcontractor) were making 4No. cubes for both types of mortar used onsite (M4 and WI mortar) and the quality of the cubes were not as expected under British Standards nor were the cubes stored correctly (see attached photograph).
| 02SL - Stations (LUL) | Cxxx-NCR-002164 | NCR | SCL - Contact Grouting Vent Pipe Missed in PL4/RTE2 Headwall |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-04-01 | 2016-03-09 15:07 | -23 | 2016-03-01 14:55 | Tunnelling - Linings - In-situ Concrete | 2500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The headwall pour in RTE2 at the PL4 interface, a single contact grouting pipe has been installed. This is the pour between CH304.435 in PTW and CH0.777 in RTE2. have not installed a grout vent point in the bay which means the process of contact grouting will be more difficult.
| 02SL - Stations (LUL) | Cxxx-NCR-002165 | NCR | WTH – Excess cover for the eastern edge of the SHW1 level-5 infill |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-03-15 | 2016-03-08 16:06 | -7 | 2016-03-01 16:02 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | have poured the SHW1 level-5 infill. At the eastern edge cover to the couplers installed by Cxxx (previous contractor) have excessive cover along a 3.1m edge (100-120mm cover). Please refer to attached sketch. The bottom mat of steel installed had the correct cover (45-72mm). However, cover to the couplers and screwed in bars was 100-120mm.
| 02SL - Stations (LUL) | Cxxx-NCR-002166 | NCR | ETH-SB cast in plate ETH-3326 out of position |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-03-30 | 2016-03-24 15:25 | -6 | 2016-03-16 12:00 | Civil - Civil Engineering General | 2000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | carried out an as built survey of the cast in plate ETH-3326 on wall W30 at L+1. Based on the as built survey the wall is out of position by 22mm towards Gridline C (GLC). This would result in the fin plate being 12 mm clear of the cast in plate therefore site work detail 14 as required by drawing Cxxx--Y-DWG-M123-51866 P4.0 cannot be carried out as shown on drawing Cxxx--X-DWG-M123-50288 P01 (see attached drawings and as built site survey Ref ETH-3326 as built). NOTE: Drawing Cxxx--X-DWG-M123-50288 P01 does not show the correct concrete profile. The cast in plate is supposed to be on the edge of the wall. This has been updated to the correct concrete profile on drawing Cxxx--X-DWG-M123-50288 P02 (Attached)
| 02SL - Stations (LUL) | Cxxx-NCR-002167 | NCR | ETH – Wall 24 Failed Pre Pour Inspection |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2016-04-08 | 2016-03-21 16:27 | -18 | 2016-03-08 18:05 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | CRL was given a signed off Pre Pour pack by for the pour of Wall 24 second lift up to Level 0. CRL therefore attended site to confirm that everything was in order prior the pour. During an inspection of the base it was noted that there were 2 items that should not have been in there, which were a piece of rebar approximately 3m long and a clamp for the shutter. These 2 items should have been removed prior to the handing over of the Pre Pour pack to CRL. These were shown to the Site Engineer to action the removal. The CRL Field Engineer then made contact with ’s Section Engineer to discuss the matter and on his arrival it was noted that had started to pour concrete into the wall without removing any of the items. On examination of the base it was noted that the rebar was 75% covered with concrete and the clamp was being removed. See attached photos.
| 02SL - Stations (LUL) | Cxxx-NCR-002168 | NCR | WTH – L-1 W39 Pour 3 Kicker Void |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-03-18 | 2016-03-16 15:10 | -2 | 2016-03-04 16:06 | Civil - Civil Engineering General | 750 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A 200mm high up-stand kicker was poured for W39 Pour 3 section. After striking the formwork for this kicker a small void was found at the base of one of the columns. This void can be seen in photos attached. Column location is at the intersection of gridline B6.
| 02SL - Stations (LUL) | Cxxx-NCR-002169 | NCR | WTH – L-1 Slab C1B – Earth Pit |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-04-04 | 2016-04-04 16:52 | 0 | 2016-03-04 16:47 | Civil - Civil Engineering General | 1250 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Earth Pits were installed in L-1 Slab C1B in accordance with drawing Cxxx-SWN-S-DDA-M123_2-79101 C06, Cxxx--E-DDD-M123_Z-75102 C01 & Cxxx-RFI-003505. One of the Earth Pits has been damaged and has been broken and cracked. (The western Earth Pit). See attached photos of condition.
| 02SL - Stations (LUL) | Cxxx-NCR-002170 | NCR | WTH - SS - Beam B3037 fabricated too long and B3040 fabricated too short |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-06-24 | 2016-06-20 15:12 | -4 | 2016-03-15 16:02 | Civil - Structural Engineering | 5000 |  | Manufacturing Defect | Rework | 3 (3-6k) | Complete | Personnel Error - Inattention to detail | Completed |  | 1 out of 4no Beam B3037's has been fabricated and delivered to site 129mm too long (fabricated to a length of 3011mm instead of the design length of 2882mm). See attached marked-up design drawing for B3037. 1 out of 3no Beam B3040's has been fabricated and delivered to site 129mm too short. (fabricated to a length of 2882mm instead of the design length of 3011mm). Refer to attached marked-up design drawing for B3040. Area 3 fabrication drawings package is also referenced below.
| 02SL - Stations (LUL) | Cxxx-NCR-002171 | NCR | WTH – L-1 Wall 38 Stage 2 Pour 2A – Movement of Formwork |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-03-22 | 2016-03-16 15:17 | -6 | 2016-03-08 08:00 | Civil - Civil Engineering General | 1750 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During placement of concrete for the Wall 38 Stage 2 Pour 2A there was an unexpected localised movement of the southern face shutter. The extent to which the shutter displacement can be seen in the attached photos – with a maximum of 35mm.
| 02SL - Stations (LUL) | Cxxx-NCR-002172 | NCR | WTH - Wrong block type used on Level -3 internal walls |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-04-25 | 2016-04-07 16:09 | -18 | 2016-03-08 10:03 | Civil - Civil Engineering General | 8500 |  | Incorrect Installation | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 1. constructed some of the internal walls on Level -3 in SH-W2 using the wrong block type, see attachment for extent of walls incorrectly built. The wall should have been constructed using 190mm wide trough blocks and instead 190mm wide slot blocks were used. Both types of blocks are covered under Cxxx--C-LRC-M123-50575 Rev 2. 2. Furthermore, the walls were demolished prior to this NCR being raised and the remedial action being agreed.
| 02SL - Stations (LUL) | Cxxx-NCR-002173 | NCR | SCL - Honeycombing on CH1 Crown Bay 6 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-06-17 | 2016-05-27 10:25 | -21 | 2016-03-10 16:22 | Tunnelling - Linings - In-situ Concrete | 2500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Upon striking CH1 Crown Bay 6, between chainage 47.157 and 55.257, it was apparant that there was a small area of honeycombing at axis level in the centre of the pour. This was at the centre of the pour and a total length of 3 metres.
| 02SL - Stations (LUL) | Cxxx-NCR-002174 | NCR | ETH - Trapezoidal Shaft - Level -1 Installation of Flexcell (Bitumen Impregnated Softboard) without MCR |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-04-08 | 2016-04-06 08:01 | -2 | 2016-03-10 18:40 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | When constructing the lining wall against Hayne Street Bridge, installed flexcell (Bitumen Impregnated Softboard) as agreed in Cxxx-FCD-001885 without an approved MCR in place.
| 02SL - Stations (LUL) | Cxxx-NCR-002176 | NCR | SCL - Failed Inspection of CH1 Bay 9 Reinforcement and Smaller Bars in Bay 8 of CH1 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-04-11 | 2016-04-09 09:57 | -2 | 2016-03-14 16:52 | Tunnelling - Linings - In-situ Concrete | 2500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | In CH1 Crown Bay 8 (CH58.051 to CH66.051) and 9 (CH66.051 to CH 69.226), the B20 bars detailed in drawing Cxxx-MMD-C4-DDD-M123_5-00637 as bar mark 60 were installed as B16s. This error was found during the pre pour inspection of CH1 Crown Bay 9 when Crown Bay 8 had already been cast. Crown Bay 8 steel had been signed off by the inspectors and was not captured at this stage. For CH1 Crown Bay 8, to ease construction, a standard set of bars was installed at a fixed distance from the opening and individual bars lapped onto the steel to provide the correct length to the CP3 opening. The distance from the construction joint to the opening of CP3 is 0.6m and the required lap on a 16mm bar in C50/60 is 880mm. Therefore the B16 bars are doubled up due to this lap therefore providing the minimum area of steel, the only non conformance is at the ends of the steel (see attached picture, area of non conformance is the yellow triangle on both sides of CH1). For CH1 Crown Bay 9, the error was correct by installing additional 16mm steel bars alongside the already 16mm bars to provide a steel quantity in excess of the design requirements.
| 02SL - Stations (LUL) | Cxxx-NCR-002177 | NCR | WTH – __ Precast Stairs - Incorrect number of 28 day cube tests |  | Contr | 201068 | FAR - Farringdon Station (West) |  | 2016-03-28 | 2016-03-14 15:20 | -14 | 2016-03-14 09:39 | Structural Engineering - Pre-cast | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | For the precast flights fabricated by __ for the WTH ESS/INS staircase cubes were made and 1 tested at 1, 7, 28, 56, 90 days. This doesn’t comply with KF10.2204 a) which requires 2No 28 day cube tests.
| 02SL - Stations (LUL) | Cxxx-NCR-002179 | NCR | WTH – Notched blockwork to accommodate cables |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-09-30 | 2016-05-12 09:30 | -141 | 2016-03-16 16:22 | Civil - Civil Engineering General | 2000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In one location in the WTH at Level -8 in the square shaft (see attached sketch for exact location – shown on extract from Cxxx--A-DDA-M123_8-76224 Rev C03) two blocks have been notched to allow cables to run through them (see attached). At a later date these blocks will have to be replaced with whole blocks.
| 02SL - Stations (LUL) | Cxxx-NCR-002180 | NCR | WTH SH-W2 Level -5 - Damage to blockwork door opening 6-WD15 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-03-30 | 2016-03-17 08:25 | -13 | 2016-03-16 17:06 | Civil - Civil Engineering General | 2000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | There is a line item in Cxxx--C-ITP-M123-50277 (Rev 1) for protecting completing door openings. Door 6-WD15 was not promptly protected and was struck by an object causing minor damage (see attached photographs).
| 02SL - Stations (LUL) | Cxxx-NCR-002181 | NCR | WTH – SHW1 Level -4 slab exceeding placement time of concrete |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-08-31 | 2016-07-26 14:27 | -36 | 2016-03-17 11:06 | Civil - Civil Engineering General | 500 |  | Equipment Breakdown | Use As-Is | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | During the concrete pour on 5/3/16 one instance occurred where the concrete placement timing was outside that stated in the clause KF10.3203h. Clause KF10.3203h from the Civil and Structural Specification (Cxxx-SWN-C-RSP-M123-00004) requires a maximum gap of 60 minutes between placing concrete onto the live pour face. The time between placement of wagons 1 and 2 was 85 minutes. This gap in placement of concrete was due to a pump malfunction. All of the above is recorded on the attached structural concrete site control sheet.
| 02SL - Stations (LUL) | Cxxx-NCR-002182 | NCR | No information could be provided during and following a CRL surveillance defining where the under platform CMS pull off design and proof loading requirements had come from. |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2016-04-08 | 2016-04-08 16:30 | 0 | 2016-03-17 14:26 | Electrical - Cable Management | 1500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | During a planned Crossrail surveillance undertaken on 3rd March 2016 which looked at the installation of the Under Platform Cable Management System (CMS), pull out test records were made available during the surveillance for the installed wall mounted and soffit mounted bracket fixings. The records (documented on Cxxx-__-E-XDS-M123-00006) which covered test locations A1-A20, detailed a design load requirement of 2.0kN and recorded acceptable proof loading up to 2.7kN for each location. A request was made as part of the surveillance Exit Note, and following that in further emails, for information on where the design and proof loading values had been derived from (calculations, assessments etc), appropriate to the Under Platform CMS installation. At the time of raising this NCR, no verifiable evidence has been provided as requested, as such it can not be confirmed where the design and proof loading values have come from. As the values cannot be confirmed, it is unclear whether the proof testing undertaken on the Under Platform CMS fixings to date is correct. Material and Workmanship Specification: Mechanical, Electrical and Public Health JY63 ‘Support Components – Cables’ states under clause JY63.1302 (o) “ Load calculations and proposed support systems shall be submitted for approval before installation commences”. ISO 9001 ‘Quality Management System – Requirements’ states under section 7.3.2 Design and Development Inputs “Inputs relating to product requirements shall be determined and records maintained. These inputs shall include a) functional and performance requirements …… The inputs shall be reviewed for adequacy.”
| 02SL - Stations (LUL) | Cxxx-NCR-002183 | NCR | ETH - Hayne Street Substation Relocation Works - Earth Bar and Copper Earth Tape |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-03-31 | 2016-03-23 10:42 | -8 | 2016-03-17 15:12 | Electrical - Electrical Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | On 17/03/2016 the contractor () used a product (Earth Bar and Copper Earth Tape) without having an approved MCR in place for the product.
| 02SL - Stations (LUL) | Cxxx-NCR-002184 | NCR | WTH – Wall 43 west level -1 to 0 exceeding placement times of concrete |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-03-31 | 2016-03-23 13:56 | -8 | 2016-03-17 15:57 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | During this pour on 25/1/16 the clause stated below was exceeded on 5 no. loads out of 9. Slump tests were carried out on these loads and the mix was found to still have sufficient workability to allow the loads to be used for the pour. See structural concrete control sheet with slump test results. One load in addition to the 9 was rejected as it was over three hours from batching when it arrived on site and the slump test showed that the workability was outside of the required range. Clause KF10.3202c from the Civil and Structural Specification (Cxxx-SWN-C-RSP-M123-00004) states that concrete is to be placed and compacted within 2 hours of the addition of water. See structural concrete control with out of time loads highlighted.
| 02SL - Stations (LUL) | Cxxx-NCR-002185 | NCR | WTH - SS - Top row of bolt holes not drilled in column C2014 for B2201 beam connection |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-06-24 | 2016-06-21 12:56 | -3 | 2016-03-18 15:39 | Structural Engineering - Steel Member | 750 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | The bolt holes highlighted on the attached marked-up __ fabrication drawing for column C2014 were stamped but not drilled. The column has been erected and the connecting beam has been installed 100mm low at this connection, utilising the 6no. existing bolt holes that have been drilled.
| 02SL - Stations (LUL) | Cxxx-NCR-002186 | NCR | WTH – SHW1 Wall 22 Level -4 to level -3 ringbeam exceeding placement times of concrete |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-04-01 | 2016-03-23 13:54 | -9 | 2016-03-18 16:26 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | During this pour on 17/3/16 the 3 hour placement time as part of the MCR for mix 29 (Cxxx--C4-LRC-M123-50124) was exceeded on 1 no. load. The flow test result was within the correct range therefore met the workability requirement and was poured. Clause KF10.3202c from the Civil and Structural Specification (Cxxx-SWN-C-RSP-M123-00004) states that concrete is to be placed and compacted within 2 hours of the addition of water. See structural concrete control sheet with out of time load highlighted.
| 02SL - Stations (LUL) | Cxxx-NCR-002187 | NCR | MEP - WTH Modification of Spare Earthing Bars at Level -7 |  | Contr | __ | FAR - Farringdon Station (West) |  | 2016-05-25 | 2016-05-17 15:10 | -8 | 2016-04-20 07:17 | Electrical - Power Distribution | 3000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Interfacing problems | Completed |  | Modification work undertaken under Cxxx-NCR-001665 to relocate the Spare Earthing Bar from the UPE to the corridor was not carried out in accordance with the design design. The Earth bars were relocated from the central location within the UPE to the adjacent wall (within the UPE) when it should have been relocated to outside section of the adjacent to the UPE door. Refer to Test report for before and after photographs of the Earthing Electrodes for further information.
| 02SL - Stations (LUL) | Cxxx-NCR-002188 | NCR | WTH - SS - HD bolts for Column H,2 cast in out of position |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-05-20 | 2016-04-07 11:18 | -43 | 2016-03-22 08:56 | Structural Engineering - Steel Member | 2000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 2no. of the HD bolts for the column H/2 have been cast 20mm out of position. This is shown on the attached marked-up drawing Cxxx--X-DWG-M123-50086 C01.
| 02SL - Stations (LUL) | Cxxx-NCR-002190 | NCR | ETH - Trapezoidal Shaft - Damage to Geothermal Loop |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-05-22 | 2016-04-18 10:30 | -34 | 2016-03-23 08:46 | Civil - Civil Engineering General | 1000 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Lack of procedure | Completed |  | ETH Trapezoidal Shaft - During testing works for geothermal loops it was identified one number loop had became blocked. it was identified that during the installation of falsework in for Level -1, a carpenter had drilled into the Level -2 slab to install a fixing thus blocking the loop. Addtional Information: Pile U201 loop damaged during work see attached drawing
| 02SL - Stations (LUL) | Cxxx-NCR-002191 | NCR | WTH SH-W2 Level -8 plinth cast without approved waterproofing drawing |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-06-02 | 2016-05-13 12:38 | -20 | 2016-03-24 10:35 | Civil - Civil Engineering General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | A CAT ladder is to be installed on Level -8 of SH-W2 in the location shown on the attached sketch (extracted from drawing Cxxx--A-DDA-M123_8-76224 C03). No plinth is shown underneath the CAT ladder. The plinth was however cast in accordance with drawing Cxxx--S-DDD-M123_Z-70330 C01. The concrete protective layer, required for the screeding, was to be cast directly against the plinth. The waterproofing detail required against the plinth was not on an approved drawing. Detail used shown on attached sketch.
| 02SL - Stations (LUL) | Cxxx-NCR-002192 | NCR | ETH - Damaged Concrete finish on Wall W33 L0 GL 9'/C' |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-04-29 | 2016-04-28 13:34 | -1 | 2016-03-31 14:25 | Civil - Civil Engineering General | 27000 |  | Damaged | Repair | 2 (6-60k) | Complete | Supervision - Insufficient supervision | Completed |  | When breaking out the cones for the holding bolts on column C16 at GL9'/C', the general operatives broke out the concrete on the near face of wall W33 causing damage to the finish as shown on the attached photo. (Refs: Cxxx/SR/ETH/SW17 and Cxxx/SR/ETH/SW18).
| 02SL - Stations (LUL) | Cxxx-NCR-002193 | NCR | ETH - Trapezoidal Shaft - Missed Earthing Test Wall 21 Level -1 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-04-12 | 2016-04-12 13:28 | 0 | 2016-03-29 09:33 | Civil - Civil Engineering General | 500 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | ETH - Trapezoidal Shaft - Missed Earthing Test Wall 21 Level -1 Following conversations with __, they have highlighted a missed earthing test. Two number bars at the base of Wall 21 were connected using copper tape and clamps. However test between starter bar and threaded bar has not been conducted. Please see attached photo.
| 02SL - Stations (LUL) | Cxxx-NCR-002194 | NCR | ETH- HD Bolts W33/35 - Overbreaking Bolt Pockets at W33/35 GL D'/9 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-04-27 | 2016-04-20 14:38 | -7 | 2016-04-06 07:02 | Civil - Civil Engineering General | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Insufficient information made available to the worker. | Completed |  | In W33/W35 at GL D/9’ whilst breaking out the cones for two of the HD bolts within this cluster – the area was overbroken and concrete was broken out all the way to the top of the anchor plate and to a width larger than the cone as shown in sketch ref: Cxxx-SR-ETH-SW16 and attached mark up ref: Cxxx--S-DDD-M123_Z-20107 P01_Markup. The bolt does not lift out when pulled vertically as the corners of the anchor plate are still wedged in the concrete.
| 02SL - Stations (LUL) | Cxxx-NCR-002195 | NCR | ETH - Holding Down Bolts in the top of W24 for Pocket Connections (ETH-2210 / ETH-2212) Cast Incorrectly |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-04-20 | 2016-04-13 15:29 | -7 | 2016-03-30 13:01 | Civil - Civil Engineering General | 3500 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Management Problem - Inadequate supervision | Completed |  | The bolts within the W24 Pocket Connections (ETH-2210 / ETH-2212) have been cast out of tolerance. Three of them have been cast too far south approx. 32mm, 23mm and 48mm. All shown on the attached pdf as built (Bolts_ETH2210 and ETH 2212). One of the bolts (Bolt C in ETH 2210 Ref: W24 Bolts Summary) has been completely broken out as and is no longer cast in – see attached photo.
| 02SL - Stations (LUL) | Cxxx-NCR-002196 | NCR | WTH - SS - Connection clash between Beam B3079 and Truss section T3010 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-05-27 | 2016-04-15 10:41 | -42 | 2016-03-30 17:16 | Structural Engineering - Steel Member | 3500 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The bottom flange of Beam B3079 and the end plate of truss section T3010 clash. This is shown in the attached marked-up extract from __’s 3D model and marked up __ Area 3 GA drawing.
| 02SL - Stations (LUL) | Cxxx-NCR-002197 | NCR | ETH - Barbican Station Pile Concrete Cube Results on 17/07/2016 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-04-14 | 2016-03-31 16:29 | -14 | 2016-03-31 15:49 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | The 28 day compresive strength results for the concrete poured at Barbican Station on the 17/07/2015 indicate that the concrete achieved a strength of 38.2 and 38.0N/mm2.
| 02SL - Stations (LUL) | Cxxx-NCR-002198 | NCR | ETH - Trapezoidal Shaft - Wall 15, L-2 to L-1 cast in dywidag bar |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-04-15 | 2016-04-15 09:27 | 0 | 2016-04-01 07:34 | Civil - Civil Engineering General | 1000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | When erecting the shutters for wall 15 between GL C & D' a temporary dywidag bar was installed to hold the South shutter face in place. This dywidag was not removed when closing up the shutter, when erecting the North face, and so has been cast into the wall. The cast in dywidag bar was only identified when striking the shutter (please see attached photo and drawing mark up for location) and therefore cannot be removed.
| 02SL - Stations (LUL) | Cxxx-NCR-002199 | NCR | WTH - SHW2 Level -8 Concrete protective layer - exceeding placement times of concrete |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-05-06 | 2016-05-04 11:37 | -2 | 2016-04-05 09:24 | Architectural - Flooring | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | During this pour on 22/03/16 for the concrete protective layer on WTH SHW2 Level -8 the clause stated below was exceeded. Slump tests were carried out on these loads and the mix was found to still have sufficient workability to allow the loads to be used for the pour. Concrete was placed within 3 hours of the addition of water. Clause KF10.3202c from the Civil and Structural Specification (Cxxx-SWN-C-RSP-M123-00004) states that concrete is to be placed and compacted within 2 hours of the addition of water. See structural concrete control with out of time loads.
| 02SL - Stations (LUL) | Cxxx-NCR-002200 | NCR | ETH - Trapezoidal Shaft - Level 0 - Wall 35 pour to incorrect level - missing starter bars for cantilever slab between GL 8’ and 9’ |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-03-31 | 2017-03-15 08:29 | -16 | 2016-04-01 06:48 | Civil - Civil Engineering General | 4000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Personnel Error - Inattention to detail | Completed |  | Following the start of level 0 slab construction, have become aware that Wall 35 was poured to an incorrect level, thus leading to a number of starter bars from Wall 35 to be missed for small cantilever slab. Please see attached marked up drawing of location. Wall 35 was cast to 116.500 (underside of main slab) instead of 115.650 (underside of cantilever slab). Bar Mark A108 No 41 link bars should have been cast into Wall 35 for cantilever slab.
| 02SL - Stations (LUL) | Cxxx-NCR-002201 | NCR | SCL - Concrete Not Cast Up to Planned Waterbar in CH1 Bay 10 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-07-01 | 2016-05-18 08:50 | -44 | 2016-04-01 09:54 | Tunnelling - Linings - In-situ Concrete | 2500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | When bringing the shutter up to CH1 Bay 10, planned to be between Chainages 69.226 and 77.226, the uplift pads and staircases clashed with CH1 headwall. This meant that the construction joint planned at CH77.226 could not be poured and was instead poured at CH 76. There was no waterbar at this new location.
| 02SL - Stations (LUL) | Cxxx-NCR-002202 | NCR | ETH - Trapezoidal Shaft - Level -2 to -1 C14 Grout Loss |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-04-15 | 2016-04-15 08:46 | 0 | 2016-04-01 08:33 | Architectural - Finishes | 750 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | ETH - Trapezoidal Shaft - Level -2 to -1 C14 Grout Loss Following striking Column C14 Level -2 to -1, identified honeycombing and grout loss between cast kicker and pour. Please see photos attached.
| 02SL - Stations (LUL) | Cxxx-NCR-002203 | NCR | SCL - Honeycombing on CH1 Crown Bay 9 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-06-24 | 2016-05-18 10:09 | -37 | 2016-04-01 12:23 | Tunnelling - Linings - In-situ Concrete | 2500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | When striking CH1 Crown Bay 9, between Chainage 66.051 and Chainage 69.226, honeycombing was apparant on both the left and right hand sides . The area is situated at and below axis level. See attached pictures of the areas affected.
| 02SL - Stations (LUL) | Cxxx-NCR-002204 | NCR | MEP - ETH Level -7 Non compliance with CMS ITP |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-04-29 | 2016-04-28 09:38 | -1 | 2016-04-11 11:31 | Electrical - Cable Management | 1500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Prior to commencement of CMS installation on level -7, __ failed to obtain a signed MEP area handover sheet (Electrical - 2.1 TDS005) in accordance with the accepted ITP. (Cxxx--ITP-M123-50003)
| 02SL - Stations (LUL) | Cxxx-NCR-002205 | NCR | SCL - Cast In Situ Inverts Cast Out of Tolerance |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-06-24 | 2016-05-27 10:27 | -28 | 2016-04-05 10:29 | Tunnelling - Linings - In-situ Concrete | 2500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | See attached Zip file of all the cast in situ inverts of the tunnel. The allowable tolerance for inverts is between +0 and +10mm. The attached zip file shows that the inverts are typically cast between +20mm and -20mm with the extreme values being +33mm big and -30mm tight to profile. It is worth noting that the extremes are only spot points within the surveys and not consistent over multiple bays and locations.
| 02SL - Stations (LUL) | Cxxx-NCR-002206 | NCR | WTH - SS - Incorrect position of beam stub at level 0 on Column Cxxx1 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-06-24 | 2016-05-04 10:28 | -51 | 2016-04-06 11:36 | Structural Engineering - Steel Member | 6000 |  | Manufacturing Defect | Rework | 3 (3-6k) | Complete | Management Problem - Inadequate administrative control | Completed |  | This NCR is divided into two sections. Part 1 - Structural steelwork column on (H-3m, 7) is included in __’s Area 1 fabrication drawing package (Cxxx--X-DWG-M123-50062 P03) and under column Cxxx1. These fabrication drawings are currently at P03 status but no FCD has been raised to cover their use in construction. Part 2 - Column Cxxx1 has an UK 610x229x113 beam stub welded to it for one of its level 0 connections – please see attached marked-up fabrication drawing and onsite photograph. This is comprised of mark numbers TA36 and PA6, welded to plate TA19. The stub has a horizontal offset of 94mm. When this column was fabricated, the stub was welded with the offset orientated in the wrong direction.
| 02SL - Stations (LUL) | Cxxx-NCR-002207 | NCR | WTH SHW1 level-3 slab excessive cover |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-04-27 | 2016-04-26 09:51 | -1 | 2016-04-13 08:35 | Civil - Civil Engineering General | 5000 |  | Incorrect Installation | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | have poured the SHW1 level-3 slab. Cover to the top mat of steel was greater than 60mm over the majority of the slab (this is greater than the maximum allowable under Cxxx-FCD-000974). A393 mesh was placed to obtain correct cover prior to the pour (see attached sketch).
| 02SL - Stations (LUL) | Cxxx-NCR-002208 | NCR | SCL - ES2 Invert Cast Without IFC Drawings and Missing Steel |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-06-24 | 2016-06-22 08:20 | -2 | 2016-04-07 08:12 | Tunnelling - Linings - In-situ Concrete | 2500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | 1. The last secondary lining invert in ES2, between the East Ticket Hall and the decline, was cast on Sunday 3 April in a different manner to the IFC drawings. The drawings are currently being updated to make the invert flat, however rebar has not been detailed for this area. received verbal confirmation that the reinforcement design intent of the invert would not change and therefore proceeded with steel fixing the proposed flat invert. The invert was then cast without IFC drawings due to a breakdown in the site process (see NCR root cause) 2. In addition to the above, when erecting the stop end, the carpenters removed the 100mm of bars protruding from the right hand side of the same invert in the near face. s intention was to use __ couplers to provide a lap, however the carpenters mistook this additional 100mm as an error on the engineers behalf and cut the bars flush with the stop end.
| 02SL - Stations (LUL) | Cxxx-NCR-002209 | NCR | SCL - Missing Waterbar - STE2 Longitudinal Joints |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-06-24 | 2016-05-18 10:10 | -37 | 2016-04-08 14:46 | Tunnelling - Linings - In-situ Concrete | 2500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | Longitudinal waterbar at the joint between invert and crown has not been placed in STE2/PL3 transition. Please see attached PDF of the two locations on both sides of the tunnel where they were not placed. Due to confusion about the placement of waterbar in this area, redundant circumferential waterbar has been installed.
| 02SL - Stations (LUL) | Cxxx-NCR-002210 | NCR | WTH SH-W2 Mastic Damage |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-09-28 | 2018-09-28 14:51 | 0 | 2016-04-11 10:22 | Civil - Civil Engineering General | 6750 |  | Damaged | Rework | 2 (6-60k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | As part of the blockwork package, mastic has to be applied to all movement joints which includes any blockwork to concrete interfaces, both horizontal and vertically and on one side of all WI columns. It has been observed that the mastic has been damaged and in some cases deliberately (see attached). Areas of damage are in all levels in SH-W2.
| 02SL - Stations (LUL) | Cxxx-NCR-002211 | NCR | STW – Inadequate concrete lintel bearing |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-05-13 | 2016-05-05 15:38 | -8 | 2016-04-11 10:50 | Civil - Civil Engineering General | 2500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | The access hatches in the perimeter walls are required to have a concrete lintel installed over the top of the void. There is no reference in the Architectural Specification (Cxxx--A-RSP-M123-50057 Rev 10) relating to the use of concrete lintels and how much they are required to bear onto the blockwork. __’s ITP (Cxxx--C-ITP-M123-50277 Rev 1) stated that the concrete lintels will bear 150mm onto the adjacent blockwork. In some instances on site it was discovered that some lintels only had approximately 95mm bearing.
| 02SL - Stations (LUL) | Cxxx-NCR-002212 | NCR | WTH – SH-W2 Level -8 Wall Built Incorrectly & Deconstructed Prior to NCR Being Issued |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-06-30 | 2016-06-10 08:59 | -20 | 2016-04-11 12:13 | Civil - Civil Engineering General | 4000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On Level -8 of SH-W2 a wall was incorrectly built ( highlighted on attached sketch). There is a change to threshold level at this location and the structural opening of the door was built to the lower level and not the higher level. On identifying the error, our blockwork subcontractor proceeded to take down the wall prior to the NCR being raised and a remedial method being agreed.
| 02SL - Stations (LUL) | Cxxx-NCR-002213 | NCR | WTH - Level -1 Damage to Cast-In U-Bars |  | Contr | 201068 | FAR - Farringdon Station (West) |  | 2016-08-10 | 2016-07-14 12:14 | -27 | 2016-04-12 10:50 | Civil - Civil Engineering General | 4000 |  | Damaged | Repair | 3 (3-6k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | U-bars were cast into the level -1 slab to allow for upstands to be cast at a later date. During steel erection works, __ have damaged a section of these by tracking their MEWP over them. See attached photo and location sketch.
| 02SL - Stations (LUL) | Cxxx-NCR-002214 | NCR | MEP - Acceptance and installation of wrong support channel |  | Contr | __ | FAR - Farringdon Station (West) |  | 2016-04-26 | 2016-04-26 07:51 | 0 | 2016-04-12 13:40 | Electrical - Switchgear | 9000 |  | Incorrect Installation | Reject | 2 (6-60k) | Complete | Management Problem - Inadequate supervision | Completed |  | The primary unistrut brackets installed in ETH Level - 7 do not comply to MCR. The unistrut which was installed was supplied by __ Company and are sourced from __ International. These __s did not have the __ brand stamped on it and is an Own Brand made specifically by __ International for Cleveland. Since identification, works have now stopped and the installed unistrut will be removed and replaced with __ Branded unistrut, as per the MCR.
| 02SL - Stations (LUL) | Cxxx-NCR-002215 | NCR | MEP - Level -7 - Use of wrong fixings type to blockwork walls |  | Contr | __ | FAR - Farringdon Station (West) |  | 2016-04-26 | 2016-04-25 09:38 | -1 | 2016-04-12 13:52 | Electrical - General | 2200 |  | Incorrect Installation | Reject | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | CMS channell support have been installed to blockwork wall using approved concrete fixing (HUS3-H). On further investigating blockwork it was found to be cavity blocks wall and the fixing used are only suitable for solid blockwork. Works have been stopped until suitable fixing is found and MCR approved.
| 02SL - Stations (LUL) | Cxxx-NCR-002216 | NCR | WTH – SHW1 Level -3 slab Exceeding Placement Time of Concrete |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-04-27 | 2016-04-13 15:54 | -14 | 2016-04-13 08:15 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | During this pour on 07/4/16 the 3 hour placement time as part of the MCR (Cxxx--C-LRC-M123-50399) and FCD (Cxxx-FCD-001960) for mix W5 W7 was exceeded on 1 no. load. The flow test result after 3 hours was within the correct range therefore met the workability requirement and was poured. Clause KF10.3202c from the Civil and Structural Specification (Cxxx-SWN-C-RSP-M123-00004) states that concrete is to be placed and compacted within 2 hours of the addition of water. This was relaxed to 3 hours as per Cxxx-FCD-001960. See structural concrete control sheet with out-of-time load highlighted.
| 02SL - Stations (LUL) | Cxxx-NCR-002217 | NCR | SCL - Crack in PL4 Flare Secondary Lining |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-05-28 | 2016-05-20 12:01 | -8 | 2016-04-12 12:18 | Tunnelling - Linings - In-situ Concrete | 2500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | On the site walkaround, 21/03/16, it was noted that a crack had formed in PTW opposite CP6 at the flare between RTE2 and PL4. Chainage within PTW is 292 to 304. The crack is longitdinal (radial) situated at 1 o clock when looking from PTW towards RTE2 and is at the location where the junction steel finishes, as shown in drawing Cxxx-MMD-C4-DDD-M123_5-00628, bar mark 21 is section A-A. Crack width is 0.4mm. have measured the crack and it is currently 0.38mm in width.
| 02SL - Stations (LUL) | Cxxx-NCR-002218 | NCR | WTH-Level-1 Perimeter Wall 39 - Damage to __r strip south of GL-4 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-04-26 | 2016-04-22 11:15 | -4 | 2016-04-12 14:38 | Civil - Civil Engineering General | 780 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The __r strip waterbar coming up the vertical CJ in wall 39 has been damaged - severed with only 50mm sticking outside of the concrete. Lcation: wall 39 3.0m south of GL4. Please refer to marked up GA drawing and photo attached.
| 02SL - Stations (LUL) | Cxxx-NCR-002219 | NCR | ETH - Trapezoidal Shaft - Downstand pipe cast in L-5 slab out of position |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-06-17 | 2016-06-16 12:43 | -1 | 2016-04-15 13:27 | Civil - Drainage | 2600 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | As part of the construction of L-5 slab, one of the downstand pipes was cast in the location shown on drawing Cxxx--P-DDA-M123_6-25208 C01. Due to steel congestion when building the slab, the center of the pipe was cast 170 mm off the wall instead of 100mm. (see photos attached and sketch SK-JS-01 attached for location and details). This have an impact on the block located in front of top of pipe. Please note that by using 45deg bend the pipe will be set back to original location.
| 02SL - Stations (LUL) | Cxxx-NCR-002220 | NCR | ETH - Trapezoidal Shaft - L-6 blockwork changes to HV Switch Room II East wall |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-04-27 | 2016-04-26 08:10 | -1 | 2016-04-13 17:19 | Architectural - Masonary | 4200 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | In drawings Cxxx--A-DDA-M123_7-26218 C03 and Cxxx--A-DDC-M123_7-26269 C02, wall elevation 5 shows that part of the wall is made of durasteel. However, __ drawing Cxxx--X-DWG-M123_7-54002 C02 shows the wall as a block wall which was missed during the checking process by our designers. Due to this fact, the wall has been built by __ as a blockwork wall.
| 02SL - Stations (LUL) | Cxxx-NCR-002221 | NCR | WTH - SHW2 Central void defects |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-11-11 | 2016-11-11 15:43 | 0 | 2016-09-27 10:43 | Civil - Civil Engineering General | 2000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following post-pour inspections for all different levels into SHW2, snags and defects were identified within the central void and due to the difficult access they couldn't be repaired until access is in place. (See layout list attached)
| 02SL - Stations (LUL) | Cxxx-NCR-002222 | NCR | ETH - Trapezoidal Shaft - Incomplete Pour Level -1 Beams |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-05-02 | 2016-04-19 12:43 | -13 | 2016-04-18 06:37 | Civil - Civil Engineering General | 2000 |  | Incomplete Works | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Insufficient quantity of material to do the job | Completed |  | Pour for Eastern Ticket Hall Level -1 Beams was conducted on 14/04/16 unfortunately the amount of concrete delivered was not sufficient to complete the pour.
| 02SL - Stations (LUL) | Cxxx-NCR-002223 | NCR | WTH - L-1 W37 Step in Concrete Face |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-04-29 | 2016-04-19 09:51 | -10 | 2016-04-15 13:18 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The concrete face of Wall 37 has been cast with a step of 8mm in the face. Please see attached location plan and photos showing the extent of the step.
| 02SL - Stations (LUL) | Cxxx-NCR-002224 | NCR | WTH - L-1 W37 Hydrophilic Strip |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-04-29 | 2016-04-29 11:07 | 0 | 2016-04-15 13:25 | Civil - Civil Engineering General | 750 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | __ hydrophilic strip was installed between the east and west pours for Wall 37. The strip that was left protruding from the top of the pour for continuation when pouring the Level 0 slab was left unprotected. The strip was now come in contact with water and will need to be replaced. Please see attached for condition of __ strip.
| 02SL - Stations (LUL) | Cxxx-NCR-002225 | NCR | WTH - L-1 W38 Pour 2 & W39 North Concrete Finish |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-04-29 | 2016-04-28 10:38 | -1 | 2016-04-15 15:02 | Civil - Civil Engineering General | 950 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The faces of W37 North Pour and W38 Pour 2 have surface finishes that have areas which have spalling & lack colour conformity. This is requires a repair in line with Concrete Repairs document Cxxx--C-GMS-M123-50318 as Repair Type G & E respectively. See attached photos showing conditions and GA location plan.
| 02SL - Stations (LUL) | Cxxx-NCR-002226 | NCR | ETH - HD Bolts GL C/1 damaged |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-05-17 | 2016-05-12 08:58 | -5 | 2016-04-26 07:43 | Civil - Civil Engineering General | 3100 |  | Supervision/Management | Repair | 3 (3-6k) | Complete | Supervision - Insufficient supervision | Completed |  | Further to Cxxx-FCD-001986, 2no. of the holding down bolts within the column at Level 0 , C/1 needed to be cut due to amendments to the base plate based on as built surveys of the bolt clusters at the ETH. See final BSL Baseplate drawing agreed through the FCD : Cxxx--X-DWG-M123-50071 C02 attached. The incorrect two bolts were cut. Therefore two of the bolts required now no longer protrude a sufficient length from the Level 0 Slab to allow the column to be fixed in position. The bolts that were cut are highlighted green and labelled Bolt A (west) and Bolt B (east)
| 02SL - Stations (LUL) | Cxxx-NCR-002227 | NCR | ETH W24 Grout thickness at Pocket Connection and Bolt Protrusion ETH-2210, 2211 and 2213 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-05-12 | 2016-05-09 11:42 | -3 | 2016-04-21 12:36 | Civil - Civil Engineering General | 3800 |  | Incorrect Installation | Use As-Is | 3 (3-6k) | Complete | Personnel Error - Inattention to detail | Completed |  | At W24 and W15 for the pocketed connection at the ETH - the level of concrete pour requires the grout thickness to be increased. Additionally bolt protrusions on some of the connections do not extend far enough to permit installation of washer detail as shown on Cxxx--S-DWG-M123-52033, 52034 and 52035.
| 02SL - Stations (LUL) | Cxxx-NCR-002228 | NCR | STW - Granite information not specified within K-Screed MCR |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-05-09 | 2016-05-09 12:07 | 0 | 2016-04-25 16:57 | Architectural - Flooring | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | It was identified during a internal screed surveillance that the K-Screed MCR "Cxxx--C-LRC-M123-50662" did not include information regarding the granite that is required in the screed mix. All information was available but missed during the submission process.
| 02SL - Stations (LUL) | Cxxx-NCR-002229 | NCR | EB Platform blockwork incorrect head cleat fixing embedement. |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-05-16 | 2016-05-05 16:03 | -11 | 2016-05-02 14:34 | Architectural - Brickworks/Blockworks | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | Following to quality surveillance, it was identified that a head cleat fixing have been fixed with 70mm embedment rather than 75mm as specified in blockwork ITP Cxxx--C-ITP-M123-50277.
| 02SL - Stations (LUL) | Cxxx-NCR-002230 | NCR | WTH - SS - Column F,11 misaligned baseplate |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-11-04 | 2016-11-03 14:41 | -1 | 2016-04-21 08:40 | Civil - Civil Engineering General | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Previous Construction - Interfacing issues | Completed |  | The baseplate of column F,11 is out of position by 25mm. This is outside the 10mm tolerance allowed for in NSSS 5th edition Clause 9.6.1. A full as-built survey of the final column position is attached. note that the tolerance provided by the wax cones around the HD bolts have allowed the bolts to remain central to the oversized holes in the column baseplate (to meet the requirements of the blast design). Please see attached photographs which demonstrate this.
| 02SL - Stations (LUL) | Cxxx-NCR-002231 | NCR | PLT- Samples not taken during pou bay 22 walls mass infill 21 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-05-20 | 2016-04-30 10:25 | -20 | 2016-04-26 13:19 | Civil - Civil Engineering General | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | didnt take cores during the pour of bay 22 and mass infill 21,
| 02SL - Stations (LUL) | Cxxx-NCR-002232 | NCR | SCL - Cracks in STW1 Secondary Lining |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-05-27 | 2016-05-27 10:29 | 0 | 2016-04-21 13:47 | Tunnelling - Linings - In-situ Concrete | 2500 |  | Design | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Not Defined | Completed |  | In STW1, a crack has appeared at the joint between the STW1 tunnel and the circular shaft. This is at the location of a proposed contraction joint which was due to be cut. Water is now flowing from the crack in excess of the allowable permitted leaks from the lining, 0.24litres/day/m2.
| 02SL - Stations (LUL) | Cxxx-NCR-002233 | NCR | WTH – W40/41 L-1 to L0 – Upper North Pour Spalling |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-08-08 | 2016-07-27 08:52 | -12 | 2016-04-22 07:35 | Civil - Civil Engineering General | 2786.96 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Post striking of the W40/41 L-1 to L0 formwork - some areas of spalling where uncovered. These can be seen in the attached photos.
| 02SL - Stations (LUL) | Cxxx-NCR-002234 | NCR | WTH - L-1 MSN7 Concrete Finish |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-08-08 | 2016-07-27 08:14 | -12 | 2016-04-22 07:46 | Civil - Civil Engineering General | 2686.06 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Post striking of the MSN7 formwork - some areas of small voids where uncovered. These can be seen in the attached photos.
| 02SL - Stations (LUL) | Cxxx-NCR-002235 | NCR | WTH-Level 0 - Upstands cast in pours 1 and 2, too much cover to the top. |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-05-28 | 2016-05-16 10:35 | -12 | 2016-04-28 16:17 | Civil - Civil Engineering General | 3250 |  | Design | Use As-Is | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Upstands to Level 0 metal deck slab in area for pour 2 have been installed as per approved RC detail drawing Cxxx-ATK-S-DWG-M123_1-50128_C01. However, the upstand links have been detailed too short to be sitting directly on the bottom mat. Therefore when fixed links had 60 mm cover to the top as oppose to 40mm as per drawing. 50mm cover would have been acceptable as it would have complied with the allowable cover tolerances.
| 02SL - Stations (LUL) | Cxxx-NCR-002236 | NCR | SCL - shutter release oil not cleaned off near face rebar STE1 bay 2 |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2016-05-25 | 2016-05-18 10:29 | -7 | 2016-04-25 16:04 | Tunnelling - Linings - In-situ Concrete | 2500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The shutter was moved into place before the shutter release oil was applied to it. The stop end had been partially built by the time this was realised and the decision was made to spray the oil from where they could, resulting in the oil covering the near face rebar. The exact extent of this unknown. This was raised by a Cxxx inspector to the shift manager, but the decision was made to not clean the oil off before the pour, due to time constraints. This means that the rebar will not be bonded with the concrete and will not work according to the design.
| 02SL - Stations (LUL) | Cxxx-NCR-002237 | NCR | WTH – SHW2 Precast Stairs Misaligned soffits |  | Contr | 201068 | FAR - Farringdon Station (West) |  | 2016-05-23 | 2016-05-13 09:35 | -10 | 2016-04-25 15:09 | Structural Engineering - Pre-cast | 2500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Previous Construction - Interfacing issues | Completed |  | The ESS1/INS1 precast stairs installed within SH-W2 are designed to have the steps align with the top of the landings and the soffit of the stairs align with the soffits of the landings. However, the majority of stairs do not have their soffits aligned with the landing soffits, most being within 10mm. The worst case is a step of 25mm. See referenced doc Cxxx--C-XSK-M123-50271 demonstrating these steps.
| 02SL - Stations (LUL) | Cxxx-NCR-002238 | NCR | PLT -Updated Wembley innovation drawing revision not on eB. |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-07-15 | 2016-07-14 13:59 | -1 | 2016-05-26 13:51 | Architectural - Brickworks/Blockworks | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | Further to the surveillance (Cxxx--O4-RGN-M123-51385) carried out on the Blockwork at Platforms – Zone 5, the drawing – Cxxx--X-DWG-M123_7-54010 C04 was marked up by __ and referenced to the __’s Quality Control Checklist. __ used the latest drawing (Revision C04) on BC, but this revision was not on eB at the time. Revision C04 and C05 are also not on eB; this is due to a miscommunication between the design and document control teams with regards to the drawings submitted to CRL.
| 02SL - Stations (LUL) | Cxxx-NCR-002239 | NCR | ETH - Screed impact tested not done in time as per BS8204-1 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-06-10 | 2016-06-03 12:49 | -7 | 2016-04-26 16:44 | Architectural - Flooring | 500 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | According to the ITP Cxxx--X-ITP-M123-50009 the impact test will be done as per BS8204-1 Cl:8.6 which specify: “The screed should pass the ISCR test 14 days after it has been laid. In cold weather, low curing temperatures can require this period to be extended. Conformity can be proved at an earlier age provided that the requirements of Table 4 can be met.” This test has not been done.
| 02SL - Stations (LUL) | Cxxx-NCR-002240 | NCR | SCL - Cracks in Secondary Lining Crown of STW2 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-07-11 | 2016-07-02 10:26 | -9 | 2016-05-20 13:08 | Tunnelling - Linings - In-situ Concrete | 2500 |  | Material | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | There is a longitudinal crack in STW2 Secondary Lining Crown, between chainage 2.486 and -0.511. The crack is approximately 3m in length and has a width greater than 0.3mm.
| 02SL - Stations (LUL) | Cxxx-NCR-002241 | NCR | SCL - CH2 Bay 1 Surface Defects |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-09-30 | 2016-09-27 12:33 | -3 | 2016-05-04 09:15 | Tunnelling - Linings - In-situ Concrete | 2500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Upon striking CH2 Crown Bay 1, Chainage 32.221 to 26.059, shallow honeycombing (~10mm) was identified below axis. The finish is below that of an F2 requirement. Additionally, hydraulic oil from the CH2 shutter spilled onto the same area of the lining as the aforementioned honeycombing, see attached picture. Lastly, an attempt was made by the concrete repair gang to repair the stop end within 24 hours of shutter being struck. This repair fell out of the lining due to insufficient bonding agent being used on the lining.
| 02SL - Stations (LUL) | Cxxx-NCR-002242 | NCR | SCL - Surface Defects on PL2 Flat Soffit Area |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-05-27 | 2016-05-26 16:27 | -1 | 2016-05-04 11:19 | Tunnelling - Linings - In-situ Concrete | 2500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | Upon striking PL2 Crown (Flat Soffit) Chainage 0, it is apparant that the soffit is not an F2 finish, there was honeycombing on the surface. have performed an independent hammer test in the area and can confirm that that the issue with the finish is only superficial in nature, a maximum of 5mm in depth. therefore propose to remove the defective concrete and smooth out the surface defects in this area.
| 02SL - Stations (LUL) | Cxxx-NCR-002243 | NCR | SCL - Contact Grouting Vent Pipe Missed in STE1/ETH Connection |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-06-29 | 2016-06-16 11:05 | -13 | 2016-05-04 09:49 | Tunnelling - Linings - In-situ Concrete | 2500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | The secondary lining crown pour in STE1/ETH connection had a single contact grouting pipe installed. have not installed a grout vent point in the bay.
| 02SL - Stations (LUL) | Cxxx-NCR-002244 | NCR | WTH - SS - Incorrect load information used in connection between column C2010 and beam B2087 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-06-24 | 2016-05-18 11:07 | -37 | 2016-05-03 07:07 | Civil - Civil Engineering General | 4000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Comments from CRL on the first issue of the detail design package for WTH Area 4 (now Area 2) identified two connections where the axial load used in the design was incorrect – This related to the end reaction used for a B8 beam in details WS281 and WS283. These details are highlighted on the attached marked-up __ GA drawing Cxxx--X-DWG-M123-50042 C01. The Area 2 design package Cxxx--Y-XCL-M123-50011 is referenced below. Both connection details were produced by SCC (__ Subcontractor Designers). The current loading drawing Cxxx-SWN-S-DDD-M123_Z-80036 rev C02 was issued to SCC prior to their connections being produced. This is evident as they used the correct axial load for the same two B8 beams in detail WS282. The Cxxx comments were only received by __ after the column C2010 had been fabricated. This comment is comment 9. within Cxxx--Y-XCS-M123-50047 rev. 2.0, referenced below. Note the __/ response to comment 9. References a revision 3.0 of the __ calculation package. This was only reviewed internally by and not issued to Crossrail as a revision 4.0 was produced soon after.
| 02SL - Stations (LUL) | Cxxx-NCR-002245 | NCR | WTH – Perimeter walls – L0/22 stub column HD bolts cast at the wrong level |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-05-26 | 2016-05-16 10:52 | -10 | 2016-04-28 09:54 | Civil - Civil Engineering General | 2900 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The HD bolts cast in perimeter wall 37 for column stub L0/22 (see attached KPS drawing) were cast 30mm too low, this prevents the nut being installed on to the top of the bolt.
| 02SL - Stations (LUL) | Cxxx-NCR-002247 | NCR | WTH - Level 0 - Metal deck slabs - Fresh to previously poured concrete placement time exceeded |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-05-13 | 2016-05-06 14:12 | -7 | 2016-04-29 10:43 | Civil - Civil Engineering General | 700 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During concrete pour Level 0 metal deck slab, the fresh concrete was placed 120mins later on the previously placed concrete. This happened due to two concrete lorries being turned away for being non Crossrail compliant.
| 02SL - Stations (LUL) | Cxxx-NCR-002248 | NCR | WTH - Level 0 - Meteal deck slabs pour 4 - Concrete batch to placement time exceeded |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-05-20 | 2016-05-16 10:39 | -4 | 2016-05-06 16:52 | Civil - Civil Engineering General | 1850 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Error by manufacturer in shipping or marking | Completed |  | During concrete pour to Level 0 Metal Deck slab on the 26th April, the batch to pour time for the 3rd has been exceeded. The load was batched 0919 and finished pouring 1340, it took over 4h to discharge it. This was due to batch time between consecutive lorries being less than requested, also due to restrictions during placement - site had to use 1m3 instead of 2m3 skip.
| 02SL - Stations (LUL) | Cxxx-NCR-002249 | NCR | SCL - CH2 Bay 2 Secondary Lining Late Application of Curing Agent |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-10-28 | 2016-10-20 15:19 | -8 | 2016-05-04 10:38 | Tunnelling - Linings - In-situ Concrete | 2500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | The application of curing agent for CH2 bay 2 (CH 32.221 - CH 26.059) was delayed due to a lack of space for manoeuvring in CH2 Tunnel. The delay was 12 hours. Curing membrane was eventually applied through the windows of the shutter. The shutter was cracked after pendulum hammer testing to check for honeycombing. The pendulum hammer was used on the insitu concrete during early ages and showed that early age strength was not affected by the missed curing.
| 02SL - Stations (LUL) | Cxxx-NCR-002250 | NCR | WTH - SS - Damage to Wall 38 during steel beam installation |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-07-22 | 2016-07-11 07:35 | -11 | 2016-05-16 16:36 | Civil - Civil Engineering General | 5500 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Structural steel beam FB5002 (fabrication drawing within Area 5 package referenced below - Cxxx--X-DWG-M123-50069) is fixed at its south end to Column F,12 and at its north end to the South elevation of Wall 38. This is shown on the __ Area 5 level 0 GA drawing Cxxx--X-DWG-M123-50055 referenced below. When __ attempted installation of this beam, there was insufficient room to pass the beam between the column and the wall due to the opposing splay angles of the wall and column flanges. __ attempted to force the beam into position using sledge hammers. This had 2 effects: 1. Damage to the paint of the beam 2. Cracking on the South elevation of Wall 38. Please see the attached photographic report showing the damage to the beam and to the wall.
| 02SL - Stations (LUL) | Cxxx-NCR-002251 | NCR | Tun-SCL - Water Ingress at PL2 Connection With WTH Box |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-10-26 | 2018-10-22 16:12 | -4 | 2016-05-06 15:16 | Tunnelling - Linings - In-situ Concrete | 7000 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Design Problem - Other | Completed |  | At the location of the connection between PL2 and SH-W2 there is a small leak at the crown of the tunnel. The leak is situated in the tolerance zone between Cxxx and Cxxx designs. The waterproofing detail for the secondary lining concrete has been installed as per RFI003387, the full extent of secondary lining concrete is sealed as per the works information, and compliant. The leak is outside of the extents of the aforementioned RFI. Full details of the extent of the leak, the investigation and the proposed repair are given in the attached documents Update: 12/06/17: Please see attached photo "PL2 Repair 070617". Following the repair method detailed originally in this NCR in attachment "PL2 Repair Investigation.pdf", further work is to be undertaken. A final repair is to take place on the crown with __ (as per Proposed Answer Update)
| 02SL - Stations (LUL) | Cxxx-NCR-002253 | NCR | WTH – W37 – Perimeter Wall Cracking |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-06-08 | 2016-05-16 10:56 | -23 | 2016-05-11 12:13 | Civil - Civil Engineering General | 850 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Post striking of the formwork for the upper W39/37 pour a 4mm wide crack was present at the top of the adjacent wall. See attached photos showing extent of the cracking.
| 02SL - Stations (LUL) | Cxxx-NCR-002254 | NCR | ETH - L-6 leaks in lining wall 1 and soffit |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-09-30 | 2016-09-23 15:53 | -7 | 2016-05-17 10:09 | Civil - Civil Engineering General | 2500 |  | Material | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Before the construction of the block walls, inspected the concrete walls and soffit in L-6 and found that water ingress has started occurring in three different areas at the construction joints between lifts and also in the soffit. Please see sketch SK-SJ-01 and photos attached for the location of the leaks.
| 02SL - Stations (LUL) | Cxxx-NCR-002255 | NCR | ETH - Trapezoidal Shaft - Level +0 - Area D1 missing hydrophilic strip Wall 23 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-07-29 | 2016-06-21 13:39 | -38 | 2016-05-13 15:45 | Civil - Civil Engineering General | 4200 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Management Problem - Inadequate supervision | Completed |  | Following pre-pour inspection of Level +0 Area D1 a small section of hydrophilic strip was missed on a lower section of wall, please see attached photo. Due to the location and rebar hydrophilic strip wasn't able to be fixed before concrete pour.
| 02SL - Stations (LUL) | Cxxx-NCR-002256 | NCR | ETH - Blockwork PFC __ damaged |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-12-21 | 2018-12-20 13:41 | -1 | 2016-05-13 11:45 | Architectural - Brickworks/Blockworks | 10000 |  | Damaged | Rework | 2 (6-60k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | As part of the construction of masonry panels works, movement joints have to be covered with intumescent mastic. After the completion of these works in different areas in the ETH and tunnels, have found while carrying post construction checks that in some areas the mastic has been damaged, installed incorrectly or debonded.
| 02SL - Stations (LUL) | Cxxx-NCR-002257 | NCR | WTH No use of Hygrometer when determining mositure content in slabs |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-06-24 | 2016-06-20 12:42 | -4 | 2016-06-10 13:59 | Civil - Civil Engineering General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Under Clause JM10.3205 of the Architectural Specification (Cxxx--A-RSP-M123-50057 Rev 11), it is specified that a hygrometer should be used to determine the moisture content in the concrete which did not use.
| 02SL - Stations (LUL) | Cxxx-NCR-002258 | NCR | ETH - Honeycombing and cold joints Wall 34 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-06-30 | 2016-06-29 13:38 | -1 | 2016-05-18 06:29 | Civil - Civil Engineering General | 17500 |  | Incomplete Works | Repair | 2 (6-60k) | Complete | Material/Preservation Problems - Other | Completed |  | Following striking of Wall 34 have become a aware of a number of concrete repair that are required. Please see attached photos Note punchwork Cxxx-PWK-00165 raised to close issue
| 02SL - Stations (LUL) | Cxxx-NCR-002259 | NCR | WTH SH-W1 and level -2 slab tie-in damage/missing __ at construction joint |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-07-01 | 2016-06-10 13:40 | -21 | 2016-05-19 09:27 | Civil - Civil Engineering General | 3150 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | At the level -2 construction joint for the tie in with SH-W1 south side and the C1B slab, historically installed __ from a previous pour has incurred minor damaged or there was insufficient __ to lap onto to comply with the technical data sheet. Available lap varies from 0mm to greater than 75mm. See sketch Cxxx--C-XSK-M123-50286 for location and photos.
| 02SL - Stations (LUL) | Cxxx-NCR-002260 | NCR | ETH-SB - Holding down Bolts in Area 8 not central to bolts holes in the base plates at GL3/A |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-06-09 | 2017-05-30 10:59 | -10 | 2016-06-30 08:15 | Civil - Civil Engineering General | 5000 |  | Design | Repair | 3 (3-6k) | Complete | Previous Construction - Interfacing issues | Completed |  | Holding down bolts in Area 8 at GL3/A are not central to the base plate holes. The columns were positioned and levelled within the tolerances required (See site survey attached Ref: Area 8 BCEL Vs Survey & SKT-3345-060516-01-C02).
| 02SL - Stations (LUL) | Cxxx-NCR-002261 | NCR | ETH-SB - Holding down Bolts in Area 8 out of tolerance on GL2/A |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-08-18 | 2016-08-01 14:13 | -17 | 2016-06-30 08:15 | Civil - Civil Engineering General | 3750 |  | Design | Repair | 3 (3-6k) | Complete | Management Problem - Inadequate supervision | Completed |  | Holding down bolts at GL2/A are out of tolerance whereby the base plate is clashing with the bolts already installed. Therefore the column cannot be positioned and levellled as required. Currently the column needs to be moved 16mm towards GL2 in order to be levelled within the required tolerances.
| 02SL - Stations (LUL) | Cxxx-NCR-002262 | NCR | WTH - SS - Fabrication error for beams B3002 and FB3006 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-06-24 | 2016-06-20 15:23 | -4 | 2016-05-19 15:21 | Civil - Structural Engineering | 4000 |  | Manufacturing Defect | Rework | 3 (3-6k) | Complete | Personnel Error - Inattention to detail | Completed |  | Beams FB3006 and B3002 are shown on the attached marked-up __ level +1 UM Area 3 general arrangement drawing (sketch number: Cxxx--C-XSK-M123-50285 P01). Beam FB3006 has 2 sets of bolt holes drilled through its web to take connecting beams B3067 and B3145. These sets of bolt holes have been drilled in the incorrect plan position by 60mm. Beam B3002 has 1no. set of bolt holes in its top flange to take a connecting column hanger Cxxx5. This set of bolt holes have been drilled in the incorrect plan position by 56mm. The plate for the connection between beam B3002 and FB3006 is also out of plan position by 56mm. Please see the attached photographic report showing these errors onsite.
| 02SL - Stations (LUL) | Cxxx-NCR-002263 | NCR | WTH - Column Encasement - Concrete placement timings exceeded |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-06-07 | 2016-06-02 16:22 | -5 | 2016-05-24 09:38 | Civil - Civil Engineering General | 750 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Error by manufacturer in shipping or marking | Completed |  | The column encasement for columns 1C, 2C & 1+4032D from L0 to L+1 were poured on 05/05/16. During this pour fresh concrete was placed on previous placed concrete with over a 120 minute period between placements. During this pour the batch to placement time also exceeded the 3 hour limit.
| 02SL - Stations (LUL) | Cxxx-NCR-002264 | NCR | SCL - Cast In Situ Crown Concrete Cast Outside Allowable Tolerances |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-07-29 | 2016-07-02 10:30 | -27 | 2016-05-20 09:28 | Tunnelling - Linings - In-situ Concrete | 2500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | have identified some areas in the cast crown which are outside the ITP tolerance of 0,+35mm. These are split into three distinct areas as per attached sketch "Regions for NCR 2264" and the table "Out of Tolerance Areas". The table splits all tunnels into 1m chainages and gives the tightest and biggest spots on each chainage and their location based upon the colours given in the sketch. For locations in which the secondary lining is greater than 35mm big, refer to Cxxx-NCR-002205 which demonstrates that areas up to 60mm big are acceptable due to the manner which the primary lining has been constructed. For those locations where the secondary lining is greater than 60mm big, have provided minimum thickness checks that are provided in the linked ITP records. Tight areas can be split into the following categories as per the sketch: - For tight back of house areas (e.g. CP1, CP7) and under platform areas (yellow on sketch) - See attached __ RFI 00650 which states that are permitted an allowable tolerance of -30mm, +35mm. The only areas tighter than 30mm are underplatform areas, refer to Cxxx-NCR-1876 which states that this is acceptable so long as MEP design is not affected. See attached email confirming from __ stating that these areas are not an issue. For areas with GRFC cladding and PES (pink on sketch) - refer to Cxxx-NCR-001876 and Cxxx-RFI-003287 where previous tight spots have been identified. As per these PTRs, propose use as is is acceptable and will coordinate any issues with their MEP, cladding and PES teams. have identified 6 locations in PTE which require milling back, see attached pdf, GFRC Tight Spots, showing these locations. Trackside areas (green on sketch) - The tightest location trackside is 15mm in STW3, Cxxx-RFI-003287 states that so long as the upstand width is achieved then this is acceptable to Cxxx, can confirm all upstand widths are achieved.
| 02SL - Stations (LUL) | Cxxx-NCR-002265 | NCR | PLT - MEP - Use of standard bends for Fire Mains |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-07-28 | 2016-07-26 08:46 | -2 | 2016-06-01 14:31 | Fire - Fire Systems & General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Insufficient work planning by the subcontractors | Completed |  | According with document "JS61 Wet and Dry Risers/Falling Fire Mains Crossrail M&W Specification" (CRL1-XRL-M-RSP-CR001-50014 Version 1.0), clause JS61.1301 "... l) All bends shall be of long radius type. ...". Nine (9) 4'' standard elbows were originally installed in the W/B & E/B platform inverts on the feeds to the hydrant landing valves. These were subsequently changed to long radius type bends, but by utilising a material that was although manufactured by the same supplier (Anvil), was not part of the accepted product range (CRL-MCR-002864 - Gruvlock). For your information, the 6'' and 8'' long radius bends of the Fire Mains system will have to be custom-made items.
| 02SL - Stations (LUL) | Cxxx-NCR-002266 | NCR | WTH - SHW2 Re-injecto grout tube ports inaccessible (Level -6 to -5) |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-06-08 | 2016-05-31 14:12 | -8 | 2016-05-25 08:47 | Civil - Civil Engineering General | 4500 |  | Incorrect Installation | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 4no re-injecto tube ports (potentially 3no loops) on wall 6, 8 & 9 between levels -6 and -5 cannot be located. (see attached survey)
| 02SL - Stations (LUL) | Cxxx-NCR-002267 | NCR | SCL - Leak in Crown of STW3/WTH Junction |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-10-28 | 2016-10-21 15:10 | -7 | 2016-07-11 14:23 | Tunnelling - Linings - In-situ Concrete | 2000 |  | Material | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | There is currently a leak/damp patch on the lining at the connection between WTH square shaft and STW3 connection. The leak is at 10 o clock when looking from the WTH into STW3. This is at chainage 0. The water appears to be coming from the ticket hall rather than a fault with the waterproofing.
| 02SL - Stations (LUL) | Cxxx-NCR-002268 | NCR | SCL - Non Conformance Against ITP Requirements for Waterproofing Records |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-08-26 | 2016-08-25 13:50 | -1 | 2016-05-25 13:22 | Tunnelling - Linings - In-situ Concrete | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | did not follow ITP - Cxxx--C4-ITP-M123-50055 item 2.17 for which the position of each reinjectable hose was not identified at the time of installation. Subsequently, have gone back to each of the boxes where items were not identified and sketches have been produced in the ITP record handovers. This is rework.
| 02SL - Stations (LUL) | Cxxx-NCR-002269 | NCR | WTH - SHW2 Level -6 to -5 wall Defects |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-06-08 | 2016-05-26 15:47 | -13 | 2016-05-25 17:04 | Civil - Civil Engineering General | 3000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following post-pour inspections of all walls cast between L-6/-7 to L-5, the following defects were identified: 1) Localized poor compaction was identified on wall 25 2) Thin layer of grout produced a misalignment on the face of the wall 3) A 20 x 20mm chamfer was missed from the external corner of wall 25 (see attached survey and site photos
| 02SL - Stations (LUL) | Cxxx-NCR-002270 | NCR | ETH - Damage to Waterproofing Layer over LU Jack Arches |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-03-24 | 2017-03-22 17:38 | -2 | 2016-05-25 14:05 | Civil - Civil Engineering General | 5000 |  | Damaged | Rework | 3 (3-6k) | Complete | Supervision - Insufficient supervision | Completed |  | ETH – While coring to establish the level of the arches in the North Yard Area an operative cored through what may be the waterproofing layer for the LU jack arches. The core extended 65mm into the concrete layer below. The activity briefing stated that once the waterproofing layer was encountered the coring would cease and this did not happen. Discussions are ongoing with regards to the repair and the NCR will be updated to reflect the repair procedure.
| 02SL - Stations (LUL) | Cxxx-NCR-002272 | NCR | WTH SH-W1 level -2 tie-in steel detail |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-06-10 | 2016-06-08 14:53 | -2 | 2016-05-26 14:55 | Civil - Civil Engineering General | 3000 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The detail for the step between the level-2 slab tie-in to SH-W1 at level -3 omitted the presence of the permanent works for the level -3 ringbeam previously cast by Cxxx. This detail was missed by __ when detailing the reinforcement. (See Section G on drawing Cxxx-SWN-S-DDL-M123_2-92105 and Section J on drawing Cxxx-SWN-S-DDL-M123_2-92107). The bottom mat steel detailing on Cxxx-ATK-DWG-M123_3-50131 along the length of the step between level -3 and level -2 requires amending and includes L bars BM246, BM249, BM206 and BM219.
| 02SL - Stations (LUL) | Cxxx-NCR-002273 | NCR | WTH – Platform wall adjacent to door 7-WD36 damaged |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-06-17 | 2016-06-10 13:44 | -7 | 2016-05-26 16:03 | Civil - Civil Engineering General | 2000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Metal bearers are temporarily cast into the blockwork walls to support the lintel blocks during the curing process. These are removed and the infills repaired once full sufficient strength has been achieved. In one location, the Eastern edge of door 7-WD36 (see attached sketch), one of the lintel blocks has been damaged as the bearers were removed. Mortar has been used to ‘plug’ the gap.
| 02SL - Stations (LUL) | Cxxx-NCR-002274 | NCR | ETH - Wrong installation of L-6 winching socket |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-01-27 | 2016-12-19 11:12 | -39 | 2016-05-28 13:43 | Architectural - Brickworks/Blockworks | 1500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the construction of blockwork at L-6, the winching sockets encased within the Wi columns located in the HV transformer room (TR1) as shown on drawing Cxxx--S-DDD-M123_Z-76800 was set out to the wrong finish floor level. This has caused the socket to be 75mm lower than the actual position. are currently looking to find a solution with minimum affect to existing work.
| 02SL - Stations (LUL) | Cxxx-NCR-002275 | NCR | WTH-Wrong Rev drawings used on level -6 block work |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-07-14 | 2016-06-27 15:34 | -17 | 2016-06-14 08:26 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | During a blockwork surveillance carried out for cleaners room level -6 on 20/05/16. It was observed that site team were using incorrect drawing revision on site. Drawings checked at the time were Cxxx--A-DDAM123_7-76222 Rev C02 (latest one in eB is P12 and with CRL) & Cxxx--X-DWG-M123_7-54102 Rev C03 (latest one in eB is rev C04 with CRL)
| 02SL - Stations (LUL) | Cxxx-NCR-002277 | NCR | WTH – SHW1 Pile breakdown levels |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-07-16 | 2016-06-30 13:40 | -16 | 2016-06-01 07:29 | Civil - Civil Engineering General | 3000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the pile breakdown the level limit was exceeded on 7 no. piles. See attached sketch Cxxx--C-XSK-M123-50291.
| 02SL - Stations (LUL) | Cxxx-NCR-002278 | NCR | ETH Screeding - D49 steel mesh not installed in joint at L-7 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-07-08 | 2016-07-04 08:03 | -4 | 2016-06-17 13:43 | Architectural - Flooring | 700 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Supervision - Other | Completed |  | __ screeded the middle area in L-7 on Friday 20/05/16, closing Level -7 for the rest of the weekend to prevent people damaging the screed. checked the area on Monday 23rd and realised that __ had left an area not screeded with no D49 steel mesh in the joint, as the ITP states. As they were screeding another area in L-7 on Monday 23rd, __ painted the joint with M-bond and completed the outstanding screed, but without the approval of or Crossrail. Please see attached the drawing with the location of the joint and two photos of the area affected.
| 02SL - Stations (LUL) | Cxxx-NCR-002279 | NCR | MEP - ETH Level - 5 Ductwork Support System. |  | Contr | __ | FAR - Farringdon Station (West) |  | 2016-06-16 | 2016-06-14 16:08 | -2 | 2016-06-02 08:45 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | Primary unistrut brackets installed in ETH Level – 5 have been sprayed with a cold zinc galvanize paint which does not comply to MCR. Works have stopped and the installed contaminated unistrut will be removed and replaced with unistrut, .sprayed with a MCR compliant paint (__)
| 02SL - Stations (LUL) | Cxxx-NCR-002280 | NCR | PES - Different Check Sheet used for the secondary steelwork parameters |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-06-16 | 2016-06-02 14:33 | -14 | 2016-06-02 10:35 | Mechanical - Platform Edge Doors | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | Subcontractor for the Platform Edge Screen () have subcontracted the manufacture of the secondary steelwork to __. __ have used a different check sheet to the one that is mentioned on the ITP Cxxx--A-ITP-50006 (see attached example of the ITP check sheet and the check sheet used).
| 02SL - Stations (LUL) | Cxxx-NCR-002281 | NCR | PES - Liquid Penetration Test (LPI) Requirement |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-06-16 | 2016-06-02 15:28 | -14 | 2016-06-02 12:00 | Mechanical - Platform Edge Doors | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | According to the ITP: Cxxx--A-ITP-M123-50006, Subcontractor have subcontracted manufacture __ to perform the Platform Edge Screen (PES) Secondary Steelworks welding inclusing tests such as the Liquid Penetration. The Liquid Penetration test was not performed as it was not requested for the PES secondary steel items according to the Spec. Cxxx--A-RSP-M123-50057 [ Rev 10.0 at the time]. Therefore the LPI test certificate cannot be submitted for deliverables on the ITP and an NCR has now been raised instead of changing the ITP.
| 02SL - Stations (LUL) | Cxxx-NCR-002282 | NCR | SCL - Timber Cast into Lower Pour of CH1 Headwall |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-07-29 | 2016-07-06 14:55 | -23 | 2016-06-02 15:37 | Tunnelling - Linings - In-situ Concrete | 1000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | 18mm thick plywood was cast into the first pour of CH1 headwall (mid axis) at Chainage 78. An F2 finish has not been achieved in the pour.
| 02SL - Stations (LUL) | Cxxx-NCR-002283 | NCR | WTH – SHW1 Cavity wall drainage displacement and reduced cover |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-06-21 | 2016-06-10 15:16 | -11 | 2016-06-07 12:23 | Civil - Civil Engineering General | 3000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The cavity wall drain pipe and gully shown on sketch moved 40mm north during the pour. As a result cover to one vertical reinforcement bar will be locally reduced to 15mm. Pre-pour inspection checks were carried out by and __ and the pipe was secured at time of inspection. However, the pipe moved during the pour.
| 02SL - Stations (LUL) | Cxxx-NCR-002284 | NCR | SCL - CH2/ES2 Knuckle Construction Joint Missing Waterbar |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-07-14 | 2016-07-07 11:52 | -7 | 2016-06-02 15:57 | Tunnelling - Linings - In-situ Concrete | 2500 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | On site, it was identified that the construction joint between the 2nd and 3rd lift in CH2/ES2 knuckle, Chainage 40 in CH2, did not match up with the pre installed waterbar location. Rather than produce a makeup piece, it was decided that it was safer and more practical to take the actions within the proposed answer. It was found that the mismatch was due to an error in the Cordek modelling rather than a site setting out error.
| 02SL - Stations (LUL) | Cxxx-NCR-002285 | NCR | WTH SH-W1 wall 22 level -3 east reduced cover |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-07-29 | 2016-07-13 10:39 | -16 | 2016-06-07 12:32 | Civil - Civil Engineering General | 3300 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Cover to the near face vertical starter bars was 70-120mm along the eastern and western sides of wall 22 at level -3. The starters were a continuation of the coupled bars from the Cxxx installed ringbeam. See Sketch Cxxx--C-XSK-M123-50294 for location.
| 02SL - Stations (LUL) | Cxxx-NCR-002286 | NCR | WTH - Level 0 - Missing upstand and wall starters above wall 45,44,43 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-03-31 | 2017-03-29 13:36 | -2 | 2016-06-14 12:21 | Civil - Civil Engineering General | 4500 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | During construction of Level 0 Metal deck slab in area 4 (South East corner of site) upstand starter bars were not installed above wall 45, over the full extent of upstand type D1 (Cxxx-ATK-S-DWG-M123_1-50128 C02, Cxxx-ATK-S-DWG-M123_1-50142_C01), also refer to sketches Cxxx--C-XSK-M123-50299 & Cxxx--C-XSK-M123-50300.
| 02SL - Stations (LUL) | Cxxx-NCR-002287 | NCR | Failure to Observe Unit Dismantling Agreement Process |  | Contr | TWC | FAR - Farringdon Station (West) |  | 2016-06-24 | 2016-06-21 13:10 | -3 | 2016-06-06 15:58 | Mechanical - Escalators | 2000 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | During week ending 03/06/16 __ commenced with the escalator dismantling process for escalators 10 and 11. were informed by escalator inspectors on 01/06/16 that escalator 10 had left the factory floor. This is not the correct procedure and escalators must be dismantled in accordance with the __ Unit Dismantling Agreement Process, this stipulates various activities that must take place before dismantling and shipping can take place, these activities did not take place.
| 02SL - Stations (LUL) | Cxxx-NCR-002288 | NCR | MEP - ETH Level -7 Ladder Installation |  | Contr | __ | FAR - Farringdon Station (West) |  | 2016-06-22 | 2016-06-18 20:16 | -4 | 2016-06-08 11:05 | Electrical - General | 2000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Insufficient surveillance of subcontractors | Completed |  | This NCR is issued for 2no Lengths of Cable Ladder installed for HV cables along the Platform Smoke Ventilation corridor at Level -7 ETH. The drawing indicates the HV ladder coming to a stop before and after the door by the gantry however the installation is continuous. The continuous ladder is installed to provide adequate support for the cables lying on the floor and along the wall.
| 02SL - Stations (LUL) | Cxxx-NCR-002289 | NCR | ETH - Damaged screed |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-12-23 | 2016-11-28 09:44 | -25 | 2016-06-17 13:49 | Architectural - Flooring | 1000 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Inadequate/insufficient tooling. | Completed |  | While carrying out a post-screeding inspection, found that the screed was damaged in the HV transformer room II in L-6. The defect is caused by a timber nail, so the size is about 3 mm wide by 3 mm deep (see photo attached).
| 02SL - Stations (LUL) | Cxxx-NCR-002290 | NCR | MEP - Use of unapproved spray paint |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2016-06-23 | 2016-06-21 07:57 | -2 | 2016-06-09 07:15 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | Second instance observed on 2/06/16 where primary unistrut brackets installed in ETH Level – 5 have been sprayed with a cold zinc galvanize paint which does not comply to MCR. Works have stopped and the installed contaminated unistrut will be removed and replaced with unistrut sprayed with a MCR compliant paint (__). Original NCR raised by Subcontractor: Cxxx-NCR-002279.
| 02SL - Stations (LUL) | Cxxx-NCR-002291 | NCR | WTH - Level -1 - OSD lift pit base - Voids in concrete |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-07-30 | 2016-07-08 09:09 | -22 | 2016-06-13 10:37 | Civil - Civil Engineering General | 3750 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | After striking Level 0 OSD lift pit soffit falsework substantial voids were detected in base slab concrete. Voids have formed between underside of the steel beems and soffit. Please refer to site photos attached.
| 02SL - Stations (LUL) | Cxxx-NCR-002292 | NCR | WTH - Chipped blockwork to lintels on SH-W2 Level -8 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-06-24 | 2016-06-24 15:33 | 0 | 2016-06-10 15:01 | Civil - Civil Engineering General | 2000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | A few blockwork lintels constructed on Level -8 of SH-W2 have been damaged. In three instances small chips are visible on the blocks, please see attached sketches.
| 02SL - Stations (LUL) | Cxxx-NCR-002294 | NCR | WTH - Level 0 Metal deck slab - Cast in upstand bars bent down to alow concrete line installation |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-09-08 | 2016-09-07 15:01 | -1 | 2016-06-15 09:40 | Civil - Civil Engineering General | 2900 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On level 0 slab area 4 adjacent to GL 7 & H cast in upstand bars have been bent to alow installatin of concrete pump line. 3 links have been bent.
| 02SL - Stations (LUL) | Cxxx-NCR-002296 | NCR | PLT Hairline cracks on internal face of GFRC Sub-frames |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-10-07 | 2016-09-26 12:41 | -11 | 2016-06-15 13:15 | Architectural - Finishes | 2500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During the standard on-site delivery inspections carried by __ hairline cracks were noted on the back of the GFRC infill strips in isolated areas.
| 02SL - Stations (LUL) | Cxxx-NCR-002297 | NCR | ETH- Trapezoidal Shaft - Wall 24, Level +2, Cast in Plates installed at incorrect location |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-09-12 | 2016-09-12 10:40 | 0 | 2016-06-21 11:55 | Civil - Civil Engineering General | 6750 |  | Supervision/Management | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the construction of the level +1 to +2 installed 2nr cast-in plates at the incorrect position. Please see as built survey for exact positions. The position of these plates mean they are 'unusable' and will have to be broken out and moved.
| 02SL - Stations (LUL) | Cxxx-NCR-002298 | NCR | WTH - Column Encasement - Pour Height |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-08-09 | 2016-08-09 13:00 | 0 | 2016-07-26 09:45 | Civil - Civil Engineering General | 2700 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Column 1C and 1+4033D were poured from Level 0 upto Level +1 Upper Mezzanine. The columns were poured with a discharge height of 5.6m, which is above the maximum permitted.
| 02SL - Stations (LUL) | Cxxx-NCR-002299 | NCR | WTH - Column Encasement - Pour Height |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-06-30 | 2016-06-20 14:05 | -10 | 2016-06-16 06:31 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Column 1C and 1+4033D were poured from Level 0 upto Level +1 Upper Mezzanine. The columns were poured with a discharge height of 5.6m, which is above the maximum permitted.
| 02SL - Stations (LUL) | Cxxx-NCR-002300 | NCR | TUN - BUI - Missed Glasroc and Fire Door Details on PES Hoarding |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-12-16 | 2016-11-11 10:17 | -35 | 2016-06-16 10:28 | Tunnelling - Walkways | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Supervision - Other | Completed |  | On the hoarding between Cxxx and Cxxx works, the vertical joints on Glasroc board (Platform side) were missed out prior to handover to Cxxx. Additionally, details for the doors were not provided at the time of handover due to a lack of clarity by the Fire Engineers as to their requirements.
| 02SL - Stations (LUL) | Cxxx-NCR-002301 | NCR | ETH - ESS5 Midlanding at 117.10 - starter bars installed without concrete cover |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-07-14 | 2016-06-28 08:13 | -16 | 2016-06-20 17:36 | Civil - Civil Engineering General | 2600 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | At the ESS5 Midlanding at Level 117.10 5No out of 8No couplers for starter bars (BM117, T1 layer, south side of midlanding / W32) were installed at the wrong height, resulting in no concrete cover. The bottom layer of the midlanding on the south side / wall W32 has been installed as per design.
| 02SL - Stations (LUL) | Cxxx-NCR-002302 | NCR | SCL - Damage to Sprayed Waterproofing - VA1-WTH Connection |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-07-30 | 2016-07-12 09:16 | -18 | 2016-06-27 15:09 | Tunnelling - Linings - Sprayed Concrete | 3000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | have identified that the sprayed waterproofing in VA1 is damaged close to the finished sprayed secondary lining. The damage is within 200mm of the joint and therefore cannot be repaired using additional TamSeal with 200mm overlap. To mitigate the issue, have raised RFI 3752 which proposes an extension of the sheet membrane termination onto the front of the SCL concrete. See attached sketch which shows which membrane is damaged and the proposed detail which will reduce and manage leaks. A reinjectable hose will provide a method of leak sealing in the future.
| 02SL - Stations (LUL) | Cxxx-NCR-002303 | NCR | SCL - Rework Capture in VA1 Connection |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-07-11 | 2016-07-02 09:34 | -9 | 2016-06-27 15:23 | Tunnelling - Linings - In-situ Concrete | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | The following incidents of rework are captured in this NCR for VA1 connection invert: - 1) The sheet membrane was initially installed without a double layer of geotextile; the membrane was removed and a second layer applied. 2) Non compliant spacer blocks, for which there is no MCR, were installed before the pouring of concrete. These blocks were removed and replaced with compliant spacers and reinforcement. 3) The grout tube to be situated on the contraction joint between the piles and VA1 was installed in the wrong place. A grout tube was installed in the correct location and the wrong tube will be cut. See attached pictures showing the amended pour indicating compliance.
| 02SL - Stations (LUL) | Cxxx-NCR-002304 | NCR | TUN - SCL - Failed Waterproofing Inspection CH2 Bay 5 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-08-26 | 2016-08-09 12:11 | -17 | 2016-06-29 07:18 | Tunnelling - Linings - In-situ Concrete | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During the inspection of the sheet membrane by Cxxx, a puncture in the membrane was found. Location of this was between chainage 0 and chainage 1.206m in CH2 crown. In addition to this, and Cxxx had found water coming from between the secondary lining and the membrane. An agreement to place hydrophilic strip and reinjectable grout hoses all the way around the construction joint, this was not in place at the time of inspection and therefore rejected. This NCR therefore captures the installation of the additional hydrophilic strip and grout hose at the construction joint at chainage 1.206m.
| 02SL - Stations (LUL) | Cxxx-NCR-002305 | NCR | WTH SHW1 west capping slab excess cover |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-08-04 | 2016-07-06 09:16 | -29 | 2016-07-05 08:18 | Civil - Civil Engineering General | 2500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Previous Construction - Problems based on previous construction errors | Completed |  | have poured the SHW1 west capping slab. Cover to the top mat of steel was greater than 70mm over the south 2390mm deep slab area and over 60 on the 600mm level -1 slab. A393 mesh was placed to obtain correct cover. See attached sketch Cxxx--C-XSK-M123-50307 for teh affected areas.
| 02SL - Stations (LUL) | Cxxx-NCR-002306 | NCR | ETH - Level L+2 Starter Bars for Beam B21 in W30 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-08-12 | 2016-08-03 12:07 | -9 | 2016-07-04 17:39 | Civil - Civil Engineering General | 2400 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Insufficient information made available to the worker. | Completed |  | The reinforcement for concrete encased beam B21 requires starter bars in W30. The starter bars as detailed in Cxxx--RFI-00707 have not been installed since they are not shown on the reinforcement drawing for wall W30 - Cxxx-ATK-S-DWG-M123_Z-50664 and the bottom bars clash with the cast in plate.
| 02SL - Stations (LUL) | Cxxx-NCR-002307 | NCR | WTH - SH-W1 – Historic Damage to Level -5 Ring Beam - North side |  | Contr | 201068 | FAR - Farringdon Station (West) |  | 2016-07-19 | 2016-07-08 15:04 | -11 | 2016-07-05 07:52 | Civil - Civil Engineering General | 4000 |  | Damaged | Repair | 3 (3-6k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Within SH-W1 the 1m deep Level -5 ring beam suffered damage during the approximately 2 years between casting and now. Details of the damage/defects are on the attachment.
| 02SL - Stations (LUL) | Cxxx-NCR-002308 | NCR | ETH - Steelwork Member Alignment at Lvl +1 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-07-19 | 2016-07-07 15:24 | -12 | 2016-07-05 14:00 | Civil - Civil Engineering General | 1600 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | Please refer to drawing Cxxx-SWN-S-DDA-M123_A-30101, and related mark-up sketch “Cxxx--C-XSK-M123-50309”. The 265mm offset from wall W24 along grid Line D for the Level +1 B1a beam fouls on the connection for the stub detail that is located at cast in plate ETH‐3303 (KPS design reference for cast in plate located along south side of Wall 24 and GL D, at level +1), __ have therefore moved the node point 100mm back toward W24 so that it is positioned 165mm along grid line D. This has since been contructed in the 165mm position prior to being made aware of this change in alignment. This detail was amended within the __ 3D model and subsequent fabrication drawings but dimension was not annotated within the GA drawing which and CRL would have reviewed. Design package Cxxx--Y-XCL-M123-50006 revision 3.0 that includes the connection of B1a to B13 has been submitted and accepted by Crossrail on 13/01/2016.
| 02SL - Stations (LUL) | Cxxx-NCR-002310 | NCR | TUN-PLT - Cxxx - STE2 FSC As built out of tolerance |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-08-03 | 2016-08-01 12:05 | -2 | 2016-07-06 11:38 | Civil - Civil Engineering General | 2500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Not Defined | Completed |  | First stage concrete at STE2 location eastbound is out of tolerance (up to -30mm) just in the north side of the FSC , please find attached as built survey
| 02SL - Stations (LUL) | Cxxx-NCR-002311 | NCR | WTH SHW1 wall 22/48 east capping slab waterproofing damage |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-08-06 | 2016-07-13 09:50 | -24 | 2016-07-07 15:50 | Civil - Civil Engineering General | 2500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | External Phenomenon - Weather or ambient condition | Completed |  | installed waterproofing for wall 22/48 prior to the west capping beam kicker being poured. The waterproofing exiting the kicker was damaged due to extreme levels of rainfall over a number of weeks, which caused the installed waterproofing to swell and require replacing. See sketch Cxxx--C-XSK-M123-50315 for the location and attached site photos taken on the day of the pour.
| 02SL - Stations (LUL) | Cxxx-NCR-002312 | NCR | WTH - MEP - FOSC 4 Grilles |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-08-12 | 2016-08-18 11:10 | 6 | 2016-07-07 13:53 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Material | Reject | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | The grilles within the FOSC 4 room on WTH L-6 have been installed without an approved MCR. CEG have requested demonstration of compliance with LU 1-085 requirements for the grille coating. The powder coating on the grilles within the FOSC 4 room would come under a minor use item as defined under section 3.4.1 of the standard.
| 02SL - Stations (LUL) | Cxxx-NCR-002313 | NCR | ETH Blockwork - East cupboard built without having final design |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-12-16 | 2016-11-28 09:52 | -18 | 2016-07-07 14:51 | Architectural - Masonary | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | The east cupboard (FOSC & LV tunnel) in drawing Cxxx--A-DDA-M123_7-01041 was built as per revision C02, whereas revision C03, which is the current revision, shows that because of PMI 521, the cupboard depth is to be reduced and the design is to be confirmed.
| 02SL - Stations (LUL) | Cxxx-NCR-002315 | NCR | ETH - Trapezoidal Shaft - Level -1 Wall 33 alignment |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-07-22 | 2016-07-20 16:54 | -2 | 2016-07-08 09:10 | Civil - Civil Engineering General | 1600 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | ETH - Trapezoidal Shaft - Level -1 Wall 33 alignment Following Cxxx-NCR-002122 (Wall 33/35 shutter movement). A lower section of Wall 33 has been broken back and will be repaired as indicated in NCR-2122. High section of Wall 33 is 33mm out of plumb, refer to attached survey. proposed to use as is.
| 02SL - Stations (LUL) | Cxxx-NCR-002316 | NCR | ETH - Trapezoidal Shaft - Level +2 Wall 24 missed cast in plates |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-01-20 | 2017-01-19 12:10 | -1 | 2016-07-08 15:25 | Civil - Civil Engineering General | 6750 |  | Incorrect Installation | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following the casting of Wall 24 Level +1 to +2. have become aware 4 number cast in plates were not cast. Please see attached extract from OSD cast in plate design. Plate number EBO-4051 to 4054. Please refer to attached Cxxx-SWN-S-DDD-M123_B-30252 for location of EBO-4051 to 4054 plates
| 02SL - Stations (LUL) | Cxxx-NCR-002317 | NCR | TUN - SCL - Honeycombing in Crown of CH2 Bay 5 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-09-09 | 2016-09-01 11:46 | -8 | 2016-07-11 14:46 | Tunnelling - Linings - In-situ Concrete | 2500 |  | System Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Upon striking CH2 Crown Bay 5, from chainage 0 to chainage 1.206, honeycombing is apparant on the surface of the crown, between 11 and 1 o clock. There is also some minor honeycombing located next to the CP6a opening below platform level. This honeycombing is greater than the permissible for an F2 finish.
| 02SL - Stations (LUL) | Cxxx-NCR-002318 | NCR | BUI - Installation of Anchors in Cracked Concrete |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-05-18 | 2017-05-17 15:37 | -1 | 2016-07-12 16:40 | Architectural - Finishes | 2500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Design Problem - NCR excessive closure due to design issue | Completed |  | This non-conformance is being raised in line with the installation of HKD anchors within 175mm of cracked concrete. The __ setting operations of the current approved anchors is to have a minimum spacing and edge distance of 175mm, there are a number of anchors that are within this edge distance. HSCI anchors to be installed in cracked locations where the crack does not exceed 0.5mm as per ETAG.
| 02SL - Stations (LUL) | Cxxx-NCR-002319 | NCR | TUN - SCL - Out of Tolerance Profiles in STE1 and STE2 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-09-23 | 2016-09-14 12:32 | -9 | 2016-07-14 15:22 | Tunnelling - Linings - In-situ Concrete | 2500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | In a similar manner to Cxxx-NCR-002264, have cast part of STE1 and STE2 tunnels outside of the allowable tolerances. See attached profiles showing the entire length of the tunnel and : - STE1 - 38mm tight (p4). 83mm big (p1) STE2 - 30mm tight (p13). 52mm big (p11) For big areas, these are in locations where the secondary lining is more than a metre thick and therefore is acceptable. For tight areas, refer to Cxxx-RFI-003827 which states that so long as the minimum upstand width is achieved, an encroachment is acceptable. confirm that the upstand is unaffected by the encroachment into the tunnel envelope.
| 02SL - Stations (LUL) | Cxxx-NCR-002320 | NCR | ETH - L-5 damaged blockwork |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-01-27 | 2016-12-16 17:15 | -42 | 2016-07-15 11:04 | Architectural - Masonary | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | While carrying out a site inspection, found damaged blockwork in SW area in L-5 (doorway 6-ED23, see attached photo and sketch for exact location)
| 02SL - Stations (LUL) | Cxxx-NCR-002321 | NCR | WTH – SH-W2 Level -8 incorrect application of M-bond |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-09-30 | 2016-09-30 10:05 | 0 | 2016-07-15 13:37 | Civil - Civil Engineering General | 3000 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | The stairwell area on the Level -8 base slab in SH-W2 has an F25 floor finish. F25 floor finish requires a layer of __ waterproofing between the concrete protective layer and the screed. Our subcontractor applied M-bond on top of the concrete protective layer as required on an F04 floor type. See attached sketch for affected area and evidence of m-bond being applied.
| 02SL - Stations (LUL) | Cxxx-NCR-002322 | NCR | WTH – SH-W2 Level -4 Wall knocked down prior to NCR being raised |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-08-05 | 2016-08-03 10:11 | -2 | 2016-07-15 13:45 | Civil - Civil Engineering General | 5000 |  | Supervision/Management | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A single wall on Level -4 of the square shaft was identified as having been constructed using the wrong type of blocks. Similarly to Cxxx-NCR-002172, the wall was built using 190mm slot blocks rather than 190mm trough blocks (both types of blocks are covered under Cxxx--C-LRC-M123-50575 Rev 2), see attached for wall identification. The wall was identified as having being built incorrectly but rather than raising the NCR and having the remedial action agreed, our subcontractor proceeded to demolish the wall without raising the necessary PTR.
| 02SL - Stations (LUL) | Cxxx-NCR-002323 | NCR | WTH - MEP - FOSC 4 ductwork |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-08-04 | 2016-08-03 14:33 | -1 | 2016-07-21 09:43 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | The circular duct sleeves within the FOSC 4 room have been installed without an approved MCR.
| 02SL - Stations (LUL) | Cxxx-NCR-002324 | NCR | ETH - FOH column GL C1 - issues with concrete finish |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-03-24 | 2017-03-15 13:04 | -9 | 2016-07-15 16:47 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The FOH column GL C1 in the South Basement basement was poured on Wednesday 13/07/2016 and the formwork was struck on Friday 15/07/2016. There are a number of issues with the concrete finish e.g. sand lines, blow holes and grout loss.
| 02SL - Stations (LUL) | Cxxx-NCR-002325 | NCR | WTH - MEP - Missing verifying documents for the determination of support systems |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-12-16 | 2017-04-04 13:57 | 109 | 2016-08-04 16:19 | Mechanical - Mechanical Engineering General | 5000 |  | Documentation and Records | Rework | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | Surveillance (Cxxx--O4-RGN-M123-51412) identified that there were no verifying documents available for the determination of support systems and for the production of structural calculations, for the WTH – Cable Management System Installation at Level -7 (HV Switch room SR HV1).
| 02SL - Stations (LUL) | Cxxx-NCR-002326 | NCR | ETH - Trapezoidal Shaft - Level -2 - Moorgate Track Slab waterproofing |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2019-06-28 | 2019-06-28 12:32 | 0 | 2016-07-19 16:26 | Civil - Civil Engineering General | 10000 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | Following the construction of Moorgate Track Slab at Level -2 it has become aware that __ 1k waterproofing detail has not be installed as shown in drawing Cxxx--C-XSK-M123-50251. __ 1K has only been installed 400mm from the top of capping beam instead of the whole capping beam face.
| 02SL - Stations (LUL) | Cxxx-NCR-002327 | NCR | TUN - SCL - Sprayed Waterproofing Applied to Uneven Surfaces |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-08-26 | 2016-08-10 08:12 | -16 | 2016-07-21 08:34 | Tunnelling - Linings - Sprayed Concrete | 2500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | In VA2 connection to the ETH, spray applied waterproofing has been applied to the area around the piles. The roughness of the surface is not compliant to specification requirements and hence there are now areas in which the sprayed waterproofing has holes where the coverage has not been even. Additionally, there has been overspray during the secondary lining works which has contaminated the Tamseal which would require cleaning/removal.
| 02SL - Stations (LUL) | Cxxx-NCR-002328 | NCR | WTH - MEP - Level -5 Duct Installation |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-08-04 | 2016-07-29 10:55 | -6 | 2016-07-21 15:30 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | Ductwork installation on WTH -5 commenced prior to the C status drawing from Hargreaves being accepted by Crossrail.
| 02SL - Stations (LUL) | Cxxx-NCR-002330 | NCR | WTH SHW1 east capping slab excess cover |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-08-25 | 2016-07-28 08:29 | -28 | 2016-07-26 10:58 | Civil - Civil Engineering General | 900 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Previous Construction - Interfacing issues | Completed |  | have poured the SHW1 east capping slab. Cover to the top mat of steel was greater than 70mm over the western area on the 600mm level -1 slab and greater than 70mm on the eastern side over the 2390mm slab and on the 600mm level -1 slab. A393 mesh was placed to obtain correct cover. See attached sketch Cxxx--C-XSK-M123-50320 for the affected areas.
| 02SL - Stations (LUL) | Cxxx-NCR-002331 | NCR | WTH SHW1 East capping slab cracks in concrete surface greater than 0.3mm |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-07-21 | 2017-07-18 12:56 | -3 | 2016-08-03 10:19 | Civil - Civil Engineering General | 2500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | The east capping slab was poured on 12 July 2016. Cracks formed on the surface in three locations that are greater than 0.3mm. See attached sketch Cxxx--C-XSK-M123-50323 for locations and corresponding photographs.
| 02SL - Stations (LUL) | Cxxx-NCR-002332 | NCR | WTH SHW1 Wall 22 level -3 step in concrete from shutter misalignment |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-10-28 | 2016-07-27 14:44 | -93 | 2016-07-26 15:03 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | have poured wall 22 at level -3 to level -1. There are a number of steps greater than 4mm between formwork panels. Grout loss also occurred at kicker level.
| 02SL - Stations (LUL) | Cxxx-NCR-002333 | NCR | WTH - Column Encasement - SFD L+1 Construction Joint |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-08-09 | 2016-07-28 08:15 | -12 | 2016-07-26 10:23 | Civil - Civil Engineering General | 1000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The construction joint between the level+1 slab and concrete column encasement around column South-Face D had not be scabbled prior to installation of formwork/ shuttering
| 02SL - Stations (LUL) | Cxxx-NCR-002334 | NCR | WTH - SH-W1 – Historic Damage to Level -5 Ring Beam - South side |  | Contr | 201068 | FAR - Farringdon Station (West) |  | 2016-11-24 | 2016-11-24 13:59 | 0 | 2016-07-27 08:20 | Civil - Civil Engineering General | 3000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Within SH-W1 the 1m deep Level -5 ring beam suffered damage during the approximately 2 years between casting and now. Details of the damage/defects for the south side only are on the attachment (north side covered in Cxxx-NCR-002307).
| 02SL - Stations (LUL) | Cxxx-NCR-002335 | NCR | WTH – SHW1 Cavity wall drainage displacement and reduced cover to upstand steel |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-10-28 | 2016-08-11 12:57 | -78 | 2016-07-27 12:36 | Civil - Civil Engineering General | 750 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | have cast the cavity wall drainage into the SHW1 slab at level -3. Two of the gully tops are out of position and protrude into the upstand footprint. The 2no. cavity wall drain pipes and gully, shown on sketch Cxxx--C-XSK-M123-50321, moved 15mm and 40mm north during the pour. Pre-pour inspection checks were carried out by and __ and the pipe was secured at time of inspection. At the time of inspection they within acceptable tolerances. However, the pipe moved prior to or during the pour. As a result of the displacement, cover to the upstand lacer at the western location is likely to be reduced to 25mm. 30mm cover for the eastern gully is achievable.
| 02SL - Stations (LUL) | Cxxx-NCR-002336 | NCR | WTH - SHW1 level -1 Suspended slab reduced cover to a B1 40mm bar and coupler |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-10-28 | 2016-08-30 09:09 | -59 | 2016-08-02 16:06 | Civil - Civil Engineering General | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | After striking the level -1 suspended slab shutters, which was poured as part of the SHW1 east capping slab, and exposing the couplers it was noted that one 40mm bar and coupler moved during the pour resulting in reduced cover to that bar over a length of 300mm. See attached sketch and photograph.
| 02SL - Stations (LUL) | Cxxx-NCR-002337 | NCR | ETH L-6 - Wi column not built as per design (built full height) |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-09-02 | 2016-08-24 11:11 | -9 | 2016-07-28 11:10 | Architectural - Masonary | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | Drawing Cxxx--X-DWG-M123_7-54002 C03 shows that two wi columns (please find attached a sketch and photo showing the location) are to be built up to lintel height. However, one of the columns was built full height.
| 02SL - Stations (LUL) | Cxxx-NCR-002338 | NCR | ETH - Mastic installed incorrectly |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-04-28 | 2017-03-17 12:33 | -42 | 2016-07-28 11:09 | Architectural - Masonary | 1500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | and Crossrail have carried out a site inspection and have found some areas in the ETH where the mastic has been installed in gaps wider than 30 mm, as specified in MCR Cxxx--C-LRC-M123-50609. Please find attached 2 examples of areas where the mastic has been installed incorrectly.
| 02SL - Stations (LUL) | Cxxx-NCR-002339 | NCR | WTH - Apse Ceiling - Use of Unapproved Concrete Mix |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-09-06 | 2016-09-06 16:30 | 0 | 2016-08-23 17:22 | Civil - Civil Engineering General | 3000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | An unapproved concrete mix has been used by __ to pour pre-cast concrete units for the WTH Upper Apse. This unapproved mix is HE20. All units cast thus far have been using the HE20 mix.
| 02SL - Stations (LUL) | Cxxx-NCR-002340 | NCR | ETH - Level L0 Columns GL D4 / D5 - Kicker poured without chamfer |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-08-25 | 2016-08-22 15:47 | -3 | 2016-07-28 10:43 | Civil - Civil Engineering General | 1000 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | The kicker of BOH columns GL D4 and D5 have been poured without a 20mm chamfer.
| 02SL - Stations (LUL) | Cxxx-NCR-002341 | NCR | WTH- Wall 50 Infill- Visible spacer block Level 0 to +1 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-08-12 | 2016-08-10 15:35 | -2 | 2016-07-28 13:04 | Civil - Structural Engineering | 800 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On a post pour inspection on the wall 50 infill, it was spotted that a concrete spacer bar was visible and an area/section of the pour was incomplete and the concrete had not passed around it during pouring leaving a small void at the base of the pour (see attached photo).
| 02SL - Stations (LUL) | Cxxx-NCR-002342 | NCR | WTH- __ type MII Benchmark not submitted in accordance with ITP |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-10-30 | 2016-10-25 10:29 | -5 | 2016-08-05 13:35 | Architectural - General | 1000 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | The ITP (Cxxx--C-ITP-M123-50299 REV 1.0) for Fire protection coating required __ to prepare a benchmark panel on the first type of spray application to a beam and a column head. During a surveillance (Cxxx--O4-RGN-M123-51415 rev 1.0) it was noted that this had not happened and works were proceeding without an approved benchmark MCR. Please note the bench mark was prepared on site and visually witnessed by CRL but __ failed to officially submit the documentation(MCR).
| 02SL - Stations (LUL) | Cxxx-NCR-002343 | NCR | Fabrication of Stainless Steel Prototype Panels without an approved MCR & ITP |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-02-24 | 2017-01-20 09:42 | -35 | 2016-08-02 13:13 | Architectural - Finishes | 2000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Works started on the fabrication of items for the ETH prototype without an approved ITP or MCR. The activity was delayed as far as possible without impacting on programme. Items that have been fabricated include all items for the ETH prototype provided by __. This includes the internal stainless steel cladding panels, light box, acoustic panel within the coffer ceiling and the associated support frames. The ITPs have now been submitted and the MCRs will be submitted ASAP once issues regarding the fire compliance requirements have been satisfied.
| 02SL - Stations (LUL) | Cxxx-NCR-002344 | NCR | PLT-TUN - Holding down bolts westbound installed out of theoretical position |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-11-18 | 2016-11-03 10:08 | -15 | 2016-08-01 13:05 | Civil - Civil Engineering General | 2500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | as a part of the platform works and PES installation works it is necessary to install a PES base plates, these base plates are installed on top the holding down bolts already installed. In Westbound at location 7292.778 the set of bolts were installed 512 mm out of their theoretical position , their actual as built centre position is : 7292.266 Also attached a plan view of the set of holding down bolts and a marked up drawing showing the set of bolts that were installed in the wrong position
| 02SL - Stations (LUL) | Cxxx-NCR-002345 | NCR | WTH – SH-W2 __ Leak on Wall 6 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-11-11 | 2016-11-07 13:53 | -4 | 2016-08-01 16:48 | Civil - Civil Engineering General | 2000 |  | System Defect | Rework | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | Three leaks have appeared on Wall 6 between Walls 10 and 11 (see attached photo for area and extent of leaks). The leaks have penetrated the __ Concentrate (Cxxx--C-LRC-M123-50469 Rev 2) applied on this wall.
| 02SL - Stations (LUL) | Cxxx-NCR-002346 | NCR | ETH - Trapezoidal Shaft - Level +0 - Waterproofing against Hayes Street Bridge And Capping Beam Wall 21 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-11-23 | 2018-11-23 17:24 | 0 | 2016-08-02 08:11 | Civil - Civil Engineering General | 6000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 1. Following the construction of Slab +0 Area C Cxxx have become aware that __proof A12 waterproofing detail has not be installed as shown in drawing Cxxx--C-XSK-M123-50249 detail 3. __proof A12 was not installed against Hayes Street Bridge. 2. Between GL 5.5 to 3.5 Along Wall 21 (East wall) Level -2. Cement Slurry has not been installed along capping beam as shown in Cxxx--C-XSK-M123-50250 detail 5. Refer also to attached site photos taken on 03/05/17
| 02SL - Stations (LUL) | Cxxx-NCR-002347 | NCR | ETH - Trapezoidal Shaft- Level 0 to+1 walls W8, W9, W10 & W36 Chamfers not installed at exposed concrete corners |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-08-17 | 2016-08-17 15:58 | 0 | 2016-08-03 07:04 | Civil - Civil Engineering General | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Following a post pour inspection of walls W8, W9, W10 & W36 a number of non conformances have been observed. 1) No chamfers (angle fillet) have been cast at the north end of wall W36 full height. 2) Dywibar has been cast into the East side of wall W36. 3) No chamfers (angle fillet) have been cast around walls W8, W9 & W10 full height 4) Box out within wall W9 (West face) was not properly cleaned prior to concreting. A re-bar tag has been cast into the wall. All non conformances listed above can be seen in the attached photos
| 02SL - Stations (LUL) | Cxxx-NCR-002348 | NCR | ETH - Trapezoidal Shaft - Level -1 to 0 Wall 33 - Concrete cube results |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-08-17 | 2016-08-04 11:31 | -13 | 2016-08-02 10:33 | Civil - Civil Engineering General | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | While compiling records for Sub-package 37 - ETH Trapezoidal Shaft Lining Walls Level -1 to 0, became aware a full set of concrete cubes were not taken for Wall 33 first pour. Please refer to Cxxx-NCR-002122 for information of issues. Concrete pour was stopped suddenly and a full set of cubes were not taken.
| 02SL - Stations (LUL) | Cxxx-NCR-002349 | NCR | Fabrication of Escalators without Approved ITP |  | Contr | TWC | FAR - Farringdon Station (West) |  | 2016-10-02 | 2016-09-16 10:32 | -16 | 2016-08-02 11:40 | Mechanical - Escalators | 2000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | __ started on the manufacture and assembly of escalators without an approved ITP in place. Due to the number of escalators that __ are required to produce across all of the Crossrail Central Stations (58 in total) they took the decision to commence with manufacture at their risk to avoid a backlog of work and a delay to their Whole Life Programme.
| 02SL - Stations (LUL) | Cxxx-NCR-002350 | NCR | WTH-SS-FB2012 Insufficently Coated/Corroding |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-09-02 | 2016-08-26 09:24 | -7 | 2016-08-03 11:38 | Civil - Civil Engineering General | 3000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | Structural steel beam FB2012 (fabrication drawing within Area 2 package referenced below - Cxxx--X-DWG-M123-50064 (C01) is located at the level +1 Lower Mezzanine. This is shown on the __ Area 2 level +2 GA drawing Cxxx--X-DWG-M123-50042 (C01). The bottom flange of this beam was found to have been insufficiently coated, after it had already been installed in its final position. Please see the attached photographic report showing the underside of the beam. (Photographic report) 1. When __ were fabricating and painting the above mentioned beam, the paint application was missed on the bottom flange. Jack Tighe preformed the fabrication checks for the phased load, and produced a certificate of conformity(please see attached). Although a DFT test was undertaken for the beam in question, it is apparent that the areas where it was taken, missed out on the areas missed by the painting. (see attached email from Martin Edwards, __ Compliance Manager). See also attached a copy of the ‘BCEL 108 Steel Surface Treatment Check Sheet’. A further DFT test was undertaken on site of various beams, although FB2012 was not included as there was no access available. 2. __ raised an internal NCR. (See attachment ‘3344 Farringdon NCR 54’) , however they prepared the beam for remedial works and carried out the works prior to a NCR being raised.
| 02SL - Stations (LUL) | Cxxx-NCR-002351 | NCR | TUN - SCL - Honeycombing on CH2 Bay 8 |  | Contr | SWN | FAR - Farringdon Station (West) |  | 2016-09-02 | 2016-09-01 11:36 | -1 | 2016-08-03 14:45 | Tunnelling - Linings - In-situ Concrete | 2500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Upon striking CH2 Crown Bay 8, Chainage 14.5 to 16.2, it was apparent that there was honeycombing at the joint between the invert and crown. The extent of the honeycombing was from chainage 14.5 to 16.2.
| 02SL - Stations (LUL) | Cxxx-NCR-002352 | NCR | WTH L0 Fire Coating of Temporary Cables |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-09-02 | 2016-09-06 11:35 | 4 | 2016-08-05 13:58 | Architectural - General | 1000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Temporary lighting cables were installed around steel beam and fire protection coating was sprayed over them. Cables were affecting the overall envelope of the fire protection coating as a result.
| 02SL - Stations (LUL) | Cxxx-NCR-002353 | NCR | WTH Damage to __ |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-09-02 | 2016-09-07 16:03 | 5 | 2016-08-05 16:33 | Architectural - General | 1000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | __ was sprayed to BEAM_B19 (minimum thickness 28mm). After activity was completed, fire protection coating was damaged with a scaffold tube producing irregularities on the overall envelope (Photos attached)
| 02SL - Stations (LUL) | Cxxx-NCR-002354 | NCR | WTH Level -1 MCC Room blockwork walls |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-09-05 | 2016-09-05 14:00 | 0 | 2016-08-08 16:37 | Architectural - General | 3500 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | There are 2 beams (Beam_B30 & B_14) which have not been sprayed because they were marked as fire boarded beams instead. Blockwork walls were built full height after not leaving enough space to spray the beam.
| 02SL - Stations (LUL) | Cxxx-NCR-002355 | NCR | WTH-Level 0- Upstand bars cast in incorrect position |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-08-24 | 2016-08-12 14:11 | -12 | 2016-08-10 06:47 | Civil - Civil Engineering General | 750 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During construction of an upstand on level 0 area 4, between gridlines 9 and 10 the vertical reinforcement bars for two small nibs were not installed in the correct position to the general arrangement drawing, Cxxx-SWN-S-DDA-M123_1-80002 (C10). In both nibs, one edge has 10mm cover and the other edge has 60mm cover(See attached photos).
| 02SL - Stations (LUL) | Cxxx-NCR-002356 | NCR | WTH – SHW1 level -1 suspended slab excess cover |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-09-30 | 2016-08-11 13:02 | -50 | 2016-08-10 15:32 | Civil - Civil Engineering General | 850 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | will pour the SHW1 level -1 suspended slab on 11 August 2016. As part of the pre pour checks it was noted that cover to the top mat of steel was greater than 70mm in four locations shown on the attached sketch Cxxx--C-XSK-M123-50330. A393 mesh was placed to obtain correct cover in these locations.
| 02SL - Stations (LUL) | Cxxx-NCR-002357 | NCR | WTH – SH-W2 Level -8 incorrect square penetrations formation |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-10-28 | 2016-10-27 14:31 | -1 | 2016-08-15 11:09 | Civil - Civil Engineering General | 3000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | On level -8 in SHW2 and specifically in section 8 of the elevation drawings Cxxx--A-DDC-M123_8-76268 (C03) there is a square penetration to the west side of the door. There is also a square penetration on top of the door. The subcontractor did not ask for clarification and read the drawing incorrectly and built these two penetrations in the wrong place. The lower penetration is built to the east side of the door (but it should be to the west) and the other is built on top of the door and slightly to the west (but it should be slightly to the east).
| 02SL - Stations (LUL) | Cxxx-NCR-002358 | NCR | WTH - SH-W2 – Precast stairs – damage to flights F1, F5, F12 and general finish |  | Contr | 201068 | FAR - Farringdon Station (West) |  | 2018-04-06 | 2018-04-04 10:40 | -2 | 2016-08-15 16:18 | Civil - Civil Engineering General | 3000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | For the precast stair elements installed in SH-W2 some of the units have been damaged either in transport, installation or in the period since installation. Also a number of flights have visible repaired blow holes and discolouration which don’t comply with the F3 finish requirement . See attached for details.
| 02SL - Stations (LUL) | Cxxx-NCR-002359 | NCR | MEP - ETH - Installation of DW144 Ductwork |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-09-01 | 2016-08-23 12:35 | -9 | 2016-08-18 07:23 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | Hargreaves have commenced with the installation of DW144 ductwork in areas over 200m3 without an approved MCR. The MCR had not been approved by CEG until concerns over the sealant had been resolved. This was resolved in a meeting with __ on 11/08/16 however the MCR had not been update, nor an FCD raised, prior to installation in 2 areas.
| 02SL - Stations (LUL) | Cxxx-NCR-002360 | NCR | ETH Early MEP Works - ETH Level -2 - Connections to lightning electrodes not installed as part of Cxxx-NCR-001418 and Cxxx-PWK-00040 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-08-29 | 2017-10-24 16:18 | 56 | 2016-08-17 12:38 | Systems - Earthing and Bonding | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Following on from Cxxx-NCR-001418 and Cxxx-PWK-00040 where connections to Pile LE10 and LE12 where not installed. Agreement was to weld a reinforcement bar between gridlines 4 and 6 on Wall 23 starter bars. s have become aware that the extra reinforcement bar has only been installed between gridline 4 and 5.
| 02SL - Stations (LUL) | Cxxx-NCR-002361 | NCR | ETH - Trapezoidal Shaft - Level +2 Wall 24 cut rebar in pockets |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-09-16 | 2016-08-26 16:37 | -21 | 2016-08-19 08:13 | Civil - Civil Engineering General | 5000 |  | Damaged | Repair | 3 (3-6k) | Complete | Supervision - Insufficient supervision | Completed |  | Following on from Cxxx-NCR-002297 & Cxxx-NCR-002316, where in the process of reinstalling cast-in plates into correct position. Operatives noticed that plates clashed with reinforcement bars, operatives decided to cut bars that clash with out consulting senior or section engineers. Once engineers had been informed of the cut bar works were suspended on wall.
| 02SL - Stations (LUL) | Cxxx-NCR-002362 | NCR | WTH inaccurate __ drawings |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-11-10 | 2016-11-11 17:41 | 1 | 2016-08-19 16:23 | Civil - Civil Engineering General | 2500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | __ has identified the layout of blockwork walls on their drawings in order to have fire board protection on those beams where blockwork wall is directly underneath along the beam. has identified mistakes on site due to inaccurate information on __ drawings (Cxxx--X-DWG-M123-54514 Rev P02) ; (Cxxx--X-DWG-M123-54500 Rev P05) B3172 [BEAM_B10] on Level +1 Upper mezzanine Area 3 has been sprayed but should not have been. B3195 [BEAM_B16] on Level 0 Area 3 has been sprayed but should not have been.
| 02SL - Stations (LUL) | Cxxx-NCR-002363 | NCR | WTH - Apse Ceiling - Non UKAS accredited operatives sampling concrete |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-09-09 | 2016-09-06 12:56 | -3 | 2016-08-23 16:42 | Civil - Civil Engineering General | 1250 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | During the audit (Cxxx--O4-RGN-M123-51424) of __ production of pre-cast concrete units it was noted that the concrete sampling (making of concrete cubes and slump-flow testing) was being carried out by __ operatives who are not accredited by UKAS.
| 02SL - Stations (LUL) | Cxxx-NCR-002364 | NCR | WTH - SS - Durbar floor plate installed without prior approvals (FCD, MCR) |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-09-07 | 2016-09-05 11:32 | -2 | 2016-08-24 12:31 | Civil - Structural Engineering | 2000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | Drawing Cxxx--X-DWG-M123-50046 C01 (referenced below) at the WTH level +1 Upper Mezzaine level shows the durbar floor plate area of the WTH. Cxxx-RFI-002628 (referenced below) was raised to confirm the steel grade of the floor plate and the answer provided by Cxxx was “Durbar plate to be grade S355JR+AR and galvanised”. This information was passed back to __ ( steelwork subcontractor). __ procured the Durbar floor plate but did not check with the supplier that the steel grade was S355JR+AR. The durbar floor plate that was supplied and installed was S275 JR+AR. A code 1 MCR for the Durbar floor plate should have been in place prior to its procurement. Note the plate is galvanised in accordance with the RFI response.
| 02SL - Stations (LUL) | Cxxx-NCR-002366 | NCR | MEP - PLT - FIRE MAINS INCORRECT HOLE SIZE |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-09-09 | 2016-09-07 09:02 | -2 | 2016-08-26 13:03 | Fire - Fire Systems & General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | BWIC holes are not correct size and location to suit pipework and fire stopping for Fire Mains and Hydrants. Hole sizes and missing holes are annotated on the attached marked-up drawings Cxxx--P-DDA-M123_8-50702 [C01] and Cxxx--P-DDA-M123_8-50711 [C01].
| 02SL - Stations (LUL) | Cxxx-NCR-002367 | NCR | ETH - Level L+1 GL4 - Damage to W28A concrete surface |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-09-30 | 2016-09-14 12:37 | -16 | 2016-08-26 14:35 | Civil - Civil Engineering General | 1000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The surface of Wall W28A (east side) at Level L+1 GL4 got damaged while striking the formwork (see attached photo). The edges of the concrete surface next to the formwork tie bars broke away. Reinforcement is not exposed.
| 02SL - Stations (LUL) | Cxxx-NCR-002368 | NCR | ETH - UER Dividing Wall Pour 4 - Incomplete pour |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-09-30 | 2016-09-14 12:27 | -16 | 2016-08-26 16:19 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Pour 4 of the Upper Escalator Ramp dividing wall was incomplete. Fortunately the incomplete pour only affects about the top 150mm from of the concrete wall over the length of 1m (see attached photos). Since the affected area is covered by the bracket for the glass wall, it won't be seen afterwards.
| 02SL - Stations (LUL) | Cxxx-NCR-002369 | NCR | WTH - SS - Fabrication error for Beams B3115 and B3147 connecting to Column G,9 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-09-30 | 2016-09-21 10:46 | -9 | 2016-09-01 08:38 | Structural Engineering - Steel Member | 3000 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | Beams B3115 and B3147 connect to column G,9 at level +2. These are highlighted on the attached marked-up __ GA drawing Cxxx--X-DWG-M123-50047 C01. The endplates of these beams at the column G,9 connection were welded upside down – this has caused the 55mm / 65mm dimensions from the beam c/l to the bolt holes to be reversed (see marked-up fabrication drawings extracted from Area 3 fabrication drawings package Cxxx--X-DWG-M123-50066 P02). The beams were installed with the Southern vertical row of bolts installed and the Northern vertical row omitted (as the bolt holes in the endplates did not align with the holes in the column web). This is shown in the attached photographs. Note see Cxxx-FCD-002007 (referenced below) for use of P status Area 3 fabrication drawings.
| 02SL - Stations (LUL) | Cxxx-NCR-002370 | NCR | TUN - SCL - Honeycombing in ES2 Top Knuckle Pour 1 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-09-28 | 2016-09-22 11:53 | -6 | 2016-08-31 12:07 | Tunnelling - Linings - In-situ Concrete | 2500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | A small area (A3 size) of honeycombing has been found upon striking the formwork of the bottom pour of the ES2 top knuckle. The location is Chainage 21, on the LHS looking up ES2. It is at the interface with the invert. Reinforcement is exposed, as per the attached photo "Photo Before Repair".
| 02SL - Stations (LUL) | Cxxx-NCR-002371 | NCR | SMM - Instrumentation not installed/read |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-09-30 | 2016-09-30 13:14 | 0 | 2016-09-01 16:20 | Geotechnical Engineering - Settlement | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | The Contractor raises this NCR to capture instrumentation not installed or read in accordance with contract specifications. Please find attached a list of monitoring points either not installed or not read.
| 02SL - Stations (LUL) | Cxxx-NCR-002372 | NCR | WTH – Construction of 245mm wide WI column without approved detail |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-07-07 | 2017-05-30 12:35 | -38 | 2016-09-06 06:53 | Civil - Civil Engineering General | 1500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | We are required to construct 245mm wide walls as per drawing Cxxx--X-DWG-M123_1-54120 (P07). These walls are built up using a skin of 140mm blocks adjacent to a skin of 100mm blocks. No 245mm wide WI column blocks exist. Where WI columns are required, our blockwork subcontractor has constructed the blocks using a smaller block cut to the internal dimension of the column as a former with which to fit two halves of a WI column block around, providing the correct width. See attached marked-up drawings and site photos. This detail has yet to be approved. An FCD will be raised to approve the use of this detail. In addition, drawing Cxxx--X-DWG-M123_1-54120 was at Revision P07 with no FCD in place covering its use.
| 02SL - Stations (LUL) | Cxxx-NCR-002373 | NCR | Tun-BUI PLT-TUN - halfen channel out of tolerance (PTE) |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-03-02 | 2018-02-22 09:44 | -8 | 2016-09-06 14:31 | Civil - Civil Engineering General | 3000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | The final as-builts for the halfen channels cast into the platform nosing in PTE are showing some points out of tolerance, tolerance being +/- 10 mm. There are 23 chainages in total, the track chainage of the locations is shown on the attached document "__ channel out of tolerance. The worst case is between 4mm and 6 mm out of tolerance. Through discussions with Cxxx in the past 18 months, the brackets being installed into these halfens have a higher permissible tolerance than expected, therefore Cxxx have progressed with the installation of the brackets without further changes to the halfens.
| 02SL - Stations (LUL) | Cxxx-NCR-002375 | NCR | ETH - Coffer Ceiling - Reduced Cover to Beam Reinforcement |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-10-14 | 2016-10-05 10:31 | -9 | 2016-09-07 20:21 | Structural Engineering - Reinforcement | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | Drawings Cxxx-ATK-S-DWG-M123_A-50112 [P03], Cxxx-ATK-S-DWG-M123_A-50113 [P03] and Cxxx-ATK-S-DWG-M123_A-50114 [P01] detail the reinforcement to the concrete encasement to the steel beams on the underside of level +1 of the ETH for the coffer ceiling. They specify 35mm cover. After installing the reinforcement, localised areas along transfer beam B24 on the south east side of the coffer ceiling (B9 on drawing Cxxx-ATK-S-DWG-M123_A-50112) were found to have less than 35mm cover. 2No areas approximately 1000mm long have 20mm cover to the outer links. For clarity, no concrete has been poured yet. Due to the fact that spacer blocks are not permitted and the reinforcement must be hung from the beams using fixed offset brackets, would prefer to use as-is rather than dismantle and re-install the bars, which will cause programme delays. propose that this minimum of 20mm cover is acceptable in localised areas for the underside of the beams, as measured on site. Justification is in the 'Technical Requirements' section. Nevertheless, will still aim for 35–40mm cover throughout, to meet the design requirements.
| 02SL - Stations (LUL) | Cxxx-NCR-002376 | NCR | TUN-GFRC Non-compliance to Approved MCR |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-05-18 | 2018-05-14 16:31 | -4 | 2016-09-09 10:56 | Architectural - Finishes | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | During a surveillance of the Acoustic GFRC panels it was noted that the RW3 tissue lined __ panels did not comply with the approved MCR Cxxx--Y-LRC-M123-50002 , LU Product registeration certificate for RW3 __ and the products materials specification drawing Cxxx--Y-DWG-M123-51001 States that RW3 is a tissue lined __ 1 piece system __ have installed a 2 piece separate tissue lining and __ that does not comply with the approved MCR. It has subsequently been found that the mineral scrim has been supplied through a different supplier than that which __ have tested. This was known by __ but not communicated to the Contractor at any stage in the project. There is a risk, therefore, that this untested material is not compliant to LU regulations and may have to be replaced.
| 02SL - Stations (LUL) | Cxxx-NCR-002380 | NCR | TUN-PLT Fabrication and onsite installation of platform equipment enclosure support brackets without approved documentation |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-06-23 | 2017-06-23 15:36 | 0 | 2016-09-13 16:52 | Archaeology - General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | Works to fabricate and install the support brackets for the Hydrant Cabinet Enclosures in the platforms has started without all the required documentation being in place. The activity was delayed as far as possible without impacting on programme. Specifically the support brackets for the Type 5E Platform Equipment Enclosures as detailed on drawing numbers Cxxx--X-DWG-M123-53143, 53144 and 53145 Rev P02 have been fabricated and installed onsite without an approved MCR. The support bracket MCR (Cxxx--A-LRC-M123-50061) is currently Code 3. Acceptance of all materials through the MCR process is a Hold Point under the relevant ITPs (Cxxx--X-ITP-M123-50014 and 50016 Rev 2.0). In addition the WPS and WPQR was not submitted before fabrication started and has since been rejected Code 3. Acceptance of the WPS and WPQR is a Hold Point in the ITP (Cxxx--X-ITP-M123-50016 Rev 2.0). Reference to the Hydrant Cabinet Enclosures (JN10.1217 Type FX-801, 802 & 806) was not included in the above ITPs in error. Additional note - the support bracket MCR (Cxxx--A-LRC-M123-50061) is now Code 1 this NCR can be closed.
| 02SL - Stations (LUL) | Cxxx-NCR-002381 | NCR | ETH-Trapezoidal Shaft Level -1.5 Feature Slab - Not constructing the falsework deck to agreed plywood lines. |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-03-03 | 2017-02-27 11:40 | -4 | 2016-09-14 14:11 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | In order to achieve an F3 finish on the level -1.5 feature slab (Soffit Level 108.009), submitted Cxxx-FCD-002280 to agree the plywood lines with Crossrail. However, this FCD has not been followed. Please see attached sketch illustrating the location of the installed plywood. Please note that the 25mm 'feature coffers' are all in the correct location. Attached ' As Built location of Plywood Joints 1' is from the origional Cxxx-FCD-002280, with the agreed marked up plywood lines (in red). The lines highlighted in green, are the actual 'as built' location of the plywood joints.
| 02SL - Stations (LUL) | Cxxx-NCR-002382 | NCR | ETH-SB - Holding down Bolts at GL9/A incorrect orientation |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-06-23 | 2017-06-22 11:33 | -1 | 2016-09-28 14:59 | Civil - Civil Engineering General | 6000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Holding down bolts at GL9/A installed with the wrong orientation. Drawing Cxxx--S-DDD-M123_Z-20103 C02 used during installation see attached. Drawing Cxxx--X-DWG-M123-50073 C01 shows the correct orientation.
| 02SL - Stations (LUL) | Cxxx-NCR-002383 | NCR | MEP - Damage to Blockwork wall during installation of Secondary CMS in SLD rooms |  | Contr | __ | FAR - Farringdon Station (West) |  | 2016-11-11 | 2016-11-11 14:16 | 0 | 2016-09-16 10:30 | Electrical - Cable Management | 2500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | This NCR is raised following damages caused to the blockwork wall during the installation of secondary CMS i.e. conduits. The installation method involves drilling a pilot hole and then the actual size of the hole required however the extra care is required to ensure the blockwall work does not bulge out during drilling.
| 02SL - Stations (LUL) | Cxxx-NCR-002384 | NCR | WTH - SH-W2 - Levels -5 & -4 Main Service Riser installation using P status drawings |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-06-09 | 2017-06-09 15:03 | 0 | 2016-09-27 09:55 | Civil - Civil Engineering General | 750 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | __ have carried out installation of level -5 and -4 Main Service Risers using P status drawings. The agreed process for working to ‘P’ revision drawings captured under the Minimum Assurance Requirements for Cxxx Drawings Matrix (Cxxx--O-LRC-M123-50001 Rev.2.0) was not followed (no FCD raised), yet construction works proceeded.
| 02SL - Stations (LUL) | Cxxx-NCR-002385 | NCR | SMM - Amber & Red Triggers outside of Design Criteria |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-10-21 | 2016-10-20 07:47 | -1 | 2016-09-19 10:11 | Geotechnical Engineering - Settlement | 1000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Please find attached a list of amber and red triggers breached on differential settlement on the Cxxx contract.
| 02SL - Stations (LUL) | Cxxx-NCR-002386 | NCR | ETH - Level L+2 - no __ channel fixed |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-04-28 | 2017-04-26 13:28 | -2 | 2016-09-19 12:10 | Civil - Civil Engineering General | 4000 |  | Supervision/Management | Repair | 3 (3-6k) | Complete | Personnel Error - Inattention to detail | Completed |  | Drawing Cxxx--A-DDD-M123_Z-25254 detail 2 shows a __ Channel to be installed in the centre of Level L+2 slab along the east site (Hayne St). The __ Channel was not installed during the construction of the Level L+2 slab between GL3.5 and GL6.
| 02SL - Stations (LUL) | Cxxx-NCR-002387 | NCR | MEP - No progressive assurance of Pipework installation to date |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2016-10-31 | 2016-10-25 06:42 | -6 | 2016-09-19 13:51 | Mechanical - Piping | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | A planned Crossrail Quality surveillance was undertaken on 14th September 2016 to look at installation of public health and mechanical pipework. At the time of the visit, installation had progressed using four types of pipework (cast iron and copper), however no installation checks had been completed to progressively assure the ongoing installation. It was stated that installation checks for the pipework would only be completed following completion of the ‘section/commissioning lot’ as stipulated in the frequency section of ITPs Cxxx--P-ITP-M123- 50001 and 50007. Installation in the ETH Level -7 was inspected where four types of pipework had been installed in multiple rooms. As the level forms a section, it was noted that no installation records would be produced until full pipework installation had been completed in the section. At the time of the visit, the works had been ongoing for two weeks. Based on the ITP frequency, checking had yet to be undertaken, and records produced as evidence of acceptable installation. The current process being adopted with respect to the sectional checking does not provide progressive assurance of the works due to the significant times for which the works can span. This process also does not align with the Works Information Volume 2B which states: “The Contractor shall provide progressive assurance that the constructed works comply with the requirements set out in the Contract. __ assurance means the confirmation of compliance by the generation of contemporaneous records”. The lack of progressive checking during installation could potentially lead to significant rework. As no records have been generated in support of the installation to date, this NCR as raised. It is recommended that the process for assuring other system installation forms part of the close out, as this NCR is not just pertinent to pipework installation.
| 02SL - Stations (LUL) | Cxxx-NCR-002390 | NCR | WTH-Level 0 to Level +1- Incomplete column pour |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-10-04 | 2016-09-29 15:31 | -5 | 2016-09-20 13:33 | Civil - Civil Engineering General | 1450 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Upon striking of the shutter, following the encasement of the column on wall 43 along gridline C(SFC) from level 0 to level +1, it was discovered that the concrete had not been cast to the soffit of the metal deck i.e. the concrete was not to the correct level on the east side of the encasement. (See attached photo)
| 02SL - Stations (LUL) | Cxxx-NCR-002391 | NCR | WTH – Level 0 Southern perimeter upstand pre-pour inspection completed unsatisfactorily |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-02-17 | 2017-02-17 11:27 | 0 | 2016-09-20 14:54 | Civil - Civil Engineering General | 2000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | invited Crossrail to inspect an upstand prior to it being poured on 11/08/2016 (see attached sketch for location). During the inspection issues were identified that should have been rectified prior to the inspection being requested. 1) Concrete from a previous pour was evident on the cast-in reinforcement 2) Cover in some areas had exceeded the maximum of 50mm (tolerance 40mm +10/-5) 3) A single cast-in bar was found to be touching the shutter at the base. This bar had been bent to achieve the cover at the top of the bar. Refer to attached site photos.
| 02SL - Stations (LUL) | Cxxx-NCR-002392 | NCR | WTH SHW1 Wall 46 1st lift low concrete strength |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-12-02 | 2016-10-20 14:45 | -43 | 2016-09-21 15:17 | Civil - Civil Engineering General | 2000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | poured the first lift of SHW1 wall 46 on 20 July 2016 with C1/2 (10mm) concrete mix, C50/60 compressive strength at 28 days. 3no. concrete wagons were used and 2no. wagons had cube sets taken from them (the second set because it was being used for a different wall). The cube results at 28 days for the one set were 51.6 N/mm2 and 51.9 N/mm2. See attached cube result sheets (EX3159). Concrete strength has not been achieved at 28 days as per Cxxx-SWN-C-RSP-M123-00004, Table KF10-01 and it is not compliant with BS EN 206:2013 criteria 2 and 3 (see attached graph). Cube results at 56 days for the low set were 57.0 N/mm2 and 58.0 N/mm2. See attached cube result sheets (EX3159). The results for the other cube results taken during the pour were acceptable. See attached cube result sheets (EX3158). Also attached is the concrete site control sheet identifying the loads where cubes were taken.
| 02SL - Stations (LUL) | Cxxx-NCR-002393 | NCR | WTH SHW1 Level -3 soffit concrete insufficiently compacted on south side |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-12-23 | 2016-11-24 10:13 | -29 | 2016-09-23 09:12 | Civil - Civil Engineering General | 2500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | a) After striking the level -3 suspended slab falsework it was noted that an area at the construction joint requires repair due to a combination of honeycombing and grout loss. b) In addition there is some tie wire visible in the soffit area. See attached photographs.
| 02SL - Stations (LUL) | Cxxx-NCR-002394 | NCR | WTH-SHW2-Level -5 Damaged Blocks |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-11-25 | 2016-11-21 09:17 | -4 | 2016-09-21 09:58 | Civil - Civil Engineering General | 2000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | During scaffold striking in the Westbound draught relief riser, the eastern perimeter blockwork wall on level -5 in SHW2, between gridlines 2 and 3, was damaged (please find photo attached).
| 02SL - Stations (LUL) | Cxxx-NCR-002396 | NCR | Tun-BUI Use of C01 reinforcement Drawings not approved by CRL |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-06-09 | 2017-06-01 10:11 | -8 | 2016-09-21 15:20 | Civil - Tunnelling | 750 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | Drawings used on site were: Cxxx-ATK-S-DWG-M123_Z-50685 C01 Cxxx-ATK-S-DWG-M123_Z-50695 C01 Drawings on eB that time were: Cxxx-ATK-S-DWG-M123_Z-50685 P02 Code 2 (PMC-12517 13/05/16) Cxxx-ATK-S-DWG-M123_Z-50695 P01 Code 2 (PMC-13319 16/08/16).
| 02SL - Stations (LUL) | Cxxx-NCR-002397 | NCR | ETH- Trapezoidal Shaft-Excess Scabbling and Breaking during the constrauction of ESS1 Mid Landing at 113.968 S.S.L |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-11-25 | 2016-10-31 09:23 | -25 | 2016-09-23 11:59 | Civil - Civil Engineering General | 1000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | During the construction of the mid-landing at SSL 113.968 in the ESS 1 Stair core in the Trapezoidal Shaft , excess concrete was broken and scabbled in search of steel reinforcement couplers on the North Face of Wall 24. The extent of this breaking is approximately 250mm long x 250mm high x 30mm deep.
| 02SL - Stations (LUL) | Cxxx-NCR-002398 | NCR | STW - MEP - Non-UKAS accredited com pull-out tests reports |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-01-27 | 2017-04-12 16:17 | 75 | 2016-09-25 21:15 | Mechanical - Mechanical Engineering General | 2500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Insufficient surveillance of subcontractors | Completed |  | All pull-out proof testing of the permanent MEP works that were performed from the commencement of works up to the 18/08/2016, were undertaken by operatives who were trained under a CFA certified company (as per the performance requirement of the CRL M&W specification JY90 and associated MCR), which was though not UKAS-accredited as per WI Volume 2B - Chapter 20.8. This arrangement was deemed not compliant on the 19/02/2016 and Cxxx-NCR-002154 was raised. Following response to Cxxx-FCD-002090, we were expected to either use a directly UKAS accredited firm for pull-out proof testing or train our operatives by, that were performing pull-out proof testing, by a UKAS accredited firm. Under Cxxx-FCD-002246, we have notified that we would utilise the "BAM Ritchies Laboratory", accredited by UKAS for pull-out proof testing of structural fixings to BS 5080-1 as per the CFA Guidance note, to perform the additional training to all of our operatives associated with pull-out proof testing. From 18/08/2016 onwards, all of our pull-out proof testing is undertaken by operatives that are trained by a UKAS accredited company, as per the requirement of Cxxx-FCD-002090. In relation to the all the pull-out proof test that were performed prior to the 18/08/2016, we would like to note the following: 1. All pull-out proof tests have been performed satisfactorily against the relevant anchor load, which is significantly greater that the CFA proposed "proof" (real - actual) load of the associated MEP services. 2. The MEP services of the station are conventional and not large in size, while our initial arrangements (of UKAS accredited Tier-3 S/Cs with appropriate CFA training from a certified person) ensure a sufficient level of compliance. 3. The design of the support system is based on the principle of "redundant fastening" in line with the DoP/s of the associated anchor/s, thus providing additional assurance against an already increased load safety factor (refer to point 1). 4. Since the works have progressed substantially, repeating these pull-out proof tests would pose a safety risk (as most of these areas are now inaccessible for this type of test) and would lead to a impact on programme.
| 02SL - Stations (LUL) | Cxxx-NCR-002399 | NCR | ETH - Failed Inspection - Cavity Wall Drainage Channels Cleanliness |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2016-10-28 | 2016-10-25 17:14 | -3 | 2016-09-26 08:15 | Architectural - Brickworks/Blockworks | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | An inspection was requested by on 20/09/2016 for CRL to inspect the cleanliness of the cavity wall drainage channels at levels -1, -2, -3 and -6 before the blockwork 'mouse holes' were blocked (ITP Cxxx--C-ITP-M123-50277 Rev 5.0 Activity 5.10 Hold Point). The inspection was undertaken on 21/09/2016 by __ (CRL FE) and it was found that the majority of the areas failed the inspection as: 1. Various materials and waste were found in the channels in various levels 2. Access to some areas was blocked by material storage 3. Level -6 - 1no gully found to be blocked and channels filled with slurry The attached document 'Cxxx-NCR-002399 ETH Trap Shaft drainage' includes photos of the failed inspection.
| 02SL - Stations (LUL) | Cxxx-NCR-002400 | NCR | WTH - Cables cast-in with Fire Protection Coating |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-02-24 | 2017-02-23 14:46 | -1 | 2016-09-26 12:57 | Civil - Civil Engineering General | 1000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | Temporary lighting cables were installed around steel beam and fire protection coating was sprayed over them. Cables were affecting the overall envelope of the fire protection coating as a result. Refer to attached location sketch and site photographs.
| 02SL - Stations (LUL) | Cxxx-NCR-002401 | NCR | MEP - Installation of Zinc coated Screws on Class 4 conduit covers instead of Brass Screws in SLD Rooms |  | Contr | __ | FAR - Farringdon Station (West) |  | 2016-10-28 | 2016-10-21 14:48 | -7 | 2016-09-26 19:53 | Electrical - Cable Management | 3000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Lack or improper material identification and traceability | Completed |  | This NCR is raised following an installation of Zinc coated screws instead of Brass screws on conduits covers within the handed over SLD rooms.
| 02SL - Stations (LUL) | Cxxx-NCR-002402 | NCR | MEP - Use of P Status Lighting Drawings for Onsite Installation without Formal CRL Acceptance in ETH Level -6/-7 - |  | Contr | __ | FAR - Farringdon Station (West) |  | 2016-10-10 | 2016-10-04 09:59 | -6 | 2016-09-26 22:59 | Electrical - Lighting | 2000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | This NCR is raised following Electrical operatives installing conduits to the Lighting Drawings without a CRL accepted drawing via a formal gate or FCD process.
| 02SL - Stations (LUL) | Cxxx-NCR-002403 | NCR | STW – Failure to comply with screeding ITP |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-12-16 | 2016-12-14 09:39 | -2 | 2016-09-27 08:08 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | Cxxx--X-ITP-M123-50009 Rev 2 was prepared and accepted regarding the screeding works. There were several items included in the ITP regarding testing of the finish screed and epoxy. Items 12.1, 12.2, 12.3, 12.4, 13.1, 13.2 and 13.3 are classed as hold points in the works for CRL, as well as for __ & . Crossrail have not always been invited to inspect these tests and yet the works have continued.
| 02SL - Stations (LUL) | Cxxx-NCR-002404 | NCR | WTH - Unapproved head detail |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-07-13 | 2018-07-12 13:47 | -1 | 2016-10-17 11:49 | Architectural - General | 2500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | LUFF Coating (Please refer to Cxxx--C-LRC-M123-50609 attached) has been installed in the blockwork head sealing inside Westbound and Eastbound Draught Relief Shaft. __ has installed LUFF Coating as a standard practice but without the detail approved.
| 02SL - Stations (LUL) | Cxxx-NCR-002405 | NCR | ETH - Fire protection coating __ Type M-II - use of primer |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-10-14 | 2016-10-06 16:57 | -8 | 2016-09-28 11:26 | Civil - Civil Engineering General | 1500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Prior to spraying the fire protection coating __ Type M-II in ETH Level L+1 between GL4-5 / GL C-D __ used the __ primer SBK-113 on the steel beams without / CRL approval. __ got stopped using the primer.
| 02SL - Stations (LUL) | Cxxx-NCR-002406 | NCR | WTH Missing labels from Wi Beams in draught relief shafts |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-04-27 | 2018-04-25 15:59 | -2 | 2016-10-17 11:44 | Architectural - Brickworks/Blockworks | 750 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | After inspection in draught relief shafts it became apparent that some of the structural members, noticeably the Wi beams were not labelled from Level 0 to Level +2. Please see the attached sketch.
| 02SL - Stations (LUL) | Cxxx-NCR-002407 | NCR | WTH - SHW2 - MSR - Subcontractor using drawings not issued to BFK |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-07-28 | 2017-07-28 14:11 | 0 | 2016-10-03 08:04 | Civil - Civil Engineering General | 1500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | __ have carried out installation of level -6, -5 and -4 Main Service Riser 1 mesh flooring using P status drawings that were not issued to . The agreed process for working to ‘P’ revision drawings captured under the Minimum Assurance Requirements for Cxxx Drawings Matrix (CCxxx--O-LRC-M123-50001 Rev.2.0) could be not followed (no FCD raised) as had no knowledge of drawing existence. The drawings used were: 1.Cxxx--X-DWG-M123_5-52024 2. Cxxx--X-DWG-M123_5-52023
| 02SL - Stations (LUL) | Cxxx-NCR-002408 | NCR | STW – Failure to undertake crack and curling test after 28 days |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-12-16 | 2016-12-14 09:51 | -2 | 2016-09-28 13:51 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | Cxxx--X-ITP-M123-50009 Rev 2 was prepared and accepted regarding the screeding works. Item 12.4 relates to the crack and curling test being completed 28 days after completion of the screed. This test has not been carried out on the 28th day.
| 02SL - Stations (LUL) | Cxxx-NCR-002409 | NCR | ETH - Wall 28 a L+1 to L+2 Grout Loss to North Section GL 6 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-10-14 | 2016-10-13 16:08 | -1 | 2016-09-29 15:27 | Civil - Civil Engineering General | 1000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | After striking the sides of the formwork to Wall 28a (last section GL 5.5 to GL6), grout loss has been identified. See attached Photo. This is due to formwork not being tight due to the difficult geometry of wall and column
| 02SL - Stations (LUL) | Cxxx-NCR-002410 | NCR | TUN - SCL - Incomplete saw cuts under platform PTE/PTW |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-10-28 | 2016-10-20 15:21 | -8 | 2016-09-30 09:57 | Tunnelling - Linings - In-situ Concrete | 2500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | In PTE/PTW some of the contraction joints being post-cut into the secondary lining are partially incomplete.The affected area is an approximately 3.5m section of the lining under the platform. It is noted that the lining was cast between 10 - 18 months previous and there is no evidence of uncontrolled cracking at these locations The locations and extent are given in the attached documents. There are 21 locations in total
| 02SL - Stations (LUL) | Cxxx-NCR-002411 | NCR | Tun-BUI PES Grille hinge mechanism |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2017-07-31 | 2017-07-19 14:25 | -12 | 2016-10-03 11:57 | Architectural - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | PES hinge is required by Cxxx-ATK-N2-RSP-CR002-00001 clause JH11.1219 (h) to be 316 stainless steel bespoke sprung slow release pivot hinge with controlled automatic vertical lift to open position to extent as indicated on the Design Drawings. The hinge as presented on the Prototype does not meet the express requirements or provide equivalent alternative performance. The action is un assisted and the grille panels rack, this will most likely lead to wear on the hinge due to stressing and because of the nature of the hinges unassisted operation there is a risk of injury to the operatives in opening it. A mechanism in accordance with the WI would mitigate this risk.
| 02SL - Stations (LUL) | Cxxx-NCR-002412 | NCR | ETH - Feature Slab/Column Snags |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2020-06-10 | 2020-09-25 15:05 | 107 | 2016-10-05 07:35 | Structural Engineering - Formwork | 5000 |  | Manufacturing Defect | Repair | 3 (3-6k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | There are a number of long bubbles / ripples on some of the polystyrene moulds for the ETH coffer ceiling. These have the potential to impact the finish achieved on the sides of the coffers. It is possible that the wet concrete pressure will push these back and flatten the surface again, although this cannot be confirmed. Update 23/02/2017: This NCR is being amended to cover all ETH fair faced concrete repairs, including the issues raised in Cxxx-NCR-002412, Cxxx-NCR-002324, Cxxx-NCR-002381, Cxxx-NCR-002469, Cxxx-PWK-00113, Cxxx-PWK-00129 and Cxxx-PWK-00143. Please find attached the ETH Fair Faced Concrete Repairs Register.
| 02SL - Stations (LUL) | Cxxx-NCR-002413 | NCR | MEP - ETH - Acceptance and use of Non MCR Adapatable Box for Copper Ceiling Cast in Installation |  | Contr | __ | FAR - Farringdon Station (West) |  | 2016-10-28 | 2016-10-25 18:07 | -3 | 2016-10-04 08:32 | Electrical - General | 2000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | This NCR is raised following the delivery acceptance and installation of a non MCR accepted adaptable boxes. Following a prototyping exercise at Silvertown, the Coffer ceiling installation detail was revised, issued and accepted under Cxxx-FCD-002271. The Change on the FCD redesigned the lighting Installation within the East Ticket Hall Coffer Ceiling at Level 0 from Standard Besa Boxes with extension rings to 150 X 150 X150 Adaptable Boxes as the only viable option for ease of installation. The Boxes used were made by Greenbrook AD instead of the MCR / FCD accepted Deta or Metpro as neither of the approved companies do make the box required box size in the MCR / FCD.
| 02SL - Stations (LUL) | Cxxx-NCR-002414 | NCR | __ using __ Brickforce masonry reinforcement without MCR in place |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-10-28 | 2016-10-26 16:33 | -2 | 2016-10-06 08:56 | Architectural - Brickworks/Blockworks | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | __ have been using __ Brickforce masonry reinforcement without MCR in place
| 02SL - Stations (LUL) | Cxxx-NCR-002415 | NCR | ETH - Wrong installation hydroduct at L-7 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-10-21 | 2016-10-19 07:25 | -2 | 2016-10-05 12:28 | Architectural - Flooring | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | carried out an inspection before screeding L-7 UPE area and found that the installation of the hydroduct was not done as per ITP. a) Hydroduct not overlapped properly, dimples filled with grout at the joint (see photos attached) b) Membrane not installed flat (see photos attached)
| 02SL - Stations (LUL) | Cxxx-NCR-002416 | NCR | Plastic Polythene not laid by __ after screeding at ETH L-7 UPE area |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-10-21 | 2016-10-19 14:33 | -2 | 2016-10-06 10:35 | Architectural - Flooring | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | __ did not lay plastic polythene over the screed the following day after screeding L-7 UPE area (see highlighted drawing) as per ITP Cxxx--X-ITP-M123-50009 Rev 2.0 activity 8.4.
| 02SL - Stations (LUL) | Cxxx-NCR-002417 | NCR | ETH - Trapezoidal Shaft - Level 0 Upstand cast in incorrect location |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-11-11 | 2016-10-27 09:22 | -15 | 2016-10-05 15:42 | Civil - Civil Engineering General | 6000 |  | Design | Rework | 3 (3-6k) | Complete | Personnel Error - Inattention to detail | Completed |  | During the construction of a small section of upstand at level 0, (354mm East of GL D and between GL 6 and GL5) have identified that it has been incorrectly positioned. Please see markup attached. The upstand was set out 70mm East of its design location in the highlighted area. This is due to the drawing not being clear with dimensions offset from GLD. GLD is not parallel to the upstand as assumed by the engineer when setting out. This error was only noticed once the upstand was completed.
| 02SL - Stations (LUL) | Cxxx-NCR-002418 | NCR | ETH Screeding - Moisture check not done before applying epoxy at L-5 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-11-25 | 2016-11-25 10:50 | 0 | 2016-10-05 14:57 | Architectural - Flooring | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | __ did not carry out Moisture check before applying epoxy on LV rooms I & II at L-5, as stated on the Screeding ITP Cxxx--X-ITP-M123-50009 rev 2.0. However, __ carried out visual inspection and the area was completely dry.
| 02SL - Stations (LUL) | Cxxx-NCR-002419 | NCR | ETH-SB - Holding down Bolts in Area 10 not central to bolts holes in the base plates GL6/A |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-04-28 | 2017-04-25 11:38 | -3 | 2016-10-06 17:10 | Civil - Civil Engineering General | 5000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Holding down bolts at GL6/A are out of tolerance whereby the holding down bolts are not central to the holes in the base plate. See attached as built survey of base type H01 at GL6/A. See attached survey (Ref; As built survey H01).
| 02SL - Stations (LUL) | Cxxx-NCR-002420 | NCR | ETH - Screeding not laid in 2 layers as per ITP at L-2 (Lower Plenum) |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-10-21 | 2016-10-18 07:23 | -3 | 2016-10-06 11:05 | Architectural - Flooring | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | carried out a site inspection while __ were screeding L-2 Lower Plenum Room and found that they were not doing the screed in 2 layers as per ITP Cxxx--X-ITP-M123-50009 Rev 2.0 clause 7.3
| 02SL - Stations (LUL) | Cxxx-NCR-002421 | NCR | WTH Level +2 upstand along GL P- Excess cover |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-11-04 | 2016-11-01 15:21 | -3 | 2016-10-10 08:12 | Civil - Civil Engineering General | 750 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Previous Construction - Problems based on previous construction errors | Completed |  | On level +2 the upstand running along Gridline P to the south of wall 15 (see attached sketch) had 20mm excess cover to its eastern side (see attached photo). The cover is 40mm as stated in the Upstand Reinforcement Details drawing: Cxxx-ATK-S-DWG-M123_B-50133 Rev.C01 and the upper limit for cover is 50mm resulting from the Cxxx-FCD-00974.
| 02SL - Stations (LUL) | Cxxx-NCR-002423 | NCR | TUN - SCL - ES2 Top/Bottom Knuckle secondary lining out of tolerance |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-11-10 | 2016-11-03 14:46 | -7 | 2016-10-13 14:29 | Tunnelling - Linings - In-situ Concrete | 2500 |  | Manufacturing Defect | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | There are various places where the secondary lining of the top and bottom "knuckle" sections of ES2 are our slightly out of tolerance and the minimum radius has not been been achieved. In summary the locations are: A - Top knuckle above platform, north side, worst case -31mm (Inclined lift zone) B - Top knuckle above platform, south side, worst case -17mm (GFRC cladding zone) C - Bottom knuckle above platform, worst case -17mm D - Bottom knuckle below platform, worst case -30mm The as-built profiles can be found on Cxxx--C4-LRC-M123-50443 (Page 364-408)
| 02SL - Stations (LUL) | Cxxx-NCR-002424 | NCR | TUN - Lack of Material Protection |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-11-11 | 2016-11-09 13:01 | -2 | 2016-10-12 11:12 | Architectural - Finishes | 3000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | This NCR is being raised in line with the non-conformance to comply with section JH40.3317 Material Protection of the Cxxx--A-RSP-M123-50057 Cxxx Farringdon Station - Architectural Specification. There are two incidences of were materials have not been adequately protected so as to stop them from being damaged during transit. The first was the steel sections of the junction panels that have the frames built in when delivered, during the lifting of these panels it was became clear once the operation was complete that the steel frames we were damaged and ultimately not suitably protected from damage. The second occurrence was during the movement of a box of passenger zone panels which were being pulled by a manual pallet truck. The operatives involved turned a corner to sharply and subsequently the box toppled over and the panels were damaged.
| 02SL - Stations (LUL) | Cxxx-NCR-002425 | NCR | ETH - Missing earthing connections |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-12-23 | 2017-01-04 17:31 | 12 | 2016-10-17 08:37 | Electrical - Lighting | 4000 |  | Incorrect Installation | Use As-Is | 3 (3-6k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | ETH - Handback packages 17 and 37 - Trap Shaft Missing earthing connection This NCR is raised because it is noted that 2no of Lightning Protection connections (DC16 and DC1/2) extensions were not installed prior to casting of the Level 0 slab. Refer to Inspection & Test Plan - Cxxx--C-ITP-M123-50009 number 9-15 Reinforced Concrete Works ETH Rev. 10 All the other connections have been tested and checksheet attached to the Handback package. See attached Cxxx--E-DDD-M123_Z-25705 C01.
| 02SL - Stations (LUL) | Cxxx-NCR-002426 | NCR | WTH_Level +3 Slab Crack Survey |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-03-31 | 2017-03-31 16:09 | 0 | 2016-11-07 14:49 | Civil - Civil Engineering General | 3000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Management Problem - Improper resource allocation | Completed |  | Cracks have formed on the Level +3 slab eastern side which was poured on the 13th of August 2016. The cracks are greater than 0.3mm wide, ranging from 0.3 to 1.0mm, and have formed in 7 locations as per the attached sketch Cxxx--C-XSK-M123-50343 and associated photographs.
| 02SL - Stations (LUL) | Cxxx-NCR-002427 | NCR | TUN - PLT - Walls out of tolerance - Concourse and cross passages |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-12-08 | 2016-11-03 10:40 | -35 | 2016-10-27 15:41 | Civil - Civil Engineering General | 2500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Not Defined | Completed |  | The final as-builts for the concourse and cross passage tunnels are showing some points out of tolerance, tolerance being +/-20mm on plan view and +/-10mm verticality. The locations are shown in he attached document "out of tolerance walls" which is extracted from Cxxx--C-LRC-M123-50809 There are only small sections of walls out in various locations on average by 5-15mm, Use as-is is proposed based on the following - Under platform areas checked as adequate for spaceproofing by follow on contractors (__) - Above platform area (ES2) spaceproofing checked as adequate for escalator installation (see attached)
| 02SL - Stations (LUL) | Cxxx-NCR-002428 | NCR | ETH - Level -7 Installation of ESS1 Insitu flight without approved drawing |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-01-20 | 2016-12-20 08:18 | -31 | 2016-10-25 14:08 | Civil - Civil Engineering General | 7000 |  | Supervision/Management | Rework | 2 (6-60k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | ETH - Level -7 Installation of ESS1 Insitu flight without approved drawing Insitu stairs at Level -7 have been constructed off Cxxx-ATK-S-DWG-M123_Z-50796 P02 which has not been approved. Additionally drawing has not been followed i.e. __ angle plate not installed. Pour has not been conducted.
| 02SL - Stations (LUL) | Cxxx-NCR-002429 | NCR | TUN - SCL - Damp patches at VA2 / PL3 connection |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-01-20 | 2016-12-21 15:12 | -30 | 2016-10-31 17:16 | Tunnelling - Linings - In-situ Concrete | 2400 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | There are 2 small damp patches at the interface between PL3 and VA2. The lining in this location complies with the performance requirement of the specification KW20 however the NCR is raised to formalise and document the subject matter. The leak has been monitored periodically by /Cxxx/CRL and the photos attached to this PTR indicate the worst case. As can be seen it is only minor weeping and there is no leakage onto any of the plaform surfaces. By inspection of this photo it is evident that the ingress is less than the stated maximum (VA2 area ˜ 200m^2). As per Cxxxs response to the orginal proposal to "use as is" the reinjectable hoses will be injected in order to treat the leak
| 02SL - Stations (LUL) | Cxxx-NCR-002430 | NCR | ETH - Level 0 Surface Cracks in Slab Area B2 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-02-10 | 2017-02-07 16:03 | -3 | 2016-10-25 08:30 | Civil - Civil Engineering General | 1000 |  | Material | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Following pouring of Area B2 Level 0 slab few surface cracks where noted, please see attached photos. Cracks are below 0.3mm permitted in specification.
| 02SL - Stations (LUL) | Cxxx-NCR-002431 | NCR | TUN - PLT - Areas of slab out of tolerance - Concourse and cross passages |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-12-08 | 2016-11-08 07:37 | -30 | 2016-10-27 15:40 | Civil - Civil Engineering General | 800 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The final as-builts for the concourse and cross passage tunnels are showing some points out of tolerance on level, tolerance being +/-10mm. The locations are shown in the document Cxxx--C-LRC-M123-50809 The extent is limited to small areas of slabs in various locations on average by 5-15mm, Use as-is is proposed based that any small discepancy in levels will be made up by the screeding
| 02SL - Stations (LUL) | Cxxx-NCR-002432 | NCR | ETH - L-6 OHLE room screed repair |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-12-16 | 2016-11-25 09:52 | -21 | 2016-10-31 13:50 | Architectural - Flooring | 2200 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | carried out a site inspection and found that the screeding in OHLE room by the doorway 7-ED30 was damaged.
| 02SL - Stations (LUL) | Cxxx-NCR-002433 | NCR | Silica aggregate used with epoxy not found in the MCR |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-12-23 | 2016-12-15 17:27 | -8 | 2016-11-10 11:43 | Architectural - Flooring | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | The information of the Silica aggregate used on site was not included in the epoxy MCR Cxxx--C-LRC-M123-50750 rev 1.0
| 02SL - Stations (LUL) | Cxxx-NCR-002434 | NCR | ETH - L-6 Platforms cupboards screeding steel mesh not installed as per ITP |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-10-26 | 2018-10-22 08:26 | -4 | 2016-11-10 11:50 | Architectural - Flooring | 2000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | and Crossail carried out a site inspection and found that the D49 steel mesh used for day joints in screed was installed in the lower third depth of screed, so it was not installed as per approved and current ITP Cxxx--X-ITP-M123-50009 Rev 2.0 (see sketch attached for location)
| 02SL - Stations (LUL) | Cxxx-NCR-002435 | NCR | ETH - L-6 Platforms cupboards - Incorrect installation of steel angle in a day joint |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-03-31 | 2017-03-23 14:56 | -8 | 2016-11-10 11:50 | Architectural - Flooring | 1500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | carried out a site inspection and as-built survey of the area screeded in L-6 Platforms FOSC cupboard and found that the steel angle was installed incorrectly.
| 02SL - Stations (LUL) | Cxxx-NCR-002436 | NCR | ETH - epoxy applied in HV transformer room II in L-6 before repairing damaged screed |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-12-08 | 2016-11-28 10:07 | -10 | 2016-11-10 11:52 | Architectural - Flooring | 500 |  | Incomplete Works | Use As-Is | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | __ applied epoxy in HV transformer room II in L-6 before repairing damaged screed (Cxxx-NCR-002289)
| 02SL - Stations (LUL) | Cxxx-NCR-002437 | NCR | ETH - Level L+2 - Extend of slab |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-06-09 | 2017-05-11 09:19 | -29 | 2016-10-31 14:24 | Civil - Civil Engineering General | 1500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Drawing Cxxx-SWN-S-DDD-M123_B-30251 C06 Detail B54 shows that between GL3.5 and 4 the Level L+2 slab extends 325mm east from GL D. have constructed the slab only flush with Beam 21 in that area (262.5mm east of GLD).
| 02SL - Stations (LUL) | Cxxx-NCR-002438 | NCR | ETH - Prototype Installation Without Approved MCRs |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-05-20 | 2017-06-08 14:18 | 19 | 2016-11-01 15:36 | Architectural - Finishes | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Works have started on the installation of the ETH internal cladding prototype without approved MCRs for all materials. The works include the prototype for the TYPE LIN-402 composite wall cladding. The following MCRs are still outstanding; Cxxx--A-LRC-M123-50059 Rev 1.0 - Lighting Box - Code 3 Cxxx--A-LRC-M123-50060 Rev 2.0 - CMS Freize Band Unit - Code 3 Cxxx--A-LRC-M123-50061 Rev 2.0 - Galvanised Powder Coated Support Brackets - Code 3 Cxxx--A-LRC-M123-50093 Rev 1.0 - CMS & Lighting Box Locks - Code 3 Cxxx--A-LRC-M123-50096 Rev 2.0 - Stainless Sheet Piano Hinge - Awaiting approval These MCRs are been through several iterations and we are in the process of addressing the comments from CRL. Several workshops and meetings have been held between CRL, and __ to agree and actions respolve issues with the outstanding MCRs. The works were delayed as long as possible without impacting on the programe to ensure the prototype is installed before starting the permanent works. Please note that fabrication of these items without approved MCRs is covered seperately under Cxxx-NCR-2343.
| 02SL - Stations (LUL) | Cxxx-NCR-002439 | NCR | WTH – Lower Apse – Minor concrete finish issues with pre-cast units |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-11-02 | 2018-11-02 16:58 | 0 | 2016-11-02 15:02 | Architectural - Ceilings & Soffits | 5500 |  | Manufacturing Defect | Repair | 3 (3-6k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Please see the attached photographic report detailing minor issues with the surface finish of some of the pre-cast diamond-shaped units that will form the Lower Apse Ceiling. There are 3 main issues: 1. Where the units have been rested on dimpled supports (photograph of typical dimpled support attached) there are some dimple marks on the soffit of the units. 2. There is a visible joint line on the vertical face of some of the pre-cast units. 3. There are excessive blowholes on some of the vertical faces of some of the pre-cast units. Note for items 2. And 3. Only the bottom 50mm of the vertical face will be visible. The top 50mm has been scabbled to form a key with the in-situ slab above the pre-cast units.
| 02SL - Stations (LUL) | Cxxx-NCR-002440 | NCR | ETH - L+1 Vent shaft - Fire protection coating - density tests |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-11-18 | 2016-11-09 11:35 | -9 | 2016-11-03 09:53 | Civil - Civil Engineering General | 1000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | During Level L+1 vent shaft fire protection coating works only 1 set of density checks (mixer slurry and wet nozzle density) - see thickness report for Level L+1 - was carried out per shift despite the __ Application Guide (Cxxx--A-RGN-M123-51105) asking for 2no of tests per shift (1no AM / 1no PM). However, all density testing values were compliant. The required frequency of testing was missed in Rev 1 of the ITP but has been amended in Rev 2. __ has subsequently carried out 2no of tests per shift (see attached quality reports for level L+3).
| 02SL - Stations (LUL) | Cxxx-NCR-002441 | NCR | MEP - PLT - Damage to Blockwork wall in FOSC 3 (ETH) |  | Contr | __ | FAR - Farringdon Station (West) |  | 2017-01-27 | 2016-12-19 11:19 | -39 | 2016-11-11 07:53 | Electrical - Lighting | 2000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | In line with CRL-OBS-12829 : This NCR is raised because of damaged caused by drilling through a blockwork WI lintel in FOSC 3 at the ETH. and The installation of the lighting without an accepted C status drawing or FCD.
| 02SL - Stations (LUL) | Cxxx-NCR-002442 | NCR | WTH – Failure to install DPM in Level -2 rooms |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-05-19 | 2017-04-28 14:11 | -21 | 2016-11-03 14:54 | Civil - Civil Engineering General | 3500 |  | Supervision/Management | Repair | 3 (3-6k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Section 5a of drawing Cxxx--A-DDD-M123_Z-75172 (C01) relates to F04 floor types, usually ground bearing slabs. Within this section, Section 9 of the same drawing is referenced with regards to the DPM location. DPM should be installed between the first and second course of blockwork on the internal walls. On Level -2 (drawing attached), this DPM was missed from some blockwork walls.
| 02SL - Stations (LUL) | Cxxx-NCR-002443 | NCR | ETH - ESS1/INS1 precast stairs cast without approved Concrete MCR |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-11-18 | 2016-11-17 15:53 | -1 | 2016-11-04 14:41 | Civil - Civil Engineering General | 1500 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | Quality team conducted an Audit on __ while they were manufacturing ESS1/INS1 precast stairs for Eastern Ticket Hall. Audit identified that __ had changed the admixture of the concrete mix from __ ViscoCrete to __ master Matrix 233. Thus leaving current Concrete MCR, __ Precast - In-house C40/50 Mix Cxxx--C-LRC-M123-50666, invalid.
| 02SL - Stations (LUL) | Cxxx-NCR-002444 | NCR | WTH - Lower Apse - Use of P status drawings for lower apse pre-cast units construction without minimum design assurance |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-11-25 | 2016-11-14 10:32 | -11 | 2016-11-07 13:31 | Civil - Civil Engineering General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | instructed __ to begin casting of the lower apse pre-cast units prior to being able to demonstrate the minimum assurance requirements for their drawings as defined in the ‘Minimum Assurance Requirements For Cxxx Drawings’ document (Cxxx--O-LRC-M123-50001). This was a necessary risk to facilitate achieving their contractual key dates for the Front of House handovers. This is a procedural NCR. These drawings were unchanged following completion of the minimum assurance processes so no units were incorrectly fabricated as a result of this procedural non-conformance. The drawing numbers are provided on the __ DRIR Cxxx--Y-LRG-M123-50003 referenced below.
| 02SL - Stations (LUL) | Cxxx-NCR-002445 | NCR | ETH-Trapezoidal Shaft-Damage to ESS1 Pre-Cast Stairs |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-02-23 | 2018-02-26 13:08 | 3 | 2016-11-07 14:35 | Civil - Civil Engineering General | 2500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | During the Installation of Pre-cast Concrete Stairs in the ESS1 Shaft there was minor damage to incurred whilst lifting and delivery of the various flights of stairs. These primarily were concrete chips to the nosing along the centre and at the sides along the strings (Please see photos attached). Also Precast Flight ESS1-F17 which goes from Level-6 (FFL 86.019) to the midlanding at FFL 88.404 on the South side of the shaft was installed to the incorrect finished floor level at the bottom of the stairs.
| 02SL - Stations (LUL) | Cxxx-NCR-002446 | NCR | WTH_Level +2 Upstand - Reduced Cover |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-12-02 | 2016-11-30 14:13 | -2 | 2016-11-11 13:43 | Civil - Civil Engineering General | 2500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A number of bars on WTH Level +2 upstand along GL B (north west) have reduced cover (20-30mm). Cover should be 40mm according to Cxxx-ATK-S-DWG-M123_B-50134 C01. Refer to sketch Cxxx--C-XSK-M123-50345 for cover survey.
| 02SL - Stations (LUL) | Cxxx-NCR-002447 | NCR | ETH - Type AHP-202 Wall Access Hatch Installation |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-05-12 | 2017-05-22 08:35 | 10 | 2016-11-08 12:25 | Architectural - Doors | 1000 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | We have started the installation of the TYPE AHP-202 Wall Access Hatches without all MCRs being approved. Specifically the outstanding MCR is for the powder coating product used on the hatches (Cxxx--X-LRC-M123-51090 - __ Powder Coating). __ Powder Coating product (BR103770G) has previously been approved for use by TubeLines but we are waiting for the fire engineer to confrm that the test results are compliant with the requirements of LU Standard 1-085 prior to submitting the document formally. The design drawing has been updated at short notice to clarify the use of __ as a packing material around the hatches. An FCD was not in place to allow works to start without approved drawings.
| 02SL - Stations (LUL) | Cxxx-NCR-002448 | NCR | ETH - Trapezoidal Shaft - Upstand cast without recess on GLD |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-08-15 | 2017-08-14 08:21 | -1 | 2016-11-08 13:50 | Civil - Civil Engineering General | 2500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | During the construction of the Level 0 upstand along GL D between GL 4 & 7' missed a number of pockets to be cast in. These pockets are shown on, Cxxx-ATK-S-DWG-M123_1-50126 C02 Cxxx-ATK-S-DWG-M123_1-50127 C02 Cxxx-ATK-S-DWG-M123_1-50144 C02 Cxxx-ATK-S-DWG-M123_1-50145 C02 As the Cxxx GA's were not updated to include these pockets, they were missed during construction. Please refer to the attached 'GA Marked location of the missing pockets' & 'RC Pocket Locations'.
| 02SL - Stations (LUL) | Cxxx-NCR-002449 | NCR | ETH - Building L-4 blockwork using P-status drawing |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-07-28 | 2017-07-26 11:47 | -2 | 2016-11-10 12:20 | Architectural - Masonary | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | In L-4 Eastern Ticket Hall, blockwork was built using P-status drawing (Cxxx--A-DDC-M123_5-26265 P09) without having an FCD approved.
| 02SL - Stations (LUL) | Cxxx-NCR-002450 | NCR | WTH - Lower Apse Ceiling damaged pre-cast concrete units delivered to site |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-04-07 | 2017-04-03 14:47 | -4 | 2016-11-15 09:01 | Civil - Civil Engineering General | 16000 |  | Damaged | Rework | 2 (6-60k) | Complete | Material/Preservation Problems - Improper handling of material | Completed |  | Please see the attached photographic report detailing the 2no. types of issues that have resulted in returning 8no. pre-cast units to __ (’s pre-cast concrete supplier).
| 02SL - Stations (LUL) | Cxxx-NCR-002451 | NCR | WTH Level -1 Wall Out of Vertical Tolerance Limits |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-12-09 | 2016-12-08 17:19 | -1 | 2016-11-14 11:28 | Civil - Civil Engineering General | 3500 |  | Workmanship | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On level -1 the wall to the south of Tunnel Side Attenuator Void (central void), and specifically the wall panel to the west of the concrete column (SC8) to the adjacent Wi Column (see attached marked-up drawing – circled section only 1m wide) has been checked and it is not plumb. At the top of the wall the blockwork is approximately 25mm out of its design plan position too far north. The ITP states a tolerance of +/-14mm. The bottom course has been checked and its position is correct (see photo attached).
| 02SL - Stations (LUL) | Cxxx-NCR-002452 | NCR | MEP - Vertical ductwork support spacing incorrect |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2017-04-14 | 2017-03-16 08:47 | -29 | 2016-11-14 17:00 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | Vertical ductwork supports installed in risers have not been installed in compliance with JY30.3102 aa) Supports for vertical ductwork in buildings shall be generally located at each floor slab but subject to a maximum spacing of 4 metres. Currently the supports are installed at min 5m intervals. Calculations proving support adequacy have not been provided to confirm 5 m is acceptable for the ductwork weight.
| 02SL - Stations (LUL) | Cxxx-NCR-002453 | NCR | WTH - Upper Apse - Appearance of Pre-cast Units |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-07-20 | 2018-07-19 10:24 | -1 | 2017-03-21 15:01 | Civil - Civil Engineering General | 17500 |  | Damaged | Repair | 2 (6-60k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Several Upper Apse pre-cast concrete units have been delivered to site with the following defects: - Dimple markings to face - Strap marks/chipping - Visible repairs This can be seen in the attached photo report.
| 02SL - Stations (LUL) | Cxxx-NCR-002454 | NCR | ETH - __ Pre-cast Stairs - Slump Flow Test not in compliance with the ITP. |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-01-30 | 2017-01-25 11:39 | -5 | 2016-12-05 12:33 | Civil - Structural Engineering | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | With reference to the __ Mix Design detailed in the MCR - Cxxx--C-LRC-M123-50666 Rev 2.0, the mix design shows the slump flow SF2 with 660mm to 750mm parameters, but the correct flow range is SF3 (760mm - 850mm). Also, the ITP - Cxxx--C-ITP-M123-50269 Rev 2.0 (ref 9b) shows the flow test requirement to be between 700mm & 800mm. Test carried out at the __ test lab recorded the flow test to be 780mm on __ Manufacturing Cube record sheet and also on __ test report. In factory next to the test area, the flow range was displayed as 720mm to 800mm.
| 02SL - Stations (LUL) | Cxxx-NCR-002455 | NCR | WTH – temporary hollowcore pre-cast concrete planks non-compliant with 2hr fire resistance requirements |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-07-28 | 2017-02-13 09:45 | -165 | 2016-11-17 08:46 | Fire - Compartmentation | 6500 |  | Design | Reject | 2 (6-60k) | Complete | Material/Preservation Problems - Other | Completed |  | The general arrangement drawings for level +2 and +3 of the WTH (B-80202 & C-80302) show voids that are to be covered by temporary pre-cast planks. These planks would then be removed by the OSD developer. The voids in question are highlighted on the attached mark-up versions of these drawings. Solid planks could not take the required loading/span without increasing their thickness – an increased thickness was proposed and rejected on Cxxx-FCD-001977. In the Cxxx response to this FCD they suggested the use of 200mm thick hollowcore planks. Cxxx-FCD-002075 was then raised to confirm acceptance of a hollowcore plank solution. The design package for the hollowcore planks, Cxxx--X-XCL-M123-54017 Rev 1.0, was returned Code 2 with a comment stating 2hrs fire resistance is required. (see comments sheet Cxxx--X-XCS-M123-50109 Rev 1.0). At this stage __ had already procured the hollowcore planks based on the acceptance of the MCR for the hollowcore planks (Cxxx--X-LRC-M123-51065 Rev 1.0). These have a fire resistance of 1hr as stated in the MCR.
| 02SL - Stations (LUL) | Cxxx-NCR-002456 | NCR | WTH – L-6 Eastbound Platform Mesh incorrectly installed at screed day joints |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-12-01 | 2017-10-05 11:00 | -57 | 2016-11-17 16:56 | Civil - Civil Engineering General | 1500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Cxxx--X-ITP-M123-50009 (Rev 2) Item 7.5 states that the mesh at day joints should be installed in the middle third of the screed On the Eastbound platform cupboards, see attached location sketch, the mesh has been installed in the bottom third of the screed (see attached photo). Other areas may be discovered where this has also occurred. If this happens, these will be raised on a separate NCR.
| 02SL - Stations (LUL) | Cxxx-NCR-002457 | NCR | ETH - L-7 screed cracks in the UPE corridor |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-07-06 | 2018-06-27 07:21 | -9 | 2016-11-21 13:58 | Architectural - Flooring | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | was carrying out a site inspection when found screed cracks at L-7 UPE corridor (see photos attached). Please note that the maximum size of the cracks observed is 0.5 mm
| 02SL - Stations (LUL) | Cxxx-NCR-002458 | NCR | WTH Level 0 Incomplete plinth pour |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-12-09 | 2016-11-29 12:28 | -10 | 2016-11-21 17:21 | Civil - Civil Engineering General | 1500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Insufficient quantity of material to do the job | Completed |  | On 13/09/2016 at level 0 around the Forced Air Damper WB Ventilation Fan there were 9 plinths ready to be poured. However, due to the high temperature (27 degrees) and the fact that the concrete had to be skipped to the area, the concrete lost its workability and blocked the chute when started pouring the first plinth. Consequently, the plinth to the north-west of the void on level 0 was left incomplete by about 50mm (attached marked up drawing and photo).
| 02SL - Stations (LUL) | Cxxx-NCR-002459 | NCR | WTH Failed Concrete Pre-Pour Inspections - Various Areas |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2017-02-24 | 2017-02-22 15:12 | -2 | 2016-11-23 11:50 | Civil - Civil Engineering General | 750 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | During w/c 14/11/2016, CRL were invited to attend several pre-pour inspections, and issues identified are listed below: 16/11/2016 Inspections: 1. SH-W1 L-1 sumps: loose nails within formwork & cleanliness of pour area required improvement. Refer to attached site photos. 2. SH-W1 L-5 plinths: gaps present in the metal upstand, with potential for grout to pour through these onto the level below. (Note access for pouring plinths was discussed with the workforce, as it was not deemed to be safe to be pouring through the handrails without any additional edge protection, e.g. harness & lanyard). Refer to attached site photos. 3. WTH L+2 upstand: Cxxx-NCR-002446 was still open at the time of the pour (still open at 23/11/2016), nails present in cover zone used to support the formwork and duct tape on reinforcement bars. Refer to attached site photos. 4. WTH L+3 upstand: nails present in cover zone used to support the formwork, tying wire off-cuts and loose screws in formwork area. Refer to attached site photos. 18/11/2016 Inspections: 1. WTH L+3 upstand: loose nails, tying wire & ply off-cuts in formwork. Duct tape on reinforcement. Refer to attached site photos. 2. SH-W2 L-8 plinths: a. No drawing revisions had been referenced on the pre-pour sheet. b. If ‘P’ revision drawings had been used, these needed to be complemented by an FCD accepting their use for construction. c. Cxxx-FCD-002460 referenced had not been issued or accepted by CRL. o Observation (i): Cxxx engineers need to sign and check each box on the checksheet, except those which are ‘N/A’. o Observation (ii): Cxxx engineers hadn’t referenced the drawing revision from which they extracted the details for their cover survey. 3. SH-W1 L-1 sumps: no issues. (Loose nails & cleanliness of pour area improved since last inspection on 16/11/2016). 4. SH-W1 L-4 plinths: a. No drawing revisions had been referenced on the pre-pour sheet. b. If ‘P’ revision drawings had been used, these needed to be complemented by an FCD accepting their use for construction. Refer to Minimum Assurance Requirements for Cxxx Drawings (CRL Document Number: Cxxx--O-LRC-M123-50001). o Observation: It was noted that __ tape had been installed on the external face of the metal upstand, but there were still a few gaps along the north end of the larger opening which CRL suggested were sealed to prevent grout runs. Refer to attached site photos. Cxxx are reminded that as a self-certifying organisation they should not be reliant on CRL picking up issues such as those outlined above. Refer to notes on Cxxx’s WTH Schedule of Nominated/Approved personnel (C453--C-LRC-M123-50683 Rev.1.0) – raised to eradicate these issues - which clearly state this. The junior members of the team should be given the necessary guidance to carry out these inspections in order ensure they have satisfied all requirements of pre-pour/pre-start inspections, prior to inviting CRL to witness theses. Note that as part of the ‘Corrective Action to Prevent Recurrence (Corrective Action)’ for Cxxx-NCR-002391 – ‘WTH – Level 0 Southern perimeter upstand pre-pour inspection completed unsatisfactorily’ – raised on 20/09/2016, Cxxx stated that ‘ will ensure future sign-off inspections are carried out by more than one engineer until we are confident all items are being identified and rectified prior to offering up the inspection to Crossrail. Better planning will allow time to carry out all checks.’ There is no evidence that this has happened since, e.g. recent Pre-Pour Sheets received have only been signed by the junior site engineers. CRL additionally note that C453--C-LRC-M123-50683 will need to be updated to capture all the current Cxxx WTH personnel (__ is not currently on this schedule) and remove the ones that have left (Jaime Sevilla).
| 02SL - Stations (LUL) | Cxxx-NCR-002460 | NCR | MEP - PLT - Drilling Through WI Column in ETH OHLE Room |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2017-02-17 | 2017-02-09 10:25 | -8 | 2016-11-23 17:00 | Electrical - Lighting | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | Further to Crossrail observation on 1 November where holes were drilled through blockwork lintels in FOSC 3 for lighting conduits, the same incidence has been observed in the adjacent OHLE room in ETH Level -5 on 15 November. The drilling has: 1) been performed through structural columns 2) caused blowouts of the blockwork, damaging __'s completed works 3) damaged mastic
| 02SL - Stations (LUL) | Cxxx-NCR-002461 | NCR | ETH - Installation of the composite panel cladding for the Prototype with P-status drawings without an FCD in place |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-01-27 | 2017-01-25 14:31 | -2 | 2016-12-14 09:01 | Architectural - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | Further to the surveillance (Cxxx--O4-RGN-M123-51454) carried out on the installation of the composite panel cladding for the Prototype, the P-status drawings were used for construction without an FCD in place.
| 02SL - Stations (LUL) | Cxxx-NCR-002462 | NCR | ETH – Trapezoidal Shaft – ESS2 As-built |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-01-27 | 2017-01-26 15:55 | -1 | 2016-11-28 13:06 | Civil - Civil Engineering General | 1500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Following as-built of ESS2 staircase, have identified that in a few locations staircase is outside the allowed tolerances. Slab level at 82.282 is at 82.294. +12mm outside limit of +10/-0 Slab level at 87.280 is at 87.291 +11mm outside limit of +10/-0 Position of Top step at Level 89.840mm is +23mm from design. Tolerance +20/-20 in plan
| 02SL - Stations (LUL) | Cxxx-NCR-002463 | NCR | WTH Level -2/-3 Lower step level Out of Tolerance |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2016-12-23 | 2016-12-14 09:59 | -9 | 2016-11-29 17:13 | Civil - Civil Engineering General | 1500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | A small set of steps exist between the landing at +102.600m SSL and the Level -2 slab (Level +103.230 FFL). The highest step that connects the landing and level -2 slab has been checked and it is 15mm lower than 103.230m FFL that it should be. Consequently, there is a 15mm level difference between the 103.230 FFL (screed level) on level -2 and the top of the step (see attached sketch and photo).
| 02SL - Stations (LUL) | Cxxx-NCR-002464 | NCR | WTH_MNS1 Staircase Concrete Finsih Defects on Level +1 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-03-31 | 2017-03-31 16:14 | 0 | 2016-12-02 11:42 | Civil - Civil Engineering General | 1500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | After striking the MNS1 Staircase formwork, from level 117.668 to 118.230, concrete finish defects - chipped corners and blowholes - were observed mainly on the side and corners of the steps (please see attached photos.)
| 02SL - Stations (LUL) | Cxxx-NCR-002465 | NCR | ETH - Barbican - 90 Day reinforced-concrete strength result lower than target compressive strength |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-03-31 | 2017-01-11 16:41 | -79 | 2016-12-05 13:57 | Civil - Civil Engineering General | 500 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | After crushing cubes for Barbican Station Pile Cap, it was found that the compressive strength did not reach the required strength as per Cxxx-SWN-C-RSP-M123-00004, Table KF10-01 concrete (Cxxx--C-LRC-M123-50318) . See attached Concrete Strengths showing test result.
| 02SL - Stations (LUL) | Cxxx-NCR-002466 | NCR | STW - MEP - Cable pulling commencement for submains |  | Contr | __ | FAR - Farringdon Station (West) |  | 2017-08-13 | 2017-06-07 08:35 | -67 | 2017-05-15 15:35 | Electrical - General | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | 4no. cables installed on incomplete cable containment into CER1 at WTH -1 and CER2 at ETH -4. See also CRL-OBS-13205
| 02SL - Stations (LUL) | Cxxx-NCR-002468 | NCR | WTH Cxxx-FCD-002407 not approved at the time of Fire Boarding Surveillance |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-01-20 | 2016-12-19 10:22 | -32 | 2016-12-12 10:18 | Architectural - General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | During Surveillance of WTH __/__ Fire Protection to Structural Steelwork (Cxxx--O4-RGN-M123-51456 Rev 1.0). It was observed had raised FCD (Cxxx-FCD-002407) to cover the use of drawing Cxxx--X-DWG-M123-54580 Rev P05 for construction purposes, in the absence of an accepted IFC drawing. This FCD was still open and not accepted at the time of this surveillance.
| 02SL - Stations (LUL) | Cxxx-NCR-002469 | NCR | ETH- Trapezoidal Shaft - Level 0 Slab - Cracking in Feature Soffit |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-03-03 | 2017-02-27 11:42 | -4 | 2016-12-06 17:26 | Civil - Civil Engineering General | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Following the level 0 area F slab gaining strength struck the falsework and within several hours cracks started appearing within an area of the 150mm thick suspended slab. Please see attached documents for the location of these cracks.
| 02SL - Stations (LUL) | Cxxx-NCR-002470 | NCR | WTH Signed Copy of Fire Boarding Benchmark MCR not available |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-02-27 | 2017-02-24 15:45 | -3 | 2016-12-20 11:26 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | During Surveillance WTH __/__ Fire Protection to Structural Steelwork(Cxxx--O4-RGN-M123-51456 Rev 1.0) it was observed that has produced the benchmark MCR and informally agree it with Crossrail, however it cannot be submitted officially until design is formally approved.
| 02SL - Stations (LUL) | Cxxx-NCR-002471 | NCR | MEP - Installation of Incorrect Fibre from FOSC3 to CER2 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-04-14 | 2017-04-10 15:49 | -4 | 2017-01-26 11:34 | Communications and Control Systems - Fibre Optic Network | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Material/Preservation Problems - Other | Completed |  | 2no. 12-core fibre optic cables have been installed from FOSC3 to CER2 instead of 2no. 24-core fibre cables. Following investigation, the cable drum was found to have been correctly marked as being for 24-core fibre, however had the incorrect cable on the drum.
| 02SL - Stations (LUL) | Cxxx-NCR-002473 | NCR | ETH - ESS5 Pre-cast stairs cast incorrectly |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-02-17 | 2017-01-25 12:10 | -23 | 2016-12-13 07:13 | Civil - Civil Engineering General | 10000 |  | Design | Rework | 2 (6-60k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | where due to install pre-cast stairs for ESS5, however on accepting delivery site team identified stairs where cast incorrectly. have conducted as-builts of mid-landing confirming they where constructed correctly to drawings and relevant RFI however __ drawings did not reflect this.
| 02SL - Stations (LUL) | Cxxx-NCR-002474 | NCR | ETH - Cracked joint between mastic and blockwork |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-04-28 | 2017-03-17 13:30 | -42 | 2016-12-09 13:53 | Architectural - Masonary | 1500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | and CRL carried out a site inspection and found that there are cracks in the joint between the blockwork and the mastic in various levels at ETH (see photos attached)
| 02SL - Stations (LUL) | Cxxx-NCR-002475 | NCR | MEP Access panels on ductwork systems not compliant |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2017-08-30 | 2017-08-31 08:24 | 1 | 2016-12-16 14:12 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Material | Repair | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | It has been observed throughout the site that the access panels installed on all ductwork systems are inconsistent with what has already been installed and agreed and the M&W Specification Cxxx--M-RSP-M123-50013 ver 3.0 JY30. 1402 g)i), 1415 sections i), l). The provision for access panels does not follow DW144 Part 7 Section 20 Table 20 and TR19 Section 3. Examples of inconsistencies: Where ductwork is to be insulated some panels have flanges to allow for insulation thickness and others do not. Some access panels have gasket material, ductwork on WTH -3 does not. They also do not have sealant around the edge adjoining to the duct. There is a mixture of ductwork where some have no retaining chain or cable, others have either. There have been two access panels damaged which have not been replaced in ETH -7.
| 02SL - Stations (LUL) | Cxxx-NCR-002476 | NCR | WTH – Upper Apse – Pre-Cast Beam PB17 Chipped Edge |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-01-20 | 2017-01-19 16:54 | -1 | 2016-12-09 15:58 | Architectural - Ceilings & Soffits | 1500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Pre-cast unit PB17 (highlighted in drawing below) for the upper apse has been damaged during installation. The area of damage (see attached photo) is required for a temporary support to be installed for structural steelwork installation.
| 02SL - Stations (LUL) | Cxxx-NCR-002477 | NCR | ETH-Hole through upstand L+3 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-02-03 | 2017-02-01 08:21 | -2 | 2016-12-12 14:31 | Civil - Civil Engineering General | 1500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the construction of the upstand south of GL3 at L+3, the 200W x 200H hole through the upstand wasn't not constructed as required by drawings Cxxx-SWN-S-DDA-M123_C-30302 and Cxxx-SWN-S-DDD-M123_B-30251. (see attached mark up drawings)
| 02SL - Stations (LUL) | Cxxx-NCR-002478 | NCR | ETH-Installation of Beam BEAM_B1 B10062 Level +0.5 Crash Deck Area 10 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-01-27 | 2017-01-24 17:37 | -3 | 2016-12-12 14:46 | Civil - Civil Engineering General | 4000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Previous Construction - Improper As Built | Completed |  | Beam B10062 not installed due to not being able to fit between beams FB10007 FAB-BEAM_B25 at GL4 and FB803 FAB-BEAM_B25 at GL3. The columns at GL3 and GL4 are already concrete encased and the space between the connection plates is 8.749m as built on site. The required distance according to the fabrication drawing is 8.758.
| 02SL - Stations (LUL) | Cxxx-NCR-002479 | NCR | WTH Level +3 exposed tying wire & cast-in nails |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-12-22 | 2017-12-15 13:06 | -7 | 2016-12-20 11:40 | Civil - Civil Engineering General | 2500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | a) After striking the level +3 slab shutters it was noted that some tie wire has been cast into the face of the slab and requires repair. b) As part of the shutter installation the shutters were nailed to the wall below. These nails need removing and the remaining holes repaired. See attached photographs.
| 02SL - Stations (LUL) | Cxxx-NCR-002480 | NCR | WTH Level -3 SHW2 Blockwork Cupboards Incorrectly Set out and Constructed |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-01-13 | 2017-01-05 16:34 | -8 | 2016-12-15 15:12 | Civil - Civil Engineering General | 1500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | On level -3 SHW2 there was a discrepancy between the __ and __ drawings regarding the setting out of the cupboards to the east of the level (see attached drawings). On __ drawing Cxxx--A-DDA-M123_3-76212 (P16) the setting out of the cupboards is not very clear as the dimension 2810mm refers to the distance between the north face of the south block wall to the middle of the WP01. However, the same dimension on the __ drawing Cxxx--X-DWG-M123_3-54110 [P7.0] refers to the distance between the north face of the south block wall to the north side of the southern cupboard block wall (see attached drawings) and is stated as 2810mm. The cupboards on level -3 SHW2 were built 100mm too far south compared to the __ drawing Cxxx--A-DDA-M123_3-76212 (P16). This position of the cupboards caused a clash between the southern corner of the cupboards and __’s services.
| 02SL - Stations (LUL) | Cxxx-NCR-002481 | NCR | MEP - Use of __ Cables prior to Full MCR Acceptance |  | Contr | __ | FAR - Farringdon Station (West) |  | 2017-03-17 | 2017-03-17 13:32 | 0 | 2016-12-21 12:54 | Electrical - Lighting | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | This NCR is raised following the installation of the __ Cables prior to Full MCR acceptance. The comment received on the MCR submission provided a conditional acceptance provided a proof of compliance to BS8519 and BS6387 is met and provided. With the cable being an Option 2 MCR'ed Material with compliance previously provided on other CRL projects and also communications from CEG Seng Ling to the manufacturer's on general acceptance, __ preceded in ordering the cable. The cable were delivered and installed as part of the PES and SLD (CER1 and 2) rooms installation. Acceptance of the CE Marking is pending on the basis of provision of the a CE Marking which is not a legal requirement until 1st July 2017.
| 02SL - Stations (LUL) | Cxxx-NCR-002482 | NCR | ETH - Level L +0.5 Mezzanine Slab - FB10007 Beam - Holes drilled in wrong locations |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-02-03 | 2017-01-26 11:36 | -8 | 2016-12-19 15:06 | Civil - Civil Engineering General | 2900 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In the Level L+0.5 Mezzanine Slab (GL3-4/A-B), the holes in beam FB10007 have been drilled 35mm too high (wrong distance from top flange) to connect beams U10010 and U10019. __ have raised internal NCR Cxxx-BST-S-NCR-M123-00063.
| 02SL - Stations (LUL) | Cxxx-NCR-002483 | NCR | ETH - Level -5 Service Riser Grid Flooring Steelwork - Incorrect Fabrication of Member E13 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-02-14 | 2017-01-10 10:58 | -35 | 2016-12-20 08:30 | Architectural - Flooring | 1000 |  | Manufacturing Defect | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | One of the end plates to member E13 has been welded to the PFC in the incorrect orientation. Please refer to the marked up drawings and photo attached for details (IMG_8769, Cxxx--X-DWG-M123_6-52030 and Cxxx--X-DWG-M123_7-52043).
| 02SL - Stations (LUL) | Cxxx-NCR-002484 | NCR | WTH - Column Encasements - Column 9G+3 misplaced cubes |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-01-20 | 2016-12-22 12:39 | -29 | 2016-12-20 08:24 | Civil - Civil Engineering General | 2500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Unavailability or inadequate M&TE | Completed |  | On the 15/10/16 column 9G was encased between L-1 and L0. The cubes taken during this pour have subsequently been misplaced with no record of cube tests being carried out.
| 02SL - Stations (LUL) | Cxxx-NCR-002485 | NCR | WTH Perimeter wall 43 infill voids part 1- Grout loss |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-12-21 | 2018-08-02 10:01 | -141 | 2016-12-21 10:00 | Civil - Civil Engineering General | 1500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | After striking the wall 43 infill shutters it was noted that some grout loss had occurred on the external face of one of the voids. This has left a small gap of about 20cm over the face of the infill (See attached photo). Due to access restrictions, because of the high voltage cables, the depth was not measured but is assumed to be over 15mm i.e. a deep repair requirement. This will be assessed when access is available.
| 02SL - Stations (LUL) | Cxxx-NCR-002486 | NCR | WTH_Level +1 Upper Mezzanine Slab 17mm out of position |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-02-24 | 2017-02-16 14:59 | -8 | 2017-01-09 09:01 | Civil - Civil Engineering General | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | The slab on Level +1 Upper Mezzanine east of the MNS1 stairs was cast 17mm off the required position (to the east), see sketch Cxxx--C-XSK-M123-50354 attached for details in position of the slab edge. The blockwork wall which sits on top of the slab was built according to the drawing dimensions (+3mm) and therefore it is overhanging by 20mm (see photo).
| 02SL - Stations (LUL) | Cxxx-NCR-002487 | NCR | WTH P Status Drawings used for Lower APSE |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-05-19 | 2017-04-24 09:18 | -25 | 2017-01-19 17:25 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | During Surveillance WTH Lower Apse Ceiling First Pour (Cxxx--O4-RGN-M123-51460 Rev 1.0) it was observed that were using the following P status drawings: Cxxx-ATK-S-DWG-M123_1-50148 Rev P01 Cxxx-ATK-S-DWG-M123_1-50147 Rev P02 Cxxx-ATK-S-DWG-M123_1-50146 Rev P05 Cxxx-ATK-S-DWG-M123_1-50134 Rev P09 The agreed procedure to allow use of P-status drawings for construction is to raise FCD demonstrating minimum drawing assurance has been met. Minimum assurance is defined in the matrix found in Cxxx--O-LRC-M123-50001 Rev. 2.0 (referenced below). In this instance FCD could not be raised as minimum assurance was not achieved. took the decision to proceed with construction of the lower apse at risk – this was done to mitigate delays to the WTH critical path caused by design issues with the Upper Apse.
| 02SL - Stations (LUL) | Cxxx-NCR-002488 | NCR | WTH L-1 FCU Room Plinth - 'Unapproved 'P' Status Drawing Used |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-02-24 | 2017-02-21 16:58 | -3 | 2016-12-21 16:53 | Architectural - Flooring | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | Plinth cast-in with unapproved 'P' status drawing in WTH Level -1 FCU room (see attached) .See attached pre-pour check sheet and sketches from __ which were used at the time of pouring the plinth.
| 02SL - Stations (LUL) | Cxxx-NCR-002489 | NCR | WTH SH-W2 Level -8 Installation of transformer columns, plinths and bituthene waterproofing detail without approved drawing in place |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-06-23 | 2017-06-20 08:51 | -3 | 2016-12-20 11:34 | Civil - Civil Engineering General | 1500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | In each transformer room on Level -8 of SH-W2 there were two columns to be installed. These columns were to support cables required for an SLD handover and will eventually form part of the staircase structure required under Cxxx-PMI-00671. These columns were installed without approved drawings in place. Applicable drawings are Cxxx--X-DWG-M123_Z-52028 C01), 52029 (C01) and 52039 (P01). The first two drawings were incorrectly given a C01 revision number when issued and they have not been through the approval process and the P01 revisions have been included in the reference document section of this NCR. These __ drawings were based on __ drawings Cxxx--A-DDA-M123_8-76224 (P17), Cxxx--A-DDB-M123_Z-75202 (P02) and Cxxx--A-DDB-M123_Z-75204 (P02). These columns are fixed to plinths cast on top of the SSL of Level -8 in accordance with drawing Cxxx--A-DDA-M123_8-76256 (P02). This drawing has not been through the approval process. A further detail installed on-site without an approved drawing in place is the installation of the holding down bolts. Drawing Cxxx--X-DWG-M123_Z-52023 (P01) contains information relating to the embedment depth and the resin type to be used. also applied a Bituthene LM (Cxxx--C-LRC-M123-50220 Rev 3) around the bolts cast into the plinths on Level -8. This detail was included on Section 7 of drawing Cxxx--A-DDD-M123_Z-75187 (P02) which had not gone through the approval process either. See attached photos showing the plinths cast and the columns installed.
| 02SL - Stations (LUL) | Cxxx-NCR-002490 | NCR | WTH - Additional hole drilled in beam web outside of parameters of Cxxx-FCD-002329 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-01-20 | 2017-01-06 13:48 | -14 | 2017-01-03 12:36 | Civil - Structural Engineering | 750 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | Cxxx-FCD-002329 was raised to agree the number, location, diameter and minimum spacings of the holes required in the lower apse encased structural steel beams for the conduit routes of the cast-in electrical items. This FCD stated a minimum spacing of 40mm diameter holes was 300mm c/c. A Engineer set out the positions of the holes to be drilled and briefed the driller on these positions. Once the driller had started, operatives from __ ( M&E subcontractor) began installing the conduit routes following directly behind the driller. To remove the need for additional bends in the conduit path, the __ operative asked if the driller could re-drill one of the beam webs with an additional 40mm diameter hole, 10mm East from the original hole. The hole locations are shown on the attached marked-up GA drawing. Without checking with a supervisor or engineer, the driller drilled the additional hole as requested by the __ operative. Please see attached photo showing the additional hole.
| 02SL - Stations (LUL) | Cxxx-NCR-002491 | NCR | WTH - Level -1/MEP Earthing Connection Damaged to Column R7 |  | Contr | 201068 | FAR - Farringdon Station (West) |  | 2017-06-19 | 2017-02-01 13:37 | -138 | 2016-12-21 17:42 | Civil - Civil Engineering General | 2000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | The earthing connection from the Furse plate cast into level -1 to the baseplate of column R7 has been damaged. See attached photo with location shown.
| 02SL - Stations (LUL) | Cxxx-NCR-002493 | NCR | ETH - CMS damaged in OHLE L-6 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-01-13 | 2016-12-21 11:25 | -23 | 2016-12-21 10:54 | Electrical - Cable Management | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper handling of material | Completed |  | __ was installing CMS at ETH L-6 OHLE room when a CMS tray was accidentally painted. __ tried to clean it but the galvanized surface of the tray was damaged, so they had to replace a small section of that material.
| 02SL - Stations (LUL) | Cxxx-NCR-002494 | NCR | MEP - ETH - Riser - Comms Trunking Modification |  | Contr | __ | FAR - Farringdon Station (West) |  | 2017-07-31 | 2017-06-19 08:15 | -42 | 2016-12-21 | Electrical - Cable Management | 2000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | This NCR is raised following the modification of the 4 Compartment Trunking to make a 2 Compartment Trunking. This was modified and installed in ETH Riser and CER2. The installation on CER2 has been reinstated to a non modified (correct) trunking.
| 02SL - Stations (LUL) | Cxxx-NCR-002495 | NCR | WTH – temporary hollowcore pre-cast planks poor concrete finish |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-03-03 | 2017-02-20 16:03 | -11 | 2017-02-14 14:35 | Civil - Civil Engineering General | 750 |  | Design | Reject | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | The general arrangement drawings for level +2 and +3 of the WTH (B-80202 & C-80302) show voids that are to be covered by temporary pre-cast planks. These planks would then be removed by the OSD developer. The voids in question are highlighted on the attached mark-up versions of these drawings. Cxxx-FCD-002075 was raised to alter the requirement for solid pre-cast planks to hollowcore planks (note solid planks could not take the required loading/span without increasing their thickness – an increased thickness was proposed and rejected on Cxxx-FCD-001977). When the hollowcore planks were delivered to site it was observed that the narrow and notched planks had some loose aggregate and uneven cut lines along the edges of the concrete. Please see the attached photographic report detailing this. Note please see attached signed QA sheet for the hollowcore units in question – this confirms that the units were inspected in accordance with __ Precast’s ISO 9001 accredited quality management system.
| 02SL - Stations (LUL) | Cxxx-NCR-002496 | NCR | WTH – Upper Apse – Misaligned lower level beams |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-01-20 | 2017-01-19 16:45 | -1 | 2016-12-22 13:05 | Civil - Civil Engineering General | 750 |  | Manufacturing Defect | Use As-Is | 4 (0.5-3k) | Complete | Previous Construction - Problems based on previous construction errors | Completed |  | The Upper Apse lower level beam connection to the GLG edge beams is using a cast-in socket in the edge beam and pre-drilled bracket cast into the beams. This connection detail can be seen in drawing Cxxx--Y-DWG-M123-50116 P13. When the bolt holes from the cast-in plate of PB21 were positioned against the corresponding cast-in anchors in EB10, the joints between the two units did not align. The adjacent PB25 is aligned correctly with EB9. The joint between EB9 and EB10 is as the design at 15mm. The joint between PB21 and PB25 is misaligned and is 30mm wide. See attached annotated photo showing the joint between these units. See attached extract from drawing Cxxx--Y-DWG-M123-50111 P15 showing the location of these units on the Upper Apse Ceiling.
| 02SL - Stations (LUL) | Cxxx-NCR-002497 | NCR | WTH – Upper Apse – Exposed tie wire tags |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-07-20 | 2018-07-20 10:17 | 0 | 2017-03-20 17:00 | Civil - Civil Engineering General | 5000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Upper Apse pre-cast panels were identified for installation via the use of tags that were secured using stainless steel tying wire that protrudes from the pre-cast concrete panels.
| 02SL - Stations (LUL) | Cxxx-NCR-002498 | NCR | WTH-Level -1 – Column GL 14-3m G and GL 13-3m G Exposed Rebar On Baseplate Recess |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-02-03 | 2017-02-01 13:43 | -2 | 2017-01-17 14:45 | Civil - Civil Engineering General | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Prior to the installation of the steelwork columns located at gridlines GL 14-3m G and GL 13-3m G, the survey carried out by the Steelwork Subcontractor’s engineer revealed that the recesses cast into the -1 slab for both had been cast too small for the installation for the relevant baseplate. See attached surveys showing the line of the concrete within the baseplates and how it clashes with the line of the baseplate. In order to install the columns, set out the perimeter of the baseplates on the recesses. Once set out operatives then broke out to the line, exposing the reinforcement in the recesses. See attached photos. Although reinforcement was only exposed on one side of the column recess at GL 14-3m G, the other sides of both recesses had to be trimmed back, eating into the cover zone. In order to install the column, set out the perimeter of the baseplate on the recess, once set out operatives then broke out to the line, exposing the reinforcement in the recess see attached photos.
| 02SL - Stations (LUL) | Cxxx-NCR-002499 | NCR | WTH – Upper Apse – Damage to pre-cast concrete units – Soffit only |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-07-20 | 2018-07-19 10:25 | -1 | 2017-03-20 17:48 | Civil - Civil Engineering General | 17500 |  | Damaged | Repair | 2 (6-60k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Several Upper Apse pre-cast panels have been damaged during installation. The full extent of the damage will not be known until the upper apse temporary deck is struck. Once upper apse temporary deck is fully struck a joint survey between CRL Architect/CRL FE//__ will take place to agree scope of repairs required. This can be seen in document Cxxx--C-RGN-M123-52192.
| 02SL - Stations (LUL) | Cxxx-NCR-002500 | NCR | WTH - Delaminated mastic in blockwork joints |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-09-28 | 2018-09-28 13:19 | 0 | 2017-03-16 17:14 | Civil - Civil Engineering General | 4500 |  | Supervision/Management | Rework | 3 (3-6k) | Complete | Material/Preservation Problems - Not Defined | Completed |  | In several instances, in varying locations on the West Ticket Hall, mastic installed at the head of a blockwork wall has started to delaminate. C144 mastic (Cxxx--C-LRC-M123-50609 Rev 2) was used and since installation small gaps are evident between the blockwork wall and the concrete soffit. The areas where this has occurred include ESS1/INS staircases and isolated areas within the circular shaft at the soffit of Level -4 slab and Level -6 of the square shaft in the ERR, see attached photos 'Cxxx-NCR-02500 Evidence of delamination (Updated)'.
| 02SL - Stations (LUL) | Cxxx-NCR-002501 | NCR | WTH - Level -1 & -3 Various Damage to Blockwork |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-03-31 | 2017-03-31 16:23 | 0 | 2017-01-04 17:30 | Civil - Civil Engineering General | 2000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | 1)On level -1 Circulation Area D (south of FAN1 room) several areas of blockwork damage have been identified which were caused by the movement of scissor lifts and materials by __ and __, working there at the same time for route completion (please see photos attached). 2) There is also damage to a blockwork buildershole edge identified in the east side of the FCR room on level -1 when different subcontractors were working in the room (please see photos attached). 3) A similar issue was raised on level -3 SHW2 in Circulation Area D (north face of the electrical risers) and DC (cupboards) where __, while drilling in the blockwork to install conduits, damaged the blockwork around the hole (please see photos attached).
| 02SL - Stations (LUL) | Cxxx-NCR-002502 | NCR | WTH - Level -1 Blockwork Construction - No Drawings/Checksheet in Place Prior to Commencing |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-03-31 | 2017-03-14 17:23 | -17 | 2016-12-22 11:28 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | In the afternoon of Friday 4/11/2016 Blockwork subcontractor (__) was offered the South Eastern corner area on Level -1 in order to start building the perimeter wall (see attached drawing). They completed the setting out of the first course which was checked by an engineer. On Saturday 5/11/2016 __ completed the first lift of blockwork. However, the necessary Pre-Construction Inspection checksheet had not been completed by until Monday 07/11/2016. Also, the __ General Arrangement Drawing that was used for the blockwork construction (Cxxx--A-DDA-M123_2-76209 P11) was a ‘P’ status drawing which should not be used for construction.
| 02SL - Stations (LUL) | Cxxx-NCR-002503 | NCR | WTH - Use of P status drawings for blockwork and plinth construction |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-07-21 | 2017-07-06 10:46 | -15 | 2017-02-22 14:56 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | Cxxx-NCR-002459 was raised regarding some failings with regards to pre-concrete inspections. One item raised was that there was no FCD covering the use of P-status drawings. The P status drawings referenced to the individual pours were: Level +3 upstand – no P status drawings used SH-W2 Level -8 plinths – Cxxx--A-DDD-M123_Z-75187 (P02), Cxxx--A-DDA-M123_8-76224 (P17) and Cxxx--S-DDD-M123_Z-70330 (P05) SH-W1 Level -1 Sumps – no P-status drawings used SH-W1 Level -4 Plinths – Cxxx--A-DDA-M123_5-76219 (P13) and Cxxx--S-DDD-M123_Z-70330 (P05)
| 02SL - Stations (LUL) | Cxxx-NCR-002505 | NCR | ETH ESS5 Damage staircases |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-08-25 | 2017-08-31 10:02 | 6 | 2017-01-04 12:49 | Civil - Civil Engineering General | 4250 |  | Workmanship | Repair | 3 (3-6k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | During the installation of the Pre-Cast concrete stairs in the ESS5 Shaft there was some minor damage whilst lifting and delivery of the various flights of stairs. The damage was primarily concrete chips to the nosing along the center and at the sides of the strings (Please see photos attached and snag list)
| 02SL - Stations (LUL) | Cxxx-NCR-002506 | NCR | MEP - PLT - Duct manufactured without stiffening flanges |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-04-07 | 2017-04-05 14:37 | -2 | 2017-03-09 16:56 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | 2no. items of duct from drawing Cxxx--M-DWG-M123_7-53031 have been manufactured and delivered to site without stiffening flanges. As these items are within the wall, and manufactured to HFS-CE-SID specification, they should have stiffeners within the walls.
| 02SL - Stations (LUL) | Cxxx-NCR-002508 | NCR | MEP - ETH -7: Damaged ductwork - Pressurisation & Smoke extract systems |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2017-04-28 | 2017-03-28 12:53 | -31 | 2017-01-06 15:38 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Previous Construction - Other | Completed |  | Ductwork located in ETH -7 Platform Smoke Ventilation room North Side has been following installation. The coating on the inside of one of the sections has been chemically burned, the remainder have suffered water damage to the galvanized coating. The duct sections need to be either replaced or repaired up to the same standard as the original installation prior to the damage.
| 02SL - Stations (LUL) | Cxxx-NCR-002509 | NCR | MEP - STW - No insulation blocks on duct hangers |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-05-12 | 2017-05-16 13:23 | 4 | 2017-01-11 15:46 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Insufficient surveillance of subcontractors | Completed |  | Crossrail have raised observations CRL-OBS-13673 with regards to no sufficient length allowance has being made on the duct support hangers to install an insulation block between the duct and the bracket. This is not in compliance with clause JY50.1307 d) of document "Cxxx Farringdon Station – Mechanical Particular and M&W Specification" (Cxxx--M-RSP-M123-50013 [3.0]) as detailed within the "Technical Requirements" field.
| 02SL - Stations (LUL) | Cxxx-NCR-002510 | NCR | WTH – Column Encasement – 28-day Cube Strengths not Achieved for Columns11F Level +1 Lower; 9G Levels 0 & +2 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-01-24 | 2017-01-12 16:09 | -12 | 2017-01-10 15:07 | Civil - Civil Engineering General | 2000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Not Defined | Completed |  | had a series of concrete pours on 25/08/2016 for Columns 9G (Level 0) and 11F (Level +1 Lower); 31/08/2016 for Column 9G (Level +2). See attached plan showing locations of columns on site. These were all done with C1/C2 (10mm) mix, designed to reach C50/60 compressive strength within 28 days. Cubes were taken at a rate of 6 per 50m^3. See attached cube results for each pour. A Summary of the 28-day results are below: Columns cast 25/08/16 – 55.1 & 54.1 N/mm² Columns cast 31/08/16 – 53.2 & 52.4 N/mm² Concrete strength of 60 N/mm² has not been achieved with 28 days. See attached BS EN 206 compliance table The 56 day results show that the strength has been achieved in this time for both pours.
| 02SL - Stations (LUL) | Cxxx-NCR-002511 | NCR | MEP - PLT - Support of DW144 ductwork on fire rated brackets |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-03-24 | 2017-03-07 13:09 | -17 | 2017-02-22 15:33 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Insufficient information made available to the worker. | Completed |  | Crossrail have raised an observation (CRL-OBS-13709) relating to the general DW/144 ventilation ductwork (CRL-MCR-003174, CRL-MCR-003175) being installed on the same brackets as the CE-marked fire-rated ductwork (CRL-MCR-003155). No (RIBA F or fabrication) design detail has been produced and accepted for this, and the Hargreaves CE-marked fire-rated duct (CRL-MCR-003155) has not been tested and certified to be installed in this manner.
| 02SL - Stations (LUL) | Cxxx-NCR-002512 | NCR | MEP - STW - Protruding Trunking Screws |  | Contr | __ | FAR - Farringdon Station (West) |  | 2017-05-26 | 2017-05-15 14:04 | -11 | 2017-01-16 09:53 | Electrical - Cable Management | 500 |  | Manufacturing Defect | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | This NCR is raised following the installation of Trunking and Trunking couplers connected with screws which protrudes into the external compartments of Trunkings, an arrangement that is not in compliance with the specification (refer to "Technical Requirements" field for further details). The Trunking and associated screws are installed as per the manufacturer's detail via the materials compliance process (refer to accepted CRL-MCR-002661 for further details), as well as in accordance with the associated accepted benchmark (refer to Cxxx--E-RGN-M123-50881 for further details).
| 02SL - Stations (LUL) | Cxxx-NCR-002514 | NCR | ETH - L-5 Electrical riser missing blockwork |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-02-18 | 2017-02-09 11:03 | -9 | 2017-01-21 14:33 | Architectural - Brickworks/Blockworks | 1500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | During a site walk it was identified that a section of blockwork highlighted on the attached drawing within Level -5 electrical riser was not built.
| 02SL - Stations (LUL) | Cxxx-NCR-002515 | NCR | ETH - L-6 drainage installed without approved design |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-03-25 | 2017-03-17 12:23 | -8 | 2017-01-23 14:04 | Architectural - Masonary | 2000 |  | Incorrect Installation | Reject | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Drainage pipe in ESS1/INS1 L-6 east midlanding was installed without approved design (please find attached photo)
| 02SL - Stations (LUL) | Cxxx-NCR-002516 | NCR | STW - MEP - Non-Compliant Fire-Mains pipework installation |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-03-08 | 2017-03-03 10:19 | -5 | 2017-02-22 15:59 | Materials - Approval | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Not Defined | Completed |  | __/__have installed fire-mains pipework station-wide under CRL-MCR-002888, although this MCR is currently accepted via Cxxx-FCD-002046 to only cover platform inverts installation.
| 02SL - Stations (LUL) | Cxxx-NCR-002517 | NCR | ETH - Syphonic drainage outlets missed in the Level L+1 slab |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-04-21 | 2017-03-30 15:04 | -22 | 2017-01-24 16:38 | Civil - Concrete Pavement | 2500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Cxxx--P-DDA-M123_A-25210 C01 showes 2no syphonic drainage outlets from the Level L+1 slab (see marked up drawing between GL A and B) which have not been included in the slab construction. The outlets between GL B and C will be included in the relevant slab construction.
| 02SL - Stations (LUL) | Cxxx-NCR-002518 | NCR | ETH - L-7 ESS1 DPC installed incorrectly |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-03-17 | 2017-03-17 15:41 | 0 | 2017-02-01 10:43 | Architectural - Masonary | 2200 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | During the construction of the blockwork wall at L-7 ESS1 __ incorrectly installed DPC providing only a 15-20mm overlap between DPC sheets when a 100mm minimum overlap is required. Additionally, a 5mm projection on the face of the blockwork was not provided.
| 02SL - Stations (LUL) | Cxxx-NCR-002519 | NCR | WTH - Truss 1 Baseplate Clash With Column Bracket Weld |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-02-22 | 2017-02-06 15:40 | -16 | 2017-01-25 15:56 | Civil - Structural Engineering | 3750 |  | Manufacturing Defect | Repair | 3 (3-6k) | Complete | Previous Construction - Problems based on previous construction errors | Completed |  | On installation of the Southern section of truss T1 (member TR12003) it was found that the baseplate of the truss clashed with a weld on the shelf bracket of the connecting column (member FC4001). This is shown on the marked-up version of drawing ’Cxxx--X-DWG-M123-50097 C3.0’. This was due to the amount of weld ‘laid’ (i.e weld was slightly oversized compared to design-specified size). __ consulted their design department and the site team and it was agreed that, subject to the submission of supporting calculations and an email from the __ Designer, __ were to grind a 50mm chamfer into the baseplate of the stub column. The email from the __ Designer is attached. The calculations justifying the chamfer (and showing complete as-built dimensions of the chamfer) are attached below. Due to the restricted time period __ had the 350te mobile crane onsite, these works were carried out without first agreeing the remedial works with CRL or Cxxx.
| 02SL - Stations (LUL) | Cxxx-NCR-002520 | NCR | WTH – Temporary removal of stiffener in Area 12 beam FB12004 to allow installation of connecting beam FB12002 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-02-24 | 2017-02-24 12:44 | 0 | 2017-01-25 16:21 | Civil - Structural Engineering | 3750 |  | Design | Repair | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | In order to install the beam FB12002 highlighted on the attached __ Area 12 GA drawing (Cxxx--X-DWG-M123-50202 C1.0 - marked up) a stiffener had to be site-removed from the South side of the web of beam FB12004 – this beam is also highlighted on the attached drawing. This is because to install the beam FB12002 it is lowered in horizontally at a skewed angle relative to GL K. It is then rotated into position but in this instance this was not possible as it clashed with the stiffener in beam FB12004. The stiffener that was cut out onsite is highlighted on the attached extract from __’s Area 12 fabrication drawings (Cxxx--X-DWG-M123-50204 C1.0 - Extract of FB12004) Due to the need to install FB12002 with the 350te mobile crane and its restricted time onsite, the stiffener was removed without prior acceptance from CRL. Email confirmation of acceptance from a __ Designer and verbal confirmation from the Package Manager was provided prior to the works being carried out.
| 02SL - Stations (LUL) | Cxxx-NCR-002521 | NCR | STW - MEP - Non-Compliant Fire Mains Pipework material |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-05-21 | 2017-05-17 13:52 | -4 | 2017-02-21 17:36 | Materials - Approval | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | __/__have delivered onsite and installed fire-mains pipework, that did not have an accepted MCR.
| 02SL - Stations (LUL) | Cxxx-NCR-002522 | NCR | WTH – Erection sequence error for Upper Apse structural steelwork |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-02-24 | 2017-02-24 13:21 | 0 | 2017-01-25 16:41 | Structural Engineering - Steel Member | 4250 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | __ installed Beam FB12003 (highlighted on the attached marked-up version of __ Area 12 GA drawing Cxxx--X-DWG-M123-50202 C1.0) before installing the L16 bracket that connects the underside of this beam to the pre-cast member of the Upper Apse (highlighted on the attached marked-up version of __ drawing Cxxx--Y-DWG-M123-50115 P15) The nature of this connection (the top bracket ‘oversized’ RHS sliding over the top of the cast-in RHS protruding from the pre-cast) meant that this bracket could not be installed after FB12003 was in position. It was not possible to remove beam FB12003 to install the bracket as the 350te mobile crane had begun de-rigging when the error in the erection sequence was identified. The beam was too heavy to lift with the tower crane. __ cut out the Southern face of the RHS to allow it to be installed (i.e. ‘slid in’) underneath FB12003. The Southern face of the RHS will then be site-welded back onto the RHS with a full penetration butt weld. Please see the attached site photograph showing the L16 bracket with the Southern face of the RHS removed. The site-welded area will then be re-painted. All welding and painting works will be carried out in accordance with __’s accepted ITPs: Fabrication & welding - Cxxx--X-ITP-M123-50001 rev. 3.0 Painting - Cxxx--X-ITP-M123-50003 rev. 4.0
| 02SL - Stations (LUL) | Cxxx-NCR-002523 | NCR | ETH - Plastic Polythene not laid by __ after screeding at Eastbound Platform |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-03-03 | 2017-03-03 15:53 | 0 | 2017-02-01 13:00 | Architectural - Flooring | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | __ did not lay plastic polythene over the screed the following day after screeding L-7 UPE area (see highlighted drawing) as per ITP Cxxx--X-ITP-M123-50009 Rev 3.0 activity 7.6
| 02SL - Stations (LUL) | Cxxx-NCR-002524 | NCR | WTH - Upper Apse - Cracking of Primary Beams Around Nodal Brackets & Misaligned sockets |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-04-07 | 2017-03-31 16:31 | -7 | 2017-02-15 13:51 | Civil - Civil Engineering General | 7500 |  | Design | Repair | 2 (6-60k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The Upper Apse pre-cast nodal units located along GL H are connected to their adjacent pre-cast primary beam units with a steel bracket and anchor detail. Damage to Primary Beams: Due to blast loading requirements, the connection detail between nodal unit and primary beam was updated. This updated detail is shown on drawings: 7056-MU-FD-030-C1, 7056-MU-FD-031-C1, 7056-MU-FD-032-C1, 7056-MU-FD-033-C1 & 7056-MU-FD-034-C1. This detail required post fix anchors as the primary beams had already been cast. The details included three additional mechanical expansion anchors in each bracket, which are detailed under note “3No Hitlti HSL-3 M20/30 Anchors”. The locations of these anchors are shown on Cxxx--Y-DWG-M123-50122 (Rev 15.0). When these expansion anchors were tightened and torqued to their design value, this caused the pre-cast primary beam units to crack. Cracking was observed on PB15, PB16, PB17, PB18, PB19, PB20 & PB22. The locations and extent of damage can be seen on the attached survey “Summary of Nodal Connection Cracking”. The anchors connecting to PB21 were not torqued to the design value during installation. do not intend to attempt this design torque value in order to avoid possible cracking in this beam. This beam will therefore also be included in the repair detail. Misaligned M10 Sockets: On two of the nodal brackets the slots for M10 bolt connection are not aligning with the cast in sockets within the pre-cast nodal pieces. This has occurred on the bracket connecting PB8 to PB13 and PB18 to PB11.
| 02SL - Stations (LUL) | Cxxx-NCR-002525 | NCR | ETH - Level L+1 Connection of C-channel to Column A/4 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-03-24 | 2017-03-22 15:28 | -2 | 2017-02-06 15:13 | Civil - Civil Engineering General | 5300 |  | Supervision/Management | Repair | 3 (3-6k) | Complete | Management Problem - Inadequate supervision | Completed |  | The connection between C-channel U9004 and the concrete encased column at GL A/4 at Level L+1 can not be carried out as designed since the column including the holes required for the connections were concreted in during the construction of the concrete encased beam GL A/3-4 at Level L+1.
| 02SL - Stations (LUL) | Cxxx-NCR-002526 | NCR | Non Conforming Basket Tray |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2017-03-17 | 2017-03-06 18:11 | -11 | 2017-02-08 14:39 | Electrical - Cable Management | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Inspection points not adequate | Completed |  | CER1 Basket tray has been installed but it is not mentioned in either ITP or Method Statement
| 02SL - Stations (LUL) | Cxxx-NCR-002527 | NCR | ETH - L+1 Opening south of GL6 Vent Shaft |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-06-23 | 2017-06-22 16:20 | -1 | 2017-02-08 17:00 | Civil - Civil Engineering General | 4000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Opening on L+1 south of GL6 (2800x1700mm) not built to correct dimensions. The width of the void is too small measuring 1674mm as opposed to 1700mm (see attached as built)
| 02SL - Stations (LUL) | Cxxx-NCR-002528 | NCR | ETH - Level L+1 temporary roof - steel members require changes |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-03-24 | 2017-03-22 15:31 | -2 | 2017-02-10 17:05 | Civil - Civil Engineering General | 4250 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 3no of structural steel members had to be amended on the temporary roof at Level L+1. B10005 and B10105 were slightly too long and had to be shortened. Cxxx11 had a baseplate with the wrong orientation. See attached drawing Cxxx--X-DWG-M123-50307 C01 marked up for the location of the single members. __ has raised an internal NCR about this (NCR-071 and NCR-072).
| 02SL - Stations (LUL) | Cxxx-NCR-002529 | NCR | ETH - Plastic Polythene not laid by __ after screeding at Eastbound Platform |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-03-24 | 2017-03-03 15:42 | -21 | 2017-02-10 17:30 | Architectural - Flooring | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | __ did not lay plastic polythene over the screed the following day after screeding Eastbound Platform as per ITP Cxxx--X-ITP-M123-50009 Rev 3.0 activity 7.6
| 02SL - Stations (LUL) | Cxxx-NCR-002530 | NCR | ETH - L-6 BOH platform area - Scaffold cast in screed |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-03-17 | 2017-03-15 08:35 | -2 | 2017-02-10 17:34 | Architectural - Flooring | 2500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | It was identified that a scaffold tube has been cast in within a screed pour at L-6 ETH BOH platform level shown in the location highlighted in the attached drawing.
| 02SL - Stations (LUL) | Cxxx-NCR-002531 | NCR | ETH - L-5 Electrical riser unprotected completed work |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-03-03 | 2017-02-23 10:30 | -8 | 2017-02-10 17:53 | Architectural - General | 1700 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | Further to NCR Cxxx-NCR-002514, and to enable our blockwork contractor to build the blockwall within the riser. A section of CMS was removed by the electrical contractor to erect a scaffold in order to enable the completion of the final lift. During this operation, the CMS was damaged while stored on the scaffold please see photo 1 and there could be a potential damage to the cable due to close proximity of the scaffold board see photo 2. Note that the cable wasn't stretched and it is not tested yet to confirm if damage have occurred.
| 02SL - Stations (LUL) | Cxxx-NCR-002532 | NCR | ETH - L-6 Channel construction without approved design |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-06-02 | 2017-06-02 15:24 | 0 | 2017-02-13 07:58 | Civil - Drainage | 3500 |  | Incorrect Installation | Use As-Is | 3 (3-6k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | Following Cxxx-NCR-002515, Drainage channel in ESS1/INS1 L-6 east midlanding was installed without approved design (please find attached photo)
| 02SL - Stations (LUL) | Cxxx-NCR-002533 | NCR | WTH Level -1 Southern Pilecap Excess Cover |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-03-03 | 2017-02-15 11:34 | -16 | 2017-02-14 14:03 | Civil - Civil Engineering General | 2500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Previous Construction - Interfacing issues | Completed |  | Cxxx-FCD-000974 states that concrete members greater than 2m in depth can have cover up to +72.5mm (assuming 50mm cover). The Level -1 Southern pilecap to SH-W2 is 2.5m in depth. In some areas of the top mat there was cover of up to 80mm. In these areas A393 mesh was added to reduce the cover to allowable limits (maximum 60mm). See attached drawings showing the location of the mesh.
| 02SL - Stations (LUL) | Cxxx-NCR-002534 | NCR | WTH Level -1 Markings on blockwork walls in FAN 1 room |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-07-14 | 2017-06-26 10:41 | -18 | 2017-02-20 12:15 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | On the Eastern wall of the FAN1 room on Level -1, permanent marker has been used to indicate where a blockwork wall penetration is required. These markings have been done outside of the actual penetration location and so once this is formed, the markings will still be visible. This is illustrated in NCR attachment 'Cxxx-NCR-002534'.
| 02SL - Stations (LUL) | Cxxx-NCR-002535 | NCR | ETH - Earthing connection Level 0 slab GL1B' |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-04-07 | 2017-03-30 08:29 | -8 | 2017-02-23 15:06 | Electrical - Lighting | 1500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Earthing connection DC9 (GL 1B') on capping beam at Level 0 has been installed too low therefore it is not possible for __ to complete the connection up to level +1 (Refer to Cxxx--E-DDD-M123_Z-25705 for earthing connections at Level 0)
| 02SL - Stations (LUL) | Cxxx-NCR-002536 | NCR | WTH Level +2 upstand reinforcement cast in incorrect position |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-03-31 | 2017-03-20 11:54 | -11 | 2017-02-22 11:31 | Civil - Civil Engineering General | 750 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Previous Construction - Problems based on previous construction errors | Completed |  | On level +2 in drawing Cxxx-SWN-S-DDA-M123_B-80202 C08 the setting out of the upstand connecting walls 50&51 (to the western side) is not very clear and was considered to be flush to the edge of the void (see attached marked-up drawing) when the rebar was cast-in. However, has now realised that the eastern face of the upstand is positioned 30mm from the edge of the void. Consequently, the rebar is cast in the wrong position. In the architectural drawing Cxxx--A-DDA-M123_B-76209 (P15) a double skin blockwork wall (245mm wide) is indicated above this upstand.
| 02SL - Stations (LUL) | Cxxx-NCR-002538 | NCR | WTH - Blockwork wall built in the wrong position and NCR procedure not followed |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-06-16 | 2017-06-12 13:46 | -4 | 2017-02-27 18:37 | Architectural - General | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 1. Blockwork wall highlighted on the attachment was built in the wrong place. 2. Additionally, did not follow the normal procedure and reconstruction of the wall was carried out without NCR being raised and accepted first.
| 02SL - Stations (LUL) | Cxxx-NCR-002539 | NCR | WTH - Level -1 slab damaged (OSD basement) |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-04-07 | 2017-04-07 07:20 | 0 | 2017-02-28 15:57 | Civil - Civil Engineering General | 3750 |  | Damaged | Repair | 3 (3-6k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | 1. Concrete protective layer on level -1 (OSD basement area) highlighted in blue on the attachment (Extension of concrete protective layer removed) was demolished as per Cxxx--C-RGN-M123-52139 Rev1, using a 5T excavator. During this activity the slab underneath concrete protective layer was damaged. 2. NCR procedure not followed. The damage started to be protected before the NCR was issued and accepted.
| 02SL - Stations (LUL) | Cxxx-NCR-002540 | NCR | WTH – Blockwork Head Detail - Mastic Thickness Exceeding Maximum Permitted 40mm |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-09-29 | 2017-09-26 14:18 | -3 | 2017-03-10 09:07 | Architectural - General | 3250 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In 2 locations highlighted in the attached document (Cxxx--X-DWG-M123_6-54104 marked-up) mastic is exceeding 40mm limit determined by __ detail stated in Cxxx-FCD-002553. Full survey to be carried out when blockwork walls are signed off to confirm there is no more locations where mastic thickness exceed 40mm (maximum permitted). If new location are found, they will be incorporated to this NCR.
| 02SL - Stations (LUL) | Cxxx-NCR-002541 | NCR | TUN - BUI - Unauthorised Removal of Drop Rods to BOH Ducting |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-04-06 | 2017-03-14 07:56 | -23 | 2017-03-09 12:19 | Tunnelling - Tunnelling General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | On the night shift of the 24th of February, during the installation of the temporary hoardings in the back of house areas as stipulated in PMI 784, a operative removed two of the drop rods holding up the ductwork in this area. Please see attached photo and sketch showing the location. The drop rods were replaced on the 28th of February once they were noticed to be missing.
| 02SL - Stations (LUL) | Cxxx-NCR-002542 | NCR | WTH Level +1 Upper Mezzanine plinth cast in incorrect position |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-04-28 | 2017-03-31 12:33 | -28 | 2017-03-16 09:25 | Civil - Civil Engineering General | 750 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | On level +1 upper mezzanine the plinth to the north east corner of the FAN Isolation Damper Void (see attached marked-up drawing) was cast in incorrect position. Cxxx have to install a column on top of the plinth and the fixings of the column do not have the required distance to the edge of the plinth.
| 02SL - Stations (LUL) | Cxxx-NCR-002544 | NCR | ETH - Installation of the Mastic at Level-1 with P-status drawing without an FCD in place |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-04-28 | 2017-04-25 15:34 | -3 | 2017-03-07 16:58 | Architectural - Brickworks/Blockworks | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Further to the surveillance (Cxxx--O4-RGN-M123-51469) carried out on the installation of the mastic at Level -1, the P-status drawing (Cxxx--X-DWG-M123_2-54016 P09) was used for construction without an FCD in place.
| 02SL - Stations (LUL) | Cxxx-NCR-002545 | NCR | WTH - Lower Apse pre-cast plank damage during striking works |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-11-02 | 2018-11-02 16:59 | 0 | 2017-03-06 13:06 | Civil - Structural Engineering | 9500 |  | Damaged | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the striking works of the Lower Apse temporary deck, damage was done to corners and edges of multiple pre-cast planks. This damage was primarily chipping of concrete, ranging from 5mm to 70mm in size. There were also areas of irregularities within the in-situ channels that also need repairing. A joint /CRL inspection was carried out ( attendee was __, CRL attendees were Chrys Chimmarides and __). The agreed remedials were compiled in the post-striking report Cxxx--C-RGN-M123-52197 Rev 1.0 (referenced below). This report has been accepted Code 1 by Crossrail.
| 02SL - Stations (LUL) | Cxxx-NCR-002546 | NCR | STW No __ Benchmark not in Place Prior to Commencing Works |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2017-05-26 | 2017-05-24 10:20 | -2 | 2017-03-07 09:17 | Architectural - General | 2000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | A planned Crossrail surveillance was undertaken on 3rd March 2017 to look at Fire Stopping installation being carried out by __, it was found that the Contractor has progressed with the installation of __ cladding without an accepted Benchmark in place.
| 02SL - Stations (LUL) | Cxxx-NCR-002548 | NCR | STW Fire Protection Material Samples not in Place Prior to Commencing Works |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2017-05-26 | 2017-05-24 10:21 | -2 | 2017-03-07 09:40 | Architectural - General | 2000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | A planned Crossrail surveillance was undertaken on 3rd March 2017 to look at Fire Stopping installation being carried out by __, It was found that the Contractor has not provided Samples of the materials that are in use for the Fire and acoustic cladding in line with the requirements of the Architectural Specification Cxxx--A-RSP-M123-50057 - Rev 15 JA.4008 Post Contract Samples
| 02SL - Stations (LUL) | Cxxx-NCR-002549 | NCR | WTH Level -1 Waterproofing detail along Gridline K not installed |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-08-18 | 2017-07-27 12:55 | -22 | 2017-03-07 15:56 | Civil - Civil Engineering General | 4000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | completed blockwork on the Southern portion of Gridline K between Level -1 and the soffit of Level 0 (see attached sketch). After completing this section of works the WTH team were made aware of drawing Cxxx--A-DDD-M123_Z-75633 (C01) which shows a waterproofing detail which has not been installed.
| 02SL - Stations (LUL) | Cxxx-NCR-002550 | NCR | MEP - WTH - Level -5 - Wiring in uncleaned Trunking |  | Contr | __ | FAR - Farringdon Station (West) |  | 2017-03-31 | 2017-03-27 13:08 | -4 | 2017-03-14 11:29 | Electrical - Cable Management | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | This NCR is raised against wiring in uncleaned trunking. The trunking was clean at the time of installation however, some builders works has happened following cables install which has caused debris and dust to get in the trunking.
| 02SL - Stations (LUL) | Cxxx-NCR-002551 | NCR | WTH - L0 Steelwork Firecoating Damaged |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-08-25 | 2017-08-23 13:03 | -2 | 2017-03-16 10:04 | Architectural - General | 2500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | Concrete protective layer on level -1 (OSD basement area) highlighted in blue on the attachment (Extension of concrete protective layer removed) was demolished as per Cxxx--C-RGN-M123-52139 Rev1, using a 5T excavator. During this activity steelwork above (Level 0) was damaged. Please find attached snagging list
| 02SL - Stations (LUL) | Cxxx-NCR-002552 | NCR | WTH_Level +3 Upstand Concrete Finish Defects |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-07-27 | 2018-08-03 13:42 | 7 | 2017-03-16 15:34 | Civil - Civil Engineering General | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 1. When WTH Level +3 upstands were being cast, there were no chamfers installed as per C8 requirement of the General Note drawing Cxxx-SWN-S-DDL-M123_Z-00101 C05. 2. After striking the upstand formwork, defects (chipped corners) in the concrete finish were observed mainly in the outer face of the upstands. Please see WTH Level +3 Upstand Defects.pdf attached.
| 02SL - Stations (LUL) | Cxxx-NCR-002553 | NCR | TUN - BUI - MCR for D49 Mesh not accepted before starting works |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-06-30 | 2017-06-29 13:44 | -1 | 2017-03-17 09:30 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | __ started work on the front of house screeding without the acceptance of MCR Cxxx--X-LRC-M123-51105 for Hyten D49 Mesh. Subsequently, the MCR has been returned code 3 due to a number of typographical errors on the MCR (Cxxx-SCM-01014).
| 02SL - Stations (LUL) | Cxxx-NCR-002554 | NCR | WTH L-1 South-East Corner Damage to Drainage |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-06-30 | 2017-05-08 12:33 | -53 | 2017-03-17 11:57 | Civil - Civil Engineering General | 750 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | A drainage gully cast into level -1 was damaged during works in this area. The damage and location is shown in the attachment.
| 02SL - Stations (LUL) | Cxxx-NCR-002555 | NCR | ETH - Spray waterproofing Level +3 unapproved material. |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-05-12 | 2017-05-11 09:09 | -1 | 2017-03-20 11:36 | Civil - Civil Engineering General | 750 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | Following application of Spray waterproofing on Level +3 Eastern Ticket Hall. It was discovered _laser used __ Primer EP LT instead of __ Primer EPF as stated in MCR Cxxx--C-LRC-M123-50675 and ITP Cxxx--X-ITP-M123-50009.
| 02SL - Stations (LUL) | Cxxx-NCR-002556 | NCR | WTH - Level 0 Blockwork Wall & Doors Constructed Incorrectly |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-04-28 | 2017-04-27 09:24 | -1 | 2017-04-20 09:33 | Civil - Civil Engineering General | 6000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 1. Part of a blockwork wall on level 0 on gridline 4 (see exact location highlighted in the attachment) was built to an incorrect position (out of tolerance) and __ have to revisit the area and re-build the panel. 2. The heights of the doors 1-WD19, 1-WD20 and 1-WD26 on level 0 to the south of SR 1 riser (see attached drawing) were built to the wrong height and __ have to revisit the area and amend the doors to the correct height.
| 02SL - Stations (LUL) | Cxxx-NCR-002558 | NCR | TUN - BUI - Incorrect MCR in Place for Front of House Screeding Works |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-06-02 | 2017-06-02 11:20 | 0 | 2017-03-21 14:37 | Tunnelling - Walkways | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | __, the front of house screeding and tiling subcontractor, have started work using a reference to an existing MCR in use by __. It has subsequently been discovered that despite using the same base material, __ use a different primer and fibres within the screed which is not within the existing MCR. The referenced MCR was Cxxx--C-LRC-M123-50662 (rev 3).
| 02SL - Stations (LUL) | Cxxx-NCR-002559 | NCR | TUN - BUI - Incorrect Installation of D49 Mesh in CH2 Screeding |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-12-15 | 2017-12-05 12:07 | -10 | 2017-03-28 07:16 | Architectural - Flooring | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | During an inspection by Crossrail, it was noted that the D49 mesh at the junction between CH2/CP7 had not been cast into the middle third of the thickness and that the provided lap was only 150mm rather than the 250mm as specified by the ITP. The works were undertaken by 's subcontractor __ and is at the interface between back of house and front of house works. Subsequently, it has been found that this mesh should not have been installed as the detail from __ shows the two screeds to be installed separate from each other. This detail was not available at the time of the installation due to __ design not being fully completed. See attached sketch "Interface Between FOH and BOH Flooring" which shows that there is no mesh to be installed at this interface.
| 02SL - Stations (LUL) | Cxxx-NCR-002560 | NCR | WTH Use of P-status __ General Arrangement drawing on Level -1 plantroom |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-05-05 | 2017-05-02 10:36 | -3 | 2017-03-22 18:44 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | Drawing Cxxx--A-DDA-M123_2-76209 Rev P14 was used to construct blockwork walls and plinths and lay screed in the Level -1 plantroom. The drawing used was at P status and had not gone through the Minimum Assurance Process and therefore should not have been used on site. Cxxx-FCD-002676 accepts the use of Rev 14 for construction.
| 02SL - Stations (LUL) | Cxxx-NCR-002561 | NCR | WTH Level -1 Use of non-approved debonding material between concrete plinths and blockwork wall |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-07-14 | 2017-06-20 16:12 | -24 | 2017-03-22 18:49 | Civil - Civil Engineering General | 750 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | have poured the concrete plinths as shown on the attached drawing (Cxxx--A-DDA-M123_2-76209 Rev P14). This drawing was issued as Part of __ Bucket 5 submissions. This drawing had not gone through the Minimum Assurance Process and should not have been used on-site. An FCD will be raised once Crossrail have reviewed the drawings to allow its use on-site and Cxxx-NCR-002560 has been raised to cover the use of a non-approved drawing. A debonding material was used to separate the concrete from the blockwork perimeter wall. This material was not approved nor is it indicated on any design drawing.
| 02SL - Stations (LUL) | Cxxx-NCR-002562 | NCR | ETH - Windposts WP69A and W69B (Head Detail HB2A) - Mechanical anchors installed incorrectly |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-06-02 | 2017-05-17 12:44 | -16 | 2017-03-27 11:04 | Civil - Civil Engineering General | 3750 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Mechanical anchors for the head plate of windposts WP69A and WP69B installed incorrectly. During the installation of Package 4 (Cxxx-ATK-S-XSK-M123-50004) on site: - For Windpost WP69B head plate 6 No mechanical anchors (HDA-TR-M16X190/60) were designed to be installed. 5 No anchors were installed as required and 1 No anchors installed incorrectly. 1 No bolt installed but loose and could not be utilised. - For Windpost WP69A head plate 6 No mechanical anchors (HDA-TR-M16X190/60) were designed to be installed. 5 No anchors were installed as required and 1 No anchor installed incorrectly. Anchor bolt did not achieve the required thread of at least one thread plus the tread run-out. See attached files Ref: WP69B Head plate (HB2A) and WP69A Head plate (HB2A)
| 02SL - Stations (LUL) | Cxxx-NCR-002563 | NCR | ETH - Windpost WP61B (Base detail M11) base anchor holes incorrectly drilled on the base plate |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-06-16 | 2017-06-16 14:19 | 0 | 2017-03-27 11:04 | Civil - Civil Engineering General | 3250 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | For Windpost WP61B 3 No. base anchor holes were drilled incorrectly (10 mm) by __ on the base plate (BASE DETAIL M11) while using the template provided by . (See attached package PK-05 - Cxxx-ATK-S-XSK-M123-50005 - page 13 and site photo Base plate M11 Before).
| 02SL - Stations (LUL) | Cxxx-NCR-002564 | NCR | ETH - Fabrication and Installation of Coffer Ceiling Acoustic Cladding to P status drawings without an FCD in place |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-07-14 | 2017-07-13 09:55 | -1 | 2017-03-29 15:25 | Architectural - Finishes | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Lack of procedure | Completed |  | The drawings for the coffer ceiling cladding are as follows; Cxxx--X-DWG-M123-53000 Rev P02 - Code 2 Cxxx--X-DWG-M123-53012 Rev P02 - Code 2 Cxxx--X-DWG-M123-53031 Rev P01 - Not Issued Cxxx--X-DWG-M123-53033 Rev P02 - Code 1 Works have started to fabricate and install the coffer ceiling acoustic cladding to P status drawings without an FCD in place. The comments related to this design submission are detailed in Cxxx--X-XCS-M123-50041. Comment numbers 3 and 4 relate to the drawings Cxxx--X-DWG-M123-53000 and 53012 but do not affect the coffer ceiling panels that have been fabricated and are being installed. Cxxx--X-DWG-M123-53031 was not issued to CRL in error.
| 02SL - Stations (LUL) | Cxxx-NCR-002565 | NCR | STW - Use of Quartz sand in waterproofing without approved MCR |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-05-12 | 2017-05-11 09:11 | -1 | 2017-04-04 15:41 | Civil - Civil Engineering General | 750 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | After installation of Waterproofing on Level +3 and sections of Level +1. became aware _laser where installing waterproofing using 0.4–0.8mm quartz sand without an approved MCR. Currrent Material Compliance Record Cxxx--C-LRC-M123-50675 - __ 900MP covers Spray Waterproofing only not use of Quartz sand.
| 02SL - Stations (LUL) | Cxxx-NCR-002566 | NCR | MEP - Damage to AHU No2 |  | Contr | __ | FAR - Farringdon Station (West) |  | 2017-06-30 | 2017-06-20 07:47 | -10 | 2017-03-30 10:30 | Mechanical - Heating Ventilation & Air Conditioning | 2000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper handling of material | Completed |  | During the lowering operation to level - 2 by slight damage was sustained to the AHU number 2. this was picked up by __ Engineer and also subsequently detailed by Crossrail on CRL-OBS-14893. Please note : CRL-OBS-14893 incorrectly identifies this as AHU-1
| 02SL - Stations (LUL) | Cxxx-NCR-002568 | NCR | The Contractor has not complied with the MEP Materials Workmanship Specification |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2017-05-20 | 2017-05-15 10:05 | -5 | 2017-03-31 12:06 | Electrical - Lighting | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Insufficient information made available to the worker. | Completed |  | A planned Crossrail surveillance was undertaken on 27th March 2017 to look at the Protection of Completed and Ongoing Works. During the on site visit it was noted that there was no protection to the wall mounted light fittings. On checking the Method Statement Cxxx--E-GMS-M123-50010 (Rev 2) no reference has been made to the protection of light fittings, which is a requirement in the specification.
| 02SL - Stations (LUL) | Cxxx-NCR-002569 | NCR | MEP CMS not Installed in accordance with drawing |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-09-22 | 2017-09-22 08:47 | 0 | 2017-04-06 13:12 | Electrical - Cable Management | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Ladder Rack CMS has had to be installed in a location closer to the wall, access to install in accordance with drawing Cxxx--E-DDA-M123_7-50226 C04 was hampered at the time of install and program constraints due to SLD date completions.
| 02SL - Stations (LUL) | Cxxx-NCR-002570 | NCR | WTH - Cast-in sockets for windpost headplates in packages 21, 25, 26 and 40 not vertical |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-10-31 | 2017-10-25 09:55 | -6 | 2017-04-06 16:25 | Civil - Civil Engineering General | 3500 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | WTH windpost packages 21, 25, 26 and 40 are located between level -1 and 0 around the perimeter of the Lower Apse. Their respective __ design packages are referenced below. M24 sockets were cast into the Lower Apse slab (level 0) to connect the headplates of these windposts to the soffit of this slab. Upon installation of threaded rod anchors into these sockets it has been identified that multiple sockets have been cast in not vertical. The worst-case socket gives the anchor a slope ratio of 1:10 (i.e. for a 30mm length of anchor, it is 3mm from vertical). See the attached example mark-ups of PK-21 and PK-25 showing with an ‘X’ which sockets are not vertical. This means a standard clearance hole in a 30mm thick plate will not work as you will need 3mm clearance to accommodate the 3mm misalignment instead of the 2mm that would be given by a 26mm hole for a M24 anchor (i.e a standard clearance hole). An indicative sketch of the cast-in detail is attached in pdf, “Windpost anchor detail sketch”.
| 02SL - Stations (LUL) | Cxxx-NCR-002571 | NCR | WTH – Incorrect as-built surveys of windpost anchors for PK-21 headplates |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-07-28 | 2017-06-06 14:38 | -52 | 2017-04-06 16:27 | Civil - Civil Engineering General | 4500 |  | Incorrect Installation | Reject | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | ‘Package 21’ windposts are located along the Southern perimeter of the Lower Apse ceiling between slab levels -1 and 0. These windposts are detailed within __ sketch package Cxxx-ATK-S-XSK-M123-50021 P04 (referenced below). The windposts connect into the soffit of the level 0 slab through multiple cast-in sockets and M24 threaded rods. These cast-in sockets were surveyed by and the as-built positions sent to __. __’s fabrication drawings were completed based on these as-builts and the headplates were delivered to site. When the headplates were installed, it was found that approximately 75% of the sockets did not align with the pre-drilled holes in the headplates. The cast-in sockets were re-surveyed and a discrepancy between surveys was found – the worst case was 25mm and the average was 8mm. Please see the attached comparison of surveys for PK-21 headplates. This meant the initial as-built survey was inaccurate. The second survey was checked by both and __ engineers.
| 02SL - Stations (LUL) | Cxxx-NCR-002572 | NCR | ETH - Windposts Packages 17 and 18 Repair to head plate connection due to change in design |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-05-20 | 2017-05-17 12:41 | -3 | 2017-04-26 11:01 | Civil - Civil Engineering General | 6000 |  | Design | Repair | 3 (3-6k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | Head plates for windposts in packages 17 and 18 were fabricated by __ to the wrong revision of the design drawings. __ steel used Rev 1 of the packages 17 & 18 during fabrication of the windposts while used Rev 2 drawings used for site set out as agreed per Cxxx-FCD-002688 - 'STW – Windposts – Fabrication/installation of ‘priority two’ windposts without complete drawing assurance in place'. This NCR is being raised as agreed with Crossrail following Cxxx-FCD-002688. The drawings and windposts affected by this NCR are attached in package 17 and 18 (Cxxx-ATK-S-XSK-M123-50017 Rev 2.0 & Cxxx-ATK-S-XSK-M123-50018 Rev 2.0).
| 02SL - Stations (LUL) | Cxxx-NCR-002573 | NCR | MEP - WTH - Level -1 - Installation of Cantilever Arms to Blockwork walls without accepted fixings calculations |  | Contr | __ | FAR - Farringdon Station (West) |  | 2017-06-21 | 2017-06-19 09:31 | -2 | 2017-05-12 14:31 | Electrical - Cable Management | 2000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Interfacing problems | Completed |  | This NCR is raised following the installation of Cantilever Arms on blockwork walls without confirmation from the blockwork wall contractor that the wall is sufficient to withstand the load imposed on it by the CMS Fixings.
| 02SL - Stations (LUL) | Cxxx-NCR-002574 | NCR | MEP - WTH - Level -1 and -6 - Pipework installation on Cantilever Arms |  | Contr | __ | FAR - Farringdon Station (West) |  | 2017-07-31 | 2017-06-30 07:08 | -31 | 2017-05-12 14:54 | Mechanical - Piping | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | This NCR is raised following the installation of Cantilever Arms supporting mechanical services on blockwork walls without confirmation from the blockwork wall contractor that the wall is sufficient to withstand the load imposed on it by the pipework.
| 02SL - Stations (LUL) | Cxxx-NCR-002575 | NCR | WTH - Lower Apse level 0 GL G upstand reinforcement cast out of position |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-06-23 | 2017-06-15 15:37 | -8 | 2017-05-02 16:13 | Civil - Civil Engineering General | 4000 |  | Incorrect Installation | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The Upper Apse Ceiling was built to the setting out shown on the __ drawing Cxxx--Y-DWG-M123-50111 P15, referenced below. This gives an offset from GL G of 610mm for the Western edge of the Upper Apse Ceiling. Section 113 on Cxxx drawing Cxxx-SWN-S-DDD-M123_1-80052 C04 (referenced below) shows the level 0 upstand of the Lower Apse slab along GL G. This section shows the upstand following the line of the edge of the slab at an offset of 570mm west of GL G. As part of the design philosophy of the Upper/Lower Apse Ceilings, it was decided to cast the Lower Apse ceiling against the vertical edge of the Upper Apse pre-cast units. This has resulted in the reinforcing bars for the upstand being cast 40mm too far east.
| 02SL - Stations (LUL) | Cxxx-NCR-002576 | NCR | MEP - WTH - Incorrect Fault Rating Applied to Distribution Boards |  | Contr | __ | FAR - Farringdon Station (West) |  | 2017-12-22 | 2018-02-21 17:16 | 61 | 2017-04-11 15:25 | Electrical - Power Distribution | 5000 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | CRL-OBS-15589 was raised and notes ... "All installed distribution boards have a fault rating of 10kA. A review was undertaken of the design maximum fault current at each distribution board using the latest __ calculations (Cxxx--E-XCL-M123-50005 rev. 8.0). This found that the following DBs have been installed with the incorrect fault rating: WTH - Cable A03 / DB06 - Cable A11 / DB20 - Cable B04 / DB07 It is noted that the following cables also had fault currents in excess of 10kA however are feeding other panels (i.e. UPS, MCC, escalators, TVF, chillers): WTH Cables A08, A13, A14, A20, A21, A22, A23, A25, B13, B16, B19, B21, B22, B23, B24, B25, B28, B29" Note: See also linked NCR (Cxxx-NCR-002623)
| 02SL - Stations (LUL) | Cxxx-NCR-002577 | NCR | MEP Non Compliant - Fire Suppression Drain Valves |  | Contr | __ | FAR - Farringdon Station (West) |  | 2017-10-02 | 2017-07-05 15:30 | -89 | 2017-04-12 11:10 | Systems - Fire Detection systems and Mains | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Yellow handled ball valves have been installed on the station and tunnel fire mains for drainage as this is the current normal standard for fire mains and will aid CRL's request for the valve to be lockable to stop inadvertent drainage. However the CRL site specific standard states that gate valves to BS EN12288:2010 should be installed so the installation is therefore non compliant. This has also been raised by Crossrail on CRL-OBS-15507. __ have raised Cxxx-MCR-004261 in an attempt to regularise this installation which is considered superior to the specified one but this has been rejected and therefore requires an NCR.
| 02SL - Stations (LUL) | Cxxx-NCR-002578 | NCR | MEP - STW - Procurement and Installation of __ Circuit Protection Breakers without CRL accepted MCR |  | Contr | __ | FAR - Farringdon Station (West) |  | 2017-06-18 | 2017-06-01 16:48 | -17 | 2017-04-27 11:07 | Electrical - Switchgear | 2000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | This NCR is raised following the procurement and installation of __ circuit protection breakers prior to an accepted MCR.
| 02SL - Stations (LUL) | Cxxx-NCR-002579 | NCR | MEP - No spare capacity left on the CMS for submain cables (UPS to LVU Riser L-6) |  | Contr | __ | FAR - Farringdon Station (West) |  | 2017-06-12 | 2017-06-06 14:07 | -6 | 2017-05-03 14:29 | Electrical - Cable Management | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | An Electrical VAP visit reported "There is no spare capacity left on the CMS for submain cables ( which are cleated) from UPS to LVU riser at level -6 and horizontal run level -8 at WTH." This can be seen from the site photographs showing that the cables have been cleated so as to leave no spare capacity. This has also been recorded on OBS-15851 The specification states support a every 450mm but the cable tray only allows cleating every 300mm. __ decided to meet the specification by cleating every 300mm however this means that the cleats cannot be staggered (would be supported every 600mm) and take up the full width of the cable ladder
| 02SL - Stations (LUL) | Cxxx-NCR-002581 | NCR | WTH - Windposts - Misaligned level 0 slab edge and late revision of __ Package 27 sketch package causing site modifications to Package 27 headplates |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-07-14 | 2017-06-16 07:46 | -28 | 2017-05-03 15:17 | Civil - Structural Engineering | 4750 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Package 27 is located along the North edge of the level 0 slab South of the Upper Apse ceiling. This is shown on the __ sketch package Cxxx-ATK-S-XSK-M123-50027 P05 (referenced below). The head detail within this sketch package is an angle bracket which bolts to both the soffit of the level 0 slab and its Northern vertical face. Site modifications were required to package 27 headplates for two reasons: 1. Misaligned level 0 slab edge: The slab edge was found to be up to 26mm out of position (too far North). This is shown on the attached as-built survey 'Area 4 Level 0 Edge Trim As-built Survey'. Given the design of the windpost headplates, this meant the fin plates welded to the soffit plate needed to be cut and re-welded onsite to allow the windposts to be installed along their correct line. As part of __'s ITP for erection of structural steelwork (Cxxx--X-ITP-M123-50002 Rev. 2.0) when an area of metal decking is finished, they are required to provide with a QICS 5 'handover' form. This is normally accompanied by an as-built survey showing the edge trim of the metal decking. In this instance, no survey was appended to the QICS 5 form. 2. Further to the above, a late issuing of a revised __ sketch package (P05, referenced below) changed the setting out of the windposts as part of a co-ordination exercise with the __ architectural team. This meant that site works were required to re-position the fin plate welded to the soffit plate.
| 02SL - Stations (LUL) | Cxxx-NCR-002582 | NCR | ETH - Windposts Package 13 Maximum Grout thickness Exceeded |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-11-14 | 2017-11-01 14:56 | -13 | 2017-07-17 10:14 | Civil - Civil Engineering General | 3000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Previous Construction - Interfacing issues | Completed |  | The maximum grout thickness of more than 10 mm which is the specified maximum for the base plates by __ (See attached Package 13 Cxxx-ATK-S-XSK-M123-50013 Rev 4.0 - Page 7) - has been exceeded in 5 No locations (WP69C, WP71B, WP71C, WP71D and WP69D). [See attached Package 13 site photo and Package 13 Cxxx-ATK-S-XSK-M123-50013 Rev 4.0 - Page 2] During the installation of package 13, in 5 No locations the grout thickness varied from 12 - 17 mm. (see attached photos of windposts WP71B). Design level for L-3 slab is 100.650 and the as built ranges from 100.627 to 100.634 (see attached as built survey). Cxxx-NCR-002641 raised to cover low levels of L-3 slab.
| 02SL - Stations (LUL) | Cxxx-NCR-002583 | NCR | ETH-L+1 slab crane infill steel reinforcement threaded bar incorrect installation |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-05-30 | 2017-05-22 15:42 | -8 | 2017-05-16 13:27 | Civil - Civil Engineering General | 2000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the construction of L+1 slab, a threaded bar (1 No. B25 bar mark C24) was installed incorrectly due to a clash with bolts on the steel column at GL4/B. (See attached mark-up drawing Cxxx-ATK-S-DWG-M123_A-50102 C01 ETH S and photo - Slab reinforcement)
| 02SL - Stations (LUL) | Cxxx-NCR-002584 | NCR | WTH – Upper Apse – GLK Rotation of Pre-Cast Members |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-11-02 | 2018-11-02 15:09 | 0 | 2017-05-05 16:29 | Civil - Civil Engineering General | 7500 |  | Design | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The Upper Apse Edge Beams along GLK appear to have rotated post striking of the temporary deck. This can be seen in the attached cloud point survey ‘ITH Level 0’. This shows indicatively that the GLK Edge Beams, predominantly to the north – EB5 & EB6 – have rotated up to approximately 3.3º. 1. This rotation of the GLK units towards the east has led to widening of the primary beam to edge beam joints. During an inspection with CRL Architects the joints between EB6/EB13, EB6/PB8 & EB6/PB7 were identified as visibly dissimilar to the remainder of the EB/PB joints along GLK. This can be seen on the attached survey as 45mm max joint width (between EB6/PB8). Where the GLK Edge Beams have rotated the beam to slab joint along GLK has also widened – this can be seen on the attached survey as 30mm max joint width. 2. The rotation of EB6 has also caused this unit to appear to rest on the western flange of GLK13 column. This can be seen in attached survey ‘Photo Survey of Site Condition’.
| 02SL - Stations (LUL) | Cxxx-NCR-002585 | NCR | STW – Lack of Post Contract Blockwork Sample Panel |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-05-26 | 2017-05-19 15:43 | -7 | 2017-05-10 18:02 | Civil - Civil Engineering General | 1500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | Clause JF10.2103 of the Architectural Specification (Cxxx--A-RSP-M123-50057 Rev 17) states that sample panels of all types of blockwork are required after the contract is awarded. This was never undertaken.
| 02SL - Stations (LUL) | Cxxx-NCR-002586 | NCR | STW – Lack of precast concrete stair sample and benchmark |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-05-26 | 2017-05-19 15:51 | -7 | 2017-05-10 18:10 | Civil - Civil Engineering General | 1500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | Clause JL30.2103 of the Architectural Specification (Cxxx--A-RSP-M123-50057 Rev 17) states that sample and benchmarks of precast concrete stairs (Specification reference STR 303) are required. This was never undertaken.
| 02SL - Stations (LUL) | Cxxx-NCR-002587 | NCR | WTH - Upper Apse - Damage to precast concrete units (top) |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-03-30 | 2018-03-29 15:51 | -1 | 2017-05-18 13:37 | Architectural - Ceilings & Soffits | 8000 |  | Damaged | Repair | 2 (6-60k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Several Upper Apse pre-cast panels have been damaged during installation. The full extent of the damage has been assessed during a joint survey between CRL FE/ agreeing the scope of repairs required. This will be captured in document Cxxx--A-RGN-M123-51174. (Note that a separate NCR is already in place for damage caused to the exposed soffit – Cxxx-NCR-002499)
| 02SL - Stations (LUL) | Cxxx-NCR-002589 | NCR | WTH – Further water ingress issues in SHW3/ES1 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-08-30 | 2017-08-30 14:05 | 0 | 2017-05-11 09:49 | Civil - Civil Engineering General | 7500 |  | Damaged | Repair | 2 (6-60k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Further to previous NCRs raised in relation to water ingress issues in SHW3 (NCRs 001717, 001820 and 001844, 001925), there have since been another 2no. areas of water ingress that have become visible within the SHW3 lining walls. The attached report '17.05.10 SHW3 and ES1 Water Ingress Report' shows the locations of these areas. Please note 'Leak A' in the report refers to 'Area A' on the location drawing and photos, etc. Secondly there are 2no. location types where damp patches are visible on the top surface of the stepped ramp. Type 1 - The damp patches within ES1 that appear where the stepped ramp meet the secondary lining are covered on Cxxx-RFI-004341 (referenced below). Type 2 - The damp patches elsewhere could be from where water has flowed through the construction joints of the mass fill ramp - this is discussed in more detail in the report attached below.
| 02SL - Stations (LUL) | Cxxx-NCR-002590 | NCR | MEP - Pipe Couplings Fitted within Firestopping exlusion zone |  | Contr | __ | FAR - Farringdon Station (West) |  | 2017-09-25 | 2017-10-19 17:11 | 24 | 2017-06-27 10:13 | Architectural - Walls | 6000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | In a number of locations pipework has been fitted with couplings and joints either within or too close to the wall penetrations. See Attached Photographs
| 02SL - Stations (LUL) | Cxxx-NCR-002591 | NCR | ETH - L0 missing WI columns due to design error |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-06-16 | 2017-06-09 15:22 | -7 | 2017-05-18 10:34 | Architectural - Masonary | 6750 |  | Design | Rework | 2 (6-60k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Following __ F02 calculations update for Farringdon, it became apparent 4nr Wi columns were missing from completed block wall which was built in line with Wi drawing Cxxx--X-DWG-M123_1-54020 Rev P09 (see highlighted area on drawing attached, rooms E/B Ventilation Adit and Circulation Area CIR-S2G at L0) Please find attached a photo of the blockwork built.
| 02SL - Stations (LUL) | Cxxx-NCR-002592 | NCR | WTH – Localised damage to Level 0 slab above ESS1 staircase |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-09-08 | 2017-06-22 11:49 | -78 | 2017-05-19 11:10 | Civil - Civil Engineering General | 2000 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | The Level 0 slab edge above the ESS1 staircase has been damaged, see attached drawing and photos
| 02SL - Stations (LUL) | Cxxx-NCR-002593 | NCR | WTH – Incomplete concrete protective layer pour on Level +2 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-10-13 | 2017-07-18 10:16 | -87 | 2017-05-19 11:16 | Civil - Civil Engineering General | 2000 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | The concrete protective layer was being poured over the __ waterproofing on Level +2. An insufficient amount of concrete was ordered and the full pour could not be completed. The affected area is highlighted on the attached sketch and shown in the attached photo.
| 02SL - Stations (LUL) | Cxxx-NCR-002594 | NCR | WTH - MNS2 misaligned steelwork columns above level +1 UM |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-03-02 | 2018-03-02 13:02 | 0 | 2017-05-23 16:11 | Civil - Structural Engineering | 3000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The 4no. columns shown on drawing ‘Cxxx--X-DWG-M123-50052_C01_marked’ were installed outside of verticality and plan position tolerances (as defined in NSSS 5th Edition). The attachment ‘3344 WTH Area 4 Level +2 columns as built’ shows an as-built survey of the columns. At the time of erection this was accepted by for 3 reasons: 1. __ could not pull these columns over easily because they are 4no free standing columns only connected at their tops (no bracing). The whole frame was leaning so tightening any of the top connections would not improve the position of the frame. 2. The WTH construction programme priorities consisted of focussing on erection of the main steelwork which required mobile cranes for installation. As such, correcting these small columns was considered low priority. 3. It was agreed with __ steel that prior to the baseplates being cast into the level +1 UM slab a turfer could be put on the columns and they would be plumbed. Casting-in the baseplates would then help fix the columns in their correct position. The agreed action in option three was not implemented and the level +1 UM slab was cast, encasing the column baseplates. The 4no. columns have since also been encased in 50mm concrete to provide the required fire protection. As such, these columns are now fixed in their as-built position. The metal decking was installed in accordance with metal decking drawing Cxxx--X-DWG-M123-50182 C01 (i.e. the edge trim has a 150mm offset from the beams c/l’s). This therefore means the edge trims are also out-of-position (although slab not cast yet). The as-built survey of the edge trim is attached on ‘Area 4 edge trim as built - level 3’.
| 02SL - Stations (LUL) | Cxxx-NCR-002595 | NCR | MEP - No completed audits or surveillances submitted to the Project Manager for a significant period of time |  | Contr | __ | FAR - Farringdon Station (West) |  | 2017-10-30 | 2017-11-09 15:49 | 10 | 2017-06-12 13:34 | Health & Safety General | 0 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | No Audits or Surveillances have been submitted to the Project Manager through Eb for a significant period of time.
| 02SL - Stations (LUL) | Cxxx-NCR-002596 | NCR | STW – Failure to provide RC insitu staircase samples, benchmarks and prototypes |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-06-23 | 2017-06-19 12:54 | -4 | 2017-05-24 16:43 | Civil - Civil Engineering General | 750 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | The Architectural Specification (Cxxx--A-RSP-M123-50057 Rev 17) itemises two RC insitu staircase units, one for public access (STR-304) and the other for mass fill stairs or BOH areas (STR-305). Clause JL30 outlines which samples/benchmarks/prototypes are required. Clause JL30.2103 requires a post contract award sample, for both staircase types, JL30.2105 also requires a benchmark for the first installed type for each staircase and Clause JL30.2106 requires a prototype for type STR-304. None of these items have been done.
| 02SL - Stations (LUL) | Cxxx-NCR-002597 | NCR | ETH - W33 Cast in plate ETH-2202 out of tolerance |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-09-29 | 2017-09-19 10:53 | -10 | 2017-06-28 15:39 | Civil - Civil Engineering General | 2000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Cast in plate ETH-2202 installed in Wall W33 at L0 for Area 11 steelwork connection is 30 mm out of tolerance (see attached drawing EMP-1101 E and marked up drawing Cxxx--X-DWG-M123-50284).
| 02SL - Stations (LUL) | Cxxx-NCR-002598 | NCR | ETH - Incorrect installation of Level 0 upstand steel reinforcement |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-06-23 | 2017-07-11 14:15 | 18 | 2017-06-02 15:08 | Civil - Civil Engineering General | 2500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the construction of L0 slab upstands around the tower crane infill, starter bars (2 No. L bars - 1 B12 bar mark 10 and 1 B12 bar mark 12) were installed incorrectly due to the bars not having the required anchorage length / couplers. (See attached mark-up drawing Cxxx-ATK-S-DWG-M123_1-50126 C03 and photo - Slab reinforcement)
| 02SL - Stations (LUL) | Cxxx-NCR-002599 | NCR | TUN - BUI - C Status Drawings Used Instead of Latest P Revision Drawings for Tiling Setting Out |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-07-28 | 2017-07-26 12:52 | -2 | 2017-05-25 14:51 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | During Surveillance on the tiling in CH1, (Cxxx--O4-RGN-M123-51486 Rev 1.0) it was observed that were using the following P status drawing: Cxxx--A-DDA-M123_7-01021 Rev P10. The agreed procedure to allow use of P-status drawings for construction is to raise FCD demonstrating minimum drawing assurance has been met. Minimum assurance is defined in the matrix found in Cxxx--O-LRC-M123-50001 Rev. 2.0 (referenced below). In this instance the FCD wasn't raised before tiling works commenced in order to meet the accepted programme and not delay other subcontractors/trades. took to decision to proceed with the works at their own risk as the tile setting out dimensions and layout had not changed from Cxxx--A-DDA-M123_7-01021 Rev C3 to Cxxx--A-DDA-M123_7-01021 Rev P10. This was done to mitigate delays and additional costs of instructing the tiling subcontractor __ to leave site whilst the minimum drawing assurance was being sought.
| 02SL - Stations (LUL) | Cxxx-NCR-002600 | NCR | TUN – BUI Tunnels Dampness tests not being undertaken |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-07-27 | 2017-07-27 09:54 | 0 | 2017-05-26 12:31 | Civil - Civil Engineering General | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Following a surveillance report by __ on 22/05/17 (Cxxx--O4-RGN-M123-51486), it was discovered that the screeding and tiling subcontractor __ Contracts had not undertaken Dampness testing for moisture content on the screed before commencing tiling works, despite this being in the Architectural Specification (JM40.3204 and JM10.3205).
| 02SL - Stations (LUL) | Cxxx-NCR-002601 | NCR | ETH-C1/C2 concrete mix not achieving the required design strength. |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-08-18 | 2017-08-21 13:09 | 3 | 2017-07-20 06:55 | Civil - Civil Engineering General | 3000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | A number of concrete pours for the mix design C1/C2 do not achieve the required design strength after 28 days cube testing. See attached pdf Master Sheet - C1-C2 test results (highlighted in green and amber)
| 02SL - Stations (LUL) | Cxxx-NCR-002602 | NCR | ETH - North Yard - Use of Lytag Concrete Mix with out approved MCR |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-07-28 | 2017-07-27 13:01 | -1 | 2017-06-01 15:03 | Civil - Civil Engineering General | 1000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | Following response to Cxxx-RFI-004392, have been requested to use Lytag Concrete Mix C20/22 as a fill material on top of G134 Arches. As agreed with Crossrail __ and __, works to proceed in North Yard before MCR approval. Attached is __ Mix Design for Lytag. MCR to be produced under Cxxx--C-LRC-M123-50922.
| 02SL - Stations (LUL) | Cxxx-NCR-002603 | NCR | MEP - WTH - Fire Main Installed at Low Head Height |  | Contr | __ | FAR - Farringdon Station (West) |  | 2017-06-21 | 2017-06-12 09:06 | -9 | 2017-06-07 07:16 | Mechanical - Public Health Engineering | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | At the exit to UMC 2 in the WTH the firemain has been poorly routed such that it only provides clearance of 1.72 Metres from FFL. See attached Photograph. Note this is also recorded on CRL-OBS-16274
| 02SL - Stations (LUL) | Cxxx-NCR-002604 | NCR | MEP - Fire Damper Control Panel Heights |  | Contr | __ | FAR - Farringdon Station (West) |  | 2017-08-20 | 2017-10-11 10:46 | 52 | 2017-06-21 09:19 | Mechanical - Heating Ventilation & Air Conditioning | 7000 |  | Supervision/Management | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Other | Completed |  | the Damper Control Panel in the circulation area, adjacent to LCC1 has been installed at approximately 650mm from FFL. This is not acceptable for maintenance and access. The Damper Control Panel in the Sewage Water Sump room is installed over 2m above ffl. This is not an acceptable height for maintenance & access. 3No. Damper Control Panels in the unallocated space (access to Platform supply/smoke riser, are installed at approx. 2.4m above ffl. This is not an acceptable height for maintenance & access. See also OBS 16086,16225,16226
| 02SL - Stations (LUL) | Cxxx-NCR-002607 | NCR | MEP - Ductwork obstructing airflow to UPE |  | Contr | __ | FAR - Farringdon Station (West) |  | 2018-01-29 | 2018-02-21 15:25 | 23 | 2017-06-21 15:26 | Systems - Ventilation and Pressure Relief | 5000 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The only available route for the fire fighting lift shaft pressurisation ductwork was via Under Platform Extract Duct (UPE) and this was in accordance with the Works Information Stage E design. While the design team were aware that there was a requirement for there to be a 4sq m space throughout the UPE there is no other route for this duct available These requirements have now been compromised by the ductwork and pipework solution selected and installed (as per approved design) and hence the design and installation need reworking to revise the ductwork and maximise the available cross section of the UPE. See also CRL-OBS-15657
| 02SL - Stations (LUL) | Cxxx-NCR-002608 | NCR | MEP - PLT - Diameter of Flexible Conduit not covered by MCR |  | Contr | __ | FAR - Farringdon Station (West) |  | 2017-08-18 | 2017-08-09 14:33 | -9 | 2017-06-05 15:02 | Electrical - Lighting | 2000 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | At multiple locations along the platform, generally to serve signage, 16mm flexible conduit type __ FU, has been installed, without an accepted MCR in place. See also CRL-OBS-16484
| 02SL - Stations (LUL) | Cxxx-NCR-002609 | NCR | ETH – Adding water to Wi Concrete |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-07-21 | 2017-07-21 09:59 | 0 | 2017-06-20 16:00 | Architectural - Brickworks/Blockworks | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | During a site walk, an operative from our Masonry subcontractor was found adding water to a mortar mix at the work face without an agreed method or controls in place.
| 02SL - Stations (LUL) | Cxxx-NCR-002610 | NCR | MEP - Installation of Fire Detection Equipment Without Approved Drawings |  | Contr | __ | FAR - Farringdon Station (West) |  | 2018-01-30 | 2018-02-08 15:48 | 9 | 2017-06-06 15:07 | Fire - Detection | 500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | The following Fire Detection Systems have been installed to C status drawings that have been modified locally and have not been reapproved through the drawing approval process being followed - Fire Detection Loops - Damper Control Panels
| 02SL - Stations (LUL) | Cxxx-NCR-002611 | NCR | WTH Level -1 Use of non-approved debonding material between concrete plinths and blockwork wall (Further to Cxxx-NCR-002561) |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-09-08 | 2017-06-20 16:09 | -80 | 2017-06-06 15:10 | Civil - Civil Engineering General | 750 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | The plinth highlighted on the attached drawing had to be enlarged to take into account a design change. This was poured with a debonding material used to separate the concrete from the blockwork perimeter wall, see attached photo. This material was not approved and was not shown on any design drawing. This NCR relates to the same issue as part of Cxxx-NCR-002561.
| 02SL - Stations (LUL) | Cxxx-NCR-002613 | NCR | WTH - MEP - MEP Cable Runs Damaged by Water Ingress/Concrete Repair |  | Contr | __ | FAR - Farringdon Station (West) |  | 2017-08-18 | 2017-08-18 13:14 | 0 | 2017-06-16 12:12 | Civil - Civil Engineering General | 2000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | MEP cable runs and tray at Level -2 in the Circular Shaft have become severely rusted and require replacement. (Marked up Drawing Cxxx--E-DDA-M123_3-75212 shows extent of damage) Given the short time since install to achieve this degree of rusting and the concrete dust on the cable trays it is suggested that the damage may have been caused by repairing a concrete crack in the area. There is Cxxx cables fitted to this tray and they are hygroscopic in nature so will tend to absorb moisture so will need to be retested
| 02SL - Stations (LUL) | Cxxx-NCR-002614 | NCR | ETH - MEP - Damage to MEP caused by workforce urinating on equipment |  | Contr | __ | FAR - Farringdon Station (West) |  | 2017-07-04 | 2017-07-04 14:48 | 0 | 2017-06-20 08:41 | Construction Health & Safety - Construction Health & Safety General | 2000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Contamination | Completed |  | A number of instances have occurred to date where it has been found that completed works have been urinated on by persons unknown. This has now resulted in damage to the cable tray in a location which has seen repeated occurrences of this nature.
| 02SL - Stations (LUL) | Cxxx-NCR-002615 | NCR | STW - Redlining Code 2 drawings |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-07-10 | 2017-07-12 11:48 | 2 | 2017-06-19 08:19 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | has been redlining Code 2 __ drawings. Drawings have been identified on two CCMs - Cxxx-CCM-14878 and Cxxx-CCM-14937.
| 02SL - Stations (LUL) | Cxxx-NCR-002616 | NCR | WTH - Column Encasements - Concrete Encasement to 11F |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-07-21 | 2017-07-21 12:46 | 0 | 2017-06-21 07:07 | Civil - Civil Engineering General | 2500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Column 11F (shown on the attached annotation) was encased in 50mm concrete in order to provide adequate fire protection. However, when it came to installing the structural steelwork beam at Level 0 (highlighted on attached annotation) inside the Lower Apse slab, the concrete encasement prevented this installation. As a result, removed a section of this concrete in order to facilitate the installation of this beam.
| 02SL - Stations (LUL) | Cxxx-NCR-002617 | NCR | WTH - Windposts - PK-19 onsite remedial works to headplates |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-08-25 | 2017-08-15 09:40 | -10 | 2017-06-26 08:16 | Civil - Structural Engineering | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Package 19 windposts are founded on level 0 along the Western edge of the WTH ( parallel to GL B). __ issued PK-19 windposts sketch package to and __ on 1/3/17 (Cxxx-ATK-S-XSK-M123-50019, referenced below). __ raised a RFI on 11/4/17 identifying a discrepancy between the position of the upstands on level 0 and the relative positions of 2no. ‘20C’ windposts. This is attached – see “Cxxx-BST-RFI-00324”. The marked-up drawing appended to the RFI shows the plan locations of these windposts. Please see the attached marked-up elevation drawing which also shows the positions of the 2no. windposts. __ progressed with fabrication design, fabrication and installation of PK-19 without waiting for the RFI response (in line with the approach agreed on Cxxx-FCD-002369). This was done on the assumption that the upstand position was wrong and the windpost positions were correct. __ then completed the welding of the head brackets to the primary steel structure for the 2no. windposts referenced in the RFI by the 10/5/17. __ responded to the RFI on the 11/5/17. This is shown on the attached screenshot “Cxxx-BST-RFI-00324 response date - BC extract”. The response required both windposts to be moved 25mm. This resulted in __ having to remove the head brackets and re-weld them in their ‘new’ position.
| 02SL - Stations (LUL) | Cxxx-NCR-002618 | NCR | ETH-Level 0 Columns (C16) incorrect concrete encasement |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-08-25 | 2017-08-02 10:24 | -23 | 2017-06-28 15:44 | Civil - Civil Engineering General | 2500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | constructed 2 No C16 columns with the incorrect concrete encasement dimensions. Columns cast with 600x600 concrete encasement while on drawing Cxxx-SWN-S-DDJ-M123_Z-30000 Rev 6.0, the steel column schedule lists C16 as 900x600 concrete encased columns (See attached file Ref:Marked up drawings Cxxx-SWN-S-DDJ-M123_Z-30000, Cxxx-SWN-S-DDA-M123_1-30001 and photos IMG_20170626_133230) C16 columns were installed with galvanised D98 wrapping mesh with a minimum of 40mm cover.
| 02SL - Stations (LUL) | Cxxx-NCR-002619 | NCR | ETH-Level +1 Temporary handrail repair on upstand North of the temporary roof |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-10-06 | 2017-10-05 09:52 | -1 | 2017-06-29 11:12 | Civil - Civil Engineering General | 3000 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | During the construction of the L+1 slab, 5 No temporary handrails were installed and cast within the upstand North of the temporary roof in the ETH (see attached photos Ref: IMG_20170626_135104 and marked up drawing Cxxx-SWN-S-DDA-M123_A-30101) All the temporary handrails cast in the upstand do not have sufficient concrete cover within the upstand. Cover for the upstand in the handrail locations is currently less than 30mm (about 10-20mm).
| 02SL - Stations (LUL) | Cxxx-NCR-002620 | NCR | WTH - Pre-cast concrete void covers - minor damage to concrete surface |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-09-15 | 2017-08-15 08:58 | -31 | 2017-06-29 07:13 | Civil - Civil Engineering General | 1500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper handling of material | Completed |  | There are multiple voids formed in the level 0, +2 and +3 slabs that will be used to construct the OSD at the WTH. As part of ’s works these voids are to be temporarily covered with pre-cast concrete planks. These will provide weatherproofing to the Cxxx works until such a time that the OSD developers are ready to remove them and utilise the voids. The fabrication and installation of the planks were subcontracted to __ by . The void covers for the void highlighted on the attached marked-up drawing ‘Cxxx-SWN-S-DDA-M123_1-80001 C08 - marked-up‘ have been 50% installed with the remainder stored adjacent to the void. This is to allow To continue to use the void to lift materials to level -1 below. During the offloading, stacking or storage of the planks there has been some minor damage to the concrete surface. The attached site photographs ‘Site photographs – damage to pre-cast planks’ show the damage caused.
| 02SL - Stations (LUL) | Cxxx-NCR-002621 | NCR | WTH - PST Stairs - Concrete Finish |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-08-01 | 2017-08-01 12:25 | 0 | 2017-07-11 08:19 | Civil - Civil Engineering General | 3000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Upon striking the PST Stairs in the WTH running from Level 0 to the ITH concourse, there have been several issues with the concrete finish identified, as follows: 1) The nosing of some of the steps have been chipped during the striking of the formwork 2) On the sloping soffit, several conduits are present on the surface to allow for the pulling of cables through to the steps above. The concrete around some of these conduits has broken out during striking, leading to a poor surface finish. In one instance, this has caused the end piece of the conduit to become disconnected from the conduit 3) There are several cast in items within the stairs, which have be tied down using tie wire. There was also loose tie wire in the pour. As a result, there is now exposed tie wire protruding out of the cover zone in several locations on the stairs 4) In order to assemble to shutters, nails have been used to connect materials together, and have been left protruding into the concrete pour. During striking, these nails have remained in the concrete and not been removed with the ply Photos of all of the above have been noted in Cxxx-OBS-17012
| 02SL - Stations (LUL) | Cxxx-NCR-002623 | NCR | MEP - ETH - Incorrect Fault Rating Applied to Distribution Boards |  | Contr | __ | FAR - Farringdon Station (West) |  | 2017-12-22 | 2018-01-05 14:10 | 14 | 2017-06-30 12:24 | Electrical - LV Equipment | 5000 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | CRL-OBS-15589 was raised and notes ... "All installed distribution boards have a fault rating of 10kA. A review was undertaken of the design maximum fault current at each distribution board using the latest __ calculations (Cxxx--E-XCL-M123-50001 rev. 8.0 ETH, Cxxx--E-XCL-M123-50005 rev. 8.0 WTH). This found that the following DBs have been installed with the incorrect fault rating: ETH - A04 / DB08 - B04 / DB07 It is noted that the following cables also had fault currents in excess of 10kA however are feeding other panels (i.e. UPS, MCC, escalators, TVF, chillers): ETH Cables A13, A24, A25, A28, A29, B12, B13, B17, B27, B28, B29, B30, B31, B32
| 02SL - Stations (LUL) | Cxxx-NCR-002624 | NCR | TUN - No ITP covering the offsite manufacture of Agglo Granazzocem tiles |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2017-07-28 | 2017-07-26 14:22 | -2 | 2017-06-30 12:39 | Architectural - Flooring | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Not Defined | Completed |  | A planned Crossrail surveillance was undertaken on 29th June 2017 to look at manufacture and installation associated with screeding and tiling at Farringdon Station. During the documentation review, it was identified that no ITP existed covering activities, checks and records associated with the offsite manufacture by Agglo UK. This being (but not limited to) batch records, constituent material compliance, mould checking, curing, finish checking against the agreed control sample and acceptable fabrication tolerances (length and width +-0.5mm, thickness). JM41.1400 details requirements for material performance and finish JM41.3000 details requirements for fabrication and workmanship The onsite ‘Tiling ITP’ was presented (Cxxx--A-ITP-M123-50018) and reviewed. The only offsite process covered was for the testing of Slip Resistance. Works Information Volume 2B Part 20.8 states; “The Contractor and his subcontractors and suppliers of any tier engaged in supplying, manufacturing, construction, installation, commissioning and testing or any other service connected with the works, shall maintain ITPs appropriate for the services they provide that are accepted by the Supervisor. These accepted ITPs shall stipulate the necessary level and frequency of tests and inspections for each aspect of the works and also stipulate: • item(s) being inspected and tested; • the inspection and test activity; • acceptance criteria; • involvement of various parties including hold and witness points; • controlling specifications; and • certification/documentation/records to be generated in support of the inspection and test activities.” A new ITP should be produced to capture to offsite processes, and accepted by CRL; or the current ITP updated to include these offsite activities and again accepted by CRL. In the interim, Agglo should be engaged to ensure they are/have maintained appropriate records to support assurance of the offsite manufacture. Reference should also be made to Cxxx ITP Cxxx-LAO-O4-ITP-C101-50117 which covers offsite processes for the same product/manufacture location.
| 02SL - Stations (LUL) | Cxxx-NCR-002625 | NCR | TUN – Adhesion, Slip Resistance and Roughness testing not completed on installed screed |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2017-08-11 | 2017-08-03 13:54 | -8 | 2017-06-30 12:52 | Architectural - Flooring | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | A planned Crossrail surveillance was undertaken on 29th June 2017 to look at installation associated with screeding and tiling at Farringdon Station, in particular CP4 (benchmarked area) and CH1/CP2. A request was made for Screed Test Results for Testing completed on the installed Screed as required by Architectural Specification Section JM10 (Screeds); this being Adhesion, Slip Resistance and Roughness testing as stated below. “JM10.2202 b) Adhesion tests shall be carried out over the area of screeding works, in accordance with BS 8204: Part 1. JM10.2203 a) Testing for slip resistance shall comply with the requirements of BS 5395-1 and BS 8300 but also comply with LU slip resistance criteria as associated with a Grade A surface finish as defined in the latest revisions of LU Standards S1133 and S1135 to achieve the following Pendulum Test slip resistance Values (PTV):- JM10.2203 c) Roughness Test: Flooring shall be evaluated using a surface roughness meter, in accordance with the recommendations of the UK Slip Resistance Group, to obtain the surface roughness (Rz) value specified.” On discussion, it was identified that no Screed Testing had been completed to ensure compliance with the above. No agreement relaxing such requirements existed, i.e. FCD. As the testing had not been carried out, it is not clear what impact this may have on the constructed (and covered) works.
| 02SL - Stations (LUL) | Cxxx-NCR-002626 | NCR | TUN – __ tiling to a Setting Out drawing that is not the current version |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2017-07-28 | 2017-07-26 12:57 | -2 | 2017-06-30 13:06 | Architectural - Flooring | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | A planned Crossrail surveillance was undertaken on 29th June 2017 to look at installation associated with screeding and tiling at Farringdon Station. __ tiling works was witnessed at CH1/CP2. The __ supervisor provided the Setting Out drawing being installed to, this being Cxxx--A-DDA-M123_7-01021. The revision was noted as P09 (see picture attached). This was dated May 2016. On checking eB in the office it was identified that the ‘current’ revision was P10 dated Feb 2017. The BC management system was checked where the current version was showing as C03 dated Nov 2016. P10 did not exist on BC. The P10 revision shows clouded changes to CP2 and CP3a, where __ were working. The Design Management Plan for Cxxx (Cxxx--Z-STP-M123-50001) details the requirements for drawing control and issue to the construction teams to ensure currency. Based on the above, a breakdown has occurred in the drawing control process and issue to __ via BC resulting in __ working to a drawing two iterations old. The current installed works should be assessed against revision P10 to identify if any incorrect installation exists. In addition, as the surveillance was based on a sample, as part of the closure to this NCR should investigate to ensure this is a one off and not a common theme.
| 02SL - Stations (LUL) | Cxxx-NCR-002627 | NCR | ETH - North Yard – Level 0 Slab Couplers Cast at Incorrect Level |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-07-21 | 2017-07-18 09:15 | -3 | 2017-07-05 11:50 | Civil - Civil Engineering General | 4500 |  | Incorrect Installation | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | have started the construction of North Yard reinforced slab and during an inspection CRL have identified that a number of couplers have been cast, into Wall 33/Slab 0, at the incorrect Level. Please see attached photo and marked up drawing of location. Lower bottom mat couplers only provide 20mm concrete cover while top mat couplers have 60mm cover. A total number of 46 bottom mat bars are affected detailed on Cxxx-ATK-S-DWG-M123_1-50104.
| 02SL - Stations (LUL) | Cxxx-NCR-002628 | NCR | TUN – SCL – Blocked Reinjectable Tubes in ES1 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-08-11 | 2017-08-10 16:31 | -1 | 2017-07-04 16:17 | Tunnelling - Linings - Sprayed Concrete | 2500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following the answer to Cxxx-RFI-004341, undertook the injection of the reinjectable hoses in ES1 which was undertaken by a subcontractor ASF. Works carried out are detailed within report Cxxx--C4-RGN-M123-51262 Rev.1.0. During these injection works, it was found that a number of reinjectable hoses were blocked during the flushing of water through the tubes. See attached sketch, “ES1 Sketch” which shows which tubes were discovered to be blocked during this round of injection (tubes 5a, 6a). (Note that the presence of only one grout tube located at the crown of the tunnel is covered in Cxxx-NCR-002630)
| 02SL - Stations (LUL) | Cxxx-NCR-002629 | NCR | TUN - SCL - Leaks into Escalator Barrel 4, 5 and 6 (WTH ES1) |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-08-11 | 2017-08-30 14:02 | 19 | 2017-07-04 16:00 | Tunnelling - Tunnelling General | 10000 |  | System Defect | Repair | 2 (6-60k) | Complete | External Phenomenon - Not Defined | Completed |  | Following the installation of steps in the Cxxx escalator barrel, water has begun to appear at the joint between the Cxxx secondary lining and the mass fill stairs. This was originally believed to be water coming from the top as this had been left open to the elements, however as works have progressed and finishes have been installed, it is clear that there is a different source of this water which cannot be identified. This NCR has been raised to capture the repair works undertaken to the sprayed concrete lining works as agreed with all parties. (A separate NCR has been raised for leaks through the Cxxx-designed SH-W3 lining walls and mass-fill steps; Cxxx-NCR-002589). Note that this NCR does not apportion responsibility for this water ingress and is to capture agreement and records of all of the repair works done for this issue.
| 02SL - Stations (LUL) | Cxxx-NCR-002630 | NCR | TUN – SCL – Omissions in Cxxx Reinjectable Hose As Built Records |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-08-25 | 2017-08-24 09:09 | -1 | 2017-07-04 16:56 | Tunnelling - Tunnelling General | 2500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | As part of the SCL handover records, the Farringdon Tunnels team created document Cxxx--C4-LRC-M123-50489 Rev.2.0 which details the locations of all reinjectable hoses in the tunnels. Following the injection of the reinjectable hoses in ES1 as part of Cxxx-RFI-004341, it was found that the reinjectable hoses in VA1, VA2 and ES1 have not been detailed in the aforementioned document. These hoses are redlined on the Cxxx drawings (e.g. Cxxx-MMD-C4-DDB-M123_5-00210) but are not contained within document Cxxx--C4-LRC-M123-50489 Rev.2.0. It was also found that a single reinjectable hose within ES1 at the interface between the Sprayed Secondary Lining and Cast In Situ Concrete (one of the hoses in Cxxx-MMD-C4-DDD-M123_Z-00064 detail 2) has not been connected into the hose box and therefore cannot be used as a reinjectable hose. 1 of these hoses, however, can and has been used, please see attached sketch - Missing Hose in ES1.
| 02SL - Stations (LUL) | Cxxx-NCR-002631 | NCR | STW - MEP/Civils |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-12-01 | 2017-12-08 15:16 | 7 | 2017-07-06 16:08 | Civil - Utilities Engineering | 500 |  | Planning | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | In areas around the site MEP services have been installed through holes that do not allow a sleeve and adequate firestopping. Similarly in some locations, holes for dampers were not large enough to provide the required firestopping according to the manufacturer. Attached are the locations.
| 02SL - Stations (LUL) | Cxxx-NCR-002633 | NCR | ETH - ESS3 midlanding dimensions out of tolerance |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-08-18 | 2017-07-31 15:33 | -18 | 2017-07-19 15:56 | Civil - Civil Engineering General | 2000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | An as-built survey of the ESS3 midlanding has been carried out. (see attached) Wall W26 (wall below ESS3 midlanding) is too close to west. Also the top of the slab is slightly low.
| 02SL - Stations (LUL) | Cxxx-NCR-002634 | NCR | TUN - BUI - MCRs for Screeding not approved prior to commencing works |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-08-04 | 2017-08-02 09:37 | -2 | 2017-07-11 07:43 | Architectural - Flooring | 1000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | Following the conclusion of a Risk Reduction Meeting for Cxxx-EWN-002291 regarding water ingress into ES1, it was agreed that an RFI with a proposal to screed the escalator pit with falls would be raised. This was raised as Cxxx-RFI-004443 on the 29/06/2017. The RFI contained two new proposed materials to be used as a result of limited access to under the already installed escalator units. Neither of these materials were approved by Crossrail through the MCR process. Cxxx-RFI-004443 regarding these works had not been responded to before works commenced either (Cxxx-RFI-004443 was closed on 04/07/2017). ’s subcontractor __ started works in these areas on the 30th June and 3rd July and were originally due to only scabble the surfaces as preparation for these works. However, there was a misunderstanding between the engineers and __ supervisors which led to the primer and a layer of the screeding material to be applied before works were stopped.
| 02SL - Stations (LUL) | Cxxx-NCR-002635 | NCR | ETH - ESS5 midlanding Leve L-1 - concrete site control sheet missing |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-08-11 | 2017-07-14 10:37 | -28 | 2017-07-13 13:59 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Other human error | Completed |  | The concrete pour for the ESS5 midlanding at Leve L-1 has taken place on 18/02/2015. The Reinforced Concrete ITP Cxxx--C-ITP-M123-50009 Rev 6 requires the Structural Concrete Site Control Sheet Cxxx-SF-CON-0008_03 as a deliverable signed by the technician testing the concrete. The Structural Concrete Site Control Sheet Cxxx-SF-CON-0008_03 has been lost. can instead only provide the information recorded by the site engineer as well as the concrete cube test results from __ and the pre-pour checksheets (please find attached documents).
| 02SL - Stations (LUL) | Cxxx-NCR-002636 | NCR | WTH_Level -8 Snapped Earthing Bar |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-09-29 | 2017-09-27 07:35 | -2 | 2017-07-27 16:23 | Civil - Civil Engineering General | 3000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | One of the earthing bars on level -8 in the SH-W2 - location shown on the marked up drawing Cxxx--A-DDA-M123_8-76224 Mark Up has been accidentally cut flush with the concrete protective layer as per photo attached (bar #2), as a result __ cannot fix their clamp onto the bar. Please note bar #1 has successfully been straightened up without any defect/damage.
| 02SL - Stations (LUL) | Cxxx-NCR-002637 | NCR | TUN - PLT - Cast In Situ Pipe Omitted in Level -7 PTW West End |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-09-18 | 2018-10-30 13:56 | 42 | 2017-07-13 15:21 | Utilities Engineering - Water | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On drawing Cxxx--P-DDA-M123_8-50201, the Eastbound Under Platform Duct running at level -7 between CP1 and the WTH shaft areas has been omitted. This duct should have been cast in during the concreting of this area. Please see attached markup of the missing pipe.
| 02SL - Stations (LUL) | Cxxx-NCR-002638 | NCR | WTH_Level -6 Westbound Platform (Track side) __ Damage |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-09-22 | 2017-08-18 11:57 | -35 | 2017-08-10 13:11 | Civil - Civil Engineering General | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Westbound track possession for took place for a period of 2 weeks (05/06/17 - 19/06/17 08:00AM) to complete fireproofing and blockwork works. inspected the completed fireproofing and mastic protection (vertical durasteel) works on Monday 19/06/17 07:30AM and found 2 locations (see attached marked up drawing) where the durasteel protection of the mastic joint was damaged as per the photos attached.
| 02SL - Stations (LUL) | Cxxx-NCR-002639 | NCR | TUN - BUI - Slip Resistance Testing in CH1, CH2, CP2, CP3 and CP6 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-10-06 13:28 | 2017-08-24 13:30 | -43 | 2017-07-13 16:34 | Architectural - Flooring | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | On Friday 7th July 2017, Slip Resistance Testing was carried out by __ (using UKAS-accredited house __) on the tiles in the Concourse and Cross Passages. The testing was witnesses by Crossrail (__), London Underground (__on May), (__) and __ (__, __ and __). Testing was undertaken in CH1, CH2, CP2, CP3 and CP6 in random agreed locations. In several locations throughout the Concourses and Cross Passages, the Slip Resistance Values did not meet the requirement set out in the Architectural Specification, which states a minimum value of 45 SRV (JM41.1206). The results took a range of values, all of which were above the LU minimum requirement on 36 SRV.
| 02SL - Stations (LUL) | Cxxx-NCR-002640 | NCR | MEP - Benchmark not Approved before Installation Commenced |  | Contr | __ | FAR - Farringdon Station (West) |  | 2017-08-29 | 2017-08-29 11:56 | 0 | 2017-07-18 15:25 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Incorrect Installation | Reject | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Supply ductwork insulation bench mark offered up after some 40 / 50 meters has been installed. As The insulation installation was subsequently checked and found to be non compliant to the requirements of JY50:3111.
| 02SL - Stations (LUL) | Cxxx-NCR-002641 | NCR | ETH-Low Level installation for -3 slab |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-11-30 | 2017-11-24 16:53 | -6 | 2017-07-26 09:51 | Civil - Civil Engineering General | 3000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | An as built survey was carried showing the slab at Level -3 to be lower than the specified design level. Design level for L-3 slab is 100.650 and the as built ranges from 100.630 to 100.637 (see attached as built survey Ref: L-3 Slab As Built Survey).
| 02SL - Stations (LUL) | Cxxx-NCR-002642 | NCR | MEP - Installed 8" Firemain follows API specification not BS as per Works Information |  | Contr | __ | FAR - Farringdon Station (West) |  | 2017-08-25 | 2017-10-13 11:18 | 49 | 2017-07-18 14:33 | Materials - General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | The installed 8" (200mm) galvanised steel fire main pipework has been procured to meet the API (American Petroleum Industries) 5L specification and not the British Standard required by the works information. This is related to CRL-OBS-16963
| 02SL - Stations (LUL) | Cxxx-NCR-002643 | NCR | TUN - BUI - Straightedge Calibration |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-08-11 | 2017-08-11 16:41 | 0 | 2017-07-17 16:22 | Architectural - Flooring | 500 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Other | Completed |  | Following a surveillance by Leigh Holland of Crossrail on 29th June 2017 on the tiling works in CH1/CP2a, it was discovered that __, the tiling Subcontractor, were not using calibrated measuring equipment. Neither the straightedge nor the slip gauge used on site to measure the flatness of the tiling works were calibrated in accordance with BS 8204-1, UKAS LAB 21 and Main Contract Works Information Volume 2B. These standards stipulate that the flatness test must be carried out using a calibrated straightedge and slip gauge (or equivalent) in accordance with SR1, which allows for a maximum of 3mm underneath and 3m straightedge. A non-calibrated straightedge was being used with a 2mm packer gauge on site.
| 02SL - Stations (LUL) | Cxxx-NCR-002645 | NCR | WTH - Manhole 3 connection: 600mm void cored too large |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-12-08 | 2017-12-07 10:36 | -1 | 2017-07-28 08:47 | Civil - Civil Engineering General | 3500 |  | Supervision/Management | Repair | 3 (3-6k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | The proposed 600mm diameter hole on drawing Cxxx--P-DDD-M123_Z-50815 P04 (accepted for use in Cxxx-FCD-002791) was cored too large as shown in attachment " Cxxx WTH manhole 3 cored hole location 14 Jul 2017" and the photo.
| 02SL - Stations (LUL) | Cxxx-NCR-002646 | NCR | MEP - Elbows used for power conduit |  | Contr | __ | FAR - Farringdon Station (West) |  | 2017-10-06 | 2017-09-20 10:51 | -16 | 2017-08-17 07:44 | Electrical - General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Elbows have been used on the flexible conduit connections to the CER racks. Response to Cxxx-RFI-004279 specifically states that elbows are not to be used on power connections though. Refer to CRL-OBS - 17223
| 02SL - Stations (LUL) | Cxxx-NCR-002648 | NCR | TUN - BUI - Non UKAS Testing & No Calibrated Batching for Granazzo Tiles during Production |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-03-23 | 2018-03-15 09:38 | -8 | 2017-07-21 15:54 | Architectural - Flooring | 0 |  | Manufacturing Defect | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | It has been identified that no evidence of calibration is in place for the following as part of __’s production process for the manufacture of Granazzo Terrazzo Flooring on Crossrail: 1 Volumetric measuring of constituent materials for batching - no calibration certification 2 Dimensional measuring tools - not UKAS 3 SRV testing equipment - not UKAS
| 02SL - Stations (LUL) | Cxxx-NCR-002649 | NCR | WTH – Damage to block work at Level -6 Westbound platform Leading to CP1 and Level -1 MNS7 stairs along western wall |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-09-08 | 2017-09-07 07:29 | -1 | 2017-07-24 14:43 | Civil - Civil Engineering General | 2500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | Cxxx--C-ITP-M123-50277 Rev 5.0 activity 5.5 states ‘Exposed corner reveals will be protected once wall is complete’. The corner on level -6 Westbound platform CP1 and the wall on level -1 MNS7 stairs were not protected before damage occurred (see attached photos and location drawings for level -6 and level -1).
| 02SL - Stations (LUL) | Cxxx-NCR-002650 | NCR | WTH - one no. 28 day concrete strength test not carried out |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-09-29 | 2017-08-15 09:05 | -45 | 2017-07-28 08:07 | Civil - Civil Engineering General | 750 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | On 14 June 2017 cast part of the level 0 ITH slab at the top of PST stairs, an upstand at level 0 at the south side of the upper apse and the level -1 gridline K infill on the north side. 8 no. concrete cube samples were taken. However, only 1no. cube was crushed at 28 days instead of 2no.
| 02SL - Stations (LUL) | Cxxx-NCR-002651 | NCR | ETH - Blockwork not signed off before starting render works |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-08-25 | 2017-08-25 13:27 | 0 | 2017-07-26 15:40 | Architectural - Masonary | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | __ have started rendering Lindsey Street and Long Lane Facades with the blockwork documentation signed off by __ and but not Crossrail.
| 02SL - Stations (LUL) | Cxxx-NCR-002652 | NCR | ETH - North Yard Insufficient cover for Hydrophilic Waterbar |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-11-17 | 2017-11-17 14:35 | 0 | 2017-07-27 07:38 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | During the construction of the North Yard slab , installed __swell A-2010 Hydrophilic water-stop. This was installed on the construction joint between Wall 33 and the North Yard slab. See attached Drawing for location. installed the Water-stop at 25-30mm cover (as per CRL-OBS-17251) (See attached photo 1) from the top of concrete. In addition installed the water-stop between the 2 layers of steel. Some of this water-stop was within 10mm of the rebar steel. (See attached photo 2)
| 02SL - Stations (LUL) | Cxxx-NCR-002653 | NCR | MEP Installation of MAP dampers without approved MCR |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-09-23 10:31 | 2017-09-20 09:13 | -3 | 2017-07-27 13:24 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | E__ dampers have been installed without MCR being updated to current supplier.
| 02SL - Stations (LUL) | Cxxx-NCR-002654 | NCR | ETH - The MRS 4 (skim coat material) and fixings (for the beads) used for rendering at Lindsey Street Facade not covered in the approved MCR |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-10-01 | 2017-10-02 15:42 | 1 | 2017-08-02 14:48 | Archaeology - General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Further to the Surveillance (Cxxx--O4-RGN-M123-51492 Rev 1.0) carried out on the application of external render system at Lindsey Street Façade – Level 0 & 1, MRS 4 (skim coat material) and the fixings (for the beads) were not included in the approved MCR – Cxxx--C-LRC-M123-50885 Rev 1.0
| 02SL - Stations (LUL) | Cxxx-NCR-002655 | NCR | ETH-Sub Package 16 Missing __ sample sheets |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-08-18 | 2017-08-04 14:04 | -14 | 2017-08-04 11:00 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Other human error | Completed |  | For ETH South Basement - Sub Package 16 - Upper Escalator Ramp (L-1 to L-3) including extension to Platform L-1, Dividing Wall & Column C11 (L-1 to L0), is missing 2 No. __ Checksheets required as a deliverable record as per the Reinforced Concrete ITP Cxxx--C-ITP-M123-50009 Rev 10. can instead only provide the information recorded by the site engineer as well as the concrete cube test results from __ and the pre-pour checksheets (please find attached documents Ref: UER pre pour checksheet, EX2437, W2 pre pour checksheet & EX2045).
| 02SL - Stations (LUL) | Cxxx-NCR-002656 | NCR | MEP installation - __" Zinc rich paint incorrectly applied |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-09-22 | 2017-09-04 12:35 | -18 | 2017-08-04 15:46 | Electrical - Cable Management | 2000 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | A surveillance visit was carried out on Jul 27th 2017 WTH for conformance of Zinc rich __ paint application. It was reported that upon visual inspection of cut conduits (location – WTH -2 area WTH L.-2 circular shaft) it was noted that zinc rich paint had not being applied immediately after erection or after damage. MCR reference – CRL-MCR-002107
| 02SL - Stations (LUL) | Cxxx-NCR-002657 | NCR | Tun – The support bracket used for the Terrazzo skirting Kerb at the Tunnels was not covered in the approved MCR. |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-10-01 20:22 | 2017-08-22 20:25 | -40 | 2017-08-11 15:38 | Architectural - Flooring | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | Further to the Surveillance (Cxxx--O4-RGN-M123-51498 Rev 1.0) carried out on the installation of the Terrazzo Skirting Kerb at the Tunnels, the support bracket used was not included in the approved MCR - Cxxx--A-LRC-M123-50140 Rev 1.0 (for the Stainless Steel Screed retaining angles & Shims).
| 02SL - Stations (LUL) | Cxxx-NCR-002659 | NCR | Cxxx MEP - Incorrect Revision Drawings being used on Site |  | Contr | __ | FAR - Farringdon Station (West) |  | 2017-11-25 | 2017-11-22 10:32 | -3 | 2017-08-24 10:56 | Mechanical - Hot & Cold Water Supplies | 3000 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | During a site surveillance of the East Ticket Hall Chilled Water Installation activity (Cxxx--04-RGN-M123-51490) it was noted that the site team were not using the latest revisions of the drawing Cxxx--M-DDE-M123_Z-75103 Revision P013 on site - P014 supplied to auditor (it is noted that revision P14 was at Code 3 during the audit) Cxxx--M-DDA-M123_2-75211 Revision P08 on site - P09 supplied to auditor
| 02SL - Stations (LUL) | Cxxx-NCR-002661 | NCR | ETH - Blockwork not signed off before starting acoustic panel installation |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-09-19 | 2017-09-12 10:48 | -7 | 2017-08-29 11:29 | Architectural - General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | __ have started with the acoustic panel installation with the blockwork documentation signed off by __ and but not Crossrail.
| 02SL - Stations (LUL) | Cxxx-NCR-002662 | NCR | ETH - Level 0 Signage Band Column 2A-1B |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-11-10 | 2017-11-13 17:32 | 3 | 2017-08-30 16:50 | Architectural - General | 500 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Personnel Error - Not Defined | Completed |  | The piece of the signage band Column 2a-1b highlighted in the attached drawing Cxxx--X-DWG-M123_52006 has been fabricated 14 mm shorter. The designer has been consulted and they have provided two acceptable options (Please refer to the email attached for details)
| 02SL - Stations (LUL) | Cxxx-NCR-002663 | NCR | ETH - Damaged Geothermal pipe due to windpost installation |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2019-01-25 | 2019-01-18 16:54 | -7 | 2017-08-31 16:37 | Civil - Civil Engineering General | 3000 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | While drilling to install of Package 11 windpost Level -3 to Level -2, has drilled through a geothermal pipe cast into Level -2 slab. Refer to Package 11 Cxxx-ATK-S-XSK-M123-50011 and attached extract drawings for location
| 02SL - Stations (LUL) | Cxxx-NCR-002665 | NCR | ETH - External cladding clashing with dry riser fire mains inlet. |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-12-01 | 2017-11-29 12:10 | -2 | 2017-09-11 16:21 | Architectural - Roofing & Exterior Treatment | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The installation of the steel structure for the cladding façade on the external of the East ticket hall is clashing with the pipework and the cabinet for the dry riser fire main inlet (img: DSCI0091).
| 02SL - Stations (LUL) | Cxxx-NCR-002667 | NCR | ETH- Level 0 Signage band Column 1B-1C plate 90 degrees off |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-12-17 | 2017-12-01 17:16 | -16 | 2017-11-10 11:26 | Architectural - General | 500 |  | Manufacturing Defect | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Other human error | Completed |  | We have noticed that one of the plates attached to the signage band between columns 1B and 1C has been fabricated 90˚ off the required orientation according to the drawings. Find attached a photo of the connection fabricated and sketch showing location of the plate.
| 02SL - Stations (LUL) | Cxxx-NCR-002668 | NCR | MEP - ETH - Level -5 - [Cxxx-ELEC-ESDEX2H] - Conduits through WII Beam |  | Contr | __ | FAR - Farringdon Station (West) |  | 2017-10-02 | 2017-10-13 08:56 | 11 | 2017-09-14 14:03 | Electrical - Lighting | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | In the ETH Level -5 in the Escape Stairs II, conduit has been drilled into a structural column. This is against the Wi Column & Wi Beam - guidance for holes and fixings. This is linked to CRL-OBS-18276.
| 02SL - Stations (LUL) | Cxxx-NCR-002669 | NCR | MEP - WTH - Levels -2/-3 - [Cxxx-MECC-HCVWN1A] - Insulation of supply ductwork |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-09-29 | 2017-10-02 12:06 | 3 | 2017-09-15 10:08 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Insufficient information made available to the worker. | Completed |  | As per CRL-OBS-17306, the benchmark for the thermal insulation on WTH Level -2/-3 was rejected. The insulation did not meet the requirements set out in Cxxx--M-RSP-M123-50013 clause JY50.
| 02SL - Stations (LUL) | Cxxx-NCR-002670 | NCR | ETH - Ventshaft __ Structural beam out of tolerance. |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-08-04 | 2017-11-24 15:04 | -253 | 2017-09-18 08:43 | Architectural - General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | It was identified that the 4 beams highlighted in red on the attached drawing (NCR-2670-01) have been installed out of tolerance. Sketch NCR-2670-02 shows where the beams have been installed out of position by 100mm to the east.
| 02SL - Stations (LUL) | Cxxx-NCR-002671 | NCR | MEP - STW - All Levels - [Cxxx-PUHC-SWPWN1B/C/D & Cxxx-PUHC-SWPEN1B] - Pumped Drainage Couplings |  | Contr | __ | FAR - Farringdon Station (West) |  | 2018-02-16 | 2018-02-15 17:46 | -1 | 2017-09-26 10:59 | Mechanical - Public Health Engineering | 60000 |  | Supervision/Management | Rework | 2 (6-60k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | Following a site review of the installation, it was observed that an inadequate pumped drainage coupling type has been installed. This installation is not in line with the specifications. There are 4No pumped systems in ETH & WTH where pumped system couplings are only rated to a water pressure of 5Bar. The 4No pumped systems are over the 5bar pressure rating based on attached __ Public Health Calculation Sheet. Part of the system has a closed head pressure of 7.5bar and has to be tested to 1.5 time the closed head pressure of the system therefore needs to be tested up to 11.2bar,11.03bar and 7.14bar on parts of the pipework. These are on pumped systems: 1No 150mm system on the ETH 2No 100mm systems on WTH 1No 50mm system on WTH Saint-Gobain issued incorrect information relating to sump pumped pipework systems.
| 02SL - Stations (LUL) | Cxxx-NCR-002673 | NCR | TUN - BUI - Defective LED Circuit Boards in PES Lighting |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-02-23 | 2018-02-14 08:06 | -9 | 2017-09-29 16:18 | Architectural - General | 35000 |  | Manufacturing Defect | Repair | 2 (6-60k) | Complete | Material/Preservation Problems - Other | Completed |  | The Flair LED Light Boxes supplied by __, at Tottenham Court Road, when energised had an inconsistent lit appearance, a ‘checkerboard’ effect on the front panel, which is against the Cxxx Specification. This has now been raised as an issue with the light boxes supplied at Farringdon Station. This fault effects every PES lightbox unit along both platforms.
| 02SL - Stations (LUL) | Cxxx-NCR-002674 | NCR | ETH - __ Density testing |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-11-24 | 2017-11-06 15:07 | -18 | 2017-09-29 14:58 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | During the installation of __ to the underside of Level L+1 in the North Yard some of the wet density tests have been out of tolerance according to __ Type M-II ITP Cxxx--C-ITP-M123-50299 Rev 3. The Wet Density Test (Item 3.3) was out of tolerance but the Wet Density Nozzle Test (Item 3.4) was always within tolerance. The current ITP for the installation of __ Type M-II Cxxx--C-ITP-M123-50299 Rev 3 requires a Wet Density Test (Item 3.3) and a Wet Density Nozzle Test (Item 3.4). Both tests are required twice a day during the application of __ Type M-II. It has been noted, that the tolerance for the wet density test (794-809kg/m3) is currently much tighter than the density tolerance for the wet density nozzle test (1009-1394kg/m3). has sought clarification for this from __. __ has confirmed that the key value for the property of the __ is the sprayed density measured at the nozzle (Item 3.4). Please find attached confirmation from __. The total density range for the wet density test (item 3.3) should be 751 - 922kg/m3 taking into account the allowable 17-21 litres of water per bag of __. All density test values for Item 3.3 have always been within the "updated" density test tolerance (751 - 922kg/m3) during the installation of __ in the North Yard.
| 02SL - Stations (LUL) | Cxxx-NCR-002675 | NCR | WTH - Low slab and upstand levels beneath windpost baseplates |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-04-27 | 2018-02-12 15:35 | -74 | 2017-10-23 12:42 | Civil - Structural Engineering | 4000 |  | Incorrect Installation | Use As-Is | 3 (3-6k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | When as-built surveys of the windposts at the WTH were completed, __ made aware that some slab and upstand levels were low (beneath where the windposts are located). Initially __ proposed to set their baseplates at the correct design level by introducing more steel packs under the baseplates and casting a thicker layer of grout. 1. __ (windpost designers) rejected this proposal as the grout thickness range defined in their windpost sketch packages was critical for the anchor design. As such instructed __ to install the windposts 'low' - in some cases this was outside of NSSS tolerances for column baseplate levels (+/-5mm). This represents part 1 of the NCR. Please see the attached QICS2 handover checksheet and as-built survey which provides an example of where the windpost baseplates are outside of tolerance. 2. The low slab levels also represent a non-conformance against the slab level tolerances of +10mm / -0mm as defined in drawing Cxxx-SWN-S-DDL-M123_Z-00101 (referenced below). The worst case slab level descrepency is -36mm. 3. The low upstand levels may also represent a non-conformance against the thickness of members / dimensions of cross sections of +15mm / -0mm. This will depend on the level of the soffit underneath the upstands. (These will not be checked – see explanation in ‘proposed answer’ section). The worst case upstand level descrepency is -30mm. Please see the attached ‘windpost non-conformances' spreadsheet which highlights where non-conformances have occurred with both the column baseplates and the slab/upstand levels. Where the windposts have been numbered, see the attached pdf 'windpost diagram key' which defines the numbering system. Each windpost has been given a unique number to highlight where the slab/upstands are out of tolerance. The first part of the number relates to the package number of the windpost in question. The attached ‘as-built surveys summary drawings’ pdf shows the location of the windpost packages along with the worst case level discrepancy for each package.
| 02SL - Stations (LUL) | Cxxx-NCR-002677 | NCR | WTH Level +2 and +3 nails cast into cover zone of upstands |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-01-12 | 2017-12-20 15:05 | -23 | 2017-10-12 07:44 | Civil - Civil Engineering General | 3000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | After inspection carried out on Level +2 & Level +3 perimeter upstands, it was noticed that some nails used to fix shutter in position were cast into the cover zones of some upstands. Refer to attached marked-up drawings indicating locations affected.
| 02SL - Stations (LUL) | Cxxx-NCR-002679 | NCR | TUN - BUI - Incorrect screed mesh installation in PTE |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-10-27 | 2017-10-27 16:20 | 0 | 2017-10-13 10:23 | Architectural - Flooring | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On Monday 9th October 2017, it was discovered by a Crossrail Field Engineer that the D49 mesh was installed incorrectly in the screeding works in the Eastbound Platform. As stipulated in the Inspection and Test Plan (Cxxx--A-ITP-M123-50011 Rev 2.0), the mesh is required to be installed in the the middle third of the screed. In some locations at the end of the bay screeded for that day, the mesh in the day joint was not in the middle third, but in fact too low. It was also discovered that the mesh was omitted for an approximately 1m length of screed.
| 02SL - Stations (LUL) | Cxxx-NCR-002680 | NCR | WTH - Package 32 - Low 28 day cube strength results for C1/C2 concrete |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-10-27 | 2017-10-19 15:27 | -8 | 2017-10-13 14:55 | Civil - Civil Engineering General | 2000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Not Defined | Completed |  | Having reviewed recent concrete cube results for the C1C2 (10mm) mix, have noticed that the recent 28 day strength result for the pour on 19/06/2017 is below the design strength of 60N/mm^2. The attached extract from ’s BSEN 206 Compliance table shows that this pour doesn’t satisfy testing criteria 3, with a 28 strength result of 55.4 N/mm^2.
| 02SL - Stations (LUL) | Cxxx-NCR-002685 | NCR | ETH Sliding Gate Clashes |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-11-22 | 2017-11-24 16:10 | 2 | 2017-10-23 10:06 | Architectural - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The sliding gate head track clashes with some of the bolts that fix the signage band to the primary structure. Specifically we require 47.5mm between any part of the signage band and the center of the sliding gate head track. Details of the space available onsite is marked on the attached survey.
| 02SL - Stations (LUL) | Cxxx-NCR-002686 | NCR | WTH Mastic to underside of PST stairs exceeding maximum allowable thickness |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-02-09 | 2018-01-30 16:18 | -10 | 2017-12-08 16:54 | Civil - Civil Engineering General | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In several locations highlighted in the attached document mastic is exceeding 40mm limit determined by __ detail stated in Cxxx-FCD-002553.
| 02SL - Stations (LUL) | Cxxx-NCR-002687 | NCR | WTH - SHW1 - Breaking out of finished floor to install metalwork |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-03-02 | 2018-03-01 10:10 | -1 | 2017-10-30 17:27 | Civil - Civil Engineering General | 7000 |  | Design | Repair | 2 (6-60k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | __ are installing various metalwork components in the Circular Shaft (SHW1) comprising of steel staircases and balustrade posts. In order to facilitate the installation of these components, had to undertake various works, which can be summarised in the following 3 situations: Level -6: • This level was previously screeded to FFL 86.100m prior to metalworks commencing • 4no. pockets of screed had to be broken out to accommodate metalwork fixings • The slab levels were then surveyed, and a 120mm discrepancy was found between SSL indicated on __ drawings and the as-built). __’s drawings stated that the MNS 3B staircase was to be fixed to SSL, but the level on Metalwork drawing Cxxx--X-DWG-M123_Z-52020 P05 with a SSL of 85.950m differed to that on the structural drawings Cxxx-SWN-S-DDA-M123_7-79601 C04 and Cxxx-SWN-S-DDA-M123_&-59601 C04 which stated a SSL of 85.856m with a fall away from the track of 1:100. undertook a level survey of these areas to show the constructed slab was approximately 120mm below the SSL on drawing 52020. • As such, constructed 4no. plinths to locally raise the SSL in these areas, which was discussed and agreed with __ within the attached RFI (Cxxx--RFI-01913) • Note that for the stair stringer, a box-out was left in the screed, so no break-out was required. An additional plinth was constructed to align with the SLL on the __ drawings. Level -5 and Level -4: • For Staircase 3B, concrete plinths were cast around the voids to FFL to support the metalwork. • The plinths were then found to be redundant as the metalwork is fixed to SSL. The requirement to fix to SSL can at this level can be seen on Cxxx--X-DWG-M123_Z-52020 P05. had cast concrete plinths in these areas in line with Cxxx--RFI-01006 (attached). However, the information conveyed in this RFI was incorrect, as the staircases and balustrade posts have always been fixed to SSL, not FFL as stated in the RFI. • The pockets had to be broken out to allow the metalwork to be fixed to SLL. • (It is proposed that these pockets are now filled with screed to FFL). Level -4 and Level -3: • For staircase 3A, L-4 and L-3 were previously screeded to FFL 97.320m & FFL 102.600m respectively, prior to metalworks commencing. • The requirement to fix to SSL can at these levels can be seen on Cxxx--X-DWG-M123_Z-52018 P05. As in situation 1, had applied screed fully to these areas in the interest of site progress, as the location of the metalwork wasn’t known. • 3no. pockets (2 columns & stairs string) of screed had to be broken out to accommodate metalwork fixings to L-4 SSL. • 5no. pockets (4 balustrades & stairs string) of screed had to be broken out to accommodate metalwork fixings to L-3 SSL. • (It is proposed that these pockets are now filled with screed to FFL).
| 02SL - Stations (LUL) | Cxxx-NCR-002688 | NCR | WTH - Pre-Start Assurances not completed correctly for Acoustic Panels and External Render |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-12-01 | 2017-11-14 13:27 | -17 | 2017-11-13 16:14 | Civil - Civil Engineering General | 2000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | Quality Assurance Check Sheets for both Acoustic Panels (__) and External Render (__s) not signed off by Crossrail before works commenced as per ITP hold points: 1. Acoustic Panels ITP - Cxxx--C-ITP-M123-50320 Rev. 2 - line 2.1. Checksheet ‘QCC 01 REV 01 FRAME WORK, FIXINGS and INSTALLATION’. a. Not signed off: i. Level +2 ii. Level 0 iii. Level -1 (Room 2/793 Walls & Ceilings) iv. Level -2 (Room 3/793 Walls & Ceilings) v. Level -3 (Room 3/793 Walls & Ceilings) 2. External Render ITP - Cxxx--C-ITP-M123-50020 Rev.1 - line 2.1. Checksheet ‘Quality Control Check’. a. Not signed off: Zones A, C, D, E, I, and K.
| 02SL - Stations (LUL) | Cxxx-NCR-002689 | NCR | MEP - BMS equipment installed within Controls Enclsure without approved MCR |  | Contr | __ | FAR - Farringdon Station (West) |  | 2018-01-25 | 2018-01-26 16:44 | 1 | 2017-11-16 16:15 | Mechanical - Mechanical Engineering General | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Materials installed within __ BMS Control enclosures, were not on the current MCR list
| 02SL - Stations (LUL) | Cxxx-NCR-002691 | NCR | MEP - STW - Use of lagging materials without approved MCR |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-12-01 | 2017-11-30 19:19 | -1 | 2017-10-25 10:38 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | The lagging subcontractor SIS (working under our ductwork subcontractor Hargreaves) have proceeded to install their thermal insulation without an MCR in place for the ancillary items used with the system, specifically the self-adhesive pins and aluminium tape.
| 02SL - Stations (LUL) | Cxxx-NCR-002692 | NCR | ETH - Installation of the Fire-Stopping __ Dampers (as a benchmark) at Level-7 with P-status drawing without an FCD in place |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-01-23 | 2018-01-25 07:32 | 2 | 2017-10-25 11:26 | Architectural - Walls | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Failure to follow status stamp | Completed |  | Further to the surveillance (Cxxx--O4-RGN-M123-51516) carried out on the installation of the Fire-Stopping __ Dampers at Level -1, the P-status drawing (Cxxx--X-DWG-M123-54663 P01) was used for construction without an FCD in place.
| 02SL - Stations (LUL) | Cxxx-NCR-002697 | NCR | WTH – Structural steelwork – paint damage to Area 13 temporary beams |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-01-26 | 2017-12-07 10:50 | -50 | 2017-10-31 18:11 | Structural Engineering - Steel Member | 3000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | There are areas of paint damage to the 5no. structural steel beams in Area 13, level 0 at the West Ticket Hall. The beams are highlighted on the attached drawing ‘Cxxx--X-DWG-M123-50203 C2.0 – marked up’. The attached pdf ‘W38 to W40 SS paint repairs’ includes site photographs showing some example areas of the paint damage.
| 02SL - Stations (LUL) | Cxxx-NCR-002698 | NCR | MEP - STW - Levels -4/-5 - [Cxxx-ELEC-ESDXX1K] - Operation of the ACB in main switch panels ETH and WTH |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2019-05-31 | 2019-12-18 14:50 | 201 | 2017-11-02 11:41 | Electrical - Switchgear | 15000 |  | Testing and Commissioning | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Other | Completed |  | It has been identified that Main Switch Boards A&B (WTH & ETH) in certain operational modes, “LOCAL/ REMOTE”, and by means of test the mains Switch Board ACB does not disconnect mains supply if an under or loss of volts is detected These indicate a noncompliance with the requirements stated in, CRL1-XRL-R3-RSP-CR001-50002, paragraph 6.4 regarding operation and output signals. The following has been identified : Observation 1 When the Switchboard A is in Local control mode, ACB A Closed and Bus-coupler ACB Open. When the phase failure on switchboard A is simulated ACB A does not open. Observation 2. When the Switchboard A is in Remote control mode, ACB A Closed and Bus-coupler ACB Open. When the phase failure on switchboard A is simulated ACB A does not open. Observation 3. When the Switchboard B is in Local control mode, ACB B is open, ACB A is closed and Bus-coupler ACB is open we cannot close ACB B. We can only close ACB B when ACB A and Bus-coupler ACB are all open. Observation 4 When the Switchboard B is in Local control mode, ACB B Closed and Bus-coupler ACB Open. When the phase failure on switchboard B is simulated ACB B does not open. Observation 5. When the Switchboard B is in Remote control mode, ACB B Closed and Bus-coupler ACB Open. When the phase failure on switchboard B is simulated ACB B does not open.
| 02SL - Stations (LUL) | Cxxx-NCR-002699 | NCR | MEP - WTH - Level -1 - [Cxxx-ELEC-ESDWX2D] - Damaged to Installed MEP Assets during blockwall installation |  | Contr | __ | FAR - Farringdon Station (West) |  | 2018-01-19 | 2018-01-19 12:55 | 0 | 2017-11-27 12:54 | Electrical - Cable Management | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Following the construction of the
| 02SL - Stations (LUL) | Cxxx-NCR-002702 | NCR | MEP - STW - All Levels - Chilled Water System Insulation Blocks |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-03-30 | 2018-03-27 13:47 | -3 | 2017-11-06 09:34 | Mechanical - Piping | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | A number of cracked and damaged Foam Glass insulation blocks were identified during surveillance carried out by __/CRL on chilled water pipe installation on 25/08/17. As the works progressed more damage and cracks were occurring and a large number of failures were identified by during a detail surveillance (as per attached Insulation Blocks Failure Rate Table). Early Warning “Cxxx--EWN-01010”was raised accordingly. Due to ongoing concern __ arranged a site walkout with Technical Engineer for the Foam Glass insulation blocks supplier “__” and __ Mechanical Quality Manager (__) on Tuesday 31st October 2017. During walkout the following issues were identified. See listed below and attached photos/documents. 1. Low level blocks in walkways being damaged (site issue). 2. 3 No different insulation block method installed. 3. Blocks with foil face tape cut flush with metal sleeve - not from __. 4. Blocks with foil face and no metal sleeve - not from __. 5. Blocks cut short and within the metal sleeve - supplied by __. 6. Cracked & chipped blocks and metal sleeve damage caused during installation. Misalignment and over tightening of brackets causing cracks. 7. Gaps between the pipe and the blocks where the insulation vapour seal cannot be maintained and the pipe is free to vibrate. 8. It was also established that the blocks supplied by __ as described in item 4 do not match the Foam Glass method of installation requirements as detailed CRL-MCR-004485 and APR – 341. 9. APR-341 details attached and alluded to in the MCR are for sliding brackets and state not to use the blocks for fixed point loads. All of the foam glass blocks installed are point loaded /supported. 10. Blocks incorrectly installed to the manufacturers load distribution requirements. 11. Blocks / brackets are installed too close to tee unions valves etc, where correct lagging cannot be carried out to maintain the required vapour barrier
| 02SL - Stations (LUL) | Cxxx-NCR-002703 | NCR | TUN - SCL - Cast In __ Missing - PTW East End |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-12-05 | 2017-12-04 11:18 | -1 | 2017-11-07 16:21 | Civil - Tunnelling | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | Following a survey undertaken by Cxxx on the platform, prior to the installation of the Platform Screen Doors, it has been identified that a section of halfen in Platform Tunnel West has not been cast into the concrete as per the Works Information drawings. Drawing Cxxx--S-DDA-M123_7-10113 (C02) shows halfens to be installed on the platform. See the attached sketch (Cxxx--S-DDA-M123_7-10113- SW) which shows the halfen which has been omitted.
| 02SL - Stations (LUL) | Cxxx-NCR-002704 | NCR | WTH – 28-day Design Strength not Achieved for C1/C2 Concrete Mix for pour in WTH Package 44 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-12-08 | 2017-11-24 12:53 | -14 | 2017-11-17 13:31 | Civil - Civil Engineering General | 2000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Not Defined | Completed |  | Having reviewed recent concrete cube results for the C1C2 (10mm) mix, have noticed that the recent 28 day strength result for the pours on 26/06/2017, 05/07/2017, 19/07/2017 and 22/07/2017 is below the design strength of 60N/mm^2. The attached extract from ’s BSEN 206 Compliance table shows that the pours on 26/06/2017, 05/07/2017 and 22/07/2017 don’t satisfy testing criteria 3, and the pours on 26/06/2017 and 19/07/2017 don’t satisfy testing criteria 2.
| 02SL - Stations (LUL) | Cxxx-NCR-002705 | NCR | MEP - WTH & ETH Axial Fan Frame Supports |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2018-01-30 | 2018-01-26 11:50 | -4 | 2017-11-22 08:11 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Insufficient information made available to the worker. | Completed |  | The axial fan frame supports installation at the ETH level -2 and WTH -1 does not meet the Crossrail M&W specification JA.6402 - Access for Plant and Equipment & JY41.1303 - Durability and Maintainability requirements in that the fans frame supports are installed as such that the bottom fan units cannot be individually and independently removed without having to dismantle major component, supports and sections of ductwork. Which has introduced extra over manual handling H&S risks, management time and cost to the IM's See photo details on CRL-OBS-19684
| 02SL - Stations (LUL) | Cxxx-NCR-002706 | NCR | WTH – Column Encasement – Defects to beam infills on Level +2 along GLK |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-01-26 | 2018-01-26 16:47 | 0 | 2017-11-22 18:59 | Civil - Civil Engineering General | 3000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Upon inspection of the beam infill on Level +2 along GLK several defects were noted which require rework: 1) Cracking to the East and West faces of the beam infill between GLs 13 and 16 2) Foam cast into beam infill along Eastern edge of infill 3) Chipping to North Eastern corner of infill between GLs 7 and 9
| 02SL - Stations (LUL) | Cxxx-NCR-002707 | NCR | Temporary roof MCR |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-01-31 | 2017-11-27 13:31 | -65 | 2017-11-24 17:14 | Architectural - Roofing & Exterior Treatment | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | The ETH temporary roof installation started on 20/11/2017 with Cxxx--C-LRC-M123-50926 rev 1 approved as code 1 but that MCR document didn't contain all fixing details. Cxxx--C-LRC-M123-50926 rev 2 has been now submitted and approved as code 1 including that material information so this can be closed.
| 02SL - Stations (LUL) | Cxxx-NCR-002708 | NCR | MEP Installed Assets not as Per the Current 3D Model |  | Contr | __ | FAR - Farringdon Station (West) |  | 2018-05-29 | 2018-06-11 10:50 | 13 | 2017-11-27 14:02 | Systems - Other | 6000 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | On a review of __ Ceiling design it was identified a number of assets have been installed not as per the current 3D model and drawings. This includes 1 Lighting 2 CCTV 3 PAVA 4 Trunking 5 Cable Trays This may be due to out of sequence working. __ to review installation history and sequence of approvals and changes.
| 02SL - Stations (LUL) | Cxxx-NCR-002709 | NCR | ETH - Level -1 Door opening head breakout |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-03-02 | 2018-02-28 08:58 | -2 | 2017-11-28 20:09 | Civil - Civil Engineering General | 2000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | At the moment are doing surveys of all structural opening to enable a subcontractor to fabricate the permanent doors that will be installed. surveyed the structural opening for 2-ED08 which is on Level -1 Trap shaft Wall 34 (See attached drawings for location) and discovered that the concrete on the door head was cast 50mm lower than design.
| 02SL - Stations (LUL) | Cxxx-NCR-002713 | NCR | TUN - BUI - Inclined Lift Screen Works Started Without Approved Drawings |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-01-26 | 2018-01-24 16:09 | -2 | 2017-12-01 09:41 | Architectural - Glazing | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | have (as of 28/11/17) commenced the installation of the inclined lift screen in ES2, separating lift 9 and escalators 10 and 11. These works have commenced as per programme. Cxxx-FCD-002985 was raised on 17/11/17 to gain acceptance of the use of P status drawings for construction, however was missing R__ calculations from __ blast engineers. To date (01/12/17) these calculations have not been made available to and hence the FCD has not been accepted. As a result, works have started on site without approved drawings or accompanying FCD and hence this NCR has been raised.
| 02SL - Stations (LUL) | Cxxx-NCR-002714 | NCR | ETH - __ Ventshaft wall fixing |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-12-15 | 2017-12-15 13:52 | 0 | 2017-12-01 12:21 | Architectural - Walls | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | During a surveillance carried out by on vent shaft durasteel wall, it was identified that the fixing were installed at 250mm centres rather than 200mm as specified on the ITP and approved drawings.
| 02SL - Stations (LUL) | Cxxx-NCR-002715 | NCR | ETH - Commencing work in the __ vent shaft wall prior to closing existing NCR |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-12-15 | 2017-12-04 09:22 | -11 | 2017-12-01 12:37 | Architectural - Walls | 2000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | Work at the vent shaft continued while the following Cxxx-NCR-002670 was not formally closed. This was discussed informally with CRL engineering manager and agreed that the final solution will be use as is.
| 02SL - Stations (LUL) | Cxxx-NCR-002716 | NCR | ETH - Installation of Steel Mesh Without Approved MCR |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-02-02 | 2017-12-19 12:16 | -45 | 2017-12-04 09:06 | Architectural - General | 2000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Steel mesh types BAL-119 and BAL-163 mesh have been installed as part of the BOH stairs MNS06 and mesh screens within the Inclined Lift Machine Rooms at Levels -1 and -4 without approved MCRs for these materials. These materials will be covered under MCRs Cxxx--X-LRC-M123-51203 and 51204.
| 02SL - Stations (LUL) | Cxxx-NCR-002717 | NCR | WTH - ITP requirement for as-built slab surveys not carried out for multiple slabs |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-03-30 | 2018-02-12 15:35 | -46 | 2017-12-06 08:23 | Civil - Civil Engineering General | 750 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | When as-built surveys of the windposts at the WTH were completed, __ made aware that some slab and upstand levels were low (beneath where the windposts are located). These physical non-conformances were raised through Cxxx-NCR-002675 (referenced below) but a procedural NCR is also required as these as-built surveys should have been completed as part of the ITP checks immediately after the construction of the slabs / upstands. There are multiple reinforced concrete ITPs which cover the slabs/upstands in question – all the ITPs reference the same pre & post-pour concrete checksheet. Check item 22 is a requirement to complete a post-pour check to verify the line, level and plumbness of the cast concrete. This box has been ticked either without the surveys being carried out or without surveys of sufficient detail. The affected ITPs are referenced below.
| 02SL - Stations (LUL) | Cxxx-NCR-002718 | NCR | ETH - MEP Clashes with Inclined Lift Machine Room Mesh Screen Level -4 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-09-14 | 2018-09-03 13:11 | -11 | 2017-12-06 17:04 | Architectural - General | 3000 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | There are several items of MEP equipment including a drainage pipe and electrical trunking that need to pass through the mesh screen that has been installed in the Inclined Lift Machine Room at Level -4 (between ESC 10-11 and INC LIFT 08). These items were not picked up as part of the design co-ordination and therefore, openings have not been provided in the mesh screen. To accommodate the MEP equipment the Designer has proposed to cut openings in the mesh, repair the galvanized steelwork and then install a frame around the opening as shown in Option 1 on the attached sketch.
| 02SL - Stations (LUL) | Cxxx-NCR-002719 | NCR | ETH - Windpost pk 57 columns out of tolerance |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2017-12-27 | 2017-12-19 11:56 | -8 | 2017-12-13 12:05 | Civil - Civil Engineering General | 2500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The two windpost columns on pk 57, Lvl -3, have been installed to a maximum of 14mm out of position ie. too far West in plan view; NSSS1 allowable tolerance is 10mm.
| 02SL - Stations (LUL) | Cxxx-NCR-002720 | NCR | WTH Procedural Non Conformance - Management of Permanent drawings and Control of Change |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-04-13 | 2018-04-04 14:55 | -9 | 2017-12-15 12:08 | Civil - Civil Engineering General | 750 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | Cxxx--X-DWG-M123-54526 ( Western Entrance Area 12 Level +2 Structural Steel __ MKII Fire Protection Thickness (__) – P01 - Code 1 – not covered under any FCDs.
| 02SL - Stations (LUL) | Cxxx-NCR-002721 | NCR | WTH Procedural Non Conformance - Management of Permanent drawings and Control of Change |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-02-21 | 2018-03-01 13:15 | 8 | 2017-12-15 12:28 | Civil - Civil Engineering General | 750 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | Cxxx--A-DDA-M123_2-76207 - Western Entrance, Basement Level -1, General Arrangement Plan Setting Out, 2 of 6 (Rev P10 was presented) during a __ Screed surveillance (Cxxx--O4-RGN-M123-51524 – REV 1) exercise on 9th November 2017. Drawing presented was not latest revision – which should be at Rev P28 (16/10/2017). Also note that any P status drawings being used for construction needs to be covered within a FCD
| 02SL - Stations (LUL) | Cxxx-NCR-002722 | NCR | WTH Procedural Non Conformance against ITPs - O&M manual checklist not completed prior to commencement of work |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-03-28 | 2018-03-26 14:52 | -2 | 2017-12-15 12:53 | Civil - Civil Engineering General | 750 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | As per activity point 1.5 - O&M manual checklist needs to be completed prior to commencement of work. Procedural NCR against ITP (pre start documentation not in place against ITP requirements to be issued) – affected ITPs: Cxxx--C-ITP-M123-50320 (Rev 2) - Inspection and Test Plan – Application of external Render System (Code 1) – Activity 1.5 Cxxx--A-ITP-M123-50008 (Rev 5) - Inspection and Test Plan - Installation of Architectural and Structural Steelwork for the WTH and ETH (Code 2) – Activity 1.5 (MNS3B Staircase in circular shaft & Chillier Frame installation)
| 02SL - Stations (LUL) | Cxxx-NCR-002723 | NCR | WTH Procedural Non Conformance against ITP - CheckSheet – Fire Protection Coating Pre-Post – Construction not completed |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-02-21 | 2018-02-15 11:55 | -6 | 2017-12-15 12:22 | Civil - Civil Engineering General | 750 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | Cxxx-SF-CON-250_00 - ITP - Checksheet – Fire Protection Coating Pre-Post - Construction (1) was not completed and should have been completed prior to commencement of works, as per Cxxx--C-ITP-M123-50299 (Revision 4) – Activity 2.1.
| 02SL - Stations (LUL) | Cxxx-NCR-002724 | NCR | WTH-MEP L-2 Wi Beam Broken Through to Accommodate Services |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-02-21 | 2018-01-30 15:48 | -22 | 2017-12-15 12:13 | Civil - Civil Engineering General | 1750 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | It has previously been observed by CRL that a Wi beam at WTH L-2 has been locally reduced in size to accommodate the installation of pipework, despite there being a restriction on coring through these members - which is also clearly stated on site via the labels __ have installed. Please see attached photos and location plan
| 02SL - Stations (LUL) | Cxxx-NCR-002725 | NCR | MEP - STW - Incorrect Socket Outlets |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-03-16 | 2018-03-15 14:56 | -1 | 2017-12-19 16:51 | Electrical - Power Distribution | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Error by manufacturer in shipping or marking | Completed |  | __ have installed incorrect BSEN 60309-2 230 volt socket outlets in multiple locations.
| 02SL - Stations (LUL) | Cxxx-NCR-002726 | NCR | WTH – Reinforcement incorrectly cast on Level +2 upstand |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-04-20 | 2018-03-09 16:54 | -42 | 2018-02-28 13:34 | Civil - Civil Engineering General | 1500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | An upstand runs adjacent to Gridline 7 at the Southern end of the Level +2 slab, see attached sketch. When casting the slab, reinforcement for the upstand was installed across the full width of the opening. The drawing does not show a full width upstand, there is a gap at the Eastern end. The exposed rebar has since been cut.
| 02SL - Stations (LUL) | Cxxx-NCR-002727 | NCR | WTH Procedural Non Conformance - Management of Permanent drawings and Control of Change (__ – Erection Of Birdcage) |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-02-22 | 2018-02-08 17:18 | -14 | 2017-12-15 15:41 | Civil - Civil Engineering General | 750 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | During scheduled inspection on 21.11.2017 – status of working drawings for sub-contractor (__ – Erection Of Birdcage) Cxxx--X-DWG-M123-58902-P02 – Code 4 Windpost Pk-99 - Plans & Elevations Sheet 1 of 2 (__) Cxxx--X-DWG-M123-58903-P02 – Code 4 Windpost Pk-99 - Plans & Elevations Sheet 2 of 2 (__) Cxxx--X-DWG-M123-58904-P03 – Code 4 Windpost Pk-99 - Details Sheet 1 of 3 (__) Cxxx--X-DWG-M123-58905-P03 – Code 4 Windpost Pk-99 - Details Sheet 2 of 3 (__) Cxxx--X-DWG-M123-58906-P01 – Code 4 Windpost Pk-99 - Details Sheet 3 of 3 (__) FCD currently not in place for P status drawings. Drawings currently at status C and with document control.
| 02SL - Stations (LUL) | Cxxx-NCR-002728 | NCR | MEP - WTH - Non Compliance of Underfloor Trunking |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-02-27 | 2018-06-06 14:32 | 99 | 2018-01-05 11:24 | Electrical - Cable Management | 5000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | After CRL review of the under floor trunking the following needs to be rectified : • Partitions within floor boxes are not full height as required by JY60.1306, q) • On the corner floor boxes, the double depth tees do not maintain the full capacity of the compartments. • Water ingress into trunking, causing corrosion to earth connection at base of floor box.
| 02SL - Stations (LUL) | Cxxx-NCR-002730 | NCR | WTH Procedural Non Conformance - Management of Permanent drawings and Control of Change |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-05-25 | 2018-05-24 07:54 | -1 | 2018-01-09 15:39 | Civil - Civil Engineering General | 750 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | Cxxx--X-DWG-M123-55012 (P01) Code 1 Western Entrance Basement Level -6 Door No. 7-WD19 (a) (ASSA BLOY) & Cxxx--X-DWG-M123-55014 (PO1) Code 1 Western Entrance Basement Level -6 Door No. 7-WD20 (a) (ASSA BLOY) – not covered under any FCDs. Therefor a procedural NCR has been issued
| 02SL - Stations (LUL) | Cxxx-NCR-002731 | NCR | WTH Procedural Non Conformance against ITP - O&M manual checklist not completed prior to commencement of work |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-06-22 | 2018-01-25 15:26 | -148 | 2018-01-09 15:43 | Civil - Civil Engineering General | 750 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | O&M manual checklist needs to be completed prior to commencement of work. Procedural NCR against ITP (pre start documentation not in place against ITP requirements to be issued) As per ITP (Inspection and Test Plans - __ __ - Installation of Doors ) - Cxxx--C-ITP-M123-50316 Rev 1.0 Code 1 (activity 1.5)
| 02SL - Stations (LUL) | Cxxx-NCR-002732 | NCR | WTH_Service Yard Cable Troughs Lack of MCR |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-02-07 | 2018-01-30 09:32 | -8 | 2018-01-24 12:18 | Civil - Civil Engineering General | 750 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | Precast concrete Cable Trough installation work started in the Service Yard area on the 4th of December 2017 without an approved MCR in place. The draft copy of the MCR was submitted to CRL on the 04/12/17 and reviewed on the 05/12/17 when works had already started. The final MCR was submitted and informally approved by CRL on the 11/01/18. Works carried out without the relevant approved document in place from the 04/12/17-07/12/17, no further works have been carried out since that date.
| 02SL - Stations (LUL) | Cxxx-NCR-002733 | NCR | WTH – Lower Apse - Missing Permanent Works Anchors |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-09-07 | 2018-09-07 14:16 | 0 | 2018-03-26 10:07 | Civil - Civil Engineering General | 2500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the casting of the Lower Apse ceiling, 2 no. T-Fixx anchors were not installed (See attached drawing "Missing Anchors- Lower apse- Tomas Byrne.pdf" for positions of these). These have to be used both for the installation of __ panels by using them with a lifting beam and also in the permanent works for maintenance / replacement of these panels.
| 02SL - Stations (LUL) | Cxxx-NCR-002734 | NCR | MEP - Using pin racks within CMS without approved MCR |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-03-07 | 2018-04-05 12:31 | 29 | 2018-01-16 12:45 | Electrical - Cable Management | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Pin racks are used on Farringdon Cxxx in multiple locations , within Trunking compartments, without approved MCR
| 02SL - Stations (LUL) | Cxxx-NCR-002735 | NCR | WTH-Lack of MCR for __ __ect P250 Board |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-04-27 | 2018-04-03 09:42 | -24 | 2018-03-28 17:04 | Civil - Civil Engineering General | 750 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | Lack of approved MCR prior the commencement of P250 boards installation.
| 02SL - Stations (LUL) | Cxxx-NCR-002737 | NCR | MEP - Water ingress affecting fire alarm testing |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-04-30 | 2018-04-24 13:18 | -6 | 2018-02-01 10:47 | Fire - Detection | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Water ingress at WHT-7 & ETH Levels - 1 caused faults in fire alarm loop and devices during testing & commissioning stage. Also, the neg and earth terminals of detector base effected by water have rusted and require replacement.
| 02SL - Stations (LUL) | Cxxx-NCR-002738 | NCR | MEP - Comms Cabinet Drilling |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-03-30 | 2018-03-29 09:17 | -1 | 2018-02-01 11:43 | Communications and Control Systems | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | DC 5 cabinet within commlot CAB-FAR-MISCO-11001 and the __ RTU within Commlot CAB-FAR-MISCO-11004 were drilled in situ in contravention of the site installation guidelines and procedures. DC5 was drilled into the top of the cabinet despite cable entryways being apparent at the bottom. The __ RTU removable gland plate was not removed before drilling. Both cabinets have suffered swarfega ingress as a result. Please find attached the report compiled relating to this issue.
| 02SL - Stations (LUL) | Cxxx-NCR-002739 | NCR | WTH - Blockwork wall between ESS1/INS1 staircase constructed with no accepted drawings in place (Procedural NCR) |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-03-30 | 2018-02-01 10:00 | -57 | 2018-01-29 13:50 | Architectural - General | 750 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Interfacing problems | Completed |  | raised and had Cxxx-FCD-002981 accepted for the replacement of metal screen with blockwork between ESS1/INS1 staircase. __ changed the design to accommodate design requirements from ATK and CRL and works commenced with the latest design (P status drawing). Latest Cxxx--X-DWG-M123_Z-54204 P02 is not covered under FCD.
| 02SL - Stations (LUL) | Cxxx-NCR-002740 | NCR | WTH – SHW1 level -1 slab missing cast-in public drain |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-03-23 | 2018-03-23 13:21 | 0 | 2018-02-09 16:32 | Civil - Civil Engineering General | 3500 |  | Supervision/Management | Repair | 3 (3-6k) | Complete | Previous Construction - Problems based on previous construction errors | Completed |  | have not cast one of the cast-in 100mm internal diameter drainage pipes for a floor gully in the female toilets through the 600mm level -1 suspended slab. The slab was cast on 12 July 2016. Pre & Post-Pour checksheet attached for info. This drainage is required as part of the public health drainage. See attached file "Cxxx-NCR-002740 Missing drainage.docx"
| 02SL - Stations (LUL) | Cxxx-NCR-002741 | NCR | TUN - BUI - Joining Mesh Omitted from Screed Infills Westbound Platform |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-04-27 | 2018-04-24 16:55 | -3 | 2018-02-22 16:59 | Architectural - Flooring | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During a walk around, in was noted that mesh had been omitted from the screed infills on the Westbound Platform. Please see attached file (Missing Mesh PTW) showing two locations identified. The location of these two are adjacent to DC9 equipment cabinet and adjacent to CP4 in PTW.
| 02SL - Stations (LUL) | Cxxx-NCR-002742 | NCR | MEP - Busbar trunking storage on site |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-03-23 | 2018-03-23 15:44 | 0 | 2018-03-02 12:52 | Materials - General | 500 |  | Material | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper storage of material | Completed |  | Busbar trunking has been been adequately stored and protected by __ at WTH-5, however on several occasions protection barriers have been removed and material including scaffold tubes placed on top of the busbar which can potentially cause a damage.
| 02SL - Stations (LUL) | Cxxx-NCR-002743 | NCR | MEP - Type 2 Surge Protection |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2019-10-25 | 2019-11-25 08:53 | 31 | 2018-03-05 15:01 | Electrical - General | 1000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | No additional Type 2 Surge Protection provided to the Comms DBs as per electrical specification Cxxx--E-RSP-M123-50002
| 02SL - Stations (LUL) | Cxxx-NCR-002744 | NCR | MEP - ETH L0 FT1 Room - Drilling through Blockwork Lintel |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-05-25 | 2018-06-08 10:44 | 14 | 2018-02-22 12:30 | Architectural - Brickworks/Blockworks | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | MEP operatives drilled through blockwork lintel at ETH Level 0 North Yard FT1 Room to install services. Please find details of location on attached General Arrangement and Elevation and attached photographs of damage.
| 02SL - Stations (LUL) | Cxxx-NCR-002745 | NCR | MEP - Comms - SCADA - ITP |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-04-27 | 2018-03-29 09:22 | -29 | 2018-03-06 09:04 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Cxxx have commenced installation of cabling for the following Commlots prior to an accepted ITP being in place. CAB-FAR-MISCO-11004, CAB-FAR-MISCO-11014, CAB-FAR-MISCO-11020, CAB-FAR-MISCO-11024, CAB-FAR-MISCO-11025
| 02SL - Stations (LUL) | Cxxx-NCR-002746 | NCR | TUN - BUI - End Wall Bolt Errors |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-04-06 | 2018-03-27 16:08 | -10 | 2018-02-22 16:33 | Architectural - Glazing | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | During a walkaround on 20/02/18, it was noted that two issues had arisen due on the End Walls which were not compliant to Works Information requirements: - 1) __ Mechanical anchor bolts had not been installed correctly on the baseplates for Wall 3 (Westbound East End), the red marks indicating that sufficient embedment had not been achieved. As shown in picture "Bolts on Wall 3". 2) Through bolts in Wall 6 (CH2 End Wall) had been installed without sufficient threads protruding. As shown in picture "Bolts on Wall 6".
| 02SL - Stations (LUL) | Cxxx-NCR-002747 | NCR | MEP - Coordination of __s between Cxxx & Cxxx |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2019-03-29 | 2019-10-16 10:46 | 201 | 2018-03-05 15:02 | Electrical - LV Equipment | 10000 |  | Design | Rework | 2 (6-60k) | Complete | Design Problem - Other | Completed |  | This NCR based on the quality alert issued by CEG, Quality Alert 27 – Small Power Wiring to System Wide Equipment (see attached). The protective devices in the Cxxx CER Distribution boards have __s rated at 6A and 10A but these are being changed to 16A. The __ data cabinets also have __s rated at 6A and 10A and therefore there is no discrimination between these and the Cxxx __s circuits supplying these. Cxxx have been requested by CRL to carry out a detailed discrimination report to identify what changes need to be made to the LV distribution system to provide full discrimination between the Cxxx distribution boards and the Cxxx Data cabinets. The report has identified that full discrimination cannot be achieved unless significant changes are made to the Cxxx LV distribution system. The report also proposes the Cxxx preferred option, but this does not provide full discrimination under certain (low probability) short circuit faults. The report will be issued to CRL by 15th April 2018.
| 02SL - Stations (LUL) | Cxxx-NCR-002748 | NCR | MEP - Outdated __ Calculation |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-05-09 | 2018-06-21 10:17 | 43 | 2018-03-05 16:16 | Electrical - Power Distribution | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | __/__ __ calculations "Cxxx--E-XCL-M123-50005-WTH & Cxxx--E-XCL-M123-50001-ETH" submitted and accepted by CRL is outdated and does not reflect current installation on site.
| 02SL - Stations (LUL) | Cxxx-NCR-002749 | NCR | ETH - Inclined lift 7 - __ channel in wrong position |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-04-27 | 2018-03-26 06:37 | -32 | 2018-03-13 12:06 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Information not detailed | Completed |  | The halfen channel installed in the upper escalator ramp for inclined lift 7 are installed in the wrong location.
| 02SL - Stations (LUL) | Cxxx-NCR-002750 | NCR | MEP - WTH OHLE RTU that has had 2 x 6mm holes drilled into the RTU housing |  | Contr | __ | FAR - Farringdon Station (West) |  | 2018-04-30 | 2018-05-14 16:31 | 14 | 2018-03-07 10:14 | Communications and Control Systems | 2000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The WTH OHLE RTU that has had 2 x 6mm holes drilled into the RTU housing. Obviously this is not against the installation guidelines and not good practice.
| 02SL - Stations (LUL) | Cxxx-NCR-002751 | NCR | MEP - Discrepancies Between DBs Installed on Site and the Latest Approved __ Calculations |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2019-01-31 | 2019-04-11 15:25 | 70 | 2018-03-08 11:11 | Electrical - Power Distribution | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | The latest accepted Electrical Switchboard, Distribution Board & MCC Schedules (__ Calculation) - Cxxx--E-TSC-M123-50015 Rev 10 (see Reference Documents) was issued to CRL on 09-Dec-2016. When verifying installed Distribution Board schedules against this latest accepted __ calculation, there are some discrepancies noted. The following DB schedules have a discrepancies : • DB02/W/-3/A • DB12/E/-1/A • DB11/E/-1/B
| 02SL - Stations (LUL) | Cxxx-NCR-002752 | NCR | MEP - Use of 3 phase (TN&N) Distribution Boards for Single (SP&N) Phase Application |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-12-14 | 2019-02-21 09:01 | 69 | 2018-03-08 14:07 | Electrical - LV Equipment | 3000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | It was noted by CRL that there are single phase supplies (SP&N) going into 3 phase DBs (TP&N). 3 Phase (TP&N) DBs have been modified using 2 pole isolators on the incomer and linking out the other 2 phases. This modification then makes the DBs all Single phase (SP&N). However the __ Distribution Board MCR (Numbered CRL-MCR-003385) is only for 3 phase __ Distribution Board using TP&N isolators and NOT using the 2 Pole Isolators. This modification has not been approved by with MCR or Benchmark by CRL. In addition all labelling on these distribution boards is for 3 Phase DBs and not Single Phase DBs. The following DBs are identified by CRL: • DB42/E/-4/B • DB41/W/-2/A • EDB08/W/-2/U
| 02SL - Stations (LUL) | Cxxx-NCR-002753 | NCR | MEP Fire Main Tanks - MCR not approved prior to IRN |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-06-25 | 2018-05-25 13:07 | -31 | 2018-03-14 15:59 | Fire - Suppression | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | __Fire Main Tanks in Eastern Ticket Hall Ground Floor plantroom, have not been approved by Crossrail but have already been manufactured and installed to meet IRN Date for Fire Hydrant Systems.
| 02SL - Stations (LUL) | Cxxx-NCR-002754 | NCR | TUN - Cxxx - Damaged Glass Panel - PTW |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-04-20 | 2018-04-11 14:52 | -9 | 2018-03-19 09:35 | Architectural - Doors | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | On the 14th March 2018, whilst gaining access to the track to install the final PES post on the Westbound Platform, operatives identified that a pane of glass in the Platform Screen Doors had been damaged adjacent to the work site. The damage was only identifiable by observation from trackside and this damage had occurred prior to working in the area. This pane of glass is adjacent to a pane which Cxxx removed on the 6th of March and surrounding glass was fully wrapped in Corex protection. As the protection around the glass covered all edges from platform side, it is not possible to narrow down the date for which the damage occurred, the relevant party/parties involved nor the manner in which the damage occurred. This NCR is therefore raised to capture the damage to finish works in the Cxxx PC Area
| 02SL - Stations (LUL) | Cxxx-NCR-002755 | NCR | MEP - MEP material used on site without approved MCR |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-06-29 | 2018-07-03 17:15 | 4 | 2018-03-23 13:37 | Materials - Approval | 0 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | There are number of MEP material used on site without approved MCRs. Please refer to the attached list.
| 02SL - Stations (LUL) | Cxxx-NCR-002756 | NCR | MEP - No __ Calculations to support the 250mm D Pipework, Bracketry, Support & Fixing Arrangement |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2018-04-27 | 2018-04-26 14:05 | -1 | 2018-03-23 11:37 | Mechanical - Piping | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | Installation of 250mm diameter cast iron and stainless steel pipework was witnessed at WTH -1 Plant Room during a planned CRAF Site tour. The pipework had been fixed into the slotted ceiling deck and concrete soffit at locations using wedge anchors and __ HKD fixings. 2 x M12 fixings, drops had been used at each cast iron bracket location @ 1.8m spacing, whilst 1 x M12 fixing, drop had been used at each stainless steel bracket location @ 1.8m spacing. ‘MEPhF Support Systems Calculations’ Cxxx--O-XCL-M123-50002 at Rev 2 Code 1 was presented to confirm the witnessed configurations. However on review the following was found: - the submission only included calculations for cast iron pipework configurations up to 200mm in diameter; there was no inclusion of pipework up to 250mm diameter. - the pipework section of the document only included calculations for __ HKD type fixings, not wedge type anchors where installed into the slotted structural deck ceiling. - the document did not include calculations for welded stainless steel pipework with 250mm diameter. Furthermore, on checking the __ product data sheet for cast iron pipework, it was found that the maximum spacing is to be 1.5m max, which is different to the 1.8m witnessed on site. Until such calculations have been produced, reviewed and accepted, the installation of 250mm pipework in differing substrates is at risk until validated. M&W Specification JY90 Section 1302 states ‘Provide Matrix for all equipment to be fixed together with appropriate type and quantity of fixings and hole size to be drilled’ and 1306 states ‘Loading Details a) Provide loading details for all fixing types’.
| 02SL - Stations (LUL) | Cxxx-NCR-002757 | NCR | MEP – __ records show __ HKD fixings for Pipework supports have been over torqued per manufacturer’s requirements |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2018-05-18 | 2018-05-03 11:31 | -15 | 2018-03-23 11:40 | Mechanical - Piping | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Insufficient information made available to the worker. | Completed |  | Installation of 250mm diameter cast iron and stainless steel pipework was witnessed at WTH -1 Plant Room during a planned CRAF Site tour. __ HKD anchors had been used for fixing into the concrete soffit. Pull test records were provided by __ for M10 size anchors for 150mm diameter pipework (no pull testing completed for M12 fixings for 250mm diameter pipework as such could not be checked). This record showed both the pull test force applied for proof loading and the applied torque for the fixing at that location. The following records were sampled: (following details recorded by __ see photo attached) Bay 16-12 Invert P-1-5 Hole Depth – 40mm Applied Torque – 15Nm Proof Load 4.5kN Dated – 17.05.17 (following details recorded by __ see photo attached) Cxxx-PUHC-SWPWN1C Hole Depth – 30mm Applied Torque – 25Nm Proof Load 5kN Dated – unknown (following details recorded by __ see photo attached) Cxxx-PUHC-SWPWN1C Hole Depth – 30mm Applied Torque – 25Nm Proof Load 5kN Dated – 01.03.18 1 x record showed an applied torque of 15Nm, whilst 2 x records showed an applied torque of 25Nm. __ manufacturer’s data sheet for __ HKD fixings of M10 x 30mm or 40mm defines a Tmax value to be 15Nm (see attached), as such a number of fixings have been over torqued. This poses risk to the fixing performance and potentially compromises the bond between the fixing, anchor and concrete matrix. In addition other discrepancies were found such as hole depth and proof load applied. As the CRAF Site Tour was based on a sample, it is unclear how many fixings have been over torqued. This will require investigation.
| 02SL - Stations (LUL) | Cxxx-NCR-002758 | NCR | MEP - Installation of Leaky Feeder Cable not compliant to the current design |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-05-30 | 2018-06-21 12:28 | 22 | 2018-03-29 15:36 | Communications and Control Systems | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Current design for installation of Leaky Feeder Cable issued as per Cxxx-SMN-R3-LRG-M123-50001_Rev 23.0 - RIR under Cxxx_PMI_00872 does not take into consideration the need for galvanic isolators at the transition between station earth and traction earth at WTH&ETH Platform Level Therefore, __/__ made the following adjustments to the design (see attached marked up drawings): Cxxx-SMN-R3-DDA-M123_7-90021 [C1.0] Cables FD2190, FD2197, FD2193 and FD2200 were pulled to and cut at the circled locations instead of the indicated destination of the related couplers. Cxxx-SMN-R3-DDA-M123_7-90022 [C1.0] NCR Cables FD2204 and FD2211 were pulled to and cut at the circled locations instead of the indicated destination of the related couplers.
| 02SL - Stations (LUL) | Cxxx-NCR-002759 | NCR | WTH – SHW2 – Breaking out of In-Situ Concrete Plinths for CAT Ladder installation |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-05-11 | 2018-05-09 14:12 | -2 | 2018-04-04 14:20 | Civil - Civil Engineering General | 4000 |  | Design | Repair | 3 (3-6k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | __ drawing Cxxx--A-DDD-M123_Z-75145 C04 shows CAT-W01, CAT-W02, CAT- W03, CAT-W04 & MNS-10 to be installed in the square shaft (SH-W2). This drawing shows that each CAT ladder and the stair case is to be bottom fixed at FFL onto a concrete plinth that has been cast by . __ Drawings Cxxx--X-DWG-M123_Z-52076 through to Z- 52081 (all P02) show the same items. The use of these ‘P’-status drawings has been covered in Cxxx-FCD-003039. However, these drawings show that the bottom fixings for each item are to SSL (150mm below FFL). These drawings were used to fabricate the CAT ladders, and as such are the correct length to be installed at SSL on each level. As a result, will have to break out the plinths cast in line with __ drawing in order to facilitate the installation of the CAT ladders.
| 02SL - Stations (LUL) | Cxxx-NCR-002760 | NCR | ETH- LV02-DD2 Louvre blades door damaged |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-07-10 | 2018-05-29 17:09 | -42 | 2018-04-10 11:23 | Architectural - Roofing & Exterior Treatment | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Some of the blades of the louvre door LV02-DD-2 at ETH Hayne Street elevation has been damaged during the delivery process. (Photo and location drawing attached)
| 02SL - Stations (LUL) | Cxxx-NCR-002761 | NCR | TUN - BUI - Earth Separation at Level -6 Escalators |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-12-22 | 2019-02-21 11:26 | 61 | 2018-04-19 15:18 | Architectural - General | 6000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | In accordance with __'s Earth Management Plan, there is a requirement to segregate track and station earths. This location has been deemed as at the interface between the escalator barrel and the concourses at each ticket hall level -6. Through investigation, have found continuity between adjacent bays of GFRC panels. This is a non compliance to the Earth Management Plan.
| 02SL - Stations (LUL) | Cxxx-NCR-002762 | NCR | WTH - C1/C2 Concrete Mix - Non-Compliance with BS EN:206 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-06-15 | 2018-05-30 13:42 | -16 | 2018-05-09 13:03 | Civil - Civil Engineering General | 2000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper handling of material | Completed |  | Having reviewed all WTH concrete pours to date, have noticed that there a number of pours which do not comply with one or more of the compliance criteria set out in BS EN:206. The criteria are as follows: 1 BS EN 206 B.2(4) – The difference between the two 28 day cube strengths divided by their mean must be less than or equal to 15% otherwise the test result shall be deemed invalid 2 BS EN 206 Table B1 – Criterion 1 – The mean of groups of 6 non overlapping 28 Day Test Results must be greater than or equal to the Characteristic Strength Plus 2 = 62 N/mm2 3 BS EN 206 Table B1 – Criterion 2 – Any 28 Day Test Result should not be less than Characteristic Strength Minus 4 = 56N/mm2 The attached table shows each pour, its mix and which criteria it doesn’t comply with. There are no pours that don’t comply with 1. Pours that don’t comply with 2 are: • 22/07/2016 – MDS Level +3 (WTH) • 27/06/2017 – Level -1 Upstand & Columns (WTH) • 19/07/2017 – Cxxx-NCR-002704 • 18/08/2017 – Level -1 Upstand (WTH) Pours that don’t comply with 3 are: • 20/07/2016 – Cxxx-NCR-002392 • 25/08/2016 – WTH Columns • 31/08/2016 – WTH Columns and MDS L+2 • 04/11/2016 – MNS 1 stairs (WTH) • 19/06/2017 – Cxxx-NCR-002680 & Cxxx-002704 • 26/06/2017 – Cxxx-NCR-002704 • 27/06/2017 – Level -1 Upstand & Columns (WTH) • 05/07/2017 – Cxxx-NCR-002704 • 22/07/2017 - Cxxx-NCR-002704 • 18/08/2017 – Level -1 Upstand (WTH) • 27/10/2017 – Level 0 service yard upstand (WTH)
| 02SL - Stations (LUL) | Cxxx-NCR-002763 | NCR | ETH - Installation of the Fire-Stopping around the Electrical Trunking at Level -6 with P-status drawing without an FCD in place |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-06-03 | 2018-05-25 10:42 | -9 | 2018-04-24 09:25 | Architectural - Walls | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Further to the surveillance (Cxxx--O4-RGN-M123-51543) carried out on the installation of the Fire-Stopping around the Electrical Trunking at Level -6, the P-status drawings (Cxxx--X-DWG-M123-54657 P02 & Cxxx--X-DWG-M123-54647 Rev P06) were used for construction without an FCD in place.
| 02SL - Stations (LUL) | Cxxx-NCR-002764 | NCR | TUN - BUI - Late Issuing of PES MCRs |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-05-24 | 2018-05-23 11:10 | -1 | 2018-04-26 15:06 | Architectural - General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | During the compiling of asset data for labels, it was identified that an MCR for access hatches (Cxxx--A-LRC-M123-50044) had not been issued to Crossrail by . The aforementioned MCR was submitted onto 's document control software in 2016 and had been reviewed at the time as being compliant, but had not been forwarded onto eB.
| 02SL - Stations (LUL) | Cxxx-NCR-002765 | NCR | WTH - External Render Damage to Service Yard |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-10-19 | 2018-10-22 10:49 | 3 | 2018-04-26 17:25 | Architectural - Finishes | 2000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | As raised in Cxxx-EWN-02579, damage occurred to the WTH level 0 Service Yard render while Cxxx were striking their scaffold deck.
| 02SL - Stations (LUL) | Cxxx-NCR-002766 | NCR | WTH - Metal Deck Slabs - Missing Cube Results |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-05-18 | 2018-05-24 07:50 | 6 | 2018-04-26 14:34 | Civil - Civil Engineering General | 2000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | On the11/03/2017 the level +3 slab was poured in the areas highlighted in the attached drawing. The cubes taken during this pour have subsequently been misplaced with no record of cube tests being carried out. Please note that further non-compliances shown on the attached BSEN:206 sheet are covered under Cxxx-NCR-002762
| 02SL - Stations (LUL) | Cxxx-NCR-002767 | NCR | ETH - Blockwork L0 North Wall Doors 1-ED01 and 1-ED02 Constructed failing to account for Installation of Steel Goalposts |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-06-29 | 2018-06-27 07:18 | -2 | 2018-04-27 12:31 | Architectural - Brickworks/Blockworks | 7000 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Doorways 1-ED01 and 1-ED02, illustrated on attached Architectural GA Cxxx--A-DDA-M123_1-26202 P22, were constructed incorrectly on-site by PBL blocklayers. Architectural GA Cxxx--A-DDA-M123_1-26202 indicates the detail for steel to be installed in the area on drawings Cxxx--A-DDD-M123_Z-25272 P10 and Cxxx--A-DDD-M123_Z-25283 P01. The secondary steel to the doors was updated in revision P20 issued on 23/07/217, with on-site construction of the blockwork wall in November 2017. During construction of the wall in November 2017, PBL used the current drawing revision Cxxx--A-DDA-M123_1-26202 P20. which failed to account for the installation of steel goalpost supports for both doorways and installed a double Wi Trough Beam to support the blockwork above. As a result, the first Wi trough Beam and blockwork nibs clash with the steel goalposts to be installed.
| 02SL - Stations (LUL) | Cxxx-NCR-002768 | NCR | MEP - Use of abrasive cleaning products on the trunking |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2019-04-26 | 2019-04-30 15:40 | 4 | 2018-05-01 14:24 | Electrical - Cable Management | 10000 |  | Damaged | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Other | Completed |  | Trunking within invert at Platform Level has been cleaned using abrasive cleaning products.This has had detrimental affect on the trunking galvanising.
| 02SL - Stations (LUL) | Cxxx-NCR-002769 | NCR | MEP - Installation of __ pipework without approved benchmark |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-06-29 | 2018-06-20 09:26 | -9 | 2018-05-16 15:27 | Fire - Detection | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | The __ pipework has been installed on escalators 1,2 and 3 without approved benchmark and F2 drawings. In addition, the installation is progression on 7, 8 and 9.
| 02SL - Stations (LUL) | Cxxx-NCR-002770 | NCR | MEP - STW - [Cxxx-MECC-HCV*N1A] - Potential non-compliant materials within Air Handling Units |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-11-30 | 2019-01-18 15:06 | 49 | 2018-05-03 09:42 | Electrical - General | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | Following a inspection, as part of an IRN handover the ETH Level -2 Air Handling Units (AHUs), the below materials were questioned in relation to their material compliance: • Cable support Motor supply cable PVC rivet required to be mechanical support i.e. HDG class 4 galvanised conduit; • Cable support lights and light switches supply cable PVC rivet cable ties required to be mechanical support i.e. HDG class 4 galvanised conduit; • PVC-White compression glands required replacement with steel approved compression glands; • PVC-blanking plate required replacement with steel approved compression glands on AHU heater battery glanding plate; • PVC Light switch required replacement with steel approved __ switch.
| 02SL - Stations (LUL) | Cxxx-NCR-002771 | NCR | MEP - WTH - Water Damaged Trunking (-1 WTH Plant Room) |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2019-02-14 | 2019-04-30 15:47 | 75 | 2018-05-03 14:42 | Electrical - Cable Management | 3000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | This was discovered around late April 2017 by __ and reported to . The water ingress appears to have been happening for quite a while without being noticed as the cables within the CMS were installed a while ago, __ are to replace the trunkings and the trays in this area and need assurances that the area affected will be water tight. __ revisited the area with CRL & 30/04/18 to assess the damage and it has been confirmed that an NCR is required.
| 02SL - Stations (LUL) | Cxxx-NCR-002773 | NCR | ETH - Level -3 Lift Lobby - Clashes Between CMS and Acoustic Cladding |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2019-09-06 | 2019-08-23 14:30 | -14 | 2018-05-08 16:30 | Architectural - General | 2000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The size of the openings to accommodate the CMS routes within in the acoustic cladding panels where agreed between __, __ and CRL in December 2017. Since this date the CMS requirements and layout have changed but this has not been coordinated with the acoustic cladding design. As a result the acoustic panels have been fabricated and clash with the as-installed CMS layout onsite.
| 02SL - Stations (LUL) | Cxxx-NCR-002774 | NCR | MEP - Damaged speakers in ETH and WTH |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-09-21 | 2018-10-08 10:19 | 17 | 2018-05-09 09:43 | Communications and Control Systems - Public Address Systems | 3000 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The following Speakers have sustained damage by impact, from Scaffolding and other means during the build phase of the station :- East Ticket Hall;- MHS20, Z27/A49, Level +2 MHS20, Z27/B48, Level +2 MHS20, Z28/A43, Level -7 MHS20, Z28/B44, Level -7 MHS20, Z28/B56, Level -7 West Ticket Hall;- Sentry 6, Z26/A19, Level -4 Sentry 6, Z26/A33, Level -2/3 Sentry 6, Z26/A15, Level -2/3 Sentry 6, Z25/A31, Level -1 MCS20, Z21/A19, Level -6 MHS20, Z26/A03, Level -4 MHS20, Z26/A57, Level -5 MHS20, Z26/A53, Level -5 MHS20, Z25/A15, Level -1 MHS20, Z25/B36, Level -1
| 02SL - Stations (LUL) | Cxxx-NCR-002775 | NCR | MEP - TT Sump Pump Control Panels Not Comply with CRL Specification |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-12-13 | 2018-12-16 21:02 | 3 | 2018-05-23 11:39 | Mechanical - Pumps | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | 5 No TT Sump Pump Control Panels delivered to site on Friday 20th April 2018 are not comply with JR 20 specification and SCADA interface requirements and don't have accepted MCR. In addition, at the factory witness it was pointed out that there was a misalignment between the SCADA interface monitoring points and the current SCADA points schedule and whilst the interface monitoring points represented the actual design the SCADA points schedule cannot be changed.
| 02SL - Stations (LUL) | Cxxx-NCR-002776 | NCR | STW - Fabrication and Installation of __ floor access hatch without approved documentation |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-07-06 | 2018-07-04 14:37 | -2 | 2018-05-24 08:53 | Architectural - Flooring | 2000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | The __ floor access hatches types AHP-109 & AHP-111 have been fabricated and installed on the WTH and ETH without having the follwing approved documentation in place and formally accepted: 1. Cxxx--C-ITP-M123-50441 (Fabrication ITP) 2. Cxxx--C-LRC-M123-51023/51025 (MCR - floor access hatch types AHP-109 & AHP-111) 3. IFC Drawings/Cxxx-FCD-003207 (STW - Using p-status drawings for access hatches fabrication) Please see mark-up drawings for WTH & ETH showing the location of the access hatches that have been installed so far.
| 02SL - Stations (LUL) | Cxxx-NCR-002777 | NCR | TUN - Zone 13 and 14 Speakers damaged by PES grill opening and closing |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-07-10 | 2018-06-21 12:52 | -19 | 2018-05-11 12:57 | Communications and Control Systems - Public Address Systems | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | This is a list of the speakers in Zones 13 and 14 that have sustained some sort of damage post installation on the PES. Mainly small dents on the mesh fronting. Zone 13 Westbound Platform:- Column Speaker, Z13/A1 Column Speaker, Z13/A7 Column Speaker, Z13/A9 Column Speaker, Z13/B12 Column Speaker, Z13/A17 (No more Speakers were inspected due to access issues to the PES caused by completing the tiling along the screen doors along the Platform. To be completed once the tiling of the Westbound platform is completed) Zone 14 Eastbound Platform:- Column Speaker, Z14/A9 Column Speaker, Z14/A13 Column Speaker, Z14/B2 Column Speaker, Z14/B8 Column Speaker, Z14/B10 Column Speaker, Z14/B14 Column Speaker, Z14/B16 Column Speaker, Z14/B18 Column Speaker, Z14/B20 Column Speaker, Z14/C1 Column Speaker, Z14/C3 Column Speaker, Z14/C13 Column Speaker, Z14/C15 Column Speaker, Z14/C17 Column Speaker, Z14/D2 Column Speaker, Z14/D8 Column Speaker, Z14/D10 Column Speaker, Z14/D22
| 02SL - Stations (LUL) | Cxxx-NCR-002778 | NCR | STW - __ Priority 1 Door Installation Defects |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2019-04-30 | 2019-04-25 15:45 | -5 | 2018-05-17 22:25 | Architectural - Doors | 6750 |  | Workmanship | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | __ ‘Priority 1’ doors, as per the list below, have been manufacturer and installed to a poor level of quality. The snags that have been surveyed so far are listed in the attached ‘Snag Survey Summary NM Rev-A’ and further detailed in ‘Survey report - Farringdon East HT’ and ‘Survey report - Farringdon West HT’. WTH • 6-WD03 drawing number Cxxx--X-DWG-M123-58627 • 6-WD05 drawing number Cxxx--X-DWG-M123-58628 • 6-WD15 drawing number Cxxx--X-DWG-M123-58629 • 5-WD03 drawing number Cxxx--X-DWG-M123-58625 • 5-WD05 drawing number Cxxx--X-DWG-M123-58652 • 5-WD13 drawing number Cxxx--X-DWG-M123-58626 • 3-WD05 drawing number Cxxx--X-DWG-M123-58624 • 2-WD07 drawing number Cxxx--X-DWG-M123-58648 • 2-WD08 drawing number Cxxx--X-DWG-M123-58620 • 2-WD08a drawing number Cxxx--X-DWG-M123-58621 & Cxxx--X-DWG-M123-58622 • 1-WD08 drawing number Cxxx--X-DWG-M123-58643 • B-WD08 drawing number Cxxx--X-DWG-M123-58633 ETH • 1-ED16 drawing number Cxxx--X-DWG-M123-58600 • 1-ED19 drawing number Cxxx--X-DWG-M123-58603 • 3-ED02 drawing number Cxxx--X-DWG-M123-58608 • 3-ED03 drawing number Cxxx--X-DWG-M123-58639 • 6-ED26 drawing number Cxxx--X-DWG-M123-58609 • 8-ED16 drawing number Cxxx--X-DWG-M123-58614 • A-ED01a drawing number Cxxx--X-DWG-M123-58616 Package reference: Arch-WTH-20
| 02SL - Stations (LUL) | Cxxx-NCR-002779 | NCR | STW - __ Door Installation Without FCD for P-Status Drawings |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-09-17 | 2018-09-24 10:06 | 7 | 2018-06-22 14:32 | Architectural - Doors | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | __ have installed the following doors without an FCD in place for 'p-status' drawings. WTH • 6-WD03 drawing number Cxxx--X-DWG-M123-58627 P04 • 6-WD05 drawing number Cxxx--X-DWG-M123-58628 P04 • 6-WD15 drawing number Cxxx--X-DWG-M123-58629 P02 • 5-WD03 drawing number Cxxx--X-DWG-M123-58625 P04 • 5-WD05 drawing number Cxxx--X-DWG-M123-58652 P04 • 5-WD13 drawing number Cxxx--X-DWG-M123-58626 P04 • 3-WD05 drawing number Cxxx--X-DWG-M123-58624 P04 • 2-WD07 drawing number Cxxx--X-DWG-M123-58648 P04 • 2-WD08 drawing number Cxxx--X-DWG-M123-58620 P04 • 2-WD08a drawing number Cxxx--X-DWG-M123-58621 P03 & Cxxx--X-DWG-M123-58622 P02 • 1-WD08 drawing number Cxxx--X-DWG-M123-58643 P04 • 1-WD17 drawing number Cxxx--X-DWG-M123-58644 P04 • B-WD08 drawing number Cxxx--X-DWG-M123-58633 P02 ETH • 1-ED16 drawing number Cxxx--X-DWG-M123-58600 P04 • 1-ED19 drawing number Cxxx--X-DWG-M123-58603 P04 • 3-ED02 drawing number Cxxx--X-DWG-M123-58608 P04 • 3-ED03 drawing number Cxxx--X-DWG-M123-58639 P03 • 6-ED26 drawing number Cxxx--X-DWG-M123-58609 P03 • 8-ED16 drawing number Cxxx--X-DWG-M123-58614 P04 • A-ED01a drawing number Cxxx--X-DWG-M123-58616 P06 Associated DRIR: Cxxx--X-LRG-M123-50027
| 02SL - Stations (LUL) | Cxxx-NCR-002780 | NCR | STW - __ Doors Installation Without Approved MCRs |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-12-14 | 2018-11-28 16:03 | -16 | 2018-06-21 13:54 | Architectural - Doors | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Other | Completed |  | TTR were unable to provide details of fire and toxicity testing for the PPC paint to the doors. Due to this __ fire were unable to approve the following MCRs: Cxxx--X-LRC-M123-56135 - Standard Twin Door Solution Cxxx--X-LRC-M123-56132 - Acoustic (33DB) and Pressure (1.2kPa) Cxxx--X-LRC-M123-56133 - Acoustic (42DB) and Pressure (2.6kPa) Cxxx--X-LRC-M123-56134 - SR3 Acoustic (42DB) and Pressure (2.6kPa) Due to programme constraints, took the decision to proceed with the manufacturing and installation of all __ doors.
| 02SL - Stations (LUL) | Cxxx-NCR-002781 | NCR | ETH - Level +1 cracks in concrete topping between GLF and GL C' |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-06-29 | 2018-06-28 11:53 | -1 | 2018-05-16 15:30 | Civil - Civil Engineering General | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | Cracks have formed on the Level +1 slab concrete protection slab over lift 9 area which was poured on 6th of April 2018. The cracks are greater than 0.3mm wide, ranging from 0.3 to 0.75mm, and have formed in 3 locations as per the attached sketch Level +1 sketch and associated photographs.
| 02SL - Stations (LUL) | Cxxx-NCR-002782 | NCR | TUN - PAVA Zone 21 damaged speakers |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-07-15 | 2018-06-01 13:24 | -44 | 2018-05-16 14:34 | Communications and Control Systems - Public Address Systems | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Damage to Speakers A27 and B4. Sustained by work operatives Z21/A27 MSC20 Column Speaker Z21/B04 MSC20 Column Speaker
| 02SL - Stations (LUL) | Cxxx-NCR-002783 | NCR | PAVA Zone 22 damaged speakers |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-07-20 | 2018-07-18 13:38 | -2 | 2018-05-21 12:27 | Communications and Control Systems - Public Address Systems | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Not Defined | Completed |  | The following Speakers have been damaged in Zone 22 Z22/A09 MSC20 Column Speaker Z22/B10 MSC20 Column Speaker Z22/A11 MSC20 Column Speaker Z22/B12 MSC20 Column Speaker
| 02SL - Stations (LUL) | Cxxx-NCR-002784 | NCR | ETH Curtain Wall |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2020-09-25 | 2020-09-21 16:45 | -4 | 2018-05-18 09:22 | Architectural - General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Following removal of the protection to the low level curtain wall framework between gridlines 3 and 4 on Lindsey Street we have identified that the PPC finish to the top surface of some transoms has been scratched. The damage will be recorded on a snag list for the curtain wall detailing the agreed repairs.
| 02SL - Stations (LUL) | Cxxx-NCR-002785 | NCR | ETH - Barbican - Flood Pre-cast Plank Issues |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-07-06 | 2018-07-17 07:23 | 11 | 2018-06-04 08:42 | Civil - Civil Engineering General | 30000 |  | Manufacturing Defect | Reject | 2 (6-60k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Flood Pre-cast has delivered pre-cast planks for Barbican Platform reinstatement. On delivery inspected planks and identified several defects with the planks, including the following. 1. Exposed Reinforcement 2. Low reinforcement cover 3. Cracks larger then 0.3mm 4. Damaged planks 5. Incorrect sizes of planks 6. Poor finish to openings and edges of planks 7. Honeycomb concrete (poorly compacted) Please refer to attached plank inspection photo report. Note only 13 No planks of 43 have been inspected. Further planks are stored at external site but are in a similar state.
| 02SL - Stations (LUL) | Cxxx-NCR-002786 | NCR | TUN-BUI Changes to Structural openings for track side door installation prior to being formally agreed |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-07-06 | 2018-07-04 15:25 | -2 | 2018-05-30 14:31 | Architectural - Brickworks/Blockworks | 5000 |  | Documentation and Records | Use As-Is | 3 (3-6k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | Works progressed on site to extend track side door structural opening width, as per attached 'Tunnel walkway doors- Rev 2' sketches produced by __ and issued by __. The blockwork in the following doorway locations were adjusted by __: 7-WD-09, opening extended to 1.154m. 7-ED-38, opening extended to 1.200m. 7-WD-18, , opening extended to 1.200m. No FCD was raised to cover this change prior to works commencing. Method of blockwork removal can be seen on attached blockwork adjustment.pdf and 7-ED-38.
| 02SL - Stations (LUL) | Cxxx-NCR-002787 | NCR | MEP - Material installed on site by __ without approved MCR for Farringdon |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2019-03-04 | 2019-02-20 11:31 | -12 | 2018-05-23 10:36 | Materials - Approval | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | __ have installed UPS cabling and accessories without a MCR's specifically for Farringdon station
| 02SL - Stations (LUL) | Cxxx-NCR-002788 | NCR | WTH – Tiling - MNS6 – Incorrect SSL of In-situ Stair |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-06-20 | 2018-06-19 14:33 | -1 | 2018-05-23 17:37 | Architectural - Flooring | 1500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | MNS6 Stairs should have been cast in line with drawing Cxxx--A-DDD-M123_Z-75137 Rev. C03. Since casting these stairs have raised Cxxx--RFI-02172 to clarify the SSL/FFL at the head and base of these stairs. The proposal SK-Tiling-JB-002 was sent to ATK for review and accepted. See ATK RFI response and supplementary information provided by ATK SK-RFI-02172. However, once a survey of the stairs was undertaken, the level of one step was found out of tolerance in comparison with the theoretical step levels. If tile was laid on this step the level of tile would have been above FFL and out of the +/- 3mm tolerance stated in JM41.3218 b). See attached survey SK-Step Survey-DW-001.
| 02SL - Stations (LUL) | Cxxx-NCR-002789 | NCR | WTH - Damage to Fireboarding (CRL-OBS-22063,CRL-OBS-22155) |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-08-17 | 2018-08-14 13:58 | -3 | 2018-05-29 13:06 | Architectural - General | 2500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | Fire boarding has been damaged in 2 locations as detailed below: CRL-OBS-22063 - WTH L0 to L+1 MNS1 Damage to Fireboarding In MNS1, it was observed that the fireboarding around a beam at head level has been locally damaged. Refer to attached site photos. These boards will need to be checked by __ and replaced if its integrity has been compromised. CRL-OBS-22155 WTH L+2 MNS2 Minor Damage to Fireboarding During an inspection of the completed firecoating at the top of MNS2, it was observed that the fireboarding on the north wall of this stairwell has numerous indentations in it. Refer to attached site photos. These boards will need to be checked by __ and replaced if its integrity has been compromised.
| 02SL - Stations (LUL) | Cxxx-NCR-002790 | NCR | TUN - BUI - Interface between Curved Skirting Pieces and GFRC Panels |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2019-05-31 | 2019-10-16 11:08 | 138 | 2018-05-31 15:36 | Architectural - General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | It has been discovered that the interface between __’s curved skirting pieces and __’s GFRC panels is not acceptable in some locations in the tunnels. The Works Information stipulates that the skirting pieces are to lie 20mm below and 20mm proud of the GFRC panel. In some locations on site the gap between the skirting and GFRC panel is too large and the infill gasket can be seen.
| 02SL - Stations (LUL) | Cxxx-NCR-002791 | NCR | WTH - SS - Corrosion and paint damage to cast-in plates and temporary roof beams |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-09-28 | 2018-09-21 14:40 | -7 | 2018-06-01 12:36 | Civil - Structural Engineering | 5500 |  | Damaged | Repair | 3 (3-6k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | This NCR covers two items: 1. Multiple cast-in plates are corroding around their outside edges and within holes in the plate used to fix it in position during construction of the RC walls. 2. There is paint damage to the steel beams that support the OSD temporary roof. See attached "CRL-OBS-22157 Photos and Location Sketch".
| 02SL - Stations (LUL) | Cxxx-NCR-002792 | NCR | MEP - __ UPSs Installed Without Approved F2 Drawings |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-09-28 | 2018-09-10 08:40 | -18 | 2018-06-04 09:27 | Electrical - General | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | __ UPSs Installed Without Approved F2 Drawings
| 02SL - Stations (LUL) | Cxxx-NCR-002793 | NCR | MEP - Coax Cable for the Whip Antennas Cut Too Short |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-08-31 | 2018-09-11 15:06 | 11 | 2018-06-04 12:44 | Communications and Control Systems - General | 10000 |  | Incorrect Installation | Rework | 2 (6-60k) | Complete | Personnel Error - Other human error | Completed |  | Coax cable for the whip antennas on the platforms was mistakenly cut too short to be reused in the correct route.
| 02SL - Stations (LUL) | Cxxx-NCR-002794 | NCR | MEP - Use of P Status Drawings Without FCD |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-07-30 | 2018-07-05 09:44 | -25 | 2018-06-12 09:27 | Electrical - General | 500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Number of redlined P status drawings submitted to CRL as a part of IRN assurance documentation were without FCD raised against them
| 02SL - Stations (LUL) | Cxxx-NCR-002795 | NCR | MEP - Damaged __ Cable |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-10-31 | 2018-09-10 11:43 | -51 | 2018-06-06 14:39 | Communications and Control Systems - Fibre Optic Network | 17000 |  | Damaged | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Other | Completed |  | Upon completion of pulling 12 core optical fiber cable between LU CER and ETH CRL CER, it was tested and failed due to damage along the run.
| 02SL - Stations (LUL) | Cxxx-NCR-002796 | NCR | MEP - Non-Compliant Supply Cables Installed for the Fire Equipment |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-10-19 | 2018-10-24 16:49 | 5 | 2018-07-02 09:40 | Electrical - Power Distribution | 10000 |  | Incorrect Installation | Rework | 2 (6-60k) | Complete | Design Problem - Other | Completed |  | According to CRL M&W specification JW50.1303 (h) and JV20.1309 (b) power supply cable to the fire and life safety equipment should be carried out in enhanced fire rated cables. Currently, both LV submains and final circuit wiring have not been completed with enhanced cabling.
| 02SL - Stations (LUL) | Cxxx-NCR-002797 | NCR | MEP - Fire Alarm LV Supply Labelling |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-09-24 | 2018-10-01 09:03 | 7 | 2018-06-12 09:12 | Electrical - Power Distribution | 6000 |  | Incomplete Works | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | According to BS5839-1, paragraph 25 every isolator and protective device that can isolate supplies to the fire detection and fire alarm system should be adequately labelled to ensure supplies are not switched off. No such labelling has been installed throughout the LV distribution for fire alarm circuits.
| 02SL - Stations (LUL) | Cxxx-NCR-002798 | NCR | MEP - BZP Drop Rods |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2019-03-15 | 2019-04-09 13:57 | 25 | 2018-06-13 09:22 | Electrical - General | 10000 |  | Material | Use As-Is | 2 (6-60k) | Complete | External Phenomenon - Other | Completed |  | Specification clause JY63.1304 requires hot dipped galvanised finish for support systems, providing an anticipated design life for cable supports of 40 years. __ raised Cxxx-FCD-002859 proposing to use BZP drop rods for the support of MEP services and used BZP rods without FCD being formally accepted by Crossrail. The FCD acceptance criteria requires evidence that BZP type fit for a C2 environment for 40yrs.
| 02SL - Stations (LUL) | Cxxx-NCR-002799 | NCR | WTH Stolen CCTV WTH Level -8 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-07-14 | 2018-07-18 13:36 | 4 | 2018-06-14 13:19 | Communications and Control Systems - CCTV | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | External Phenomenon - Theft, tampering, sabotage, or vandalism | Completed |  | CCTV removed without permission or stolen from West ticket Hall, Level -8 CAM-0260 and CAM-0261. Note ; This is the second time that CAM-0260 has been removed / stolen from site.
| 02SL - Stations (LUL) | Cxxx-NCR-002800 | NCR | WTH Procedural Non Conformance - Management of Permanent drawings and Control of Change |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-07-27 | 2018-07-17 13:59 | -10 | 2018-06-25 08:58 | Architectural - Interior Design & Art | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | A surveillance was carried out on the installation of __ Glazed Cassette Bracket & Glazed Cassette frames along Elevation E/F. This took place on 10th May 2018. The following drawings were found to be used during installation. Cxxx--X-DWG-M123-53098 P04 Cxxx--X-DWG-M123-53100 P03 Cxxx--X-DWG-M123-53128 P02 Cxxx--X-DWG-M123-53129 P02 Cxxx--X-DWG-M123-53130 P02 Cxxx--X-DWG-M123-53131 P02 Cxxx--X-DWG-M123-53132 P02 Cxxx--X-DWG-M123-53133 P02 Cxxx--X-DWG-M123-53134 P02 P status drawings being used for construction needs to be covered within a FCD
| 02SL - Stations (LUL) | Cxxx-NCR-002801 | NCR | WTH - Material installed on site without approved MCR |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-08-30 | 2018-09-04 10:48 | 5 | 2018-06-25 08:59 | Architectural - Interior Design & Art | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | A surveillance was carried out on the installation of __ Glazed Cassette Bracket & Glazed Cassette frames along Elevation E/F. This took place on 10th May 2018. As per activity 2.4 Cxxx--A-LRC-M123-50186 – Material Compliance Record (WTH Glazed Cassette Frames & Metalwork) - Fit for acceptance (not approved)
| 02SL - Stations (LUL) | Cxxx-NCR-002802 | NCR | WTH - OSD rainwater drainage in level 0 slab |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-09-14 | 2018-09-14 15:22 | 0 | 2018-07-04 12:17 | Civil - Civil Engineering General | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | 2no. rainwater outlet gullies for OSD were omitted from the WTH level 0 area 13 200mm slab. See attached marked up version of Cxxx--P-DDA-M123_1-75200 C01.
| 02SL - Stations (LUL) | Cxxx-NCR-002803 | NCR | ETH -Trap Shaft - Level of concrete outside permitted tolerance |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-07-06 | 2018-06-25 13:11 | -11 | 2018-06-22 12:20 | Civil - Civil Engineering General | 2000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | has conducted an as-built survey of Level 0 Slab for Sub-package 35 Level 0 Reinforced Concrete Slab. has identified a few areas which are outside the required tolerances of +10mm/-0mm specified on Cxxx-SWN-S-DDL-M123_Z-00101 C05.Please refer to attached as-built survey.
| 02SL - Stations (LUL) | Cxxx-NCR-002804 | NCR | TUN - BUI - Platform Totems Defects |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-10-26 | 2018-10-31 23:20 | 5 | 2018-06-22 14:34 | Architectural - Finishes | 6000 |  | Manufacturing Defect | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | During a benchmark inspection of the platform totems, and Crossrail became aware of a number of quality defects in the totems that required correcting. These defects include but are not limited to: • Unequal spacing of grille fins and damaged to mesh • Location of horizontal emergency lighting • Doors not closing completely • Scuffs around door locks • Sharpness of corners
| 02SL - Stations (LUL) | Cxxx-NCR-002805 | NCR | ETH Louvre LV02 door installation is not according to approved Colt drawings. |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-12-20 | 2018-09-12 10:10 | -99 | 2018-06-22 16:36 | Architectural - Roofing & Exterior Treatment | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | ETH Level +1 LV02 Louvre doors installation has not been done according to approved Colt drawing Cxxx--X-DWG-M123-58805. Metal brackets have been installed by the subcontractor Colt to support these doors without design/calculations previously approved. Door brackets installed on site are showing different types and number of fixings depending on the bracket (Site survey document with photos attached). It has been formally requested to the louvres subcontractor Colt to provide asap design and structural calculations for these brackets to amend installation accordingly when reviewed and approved. Structural calculation has been received and submitted to ATK for review. ATK is currently reviewing these structural calculations and response comments will be formally sent to the subcontractor in bc. Cxxx--C-LRC-M123-50951 rev05 has been submitted with material/drawing door brackets to CRL for approval.
| 02SL - Stations (LUL) | Cxxx-NCR-002806 | NCR | MEP - UPS Cable Calculations and __ Coordination |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-10-26 | 2018-12-07 13:45 | 42 | 2018-07-04 12:05 | Electrical - Power Distribution | 3000 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | CRL haven’t seen and approved __’s equipment cable calculation or __ coordination
| 02SL - Stations (LUL) | Cxxx-NCR-002807 | NCR | MEP - UPS SAT Test Documentation |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-08-03 | 2018-08-22 11:51 | 19 | 2018-07-04 12:18 | Electrical - Power Distribution | 500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | To avoid program impact __ proceeded with the commissioning without SAT documentation officially submitted to CRL via eB.
| 02SL - Stations (LUL) | Cxxx-NCR-002808 | NCR | WTH – Metal Deck Slabs – Missing Cube Results (Extension of Cxxx-NCR-002766) |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-07-13 | 2018-07-18 08:33 | 5 | 2018-06-25 14:53 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | On the 4/03/2017 the level +3 slab was poured (40m^3) in the areas highlighted in the attached drawing. The cubes taken during this pour have subsequently been misplaced with no record of cube tests being carried out. Please note that this NCR is an extension of Cxxx-NCR-002766
| 02SL - Stations (LUL) | Cxxx-NCR-002809 | NCR | WTH Damaged speakers Throughout Station |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-07-07 | 2018-07-18 13:30 | 11 | 2018-06-26 14:13 | Communications and Control Systems - Public Address Systems | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | The following Speakers have sustained damage by impact, from Scaffolding and other means during the build phase of the station in 2017 and were replaced by speakers from stock at Farringdon to complete PAVA zone IRN's :- West Ticket Hall Escape Stairs; Sentry 6, Z23/A25 Sentry 6, Z23/B04 Sentry 6, Z23/B06 Sentry 6, Z23/A05 Sentry 6, Z23/A07 East Ticket Hall Escape Stairs; Sentry 6, Z24/B04 Sentry 6, Z24/B06 East Ticket Hall Back of House; MHS20, Z28/A43 MHS20, Z28/B44 MHS20, Z28/B56 The following Speakers have sustained damage by impact, from Scaffolding and other means during the build phase of the station in 2018. Also Speakers used to replace damaged ones in 2017 are now needed in these zones and Need to be replaced:- West Ticket Hall Back of House; MHS20, Z25/A71 MHS20, Z25/A57 CELL10, Z25/A63 Sentry 6, Z25/A65 Sentry 6, Z25/A39 Sentry 6, Z25/A45 Sentry 6, Z25/A15 Sentry 6, Z25/A13 MHS20, Z25/B60 Sentry 6, Z25/B58 Sentry 6, Z25/B70 MHS20, Z25/B50 Sentry 6, Z25/B44 Sentry 6, Z25/B40 Sentry 6, Z25/B06 Sentry 6, Z25/B12 East Ticket Hall Back of House; Sentry 6, Z27/A79 MHS20, Z27/A39 MHS20, Z27/A37 MHS20, Z27/A41 MHS20, Z27/B50 MHS20, Z27/B42 MHS20, Z27/B40 Sentry 6, Z27/B38 MHS20, Z27/B36 Sentry 6, Z27/B12 Also required due to it's non-inclusion of the Layout design and PAVA schematics for ZONE 17 escalators:- RSC4 ceiling speakers x4 We have not seen any speakers ordered from our previous NCR which was raised concerning damaged speakers Cxxx-NCR-002774. These speakers are urgently required too So in conclusion, a total of 40 Speakers are required to be replaced by Cxxx in this NCR. Sentry 6 = 21 MHS20 = 14 CELL10 = 1 RSC4 = 4
| 02SL - Stations (LUL) | Cxxx-NCR-002810 | NCR | MEP - Installation of Foul Drainage Tank at WTH |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-11-30 | 2018-12-16 16:44 | 16 | 2018-07-02 08:55 | Mechanical - Public Health Engineering | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | The installed pumped foul drainage tank located in the WTH -2/3 circular shaft does not comply with the __ specification Cxxx--P-TSC-M123-50004, PH_06_FAR_W_FWT in that the tank is manufactured in two sections and not as the modular type using 1000mm x 1000mm sectional tank construction method. The tank is too large to pass through the single and double doors on route to its final location thus does not comply with the maintenance and access replacement strategy document Cxxx--Z-STP-M123-50008 Rev 11.0 which was raised on CRL-OBS-21871 dated 03-04-2018. To get the tank to its current location it accessed the station WTH-2/3 via the OSD tower crane base / foot print which was removed on 30th may 2018 and the temporary OSD stab opening has now been constructed /closed. The tank was then split in two sections, the double doors were removed to allow access to the tank installed in location as per attached photos.
| 02SL - Stations (LUL) | Cxxx-NCR-002811 | NCR | ETH Pipework flanges cast in screed |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-09-21 | 2018-09-19 07:59 | -2 | 2018-06-29 13:00 | Civil - Drainage | 2000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | ETH L-2 the flange connections from the sump pumps have been cast in screed below the FFL.
| 02SL - Stations (LUL) | Cxxx-NCR-002812 | NCR | MEP Copex glans not installed on both ends of copex |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2018-07-27 | 2018-07-24 07:25 | -3 | 2018-06-29 15:01 | Communications and Control Systems - CCTV | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Copex glands need to be fitted to both ends of copex to protect cable and operatives from sharp edges but also to stop the copex from unravelling.
| 02SL - Stations (LUL) | Cxxx-NCR-002813 | NCR | Damaged speakers, Back of House East and West ticket halls |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-07-20 | 2018-07-10 08:27 | -10 | 2018-07-06 07:58 | Communications and Control Systems - Public Address Systems | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | External Phenomenon - Theft, tampering, sabotage, or vandalism | Completed |  | The following Speakers have sustained damage by impact, from Scaffolding and other means during the build phase of the station in 2018. Also Speakers used to replace damaged ones in 2017 are now needed in these zones and Need to be replaced:- West Ticket Hall Back of House; MHS20, Z26/A47 MHS20, Z26/B36 CELL10BD, Z26/A73 MHS20, Z26/A35 MHS20, Z26/B56 MHS20, Z26/A37 Sentry 6ST, Z26/B58 MHS20, Z26/A53 Sentry 6ST, Z26/B06 CELL10BD, Z25/A23 MHS20, Z25/A05 MHS20, Z25/B50 MHS20, Z25/B68 MHS20, Z25/A71 MHS20, Z25/A33 Sentry 6ST, Z25/B06 Sentry 6ST, Z25/B58 Sentry 6ST, Z25/B52 East Ticket Hall Back of House; CELL10BD, Z27/A61 MHS20, Z27/A37 MHS20, Z27/A39 MHS20, Z27/A41 MHS20, Z27/B36 MHS20, Z27/B40 MHS20, Z27/B42 MHS20, Z27/B50 MHS20, Z27/B32 MHS20, Z27/A33 Sentry 6ST, Z27/B04 Sentry 6ST, Z27/B12 Sentry 6ST, Z27/A11 Sentry 6ST, Z27/A79 Also required due to it's non-inclusion of the Layout design and PAVA schematics for ZONE 17 escalators:- RSC4 ceiling speakers x6; RCS4, Z17/A27 RCS4, Z17/A55 RCS4, Z17/B28 RCS4, Z17/B56 RCS4, Z17/A25 RCS4, Z17/B26 So in conclusion, a total of 38 Speakers are required to be replaced by Cxxx in this NCR. Sentry 6 = 9 MHS20 = 20 CELL10 = 3 RSC4 = 6
| 02SL - Stations (LUL) | Cxxx-NCR-002815 | NCR | WTH – Geothermal system installation without approved documents |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2019-06-28 | 2019-11-29 15:19 | 154 | 2018-07-06 16:43 | Civil - Civil Engineering General | 5000 |  | Documentation and Records | Rework | 3 (3-6k) | Complete | Subcontractor Problems - Other | Completed |  | This NCR is to cover a number of events regarding the geothermal manifold installation by __. __ came to site in February 2018 to install the manifold to handover to OSD as per approved drawing Cxxx--C2-DWG-M123-50036 C01. Instead a non-approved steel manifold was installed and left insitu (this is illustrated on attached drawing steel manifold sketch) __ were asked to supply design information to have the manifold approved before dosing the system according to Cxxx-PMI-00971. During this interim period it became apparent that __ would be unable to procure the required dosing solution and obtain the warranties for dosing proposal in Cxxx-PMI-00971. A draft ITP was prepared for this method but was never officially submitted due to changes in the method (Cxxx--C-ITP-M123-50440). A meeting was held in May 2018 to discuss and approve an alternative dosing method with the anticipated OSD handover date of 30 June 2018 being an important milestone at the time. In June __ returned to dose and install the manifold with ITP and design information still being worked on. At this point in time the design for the metal manifold was still not approved as were awaiting design and material information from __. The metal manifold was removed and was replaced by a plastic manifold as requested in the response to Cxxx-RFI-003872. See attachment plastic manifold sketch. The system was then dosed without an approved ITP in place.
| 02SL - Stations (LUL) | Cxxx-NCR-002816 | NCR | WTH - Geothermal system further blockage of 3no. full pile loops |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2020-05-15 | 2020-06-22 15:01 | 38 | 2018-07-06 17:00 | Civil - Civil Engineering General | 5000 |  | Damaged | Use As-Is | 3 (3-6k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | During the dosing and pressure testing of the geothermal system by __ 3 no. full pile loops have been reported as being blocked. This follows on from blockages previously reported in Cxxx-NCR-001346, Cxxx-NCR-001358 , Cxxx-NCR-001392 and Cxxx-NCR-001933.
| 02SL - Stations (LUL) | Cxxx-NCR-002817 | NCR | Damaged and missing __ back plates for telephones |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-07-23 | 2018-07-13 11:51 | -10 | 2018-07-09 09:00 | Communications and Control Systems - Telephony | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | Throughout the East and Test ticket hall areas, Telephone RJ45 Wall Outlets have been damaged and in one or two case removed from the wall by others. This damage occurs mostly through, being struck by scaffolding, during erection or striking of a tower. The following Telephones require a __ Wall Outlet :- FAR-00-LUA-30001 FAR-00-LUA-30002 FAR-00-LUA-30003 FAR-00-LUA-30006 FAR-00-LUA-30007 FAR-01-LUA-30103 FAR-01-LUA-30106 FAR-01-TEL-10102 FAR-01-TEL-10106 FAR-02-LUA-30201 FAR-02-LUA-30203 FAR-04-TEL-10401 FAR-05-TEL-10501 FAR-05-TEL-10502 FAR-07-TEL-10704 15x __ RJ45 Wall Outlets in total
| 02SL - Stations (LUL) | Cxxx-NCR-002818 | NCR | STW - Additional Cables required for Fire Mic installation |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-07-24 | 2018-07-10 15:15 | -14 | 2018-07-10 08:46 | Communications and Control Systems - Public Address Systems | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Insufficient quantity of material to do the job | Completed |  | Additional 300m of FT120 cable is required to complete the installation of the two Fire Mic's on Farringdon Station, these items are safety critical.
| 02SL - Stations (LUL) | Cxxx-NCR-002820 | NCR | STW - PAVA 4 core Fibre cable required |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-07-25 | 2018-07-31 09:33 | 6 | 2018-07-11 07:55 | Communications and Control Systems - Public Address Systems | 17000 |  | Incorrect Installation | Rework | 2 (6-60k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | A new 1200m __ 4 core multimode fibre is required at Farringdon. This is to replace one already installed but into the wrong route through the station. It has been agreed that this cable will be used for commissioning purposes, until a new fibre cable has been run correctly through the diverse route from one side of the station to the other.
| 02SL - Stations (LUL) | Cxxx-NCR-002821 | NCR | ETH - Barbican Use of Shingle without approved MCR |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-08-24 | 2018-08-31 06:56 | 7 | 2018-07-26 15:14 | Civil - Civil Engineering General | 750 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | The Barbican Platform 3 reinstatement design sketch (Cxxx--S-KSK-M123-50200 Rev.P01) – accepted under Cxxx-FCD-003264– details the use of use shingle as a backfill material in any void areas under the 175mm slab. An MCR for this material was not prepared and accepted prior to use on site, as per the Works Information requirements
| 02SL - Stations (LUL) | Cxxx-NCR-002822 | NCR | ETH - Installation of header tank support frame |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2020-06-06 | 2020-06-04 13:33 | -2 | 2019-05-01 14:43 | Civil - Civil Engineering General | 2000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The header tank has been initially installed as per Cxxx--S-DDL-M123_Z-20900 P03 which has been reviewed and comment status is closed. However, access for maintenance of the tank had not been considered in the design as detailed in Cxxx-PWK-00669.
| 02SL - Stations (LUL) | Cxxx-NCR-002823 | NCR | CCTV No compression glands fitted to camera's on -6 level FOH |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2018-07-30 | 2018-07-18 08:00 | -12 | 2018-07-16 15:15 | Communications and Control Systems - CCTV | 1000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | On inspection I found that __ had not installed compression glands on CCTV cameras where the CAT5e cable enters the camera to keep in tacked the IP rating of camera although the compression glands comes supplied in camera box.
| 02SL - Stations (LUL) | Cxxx-NCR-002824 | NCR | MEP - Chilled Water Foam Glass Blocks |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-07-31 | 2018-08-03 00:58 | 3 | 2018-07-17 07:31 | Mechanical - Public Health Engineering | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Further to "Cxxx-NCR-002702-MEP - STW - All Levels - Chilled Water System Insulation Blocks" it was agreed that remedial works will be carried out according to "Step by Step Guide to Fitting Foam Glass Blocks" document , however taking into account latest foam blocks manufacturer site visit and review the following was agreed (see attached email and Farringdon Blocks document)
| 02SL - Stations (LUL) | Cxxx-NCR-002825 | NCR | MEP – STW – [Cxxx-FIPC-FADEX1A, Cxxx-FIPC-FADWX1A, Cxxx-FIPC-FADWX1B] – “F1-specified” Damper Control Panels (DCPs) missing from F2 design |  | Contr | __ | FAR - Farringdon Station (West) |  | 2018-11-15 | 2019-01-14 11:06 | 60 | 2018-09-13 09:33 | Fire - Detection | 10000 |  | Design | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Other | Completed |  | The following Damper Control Panels (DCPs) have been missed from F2 design due to revised mechanical service design not passed on to the fire alarm design team to allow update to Fire design. 1. DCP -71 2. DCP -73 3. DCP -74 4. DCP -75 5. DCP -76 6. DCP -77 7. DCP -78 8. DCP -79 9. DCP -80
| 02SL - Stations (LUL) | Cxxx-NCR-002826 | NCR | MEP - STW - Loss of Wrap around labels for SCADA cables |  | Contr | __ | FAR - Farringdon Station (West) |  | 2018-10-25 | 2018-11-26 10:48 | 32 | 2018-09-13 08:55 | Communications and Control Systems | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Due to the misplacement of the SCADA wrap around labels issued to us by __, we require a new set of wrap around labels of all the SCADA cables on the schedule.
| 02SL - Stations (LUL) | Cxxx-NCR-002827 | NCR | TUN - FITOUT - Damage to Cxxx PES glass panel |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-08-24 | 2018-09-11 17:06 | 18 | 2018-07-24 08:32 | Architectural - Finishes | 6000 |  | Damaged | Repair | 3 (3-6k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | On Friday 20th 2018 identified that a pane of glass on the Eastbound East End installed by systemwide contractor Cxxx Knorr Bremse on the Platform Screen Doors had been damaged. Damage looks to be by the use of a pallet truck driving into the screen causing two holes in the panel.
| 02SL - Stations (LUL) | Cxxx-NCR-002829 | NCR | Damaged radio cables |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2018-09-21 | 2018-10-04 13:31 | 13 | 2018-07-26 09:21 | Communications and Control Systems - Radio | 11000 |  | Damaged | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Other | Completed |  | __ have replaced radio 7/8” cable FD2200 and FD2197 due to both cables failing test. Looks like both cables were damaged on install. Both cables are 105m long. Both cables were cut out then new cable pulled in from CER1 to level -6 GI location, Both cables have been dressed and cable tied on CMS. The work above took 12 operatives 4 shifts to complete the work above. Cable FD2193B 7/8” also fail test, __ found the damaged by DC13 which was done on install, as __ had left a coil at the other end of the cable they cut all the cable ties and pulled the damage part of the cable pass the termination point and then tied and dressed the cable back on to the CMS. Length of cable 60m. The work above took 7 operatives 1/2 shift to complete the work above.
| 02SL - Stations (LUL) | Cxxx-NCR-002830 | NCR | WTH – Internal Cladding – CMS Panel Colour |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-08-15 | 2018-09-04 11:03 | 20 | 2018-08-01 14:16 | Archaeology - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | WTH Internal Cladding CMS Panels have been fabricated and delivered to site with a standard stainless steel finish. These panels should have been fabricated with “Rimex stainless steel (champagne coloured)” as detailed in Cxxx Architectural Specification Cxxx--A-RSP-M123-50057 JH43.1203 h) for TYPE LIN-301 WTH COMPOSITE WALL CLADDING METAL RIMEX CMS ACCESS PANELS Affected CMS Panels can be shown in the attached Elevation Mark-up ‘SK-INTCLAD-JB-009 R2.0’.
| 02SL - Stations (LUL) | Cxxx-NCR-002833 | NCR | WTH - Wrong DOO cable installed. |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-09-21 | 2018-12-04 15:42 | 74 | 2018-08-01 10:04 | Communications and Control Systems - Driver only Operation CCTV | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Supervision - Other | Completed |  | __ / __ accidentally installed an incorrect cable, using standard LCF12/50 radio cable for DOO, which requires a specific cable LMR600 12/50 cable.
| 02SL - Stations (LUL) | Cxxx-NCR-002834 | NCR | ETH-Lighting plinths poured without Pre-pour check sheet |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-08-27 | 2018-08-20 07:44 | -7 | 2018-08-13 12:18 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | poured the 3 Barbican lighting plinths highlighted on attached drawing (Cxxx--A-DDA-M123_3-26060) without the required Pre-pour inspection check sheet and supplementary evidence compiled, as is required. Note that Cxxx--S-XSK-M123-50193 P01 (Which has now been incorporated into drawing(Cxxx--S-DDD-M123_Z-41200 Detail D3) and accepted under Cxxx-FCD-003317, DRIR Cxxx--C-LRG-M123-50035 Rev.21.0 and drawing Cxxx--S-DDD-M123_Z-41200 P06 (accepted under Cxxx-FCD-003317, DRIR Cxxx--C-LRG-M123-50035 Rev.21.0) were the __ drawings used to construct these plinths.
| 02SL - Stations (LUL) | Cxxx-NCR-002835 | NCR | WTH - damage to perimeter wall waterproofing on wall 43 at level -1 external face (Snowhill basement) |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2019-01-18 | 2019-01-15 12:04 | -3 | 2018-08-02 15:44 | Civil - Civil Engineering General | 1500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | Waterproofing installed on the external face of wall 43 at level -1, accessible from Snowhill basement, has been damaged in a number of places or has become detached from the wall. See attached zone of repairs and photo for details. Note that if any damage is noticed in the ‘green’ area, this will also be repaired in the same manner as detailed below.
| 02SL - Stations (LUL) | Cxxx-NCR-002836 | NCR | TUN - Damaged DOO camera Bracket on West Bound Platform |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-09-21 | 2018-10-12 08:10 | 21 | 2018-08-02 13:20 | Communications and Control Systems - Driver only Operation CCTV | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Early last week 25th July 2018 an operative working in close proximity to a DOO camera on the Westbound platform, accidentally struck DOO camera 4 as his MEWP maneuvered into a new position for him to continue the works. The camera and it's housing sustained no damage at all, but the bracket which holds it, had two pins which hold the bracket gimble shear off. __ will be supplying new components for the damaged bracket. __ have removed the DOO camera and housing to protect it. and will re-instate once the bracket has been repaired or replaced
| 02SL - Stations (LUL) | Cxxx-NCR-002837 | NCR | STW - PAVA 1.5mm cable required to complete Station installation |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-09-21 | 2018-10-09 15:45 | 18 | 2018-08-03 09:34 | Communications and Control Systems - Public Address Systems | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | __ / __ have provided us with a spreadsheet detailing how much 1.5mm PAVA cable is required to complete the Installation at Farringdon. Cable Required; Firetuf FT30 2C-E 1.5mm White Cable.. FTES2EH1.5 5x 500m drums and 1x 100m drum required from __ to complete.
| 02SL - Stations (LUL) | Cxxx-NCR-002838 | NCR | ETH Barbican Platform - Pour 2 (Under hayne street bridge) poured to incorrect level |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-09-28 | 2018-09-28 13:05 | 0 | 2018-08-16 11:44 | Civil - Civil Engineering General | 2500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following the Barbican Platform Pour 2(under Hayne street bridge area) carried out a survey of the concrete level and found that it was poured to the wrong fall meaning levels were too high at interface with ETH. TOC level should have been 109.884 where the Barbican meets the ETH, but the as built level is actually 109.974. The rebar was installed at the correct level. The area in question will have Asphalt works above incorporating falls to the ACO channel. See attached As built survey and photos of the area.
| 02SL - Stations (LUL) | Cxxx-NCR-002839 | NCR | TUN - BUI - Lux Levels in CH1 and CH2 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2020-06-19 | 2020-07-07 15:09 | 18 | 2018-08-09 12:21 | Electrical - Lighting | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Further to the testing and commissioning of the totem uplighters at Farringdon on 07/08/18, it was discovered that there is a drop off in lux levels between the ES2 escalators/inclined lift and nearest totem in CH2 - see attached mark up. It is believed that the lux levels in this area will not meet the requirements of LUL S1066. It is noted that the totems were turned on without the prototype baffles which will further reduce lux levels. However, there was no light coming from the escalators. 08/10/18 update: It has since been established that there is a drop down sign with lighting in this area, therefore further testing will be carried out when the sign and lights are installed at the end of October.
| 02SL - Stations (LUL) | Cxxx-NCR-002840 | NCR | ETH - Blockwork ESS1 Use of non-approved drawing for construction |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-09-07 | 2018-08-16 10:11 | -22 | 2018-08-10 15:38 | Architectural - Brickworks/Blockworks | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | Blockwork was constructed in the ESS1 main staircase from Level -6 to Level 0 drawing Cxxx--X-DWG-M123_Z-54205 Rev P04. The drawing was not issued or accepted by Crossrail prior to construction on site.
| 02SL - Stations (LUL) | Cxxx-NCR-002841 | NCR | WTH - Removal of Render in Toilet Lobby (FOH) |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-09-05 | 2018-09-04 09:32 | -1 | 2018-08-22 10:52 | Architectural - General | 2000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | The lobby area of the WTH Public toilets (highlighted on the attached drawing) is to have a condensation insulation applied before the render and tiles. However, in this area the render was applied before insulation in some areas. This affected the CMS space on the Western wall, and as a result, this render has had to be removed.
| 02SL - Stations (LUL) | Cxxx-NCR-002842 | NCR | WTH - Alignment of __ Grating Panels |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-09-28 | 2018-10-03 06:41 | 5 | 2018-08-15 13:40 | Architectural - Roofing & Exterior Treatment | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Along the northern most section of the WTH __ Grating (located to the western elevation of +1 lower mez. and highlighted on the attached drawing - 'Cxxx--Y-DWG-M123-51880 SK'), the vertical joints of the elefant grating do not alight with the joints of the clamping plates. This was raised in the joint __/CRL/ inspection on 26/7/18 and detailed in the attached document '180726 - Inspection __ gratings'. All other items mentioned within this document have been closed out. The alignment is further highlighted within IMG_1,2&3 attached.
| 02SL - Stations (LUL) | Cxxx-NCR-002843 | NCR | MEP - STW - [Cxxx-ELEC-ESD*X3] - Damaged DALI cable |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2019-01-31 | 2019-02-25 13:38 | 25 | 2018-08-17 07:30 | Electrical - Lighting | 5000 |  | Damaged | Rework | 3 (3-6k) | Complete | External Phenomenon - Not Defined | Completed |  | The "dead" testing ITP activitiy for the "DALI" cable from LCM33 to station control room (see attached drawing Cxxx--E-DWG-M123_Z-53023 [P01] - "Western Ticket Hall Lighting Control Schematic (__/__)") failed. Following initial investigation, it was revealed that the cable was damaged along it's route.
| 02SL - Stations (LUL) | Cxxx-NCR-002844 | NCR | WTH Level +2 Use of non-approved debonding material between blockwork wall and concrete plinth |  | Contr | BAM | FAR - Farringdon Station (West) |  | 2018-10-05 | 2018-10-04 09:19 | -1 | 2018-08-20 13:28 | Civil - Civil Engineering General | 1000 |  | Material | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | used a debonding material called ‘Flexcell’ in the locations marked on the attached drawing.The material was not approved nor was it shown on any design drawings. made the decision to use the material as there was the possibility the block work wall could crack if concrete was poured against it.
| 02SL - Stations (LUL) | Cxxx-NCR-002845 | NCR | WTH - reduced rebar cover in level 0 slab nib at smoke vent 2 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-08-31 | 2018-08-24 09:42 | -7 | 2018-08-23 07:49 | Civil - Civil Engineering General | 2500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Previous Construction - Problems based on previous construction errors | Completed |  | 2no. couplers exposed for the level 0 nib to the south side of smoke vent 2 have reduced cover of around 5-10mm. See area marked in blue on drawing Cxxx-ATK-S-DWG-M123_1-50132 C04.
| 02SL - Stations (LUL) | Cxxx-NCR-002846 | NCR | MEP - BFK - Cxxx damaged cable (Fibre Optic) WTH |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-09-25 | 2018-11-06 15:57 | 42 | 2018-08-28 13:11 | Communications and Control Systems - Fibre Optic Network | 3000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Fibre Optic cable in 300mmx75mm trunking at WTH -4 Circular Shaft. The cable has been damaged after it has been pulled in. The cable has kinked, which has caused glass in the cable to be damaged. The cable that has been damaged is a 12 core SM and it is 130 meters in length
| 02SL - Stations (LUL) | Cxxx-NCR-002847 | NCR | MEP Disappearance of Cxxx CCTV cameras |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-09-12 | 2018-10-04 13:39 | 22 | 2018-08-29 08:36 | Communications and Control Systems - CCTV | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | External Phenomenon - Theft, tampering, sabotage, or vandalism | Completed |  | The total of 4 CCTV cameras has gone missing. The Id of the camera is the following; 1) FAR -00-CAM-0136 ETH 0 2) FAR-07-CAM-0260. This has been removed twice. 3) FAR-07-CAM-0261
| 02SL - Stations (LUL) | Cxxx-NCR-002848 | NCR | WTH – Metalwork – Use of ‘P’ Status drawing for MNS2 detailing without minimum drawing assurance |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-09-12 | 2018-08-30 09:00 | -13 | 2018-08-29 13:55 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | instructed __ to begin design and installation of MNS2 staircase prior to being able to demonstrate without being able to demonstrate the minimum assurance requirements for drawing Cxxx--A-DDD-M123_Z-75138 P01. This is a procedural NCR.
| 02SL - Stations (LUL) | Cxxx-NCR-002849 | NCR | WTH - Incorrect concrete pouring of smoke vent 3 nib |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-10-05 | 2018-10-05 13:29 | 0 | 2018-08-30 14:44 | Civil - Civil Engineering General | 1500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | poured the level 0 slab nibs at smoke vent nibs 1,2 and 3 on 24 August 2018. The north-western corner of smoke vent 3 nib was not cast correctly with concrete not filling the correct volume and shape enclosed by the __ waterproofing. Damage to the waterproofing is also likely to occur.
| 02SL - Stations (LUL) | Cxxx-NCR-002850 | NCR | __ cable damaged by wifi contractors |  | Contr | __ | FAR - Farringdon Station (West) |  | 2018-10-31 | 2018-11-06 15:52 | 6 | 2018-09-13 09:03 | Communications and Control Systems | 17000 |  | Damaged | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Other | Completed |  | Upon completion of pulling 12 core optical fiber cable between LU CER and ETH CRL CER, it was tested and failed due to damage along the run.
| 02SL - Stations (LUL) | Cxxx-NCR-002851 | NCR | ETH Barbican – Documentation not in place before works carried out. |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-09-21 | 2018-10-16 08:19 | 25 | 2018-09-04 12:55 | Civil - Civil Engineering General | 1000 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | are reinstating Platform 3 on the Barbican platform. During construction it was observed that there were some materials used to construct the structure that did not have accepted Material Compliance Records in place prior to works commencing. This includes materials such as blockwork, Hydrocell XL, and lamp posts. Also some activities were not captured in an approved ITP. Activities include access hatches installation, tiling works, Radfex and Densoband installation, and installation of lamp posts.
| 02SL - Stations (LUL) | Cxxx-NCR-002853 | NCR | MEP No protection for Radio Connectors and cable ends |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-10-26 | 2018-10-05 10:57 | -21 | 2018-09-04 11:00 | Communications and Control Systems - Radio | 1000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | It has been observed, that cable ends and connectors have not been protected stationwide.
| 02SL - Stations (LUL) | Cxxx-NCR-002854 | NCR | MEP Telephone damaged and taken of wall. |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-09-18 | 2018-10-08 10:11 | 20 | 2018-09-04 11:22 | Communications and Control Systems - Telephony | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | A telephone (Serial Number - 00878) was taken of the wall by an unknown party. The location is WTH-6.
| 02SL - Stations (LUL) | Cxxx-NCR-002855 | NCR | WTH - Tiling - Tiling not installed in line with setting out information |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-09-25 | 2018-10-05 15:32 | 10 | 2018-09-11 10:03 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The tiles installed in the corridor on Level -1 between MNS05 and MNS06 have been installed on the wrong lines. As such, the tile joints don’t line up with the access hatch to be installed. The correct location of the joints can be seen in page 1 of the attached PDF (Level -1 Corridor).
| 02SL - Stations (LUL) | Cxxx-NCR-002856 | NCR | Cxxx- Radio connectors, assets and cable ends not protected from dust and moister ingress |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2019-01-18 | 2019-01-22 09:45 | 4 | 2018-09-10 09:40 | Communications and Control Systems - Radio | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | I have raised and OBS for radio connectors and cable ends not being protected for dust and moister ingress. The lads have been told to make sure the ends of the cables, connectors and assets are protected either by using dust caps or tape. Some connectors may need terminating and some assets replaced.
| 02SL - Stations (LUL) | Cxxx-NCR-002857 | NCR | MEP - Blockwork adjustment Westbound East End |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2019-03-22 | 2019-04-09 12:07 | 18 | 2018-09-11 11:19 | Electrical - Cable Management | 3000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Works have been undertaken to allow for widening of an emergency opening for door 7-ED-21, as per Cxxx-PMI-00993. The solution required for a rotated Wi column, this to allow for fixing of high pressure track side door installation. The Wi column has been installed in front of existing CMS trunking. This structural Wi column is now restricting access to the front of the CMS. Attached photographic survey.
| 02SL - Stations (LUL) | Cxxx-NCR-002858 | NCR | STW - MEP & WTH - Transformer Room Integrity Testing |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2019-09-20 | 2019-08-29 15:14 | -22 | 2018-09-12 10:08 | Mechanical - Public Health Engineering | 500 |  | Supervision/Management | Reject | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Two issues have arose surrounding the Integrity Testing of the Western Ticket Hall Transformer Room on the 31/08. A previous test on the 15/08 failed for the following reasons: 1) Both tests took place using temporary seals surrounding the Rhino doors to trackside. As this is not the permanent condition, a retest will be required once the permanent seals are in place. 2) The results of the test on the 15/08 state that HV cables need to be lowered to achieve the Retention Time Requirement due to the protected height and this was a failure criteria. For the test on the 31/08, the cables remained in the same position but the test was a deemed a pass as the protected height was lowered to the height of the transformer. Further investigation is required to understand how this discrepancy occurred. It should be noted that the Integrity Testing of the Eastern Ticket Hall Transformer Room passed using a different criteria (similar to the 15/08 test at the WTH) and this also needs to be confirmed in a Risk Assessment.
| 02SL - Stations (LUL) | Cxxx-NCR-002860 | NCR | MEP - Damper Control Panels Installed Underneath Urinal Cisterns |  | Contr | __ | FAR - Farringdon Station (West) |  | 2018-10-11 | 2018-10-12 09:33 | 1 | 2018-09-13 13:49 | Fire - Detection | 5000 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | 2No Damper Control Panels and associated conduit have been installed in maintenance service void for Gents toilet at at WTH -1, directly underneath urinal cisterns. The cisterns when installed could leak or condensate in the future onto panels.
| 02SL - Stations (LUL) | Cxxx-NCR-002861 | NCR | WTH - Level 0 ITH balcony extension slab missing concrete cube strength results |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-11-23 | 2018-11-23 11:44 | 0 | 2018-10-27 10:28 | Civil - Civil Engineering General | 1500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | The __ designed WTH level 0 ITH balcony extension slab was cast on 3rd July 2018 using a C50/60 mix called C1/C2. The cubes for this slab have gone missing. Also, __, the supplier, did not take cubes for this load either.
| 02SL - Stations (LUL) | Cxxx-NCR-002862 | NCR | WTH- Level 0 misaligned and out of position cast concrete along building line on Cowcross Street |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2019-07-26 | 2019-09-26 11:47 | 62 | 2018-11-02 16:53 | Civil - Civil Engineering General | 7500 |  | Incorrect Installation | Use As-Is | 2 (6-60k) | Complete | Previous Construction - Interfacing issues | Completed |  | have cast the concrete protective layer at level 0 along Cowcross Street. The line of the pour is further north and also has an irregular concrete line which is not in accordance with drawing Cxxx-SWN-S-DDA-M123_1-80001 Rev.C08. See attached photos in CRL-OBS-24530 and the as-built information in the attached file Cxxx-NCR-002862. When were constructing the Northern RC perimeter walls from level -1 to level 0, it was discovered that the outside face of these walls were located 90-1000mm south from the mass-filled existing Cowcross Street bridge structure. Instead of breaking back the existing Cowcross Street bridge structure (an activity with inherent risk to the public) to allow a traditional shutter and man access to be created around the outside of the perimeter wall, it was more sensible to install Cordek against the bridge structure and cast against this. This same logic was applied to rule out the option of partially breaking the bridge structure back to form a straight concrete line. This approach meant that when the __ waterproofing sheeting was installed against the Cordek, it followed the irregular line of the bridge structure, outside the ‘design footprint’ of the station. The detail where this __ laps onto the level 0 slab requires a 100mm concrete protective layer to be cast over the horizontal __ lap. Hence this has followed the same line as the __ and has resulted in an irregular ‘edge of concrete’ line along the Northern site boundary.
| 02SL - Stations (LUL) | Cxxx-NCR-002863 | NCR | ETH Barbican – Poor Workmanship of Permascreed/Permapark works |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-11-09 | 2018-11-06 08:10 | -3 | 2018-09-19 17:36 | Civil - Civil Engineering General | 3000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | are reinstating Platform 3 on the Barbican platform. Permascreed and Permapark works were carried out with poor workmanship observed namely: 1) Tyre marks from the wheelbarrow present on the permascreed north of the Aco channel 2) Poor finish of permapark in some locations along Aco channel around the access hatches Please see attached site photos and location sketch Repairs also commenced without these having been accepted by NCR first, which is not in accordance to CRL NCR procedure
| 02SL - Stations (LUL) | Cxxx-NCR-002864 | NCR | WTH - Metalwork - No approved Drawings for PST Construction |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-11-09 | 2018-11-06 08:26 | -3 | 2018-09-21 10:47 | Civil - Civil Engineering General | 1000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | The construction of the Public Staircase (PST) in the WTH began without accepted IFC drawings being in pace. These should have been prepared and submitted to __ for review, and subsequently accepted by Crossrail before construction commenced.
| 02SL - Stations (LUL) | Cxxx-NCR-002865 | NCR | MEP - LV Busbars at WTH & ETH installed without approved F2 drawings |  | Contr | __ | FAR - Farringdon Station (West) |  | 2019-03-08 | 2019-03-05 13:19 | -3 | 2018-09-26 16:12 | Electrical - LV Equipment | 500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | LV Busbars being installed by __ at WTH & ETH has no approved F2 drawings. The drawings used by Siements on site are at Rev. 14 to Rev 16 however the latest approved Busbar F2 drawings on eB are at Rev 01.
| 02SL - Stations (LUL) | Cxxx-NCR-002866 | NCR | MEP - Damaged OSD Earth Mat connections at WTH Level 0 |  | Contr | __ | FAR - Farringdon Station (West) |  | 2018-12-14 | 2018-11-26 10:22 | -18 | 2018-09-27 11:52 | Electrical - Earthing & Bonding | 5000 |  | Damaged | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | DC13 and DC14 earthing cables at WTH Level 0 have been damaged and required replacement (see attached photos).
| 02SL - Stations (LUL) | Cxxx-NCR-002867 | NCR | MEP - Provision of support loading calculations for the Busbar system |  | Contr | __ | FAR - Farringdon Station (West) |  | 2019-01-26 | 2019-03-11 08:52 | 44 | 2018-09-26 16:47 | Electrical - LV Equipment | 1000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | CRL is raising concern regarding support loading calculations for the Busbar system at ETH&WTH, however Busbar has been supported and installed in accordance with supplier's approved installers and in association with manufacturer's guidance and recommendation, as detailed within in CRL-MCR-001146
| 02SL - Stations (LUL) | Cxxx-NCR-002868 | NCR | WTH - Lower Apse - water egress and damp patches on slab soffit |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2020-06-26 | 2020-06-12 11:33 | -14 | 2018-10-08 15:43 | Civil - Structural Engineering | 1500 |  | Planning | Repair | 4 (0.5-3k) | Complete | Previous Construction - Interfacing issues | Completed |  | During the repair works to the Lower Apse ceiling, 4no. locations of water egress or dampness were identified across the footprint of the ceiling. These areas are shown on the attached pdf - 'Lower Apse ceiling - water egress and damp patch locations'.
| 02SL - Stations (LUL) | Cxxx-NCR-002869 | NCR | TUN - BUI - Platform Benches Height |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-10-30 | 2018-10-30 16:05 | 0 | 2018-10-02 14:48 | Architectural - General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Platform benches have been installed 50-60mm higher than specified in Cxxx-ATK-A-DDD-CR001_Z-43300 and Cxxx--A-DDD-M123_7-43300. The distance from the floor to the bench top is 500 mm (as opposed to 450mm), and from the floor to the bottom of the beam is 360 mm (as opposed to 300mm). The technical note (HF study) attached presents the reasons that lead the bench intallation to be higher than specified and an "ALARP" case focusing both on the height of the seat and the clearance of the bottom beam from the floor. Moreover, different solutions are presented in case the height of the support beam is not accepted to be used as is.
| 02SL - Stations (LUL) | Cxxx-NCR-002870 | NCR | ETH - Opening in Level 0 Slab for __ Pipes |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2019-02-15 | 2019-02-25 11:44 | 10 | 2018-10-02 16:13 | Civil - Civil Engineering General | 15000 |  | Incorrect Installation | Use As-Is | 2 (6-60k) | Complete | Personnel Error - Inattention to detail | Completed |  | The opening in the level 0 slab for the __ pipes has been cut in the incorrect position. The as installed position has been highlighted in blue on the attached plan drawing.
| 02SL - Stations (LUL) | Cxxx-NCR-002871 | NCR | WTH - OSD perimeter waterproofing |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-11-30 | 2018-11-08 08:08 | -22 | 2018-10-02 17:33 | Architectural - General | 5500 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Waterproofing detail around OSD area on WTH Level 0 was applied only up to FFL. Indicative drawings attached shown waterproofing going higher than concrete protective layer and following recommendation from _laser (__ applicators) propose to remove 100mm strip of concrete in order to allow waterproofing to be extended at least 100mm above FFL. Please see attached location marked-up and sketch showing before/after situation.
| 02SL - Stations (LUL) | Cxxx-NCR-002872 | NCR | WTH – SH-W1 L-6 Wall Access Hatch 7-WWH07 Not Able to Open Fully |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-11-30 | 2018-10-25 07:32 | -36 | 2018-10-05 12:05 | Architectural - General | 1500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Due to the secondary steel support for MNS 3 (B) Maintenance Stairs being installed in front of wall Access Hatch 7-WWH07, the hatch into the cavity wall cannot open fully. Refer to attached site photos and drawing Cxxx--A-DDA-M123_7-76223.
| 02SL - Stations (LUL) | Cxxx-NCR-002873 | NCR | CER not kept clean or tidy and also build up of dust |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2018-11-07 | 2018-11-09 09:46 | 2 | 2018-10-06 11:29 | Communications and Control Systems | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | I have inspected CER1 and found it to be unclean, rubbish laying all over the floor and also a build up of dust. I have raised OBS and emailed on numerous occasions regarding this issues and was told that would clean and hoover the room and also keep a hoover in the room so contractors can use it to clean up there mess
| 02SL - Stations (LUL) | Cxxx-NCR-002874 | NCR | DOO installation |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2018-12-22 | 2018-12-19 09:58 | -3 | 2018-10-06 12:32 | Communications and Control Systems - Driver only Operation CCTV | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | All coax’s had to be re-terminated in CER1&2 and at camera's due to poor workmanship, camera build incomplete and missing components which __ have lost and now have to source; this includes bolts, isolating rubbers and camera stabilisers.
| 02SL - Stations (LUL) | Cxxx-NCR-002875 | NCR | WTH - Clow Group - starting works without all quality assurance documentation submitted |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2019-05-31 | 2019-11-27 10:36 | 180 | 2018-10-08 12:43 | Civil - Structural Engineering | 3000 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Clow Group are a subcontractor employed to construct a maintenance gantry behind the trumpet cladding on level -1 of the WTH. They commenced works onsite on 3/10/18 without submitting a number of quality assurance documentation (multiple MCRs and their welding competencies document). These have been assigned eB numbers and the placeholders are referenced below.
| 02SL - Stations (LUL) | Cxxx-NCR-002876 | NCR | MEP - Damage to __ Cables in WTH Level -4/-5 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-12-14 | 2018-12-19 10:11 | 5 | 2018-10-26 12:21 | Communications and Control Systems - Fibre Optic Network | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | The following cables were identified as being damaged on 24/08/18 at 07:04am. These run from West Bound FOSC4 Room to CER1 Room, CAB-7733WUI to CAB-2731U10 in 3 runs of 200m metres: - M123-DAT-00617 M123-DAT-00191 M123-DAT-00173 Please see attached photos of the damage incurred. The time and date of damage of these cables is known due to the Fibre Optic network being live and monitored centrally. 3 new cables as per following specification will need to be reordered: - Description: 373-BEL-LTDCT-24LUL Part Number: GUSL824 MCR: CRL-MCR-002441
| 02SL - Stations (LUL) | Cxxx-NCR-002878 | NCR | WTH Level 0 Installation of Procter Gate without approved documentation |  | Contr | BAM | FAR - Farringdon Station (West) |  | 2018-11-23 | 2018-11-19 18:40 | -4 | 2018-10-23 11:34 | Architectural - Doors | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Insufficient work planning by the subcontractors | Completed |  | Procter manufactured and installed the service yard gate without approved MCR or ITPs in place.
| 02SL - Stations (LUL) | Cxxx-NCR-002879 | NCR | ETH – Level +1 upstand/concrete slab edge out-of-tolerance |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-12-21 | 2018-12-20 12:22 | -1 | 2018-10-23 15:14 | Civil - Civil Engineering General | 3500 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Concrete upstand/slab edge between Gridlines 5/7 and Gridline A (West face of Level +1) found to be out-of-tolerance by up to 8mm (23mm from design, 8mm above 15mm tolerance). Refer to __ drawing FED-1430-00-01-DR-X-0003 Rev 03 or Cxxx-SWN-S-DDA-M123_A-30101 Rev C08. An as-built survey has been carried out to determine the areas within the upstand which are out of tolerance.
| 02SL - Stations (LUL) | Cxxx-NCR-002880 | NCR | MEP - Cxxx - CH2 Speaker Damage |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2019-02-09 | 2019-03-21 17:22 | 40 | 2018-10-24 11:11 | Communications and Control Systems | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | External Phenomenon - Theft, tampering, sabotage, or vandalism | Completed |  | Drop pole mounted speaker in CH2, has been damaged following installation. Damage looks to be superficial damage to the cover grill only. Damage shown on attached photograph.
| 02SL - Stations (LUL) | Cxxx-NCR-002881 | NCR | MEP - STW - [Cxxx-FIPC-FADXX1A] - Requirements of diverse routing for fire system network cables not implemented |  | Contr | __ | FAR - Farringdon Station (West) |  | 2018-12-21 | 2018-12-14 08:57 | -7 | 2018-10-26 09:58 | Fire - Detection | 3000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Requirements of diverse routing for fire system network cables, as defined within Cxxx-RFI-004395, have not been implemented, as the conduit runs were supported by the same hanger system.
| 02SL - Stations (LUL) | Cxxx-NCR-002882 | NCR | MEP - WTH - Level 0 - [Cxxx-FIPC-FISWW1A] - Poor housekeeping in Water Mist Room |  | Contr | __ | FAR - Farringdon Station (West) |  | 2018-11-16 | 2018-11-19 13:59 | 3 | 2018-10-26 16:46 | Fire - Suppression | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Following weekly WTH site inspection by the __ Quality Manager, poor housekeeping was identified in the WTH Level 0 area where the Water Mist Plant and Tank are installed.
| 02SL - Stations (LUL) | Cxxx-NCR-002883 | NCR | MEP - STW - [All CommLots] - Unallocated MCRs to CommLots |  | Contr | __ | FAR - Farringdon Station (West) |  | 2019-03-04 | 2019-03-08 11:14 | 4 | 2018-10-29 16:35 | Mechanical - Mechanical Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Following verification of the Cxxx MEP MCR database, it has become apparent that there were MCRs (refer to attachment) that have not been declared by the site teams within their Records Package Listings submitted as part of the IRN process.
| 02SL - Stations (LUL) | Cxxx-NCR-002884 | NCR | MEP - STW - Materials with F2 acceptance installed in rooms with volume greater than 200m3 |  | Contr | __ | FAR - Farringdon Station (West) |  | 2019-06-28 | 2019-08-22 08:16 | 55 | 2018-10-29 17:07 | Mechanical - Mechanical Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Following AIMS verification, it has become apparent that certain Code-1 accepted materials with conditional F2 acceptance (installed within rooms with volume less than 200m3), have been installed in rooms with volume greater than 200m3, thus breaching the acceptance condition obtained under the materials compliance process.
| 02SL - Stations (LUL) | Cxxx-NCR-002885 | NCR | WTH MEP – Low Pressure Water Mist System Installed on Site Not in Accordance With Accepted Design |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2019-05-31 | 2020-01-17 15:31 | 231 | 2018-10-30 09:33 | Fire - Suppression | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | At the joint CRL /CEG/Cxxx/__ /__ installation inspection on 27th September 2018 CRL noted that the WTH Low Pressure Water Mist System installation works within the tanks / pump room has now been completed without a FCD being raised to capture the deviations to the previously-submitted design information.The Cxxx Fire Engineer nor the CEG Fire team & CRL FE were consulted regarding these deviations. It was found the installation did not reflect the current Cxxx--P-DDA-M123_1-75705 drawing with the key discrepancies listed below: 1. Change to the tank type & size from a two compartment split type to a singular 2. Additional nozzles in the tank/pump room (4 No on DRW 8 No installed) 3. Increase infill cold water main pipe diameter to the tank to offset the need to increase the tank loading. It was confirmed the structural engineer rejected the option to increase the tanks size. BKF / __ then opted to increase infill cold water main pipe diameter to offset the requirement to increase the tank size /loading. 4. The nozzles within the tank/pump room are installed at approx 7.45 meters - AFFL outside the VdS fire test parameters criteria for nozzle heights of 5 meters AFFL resulting in a system that is not certified for the protected risk. 5. No design drawings for the fire pump control, sensors and field wiring/cms are in place due to a scope gap between __ and their fire contractor - Protec.
| 02SL - Stations (LUL) | Cxxx-NCR-002886 | NCR | MEP - STW - [Cxxx-FIPC-FADWX1A, Cxxx-ELEC-ESD*2] - Observations raised from CRL Quality Surveillance |  | Contr | __ | FAR - Farringdon Station (West) |  | 2019-04-26 | 2019-04-24 09:58 | -2 | 2018-11-21 00:37 | Fire - Detection | 1000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Following CRL Quality Surveillance, the following non-compliances were identified relating to the fire alarms and detection installation, for which the CRL Auditor & FE have raised relevant observations against: [CRL-OBS-25248] Positioning of adaptable box bush and adjacent conduit is putting unnecessary duress on the fire alarm loop cable - relevant to CommLot [Cxxx-FIPC-FADWX1A]. [CRL-OBS-25254] Conduit has been kinked during installation and is potentially split - relevant to CommLot [Cxxx-FIPC-FADWX1A]. [CRL-OBS-25255] It was observed that the fire alarm cabling has inadequately supported cable tray and cabling is potentially stressed on entry to adaptable box. [CRL-OBS-25256] Conduits appear to be inadequately supported and not in accordance with Selection & Erection guidelines.
| 02SL - Stations (LUL) | Cxxx-NCR-002887 | NCR | Procurement of radio cable. 500mts 7/8 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-12-21 | 2018-12-13 11:34 | -8 | 2018-11-01 11:22 | Communications and Control Systems - Radio | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Because of damaged cables, additional quantity of 500 meters of 7/8 radio cable is required. The ID of the damaged is the following; 1. FD2190 2. FD2197
| 02SL - Stations (LUL) | Cxxx-NCR-002888 | NCR | TUN - FITOUT - SGN120 bracket |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2019-02-08 | 2019-02-19 15:32 | 11 | 2018-11-02 13:18 | Architectural - Signage | 5500 |  | Material | Rework | 3 (3-6k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | Bracket for SGN120 projecting through the PES grill has a stainless steel finish. A bench mark was undertaken on the 11th October 2018 (Cxxx--A-LRC-M123-50297) with comment raised by CRL __ that bracket to be “black to match other brackets”.
| 02SL - Stations (LUL) | Cxxx-NCR-002889 | NCR | MEP - WTH - Level -2 - [Cxxx-PUHC-SWPWN1A, Cxxx-ELEC-ESDWX2E] - Incorrect installation of foul sump pump control panel |  | Contr | __ | FAR - Farringdon Station (West) |  | 2019-02-15 | 2019-04-24 12:29 | 68 | 2018-11-02 23:51 | Mechanical - Public Health Engineering | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Management Problem - Other management problem | Completed |  | Following the LUL/CEG/CRL team site review, it was observed that the foul sump pump control panel located at WTH Level -2 has not been installed in the position specified on drawing Cxxx--E-DDA-M123 3-75408 [P09] and by that has introduced safety hazards as the maintenance operative will have to pass through a bund area (constructed to contain spillage from the tank /pipe services) with trip hazards (tank and pump frames) to access the control panel. Additionally, although the afore-mentioned drawing was specifying that the panel fascia will need to be facing the pumps and the 4P 40A pump isolators are to be located on the bunded (wet side), this arrangement would also contribute to the afore-mentioned safety hazard.
| 02SL - Stations (LUL) | Cxxx-NCR-002890 | NCR | MEP - ETH - Level 0 - [Cxxx-FIPC-CFMXX1C, Cxxx-ELEC-ESDEX1C] - Tunnel Fire Mains / CMS proximity and damaged insulation |  | Contr | __ | FAR - Farringdon Station (West) |  | 2019-03-08 | 2019-03-22 09:12 | 14 | 2018-11-21 00:45 | Fire - Fire Systems & General | 2000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Following a Cxxx/CRL site visit at the ETH, it was observed that the tunnel fire-mains' pipe exiting the ETH Level 0 Fire Tank Room (Cxxx--P-DDA-M123_1-25701 [P04], not accepted for construction via FCD, even though the changes were affecting the afore-mentioned area) and the CMS (Cxxx--E-DDA-M123_1-25206 [C04]) did not comply with the minimum spacing requirements set within JY61.3202 d) and JY60.3202 b). Additionally, the CMS installation (that was subsequent to the fire-mains one) has damaged the lagging vapour barrier.
| 02SL - Stations (LUL) | Cxxx-NCR-002891 | NCR | MEP - STW - [Cxxx-ELEC-ESDXX3A] - __ F2 drawings not accepted for construction |  | Contr | __ | FAR - Farringdon Station (West) |  | 2019-01-04 | 2018-12-14 08:59 | -21 | 2018-11-05 15:44 | Electrical - Lighting | 500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | During a Cxxx/CRL joint inspection of the "Lighting Control System (DALI) - Primary Loop & Human Machine Interface" scope of works as part of the INR process for the [Cxxx-ELEC-ESDXX3A] CommLot, it became apparent that the following F2 drawings were not accepted for construction: 1. "Eastern Ticket Hall Lighting Control Schematic" (Cxxx--DWG-M123_Z-53022) 2. "Western Ticket Hall Lighting Control Schematic" (Cxxx--DWG-M123_Z-53023) 3. "Platform Lighting Control Schematic" (Cxxx--DWG-M123_Z-53024)
| 02SL - Stations (LUL) | Cxxx-NCR-002892 | NCR | MEP - PAVA Zone 25 Speaker damaged |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2019-01-18 | 2019-02-26 15:49 | 39 | 2018-11-08 16:44 | Communications and Control Systems - Public Address Systems | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | Three speaker have been damaged in total in Zone 25 in WTH-1, the drawing attached shows the location of the speaker the ID number of the speakers are the following; 1.A11 2.A17 3.A19.
| 02SL - Stations (LUL) | Cxxx-NCR-002893 | NCR | Procurement of radio cable. 750 Meters, |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-11-23 | 2018-12-17 15:19 | 24 | 2018-11-09 09:17 | Communications and Control Systems - Radio | 15000 |  | Material | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Other | Completed |  | Due to damaged radio cables/not meeting 20.8 dB threshold, the ID of the following 7/8 cable is to be replaced; FD3261 FD259 FD3039 FD3056 FD054 FD3008 FD2193 FD3046 FD276 FD2201 FD112 FD138 FD2190 FD2197 FD2190B Cable order number is CELLFLEX 78-50, Part number is LCF78-50JFNA.
| 02SL - Stations (LUL) | Cxxx-NCR-002894 | NCR | MEP - Cxxx - Telephones missing/Damaged |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2019-02-28 | 2019-02-26 15:52 | -2 | 2018-11-09 15:02 | Communications and Control Systems - Telephony | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | External Phenomenon - Theft, tampering, sabotage, or vandalism | Completed |  | NCR is to be raised due to missing/damaged telephones. The model description of the Telephones is LU __ 3905. These are the ID numbers of the following telephones; 30005 30404 30201 10612 30602 10107 30401 30603 30604 30701 30102 10105
| 02SL - Stations (LUL) | Cxxx-NCR-002896 | NCR | TUN-BUI - Bi-metallic isolation has not been installed between dissimilar metals as specified. |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2019-04-01 | 2019-04-26 08:42 | 25 | 2018-11-16 11:24 | Architectural - Signage | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Supervision - Other | Completed |  | A planned surveillance was carried out on Station Signage. The installation of sign type SGN120 on the East and Westbound was inspected and it was found that the stainless steel signage support bracket which is connected to the galvanised PES framework had no Bi Metallic isolation installed separating the two surfaces, preventing the potential for bi-metallic corrosion. This does not meet the requirements of Cxxx Architectural Specification that requires the following: JN15 ‘Signs’ 1401 states; b) “Fixings shall accord with Section JZ20 of the Specification”. Clause JZ20 ‘Fixings’1101 states; h) “Adequate measures shall be taken to prevent bi-metallic corrosion between dissimilar metals”
| 02SL - Stations (LUL) | Cxxx-NCR-002897 | NCR | TUN-BUI - Contractor unable to supply welding compliance records |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2019-04-01 | 2019-08-06 22:19 | 127 | 2018-11-16 11:30 | Architectural - Signage | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | A planned surveillance was carried out on Station Signage. On request the Contractor was unable to supply evidence of __s fabrication competence and manufacture records these being; Weld Procedure Specification (WPS), Welder Qualification Record (WPQR) that forms part of the WPS. Manufacturing records were supplied but deemed as not adequate as weld procedure and welding operative are not defined on check sheets, as such it could not be verified that the welding had been carried to a procedure and the level of competence required. JN15.3102 h) Where welding is required, it shall be by the process known as manual inert gas tungsten-arc welding and it shall be carried out by a procedure in accordance with BS EN ISO 15614: Part 1 and by welders tested in accordance with BS EN 287: Part 1.
| 02SL - Stations (LUL) | Cxxx-NCR-002898 | NCR | TUN-BUI - Pull Testing was completed without evidence of competence. |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2019-04-01 | 2019-04-26 08:51 | 25 | 2018-11-16 11:35 | Architectural - Signage | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | A planned surveillance was carried out on Station Signage. The Contractor was requested to provide evidence of the competency of the operatives that have carried out pull testing on signage connections for __. The Contractor has not been able to provide this evidence, therefor it can not be verified that the testing has been carried out correctly.
| 02SL - Stations (LUL) | Cxxx-NCR-002899 | NCR | Procurement of Radio connectors |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-11-30 | 2018-12-17 15:10 | 17 | 2018-11-16 14:44 | Communications and Control Systems - Radio | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper handling of material | Completed |  | Connectors to complete radio installation are required to be procured. The attachment shows what parts are required along with the quantities.
| 02SL - Stations (LUL) | Cxxx-NCR-002900 | NCR | MEP - FAR-10-11-18-Cxxx Telephone cable termination at data outlet not compliant |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2019-03-04 | 2019-04-15 07:39 | 42 | 2018-11-17 14:30 | Communications and Control Systems | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | On a PRE IRN inspection I look at 4 telephone outlets and found the Cat 6a Cables not terminated as specified in __ installation guide line Cxxx-SMN-R3-GPD-CR001-50025 or to __ installation bulletin SMN-R3-GPD-CR001-50017. Cable foil is not cover up adequately. See attached photos. TEL-FAR-TEL00-08001 (LUA 30005,30001) TEL-FAR-TEL00-08002 (LUA 30102,30104 TEL 10105,10106) TEL FAR-TEL00-08003 (TEL 10402) TEL FAR TEL00-08004 (LUA 30601,30602 RTL 10601,10602,10603,10604,10605,10606,10608)
| 02SL - Stations (LUL) | Cxxx-NCR-002901 | NCR | FAR-10-11-18-Cxxx Radio antenna's connector not protected from dust |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2018-12-10 | 2019-01-28 09:19 | 49 | 2018-11-17 14:42 | Communications and Control Systems - Radio | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | On the EB&WB platforms the directional antennas have been disconnected and most of the connectors have not been protected from dust or moister ingress. The installers have had T__ telling them to protect the connector with tape or dust cap
| 02SL - Stations (LUL) | Cxxx-NCR-002902 | NCR | MEP - ETH - Level -7 - [Cxxx-PUHC-SWPEN1B/C] - Rusting of surface sewage pumps |  | Contr | __ | FAR - Farringdon Station (West) |  | 2019-05-17 | 2019-06-28 14:43 | 42 | 2018-11-21 16:58 | Mechanical - Public Health Engineering | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During SAT Testing activities, __ Site Team have noticed extensive rusting on 2No XYLEM sewage pumps as well as galvanised fittings and pump rails, associated with Pumped Drainage Systems FAR-P-SWS-01 (CRL-MCR-004286) & FAR-P-SWS-03 (CRL-MCR-004285). These systems are located in Level -7 Inverts, and are receiving surface water from station.
| 02SL - Stations (LUL) | Cxxx-NCR-002903 | NCR | MEP - WTH - Level -7 - [Cxxx-PUHC-SWPWN1F] - Incorrect sump pump size installed |  | Contr | __ | FAR - Farringdon Station (West) |  | 2019-01-25 | 2019-02-25 11:35 | 31 | 2018-11-21 01:14 | Mechanical - Public Health Engineering | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | During commissioning activities on the sewage pumping system FAR-P-SWS-04 (CRL-MCR-004285), it was noticed that the design discharge volumes could not be achieved. Following further investigation, it was realised that the pump size was incorrect against the one specified in the design and ordered.
| 02SL - Stations (LUL) | Cxxx-NCR-002904 | NCR | MEP - FAR-17-11-18-Cxxx SCADA 2c fan cable bend radius not compliant in CER1&2 cabs |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2019-05-10 | 2019-06-05 09:56 | 26 | 2018-11-21 09:55 | Communications and Control Systems | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | On a PRE IRN inspection I found 9 cabs in CER1&2 which have the 2c SCADA FAN cable doubled over in the finger trunking; this compromises the bend radius of the cables, one in each cab. Cables will have to be cut back, re-terminated and tested. CER1 cab U3, U4, U5, U8, U9 CER2 Cab U3, U4, U8, U9, U11
| 02SL - Stations (LUL) | Cxxx-NCR-002905 | NCR | FAR-17-11-18-Cxxx DC7 CAT6a modules not locked into patch panel |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2018-12-10 | 2019-01-03 10:30 | 24 | 2018-11-21 10:06 | Communications and Control Systems | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | On PRE IRN inspection I found DC7 CAT 6a module not secured in panel port and cable not secured on patch panel by clamp.
| 02SL - Stations (LUL) | Cxxx-NCR-002906 | NCR | FAR-18-11-18-Cxxx DOO camera and bracket/arm not siting level |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2018-12-10 | 2018-12-19 11:00 | 9 | 2018-11-21 10:19 | Communications and Control Systems - Driver only Operation CCTV | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | DOO cam 5 on the EB. Camera and bracket/arm not sitting level, looks like it may have been hit with a MEWP. See photos.
| 02SL - Stations (LUL) | Cxxx-NCR-002908 | NCR | ETH – Use of P-status drawings for construction of Level -2 riser infill with no FCD in place |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2018-12-14 | 2018-12-05 13:45 | -9 | 2018-11-26 17:49 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | Metal decking and reinforced concrete was installed for the Level -2 riser infill using drawings Cxxx--S-DDD-M123_3-25000 P01, Cxxx--S-DDD-M123_3-25001 P01 and Cxxx--S-DDD-M123_3-25002 P01. All drawings are currently P-status. All drawings were issued to CRL for review and commented on (see Cxxx--C-XCS-M123-51161 Rev 220) prior to construction on site, however an FCD was not raised to allow the use of P-status drawings for construction. The comments on Cxxx--C-XCS-M123-51161 Rev 220 for the 3 drawings had been reviewed and comments have been addressed by . Formal close-out/acceptance from Cxxx outstanding.
| 02SL - Stations (LUL) | Cxxx-NCR-002909 | NCR | STW - PAVA 4 core Fibre cable required |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2019-04-30 | 2019-04-25 15:28 | -5 | 2018-11-26 11:45 | Communications and Control Systems - Public Address Systems | 10000 |  | Incorrect Installation | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | PAVA Fibre Cable didn't follow the designed route.
| 02SL - Stations (LUL) | Cxxx-NCR-002910 | NCR | MEP - Cxxx Radio- __ & __ not carrying out the ITP check sheet for cable installation before terminating cables |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2019-01-25 | 2019-04-04 12:45 | 69 | 2018-11-26 11:45 | Communications and Control Systems - Radio | 500 |  | Planning | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Throughout site, it has been found that the cables have been terminated and tested but had not been dressed or cable tied correctly into the CMS and ITP check sheet for cable install not been done. These tests are non compliant and the installers have to revisit all there work and address the issues we found it will lead to cables having to be re-installed. __ and __ have told , __ and __ that before they terminate any cables they have to confirm that the cables had been installed as to there ITP cable check sheet which they have not done and just run away with the terminating.
| 02SL - Stations (LUL) | Cxxx-NCR-002911 | NCR | TUN-BUI - No evidence of torque values used for signage installation was provided |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2019-02-08 | 2019-02-26 22:56 | 18 | 2018-11-26 14:59 | Architectural - Signage | 3000 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | A planned surveillance was carried out on Station Signage installation. The Contractor was requested to provide evidence of torque values used. ITP ‘Signage Installation’ Cxxx--A-ITP-M123-50026 (Rev 1) inspection number 4.4 states; Fixings to be torqued to the value stated on approved construction drawings. On review the drawing Cxxx--X-DWG-M123-55882 showed no reference to torque values. Architectural Specification Cxxx--A-RSP-M123-50057 (Rev 18) JN15.1416 Fixing; The type, size and positioning of all bolts, anchors, brackets, screws, rivets and nuts shall be shown on the Working Drawings, together with full details of their installation technique and torque settings, where appropriate.
| 02SL - Stations (LUL) | Cxxx-NCR-002913 | NCR | TUN - BUI - No __s Drawing Showing Connection Detail Between PES and Projecting Signage |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2019-04-04 | 2019-08-23 14:49 | 141 | 2018-12-11 16:33 | Architectural - Signage | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | On a signage surveillance on the 15/11/18, it was found there was no drawing detailing the connection between the PES structure and the projecting signs for the PES. The connection has been shown on a drawing by (e.g. Cxxx--X-DWG-M123_7-51053), however there is no __s drawing showing the connection in a similar manner. The details are shown in design calculations however is not sufficient to provide information for installation. This lack of drawing is linked to the following NCRs: - Cxxx-NCR-002896 and Cxxx-NCR-002911
| 02SL - Stations (LUL) | Cxxx-NCR-002914 | NCR | MEP - WTH - [Cxxx-ELEC-ESDWX1] - Pin racks not installed in WTH LVU Riser CMS |  | Contr | __ | FAR - Farringdon Station (West) |  | 2019-03-29 | 2019-04-17 09:58 | 19 | 2019-02-22 22:22 | Electrical - Cable Management | 1500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | CRL/__ have raised [CRL-OBS-25645], as pin racks have not been installed within the WTH LVU Riser CMS, despite cabling being already installed.
| 02SL - Stations (LUL) | Cxxx-NCR-002915 | NCR | MEP - STW - [Cxxx-ELEC-ESD] - Final Circuit IRN scope not offered for handover in Emergency Escape Stairs and Cxxx areas |  | Contr | __ | FAR - Farringdon Station (West) |  | 2019-04-05 | 2019-04-11 14:55 | 6 | 2018-12-03 15:55 | Electrical - Lighting | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | CR/__ have reported to __ that following their review on the currently handed-over Final Circuit Electrical Work Packages (Cxxx-ELEC-ESD*X2*), it appears to them that there are various areas that were omitted from their scope (mostly the ETH&WTH emergency escape stairs but other Cxxx areas have also been excluded). CR/__ noted to __ that the lighting and small power installation has neither been offered for inspection at any point nor have they been included in any outstanding works lists, thus introducing an assurance gap in on the electrical systems in these areas.
| 02SL - Stations (LUL) | Cxxx-NCR-002916 | NCR | MEP - WTH - Level -1 - [Cxxx-ELEC-ESDWX2D] - Insufficient support of Public Toilet and Staff Locker Room luminaires |  | Contr | __ | FAR - Farringdon Station (West) |  | 2019-08-23 | 2019-08-23 09:48 | 0 | 2018-12-03 16:17 | Electrical - Lighting | 6000 |  | Supervision/Management | Repair | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | Following a site inspection, CRL/__ have notified __ that the WTH Level -1 Public Toilet and Staff Locker Room (SLR-1) luminaries fixings do comply with the CRL M&W specification JV21.3202 of document (Cxxx--E-RSP-M123-50002 [4.0] "Electrical Particular and M&W Specifications"). Specifically, the luminaires are currently supported by the ceiling, using a secondary safety chain fixed to the conduits above, without prior CRL acceptance.
| 02SL - Stations (LUL) | Cxxx-NCR-002917 | NCR | MEP - WTH - Level -1 - [Cxxx-MECC-HCVWE1B, Cxxx-ELEC-ESDWX2D] - Air release top fan removal clash with conduit |  | Contr | __ | FAR - Farringdon Station (West) |  | 2019-03-22 | 2019-05-13 12:55 | 52 | 2019-02-22 22:54 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | Conduit installation, that has occurred post the installation of the WTH Air Release Fans (Cxxx--M-DDA-M123_2-75211), has been implemented in such a manner that is currently blocking the removal of the top fan.
| 02SL - Stations (LUL) | Cxxx-NCR-002918 | NCR | WTH - Metal Deck Slabs – Missing Cube Results Level +1 Upper mezzanine |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2019-01-11 | 2018-12-21 12:13 | -21 | 2018-12-08 09:20 | Civil - Civil Engineering General | 2000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | On the 27/06/2016 part of the level +1 Upper mezzanine slab was poured with no cubes taken or cube results available. The pour was aborted after 16m3 of concrete was poured due to vehicle compliance issues. Temporary stop-ends were put in due to the abortive pour. See attached highlighted location sketch of the pour area. Please note that this NCR is similar to Cxxx-NCR-002762, Cxxx-NCR-002766, Cxxx-NCR-002808 and Cxxx-NCR-002861.
| 02SL - Stations (LUL) | Cxxx-NCR-002919 | NCR | MEP - Misplaced projection speaker - Cell20 - RAL9006 Grey |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2019-02-05 | 2019-02-25 11:03 | 20 | 2018-12-06 12:27 | Communications and Control Systems - Public Address Systems | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | A projection speaker has been misplaced. Cell20 - RAL9006 Grey.
| 02SL - Stations (LUL) | Cxxx-NCR-002920 | NCR | WTH – Upper Apse – Missing Cube Results for PCC Units |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2019-01-11 | 2019-01-18 15:27 | 7 | 2018-12-12 15:06 | Architectural - Finishes | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper storage of material | Completed |  | __ Upper Apse fabrication ITP ‘WTH Precast Apse Ceiling – __ Factory’ Cxxx--C-ITP-M123-50256 Rev4.0 Item 12.13 states that cube results are required for each PCC unit at 28 days to achieve 50N/mm². __ are unable to provide 28 day concrete cube results for the following beams: 16/09/16 – EB9 29/10/16 – EB14 & PB25 There are also various 56 day cube results missing – but these are not a requirement in the ITP item 12.13. All missing cube results are shown in Red on the attached – “Prod Quality Log D1 20 Upper Apse” There are some instances where checksheets have not been provided by __ – shown in orange on the attached – “Prod Quality Log D1 20 Upper Apse”. However in each of these cases, the result is verified by either another 28 day or 56 day result.
| 02SL - Stations (LUL) | Cxxx-NCR-002921 | NCR | STW- Surespan Access Hatches -Starting works without all the required documentation in place. |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2020-05-29 | 2020-12-03 12:35 | 188 | 2018-12-12 19:12 | Architectural - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Other | Completed |  | STW Surespan Access Hatches package has started fabrication/installation without all the required documentation in place. Non exhaustive list of outstanding approved documents: 1. Approved ITP fabrication 2. Welding qualification/procedure document. 3. Fire report assessments for some of the Access Hatches 4. Drawings with P status 5. Material Compliance Records and technical documents for electrical components.
| 02SL - Stations (LUL) | Cxxx-NCR-002922 | NCR | MEP - Procurement of LCF 1/2 Inch cable |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2019-01-25 | 2019-02-07 13:14 | 13 | 2018-12-13 14:10 | Communications and Control Systems - Radio | 6000 |  | Damaged | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | 1500 meters of 1/2 inch radio cable is required for various reasons, cable length too short, cable damage (see attached spreadsheet).
| 02SL - Stations (LUL) | Cxxx-NCR-002923 | NCR | MEP - No __ Assurance Documentation for Smoke Control System Works - Cxxx-PCC-008 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2019-02-21 | 2019-02-25 11:24 | 4 | 2018-12-20 10:13 | Mechanical - Mechanical Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Following discussions between , __ and Crossrail, it is apparent that no assurance documentation for the PLC smoke control system for the Pressurisation System of the ETH has been made available at the PCC stage, despite previous assurances at the 2.1 IRN stage. These records should have been provided to a similar standard as an IRN. It is a contractual requirement that the Contractor is to undertake progressive assurance of the works, however the site teams cannot provide records for this system at the PCC stage. This NCR covers Cxxx-PCC-008 (Cxxx--M-CER-M123-50053)
| 02SL - Stations (LUL) | Cxxx-NCR-002924 | NCR | ETH - __ Access hatches Level -6 installed higher than specified. |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2019-03-29 | 2019-02-26 22:15 | -31 | 2018-12-19 15:41 | Architectural - Flooring | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | has conducted an as-built survey of Level -6 __ Hatches. has identified a few areas which are outside the required tolerances of +/-3mm specified on ITP. Please refer to attached as-built survey.
| 02SL - Stations (LUL) | Cxxx-NCR-002925 | NCR | MEP - No __ Assurance Documentation for Smoke Control System Works - Cxxx-PCC-009 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2019-02-21 | 2019-02-25 11:25 | 4 | 2018-12-20 10:33 | Mechanical - Mechanical Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Following discussions between , __ and Crossrail, it is apparent that no assurance documentation for the PLC smoke control system for the Air Release System of the ETH has been made available at the PCC stage, despite previous assurances at the 2.1 IRN stage. These records should have been provided to a similar standard as an IRN. It is a contractual requirement that the Contractor is to undertake progressive assurance of the works, however the site teams cannot provide records for this system at the PCC stage. This NCR covers Cxxx-PCC-009 (Cxxx--M-CER-M123-50054)
| 02SL - Stations (LUL) | Cxxx-NCR-002926 | NCR | MEP - No __ Assurance Documentation for Smoke Control System Works - Cxxx-PCC-010 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2019-02-21 | 2019-02-25 11:27 | 4 | 2018-12-20 10:35 | Mechanical - Mechanical Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Following discussions between , __ and Crossrail, it is apparent that no assurance documentation for the PLC smoke control system for the Pressurisation System of the WTH has been made available at the PCC stage, despite previous assurances at the 2.1 IRN stage. These records should have been provided to a similar standard as an IRN. It is a contractual requirement that the Contractor is to undertake progressive assurance of the works, however the site teams cannot provide records for this system at the PCC stage. This NCR covers Cxxx-PCC-010 (Cxxx--M-CER-M123-50055)
| 02SL - Stations (LUL) | Cxxx-NCR-002927 | NCR | MEP - No __ Assurance Documentation for Smoke Control System Works - Cxxx-PCC-011 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2019-02-21 | 2019-02-25 15:36 | 4 | 2018-12-20 10:37 | Mechanical - Mechanical Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Following discussions between , __ and Crossrail, it is apparent that no assurance documentation for the PLC smoke control system for the Air Release System of the WTH has been made available at the PCC stage, despite previous assurances at the 2.1 IRN stage. These records should have been provided to a similar standard as an IRN. It is a contractual requirement that the Contractor is to undertake progressive assurance of the works, however the site teams cannot provide records for this system at the PCC stage. This NCR covers Cxxx-PCC-011 (Cxxx--M-CER-M123-50056)
| 02SL - Stations (LUL) | Cxxx-NCR-002928 | NCR | MEP - No __ Assurance Documentation for Smoke Control System Works - Cxxx-PCC-014 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2019-02-21 | 2019-02-25 15:19 | 4 | 2018-12-20 10:41 | Mechanical - Mechanical Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Following discussions between , __ and Crossrail, it is apparent that no assurance documentation for the PLC smoke control system for the Platform Smoke Extract System of the ETH has been made available at the PCC stage, despite previous assurances at the 2.1 IRN stage. These records should have been provided to a similar standard as an IRN. It is a contractual requirement that the Contractor is to undertake progressive assurance of the works, however the site teams cannot provide records for this system at the PCC stage. This NCR covers Cxxx-PCC-014 (Cxxx--M-CER-M123-50059)
| 02SL - Stations (LUL) | Cxxx-NCR-002929 | NCR | MEP - No __ Assurance Documentation for Smoke Control System Works - Cxxx-PCC-017 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2019-02-21 | 2019-02-25 15:27 | 4 | 2018-12-20 10:43 | Mechanical - Mechanical Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Following discussions between , __ and Crossrail, it is apparent that no assurance documentation for the PLC smoke control system for the Platform Smoke Extract System of the WTH has been made available at the PCC stage, despite previous assurances at the 2.1 IRN stage. These records should have been provided to a similar standard as an IRN. It is a contractual requirement that the Contractor is to undertake progressive assurance of the works, however the site teams cannot provide records for this system at the PCC stage. This NCR covers Cxxx-PCC-017 (Cxxx--M-CER-M123-50062)
| 02SL - Stations (LUL) | Cxxx-NCR-002930 | NCR | MEP - ETH - [Cxxx-ELEC-ESDEX2C, Cxxx-FIPC-FADEX1A, PAV-FAR-PAV00-06024, CTV-FAR-CTV00-02002] - Installation of services within the Barbican Link PRM Lobby Area |  | Contr | __ | FAR - Farringdon Station (West) |  | 2019-03-29 | 2019-11-29 11:28 | 245 | 2019-01-04 12:43 | Fire - Detection | 20000 |  | Design | Rework | 2 (6-60k) | Complete | Design Problem - Other | Completed |  | The ETH Level -1 Barbican link PRM Lobby CON-P 6 (2-ATK-E025) is considered a public area. Following a CRL/Cxxx site visit, it has been observed by CRL/FE that below MEP services in this area have been installed in a manner that makes them easily accessible, thus prone to safety and vandalism risk from the public: 1. __ Fire alarm panel control controls; 2. Fire Alarm I/O panels and junction boxes; 3. LV power junction boxes; 4. Luminaire plug & sockets; 5. PA/VA Speakers; 6. CCTV Cameras. Furthermore, the CRL/FE observed that the CMS arrangement within this area could potentially introduce a security risk, as it creates areas where items can be placed out of sight.
| 02SL - Stations (LUL) | Cxxx-NCR-002931 | NCR | MEP - WTH - [Cxxx-MECC-BMSXN1A, Cxxx-ELEC-ESDXX1A, Cxxx-FIPC-FADXX1A] - SOR MEP works |  | Contr | __ | FAR - Farringdon Station (West) |  | 2019-03-29 | 2019-05-01 08:47 | 33 | 2019-01-04 14:59 | Electrical - Electrical Engineering General | 3000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Installation MEP works (related to BMS, DALI, Fire Alarms and Detection and associated CMS, associated Comms) to the Farringdon LU SOR have progressed without a formally accepted design and associated assurance records have not been submitted in accordance with the IRN process.
| 02SL - Stations (LUL) | Cxxx-NCR-002934 | NCR | MEP - Cxxx - Horn Speakers to be Replaced for Zones 26 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2019-07-26 | 2019-07-30 07:52 | 4 | 2019-03-18 09:42 | Communications and Control Systems - Public Address Systems | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | The following Horn Speakers have been damaged and potentially need replacing. Listed below: Zone 26 (Horn Speakers) A53,A57,B58,B48 and B44. Please see attached drawing for location. Note that these speakers have already been handed over as part of IRNs and therefore an assessment of whether they need replacing needs to be made by the Field Engineer. It is understood that they will be replaced.
| 02SL - Stations (LUL) | Cxxx-NCR-002935 | NCR | MEP - Cxxx - Requirement for Reissue of Radio Cable Asset Labels |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2019-03-25 | 2019-05-08 14:13 | 44 | 2019-01-28 11:37 | Communications and Control Systems - Radio | 500 |  | Planning | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Following an internal surveillance on the identification of Asset Tag labels for Cxxx, it has been identified that the following two situations have occurred: 1) There have been design changes to the Radio design subsequent to the issuing of the Radio cable asset tags to and hence these labels need to be issued. The cost of checking against all the schedules against the already issued asset tags will constitute tens of man hours, far exceeding the cost of the labels themselves. 2) In one location, Western Ticket Hall Level -5, the associated asset tags can no longer be located and are therefore presumed missing. therefore require the reissuing of asset tags by __ for the Cxxx radio cables.
| 02SL - Stations (LUL) | Cxxx-NCR-002936 | NCR | MEP - WTH - Level -1 - [Cxxx-ELEC-ESDWX2D] - Clashing of CMS with false ceiling access hatches within the Public Toilets |  | Contr | __ | FAR - Farringdon Station (West) |  | 2019-07-12 | 2019-08-23 09:52 | 42 | 2019-02-25 14:39 | Electrical - Lighting | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Following a CRL/__ inspection at WTH Level -1 Public Toilets, __ were notified that an access hatch in the female toilets section is restricted by cable tray (Cxxx) and conduit. CRL/__ have raised CRL-OBS-26390.
| 02SL - Stations (LUL) | Cxxx-NCR-002937 | NCR | MEP - STW - [Cxxx-MECC-HCVWE2, Cxxx-MECC-HCVEE2] - Incorrect installation of the Smoke Control fans vibration pads |  | Contr | __ | FAR - Farringdon Station (West) |  | 2019-03-15 | 2019-05-15 06:55 | 61 | 2019-02-25 23:29 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | During a Cxxx/CRL joint inspection on the ETH UMC fan motor replacement, the Flakt-Woods technician observed that the OPE ISL Fan Anti-Vibration mounts have not been installed in line with the manufacturers recommendations. Specifically, the anti-vibrations mounts are off-centre against the rubber anti-vibration, thus resulting in them touching the outer metal casting. The Flakt-Woods technician confirmed that this would result in early failure and would be captured at the start of a standard maintenance inspection.
| 02SL - Stations (LUL) | Cxxx-NCR-002938 | NCR | FAR-21-12-18-Cxxx radio cables ETH-2 have to much tension on the cable and cable exceeds 500mm unsupported |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2019-04-26 | 2019-05-01 13:20 | 5 | 2019-01-30 15:02 | Communications and Control Systems - Radio | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Level -2 plant rooms Drawing Cxxx-SMN-R3-DDA-M123_3-90006 and 3-90012. Bend radius to small and is twisting the connections to the splitters. Both 7/8” cables exceed the 500mm unsupported rule. Both cables need to be re-installed and terminated 2m to the left of the exiting position and not over the LV cables as they are at the moment. Cables to be were cut back and re-terminated are FD3193, 3216, 214 & 338. Cables to be replaced are FD3216 & FD214 approx 2M
| 02SL - Stations (LUL) | Cxxx-NCR-002939 | NCR | FAR-18-01-19-Cxxx SCADA Cables bend radius not being achieved |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2019-03-04 | 2019-04-17 07:01 | 44 | 2019-01-30 15:21 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Partial IRN. __-FAR-__00-10005 Escalator 4-11 SCADA Cables bend radius not being achieved and CMS incomplete, no end caps on trunking and fire stopping compound used as end cap. CMS to be completed and re-worked to achieve the bend radius of the cables, this will mean the cable will need to be pulled back to problem area.
| 02SL - Stations (LUL) | Cxxx-NCR-002940 | NCR | MEP - STW - [Cxxx-ELEC-ESDx2] - __ luminaire LED module failures |  | Contr | __ | FAR - Farringdon Station (West) |  | 2019-08-16 | 2019-08-21 08:45 | 5 | 2019-03-20 00:21 | Electrical - Lighting | 1500 |  | Material | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | CRL/__ notified __ that they have observed LED module failures within the __ Luminaires in a few areas of the station, as below (see also attachment): - ETH Emergency Escape stairs L-3/-4 - WTH L-6 WB platform Emergency escape Corridor - ETH emergency stairs - ETH L+1 Plant Room CRL/__ noted that although the failures are not high in numbers, similar failures have been reported at other CRL sites, thus there is concern that there might be a material issue. CRL/__ requested __ to raise an NCR, in order to formally engage the manufacturer (__) to investigate further in order to plan potential appropriate actions.
| 02SL - Stations (LUL) | Cxxx-NCR-002941 | NCR | MEP - ETH - Level 0 - [Cxxx-ELEC-ESDEX1C, Cxxx-FIPC-FADEX1] - Fire Alarm conduit incorrect installation |  | Contr | __ | FAR - Farringdon Station (West) |  | 2019-04-29 | 2019-08-09 08:23 | 102 | 2019-04-08 20:32 | Fire - Detection | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During a CRL/__ site visit, the following issues were noted on the Fire Alarm conduit installation, that were not deemed acceptable: 1. ETH Level 0 Fire tank room – Conduit kinked/damaged (L29D29) - refer to attached photos 1 & 2; 2. ETH Level 0 end of corridor CIR-S2B outside maintenance access hatch room - unnecessarily buried conduits (L29D24-L29D09) - refer to photos 3 & 4.
| 02SL - Stations (LUL) | Cxxx-NCR-002942 | NCR | WTH - Damages / Defects to Blockwork |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2019-03-29 | 2019-03-28 10:50 | -1 | 2019-02-20 11:28 | Architectural - Brickworks/Blockworks | 3000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | 1. WTH SH-W2 L-6 FOSC2 & Cleaners Room - Damages to door frame (See attached pdf drawing with photos - L-6 Cleaners Room damages) 2. WTH L+2 Chiller Area - Damage to southern perimeter wall due to scaffold tie (See attached pdf drawing with photos - L2 Chiller Area damages)
| 02SL - Stations (LUL) | Cxxx-NCR-002943 | NCR | STW - No Sleeve Protrusion for Penetrations in Staircases |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2019-05-31 | 2019-06-28 15:20 | 28 | 2019-02-05 10:09 | Civil - Civil Engineering General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | A number of Radio Cables within the main staircases at the ETH and WTH pass through each landing by the means of cored penetrations in the concrete. These penetrations do not have a sleeve and therefore do not comply to the Works Information. Please see attached picture of the installation on site.
| 02SL - Stations (LUL) | Cxxx-NCR-002944 | NCR | MEP - WTH - [Cxxx-FIPC-FISWW1A] - Non Compliance of the Low Pressure Water Tank Float Valve arrangement |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2019-09-27 | 2019-09-17 15:54 | -10 | 2019-02-26 16:31 | Fire - Fire Systems & General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | CRL/__ and CEG have raised concerns over the current design of the Low Pressure Water Tank and specifically that: 1. It has a reduced capacity / storage and is relaying on the infill towns main; 2. At present, the installed tank does not comply with associated VdS standard, section 8.3.4.a, in that it has one float valve instead of two. 3. The requirement for 2 float valves is to ensure system availability, when float valve is removed for maintenance, as this would have to otherwise be executed during engineering hours should only one float is provided.
| 02SL - Stations (LUL) | Cxxx-NCR-002945 | NCR | STW - MEP & WTH - WTH Public Toilets Cxxx-PMI-00085 Requirements Not Followed by Cxxx |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2019-10-18 | 2019-10-16 11:02 | -2 | 2019-02-12 16:45 | Architectural - Sanitary Fittings | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | It has been found that the toilet area WTH Front of House Level -1 has not been fully coordinated with the relevant parties to ensure their buy in. This was stipulated in Cxxx-PMI-00085 which states: - " The Contractor shall develop the design to the Project Manager’s approval and take the design through the appropriate assurance process. Please note particular liaison will be required with London Underground, the Transport Police and the Employer’s security advisor to ensure the final layout is acceptable and conforms to all relevant interface requirements. Please also bear in mind that LBI as the local authority has shown a keen interest in this improvement to the services provided in the Station and would wish to receive regular updates on progress, through the routine meetings. " have failed to properly coordinate the design and documentation in this area. As a result, this has caused the following issues to be recognised: - 1) Issues surrounding Access and Maintenance - e.g. changing light fittings had not been considered 2) Design coordination has not been completed - e.g. the wall construction type and the sensors specified are incompatible 3) There is a lack of clarity as to the responsible party for this area of work between different parties in and this led to the item being a gap in each team's scope 4) There is currently no Material Compliance Record Assurance Documentation provided to Crossrail for the installation of sanitarywear
| 02SL - Stations (LUL) | Cxxx-NCR-002946 | NCR | Damaged radio cable FD160 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2019-03-15 | 2019-04-08 10:56 | 24 | 2019-02-12 16:30 | Communications and Control Systems - Radio | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Please see attached images which shows the damaged radio cables FD160 in the westbound inverts. The cable has been damaged as a subsequent consequence from another activity.
| 02SL - Stations (LUL) | Cxxx-NCR-002947 | NCR | Lost and damaged radio assets |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2019-02-26 | 2019-03-20 15:18 | 22 | 2019-02-12 16:45 | Communications and Control Systems - Radio | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Multiple items have been damaged or lost.
| 02SL - Stations (LUL) | Cxxx-NCR-002948 | NCR | PAVA - Z15 Column |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2019-08-30 | 2019-05-08 08:44 | -114 | 2019-02-14 17:02 | Communications and Control Systems - Public Address Systems | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | PAVA Z15 Column speakers which sit in the architectural steal panelling should have perforated cover panels in front of them and not solid panels as shown in the photos.
| 02SL - Stations (LUL) | Cxxx-NCR-002949 | NCR | WTH - Missing earthing points for OSD at level 0 in Wall 50 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2019-04-12 | 2019-04-12 15:19 | 0 | 2019-02-25 13:48 | Systems - Earthing and Bonding | 5000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Mark-ups of drawings Cxxx--E-DDD-M123_Z-75711 C01 and Cxxx--E-DDD-M123_Z-75102 C01 show 2no. earthing points at level 0 in Wall 50; these are for the OSD. The earthing points and electrically continuous rebar within the concrete were not installed.
| 02SL - Stations (LUL) | Cxxx-NCR-002950 | NCR | PAVA Zone 27 speakers - Damaged |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2019-03-20 | 2019-03-08 14:40 | -12 | 2019-02-18 17:41 | Communications and Control Systems - Public Address Systems | 0 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | The attached document shows the list of damaged horn speakers that may require replacing. The attachment shows which speaker is damaged along with the speaker number.
| 02SL - Stations (LUL) | Cxxx-NCR-002951 | NCR | ETH- Misalignment between vertical axis of infillstrip GFRC panels and axis of __ panels |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2019-07-31 | 2019-03-12 21:29 | -141 | 2019-02-20 15:00 | Architectural - General | 5000 |  | Design | Rework | 3 (3-6k) | Complete | Subcontractor Problems - Interfacing problems | Completed |  | Marked up ETH level -3 areas highlighted in the attached drawings present a misalignment between vertical axis of infillstrip GFRC panels installed by __ and the axis of __ panels located above. Attached photos show the area and detail of the misalignment.
| 02SL - Stations (LUL) | Cxxx-NCR-002952 | NCR | ETH - L-7 Firestopping to be Removed for Access to Cable Ducts |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2019-09-13 | 2019-09-20 13:25 | 7 | 2019-03-05 11:39 | Architectural - Walls | 6000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | As per appended architectural GA (Cxxx--A-DDA-M123_8-26221 Rev P22) and elevation (Cxxx--A-DDC-M123_8-26271 Rev P11 Elevation 3), firestopping was installed around MEP services in the cavity blockwork wall. This opening was firestopped following the issue of a Permit to Seal by the MEP team (attached – E70301). However, it has been requested to remove the firestopping in order to maintain access to the cable ducts behind. Each individual cable duct has been firestopped as per detail Cxxx--X-DWG-M123-54672 Rev C03 as shown in attached photograph. In order to maintain the fire compartmentation requirements, propose to firestop the cavity between the blockwork and reinforced concrete walls as per appended sketch ’01-03-19 - SKT-003.pdf.’ Following rework of NCR, please see comments below to address queries: Photos attached to show penetration on site clearly showing that the firestopping is carried out to the underside of the soffit - hence, a three-sided firestopping is required. Please refer to mark-up sketch detailing the construction process for the rework (22-05-19-SKT-001) and Photo Report L-7 Firestopping. This solution was developed on-site with the specialist subcontractor (__), package manager (--), design manager (--) and Cxxx __ fire engineer (--).
| 02SL - Stations (LUL) | Cxxx-NCR-002953 | NCR | MEP - ETH - Level -3 - [Cxxx-ELEC-ESDEX2F] - Insufficient lighting levels in front of Lift Lobby PR9 |  | Contr | __ | FAR - Farringdon Station (West) |  | 2019-08-31 | 2019-07-16 13:57 | -46 | 2019-04-08 21:18 | Electrical - Lighting | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | have notified __ that, following relevant LUX readings additional lighting is required in Lift Lobby ETH Level-3 PR9 - refer to e-mail attached. requested __ to raise NCR, in order to address this non-compliance.
| 02SL - Stations (LUL) | Cxxx-NCR-002954 | NCR | MEP - WTH Low Pressure Water Mist System - Installation Incomplete |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2019-05-31 | 2019-09-06 13:00 | 98 | 2019-02-22 12:20 | Mechanical - Mechanical Engineering General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | In accordance with Cxxx-PMI-00866, a water mist system should be installed for a number of rooms, including WTH Level -7 NR Store Room; room 8/410. This has been detailed on the site fire plan: Cxxx--A-DDA-M123_8-75027. It has been identified recently that the existing MEP design for these works does not include room 8/410 in the Watermist design. This NCR has been raised to capture the incomplete works on this system.
| 02SL - Stations (LUL) | Cxxx-NCR-002955 | NCR | MEP - ETH - Level -5 - [Cxxx-ELEC-ESDEX1K] - Minimum spare capacity no provided within LVA Switchboard |  | Contr | __ | FAR - Farringdon Station (West) |  | 2019-06-28 | 2019-07-23 17:12 | 25 | 2019-05-14 21:44 | Electrical - Power Distribution | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | CRL/__ notified __ that the latest revisions of the ETH LV-A switchboard GA (Cxxx--E-DWG-M123_6-53004 [C03]) indicate that the 1 x 400A spare frame capacity is not provided, as required by JY71.1301 M&W specification. CRL/__ noted that the minimum spare frame capacity requirements are: 1 x 400A 2 x 250A 4 x 125A while the ETH LVA switchboard only provides: 3 x 250A 4 x 125A CRL/__ requested __ to raise a NCR in order to investigate this further.
| 02SL - Stations (LUL) | Cxxx-NCR-002956 | NCR | MEP - ETH - Level 0 - [Cxxx-ELEC-ESDEX2C] - Insufficient lighting within E/B ventilation adit |  | Contr | __ | FAR - Farringdon Station (West) |  | 2019-08-02 | 2019-10-21 15:22 | 80 | 2019-05-14 22:00 | Electrical - Lighting | 5000 |  | Design | Repair | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | CRL/__ have notified __ that the lighting provided in the Eastbound ventilation adit (refer to ETH Level 0 lighting layout, Cxxx--E-DDA-M123_1-25305 [C03] & Cxxx--E-XCL-M123-50001 (p71) ETH Lighting Calculations) has not taken into account the whole room space, subsequently, the lighting levels are not deemed sufficient to enable maintenance / inspection (a 3 monthly activity) of the dampers / actuators in the room. CRL/__ noted that they have completed a quick review of other Cxxx spaces and lighting appears to have been properly provided, so according to CRL/__, this case appears to be an oversight. CRL/__ requested __ to raise a NCR, in order to investigate this further.
| 02SL - Stations (LUL) | Cxxx-NCR-002957 | NCR | Damaged CAT 6 Cable |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2019-03-08 | 2019-03-20 14:14 | 12 | 2019-02-22 16:01 | Communications and Control Systems | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Installed CAT 6 cables found to be damaged for the following; 1. PAM 2. CIS Screen (WTH and PLT) 3. CCTV - 160 4 2 x PHPs We require 1500meter of CAT 6 cable to complete the installation at Farringdon.
| 02SL - Stations (LUL) | Cxxx-NCR-002958 | NCR | Damaged 2 core 1.0 mm SCADA cable |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2019-03-08 | 2019-03-27 15:01 | 19 | 2019-02-22 16:09 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | • Cxxx design cable lengths do not accurately reflect the installed lengths • Previously installed cables damaged and re-installed • Changes to the doors have meant re-location of Junction boxes and there for a rewire required
| 02SL - Stations (LUL) | Cxxx-NCR-002960 | NCR | MEP - ETH - Level 0 - [Cxxx-ELEC-ESDEX1C] - Protective devices of DB/E/49 & DB/E/50 not coordinated with C690 design |  | Contr | __ | FAR - Farringdon Station (West) |  | 2019-06-14 | 2019-07-15 09:12 | 31 | 2019-05-07 21:25 | Electrical - Power Distribution | 1000 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | CRL/__ inspection have notified __ that it has become apparent to them that the design and installation of protective devices in ETH Level 0 DB49 & DB50 have not been fully coordinated with the C690 design requirements. Relevant DB schedule Cxxx--E-TSC-M123-50015 [14.0], does not align with the requirements of C690 power supply schematic, C690-XRL-M-DWG-M123-50002 [4.0]. The C690 design requires type B RCBOs on individual circuits. The Cxxx design requires that either type C RCBOs or type C type C __/RCDs are used on individual circuits. Multiple circuits are protected by a single RCD though. Furthermore the installed device protection current ratings do not match either the Cxxx design or the C690 design. CRL/__ also note that an update of the C690 power supply schematic, C690-XRL-M-DWG-M123-50002 [7.0] (referenced within), will be issued shortly and the installation will need to consider this updated design, therefore close coordination with C690 will be required to ensure their requirements are met in the updated Cxxx design.
| 02SL - Stations (LUL) | Cxxx-NCR-002961 | NCR | ETH - Access hatch 3-EFH08 Orientation |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2019-03-25 | 2019-03-25 11:49 | 0 | 2019-03-11 12:44 | Architectural - Flooring | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Due to site condition EJCO installed Access hatch 3-EFH08 in an orientation 90 degrees different to the specified design (See attached Mark-up). This was done to mitigate potential clash with service pipes as the hatch was opened.(See attached photo). In the current installed position of the hatch it no longer clashes with any services and the lid can fully open to enable the arms to be engaged. __ have confirmed the new orientation is acceptable (See attached __ RFI response). The anchor points would need to been reposition to accommodate the new orientation (Cxxx-FCD-003594)
| 02SL - Stations (LUL) | Cxxx-NCR-002962 | NCR | ETH- No Approved MCR for Sliding Gate Rails and Hangars Replacement |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2019-06-28 | 2019-04-30 10:24 | -59 | 2019-02-26 15:08 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | start work on replacing ETH sliding gate rails and hangars without an approved MCR in place. This is because of the pressure to start work due to programmed, as discussed with Crossrail. Propose to submit MCR and close out this NCR.
| 02SL - Stations (LUL) | Cxxx-NCR-002963 | NCR | Comms - STW - [__-FAR-__00-10016] - Cat6A Cable "M123-DAT-02570" exceeds maximum length |  | Contr | __ | FAR - Farringdon Station (West) |  | 2019-03-29 | 2019-04-17 16:16 | 19 | 2019-03-05 12:47 | Communications and Control Systems - SCADA/Central Management System | 0 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | During testing, it was determined that the Cat6A cable "M123-DAT-02570" (CommLot: __-FAR-__00-10016) actual overall length is 106.9 m, thus exceeding the maximum allowable length of the relevant specification.
| 02SL - Stations (LUL) | Cxxx-NCR-002964 | NCR | MEP - STW - [Cxxx-FIPC-FAD] - Removal of detection equipment prior to design approval |  | Contr | __ | FAR - Farringdon Station (West) |  | 2019-07-26 | 2019-10-25 14:45 | 91 | 2019-05-07 21:57 | Fire - Detection | 500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | __ Tier-3 S/C Global Fire & Security have removed fire detection assets prior to acquiring approval via the PTR/FCD process, in areas included within below drawings: Loop Drawings: Cxxx--E-DWG-M123_1-53032 P05 Cxxx--E-DWG-M123_1-53030 P05 Cxxx--E-DWG-M123_2-53027 P04 Cxxx--E-DWG-M123_2-53028 P03 Cxxx--E-DWG-M123_B-53013 P04 Damper Drawings: Cxxx--E-DWG-M123_1-53029 P01 Cxxx--E-DWG-M123_1-53110 P01 Cxxx--E-DWG-M123_2-53023 P04 Cxxx--E-DWG-M123_1-53022 P03 Cxxx--E-DWG-M123_1-53013 P01
| 02SL - Stations (LUL) | Cxxx-NCR-002965 | NCR | Comms - WTH Level-1 - [CAB-FAR-MISCO-11001] - Unprotected power cables and drilling of DC5 cabinet |  | Contr | __ | FAR - Farringdon Station (West) |  | 2019-06-14 | 2019-06-21 15:21 | 7 | 2019-03-08 21:42 | Communications and Control Systems | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | CRL/FE have notified __ of below non-compliances: 1. DC5 power single cables are exposed in cabinet and need protecting or replacing with electrical flex. 2. DC5 cabinet has been drilled in the side panel for the power, thus compromising the IP rating - reoccurrence (refer to Cxxx-NCR-002738). CRL/FE raised CRL-OBS-26684 and requested from __ to raise NCR accordingly.
| 02SL - Stations (LUL) | Cxxx-NCR-002966 | NCR | MEP - STW - [Cxxx-ELEC-CMSXX10] - Use of __ HIT-HY 270-A anchor without provision of support calculations |  | Contr | __ | FAR - Farringdon Station (West) |  | 2020-05-29 | 2020-11-05 14:42 | 160 | 2019-03-09 10:49 | Electrical - Cable Management | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | During certification checks in the electrical work packages, it has become apparent that the __ HIT-HY 200-A anchor has been mistakenly declared within the document "Cxxx MEP – Phase 2.1 – Support System Calculations" (Document Number: Cxxx--O-XCL-M123-50002) as been used for certain CMS applications, while it has been confirmed with __ Site Team that the __ HIT-HY 200-A anchor has been used instead. The support calculations for the __ HIT-HY 270 anchor have not been included within the afore-mentioned document.
| 02SL - Stations (LUL) | Cxxx-NCR-002967 | NCR | MEP - WTH Level -1 [Cxxx-ELEC-ESDWX2D] - Access & Maintenance of Public Toilets electrical assets within false ceiling |  | Contr | __ | FAR - Farringdon Station (West) |  | 2019-09-13 | 2019-09-17 11:19 | 4 | 2019-04-30 23:27 | Electrical - Lighting | 10000 |  | Design | Use As-Is | 2 (6-60k) | Complete | Design Problem - Other | Completed |  | CRL have notified __ that they consider current access & maintenance arrangements of the electrical assets located within the WTH Level-1 Public Toilets false ceiling are insufficient and thus they have requested __ to raise a non-compliance against currently accepted design. In specific, CRL/__ highlighted that: 1. Luminaires are difficult to remove from the ceiling 2. It is not possible to access conduits and sockets above the ceiling through the "downlight" holes.
| 02SL - Stations (LUL) | Cxxx-NCR-002968 | NCR | MEP - STW - [Cxxx-ELEC-CMSXX10] - Workmanship and assurance of Comms cable tray installation |  | Contr | __ | FAR - Farringdon Station (West) |  | 2019-07-31 | 2020-01-31 16:12 | 184 | 2019-05-14 21:24 | Electrical - Cable Management | 5000 |  | Supervision/Management | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | CRL/__ notified __ that following their site inspection, they have identified numerous additions to the Cxxx CMS throughout the station to enable the connections to various Comms equipment. According to CRL/__, these tray installations have not been through any quality checks or been offered to the CRL FE team for inspection. CRL/__ highlighted a number of issues that they have been noted with these installations (refer to e-mail notification): · Missing brackets · Inadequate supports · Drop rods cut too short · Missing support components (flat washers, drop rod end protective caps, unistruct support missing end caps) · Missing cross bonds · 25% spare capacity not provided (to be dealt in a separate NCR, as this affects also non-Comms CMS) · __ paint not applied to cut ends · Manufacturers bends not used for junctions · Redline drawings not updated to reflect changes CRL/__ have requested __ to raise a NCR for this matter.
| 02SL - Stations (LUL) | Cxxx-NCR-002969 | NCR | MEP - STW - [Cxxx-ELEC-CMSXX10] - CMS spare capacity of 25% not provided |  | Contr | __ | FAR - Farringdon Station (West) |  | 2019-10-31 | 2020-02-03 14:33 | 95 | 2019-06-04 06:19 | Electrical - Cable Management | 10000 |  | Design | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Other | Completed |  | CRL/__ following their inspection have notified __ that various points around the site that 25% spare capacity on CMS (tray & trunking) has not been provided, as required by JY63.1302 & JY60.1301. The Radio system, CERs and routes into CERs are particular areas of concern (refer to attached e-mail notification). CRL/__ have requested that __ raise an NCR on this matter.
| 02SL - Stations (LUL) | Cxxx-NCR-002970 | NCR | WTH - Level +2 Chiller Area Drainage (HRU) |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2019-09-06 | 2019-11-28 09:40 | 83 | 2019-03-20 16:28 | Architectural - General | 15000 |  | Design | Repair | 2 (6-60k) | Complete | Design Problem - Inadequate or defective design | Completed |  | After an inspection carried out on Level +2 Chiller Area (HRU) the following issues were identified: 1. Finish floor level is not flat therefore water accumulates in the lowest areas. 2. Rainwater outlets grids are damaged or inadequate. Also there is no clear specification requirements for those.
| 02SL - Stations (LUL) | Cxxx-NCR-002972 | NCR | MEP - STW - [Cxxx-ELEC-ESD*X2, Cxxx-FIPC-FAD] - Metpro Adaptable Boxes conditional MCR acceptance |  | Contr | __ | FAR - Farringdon Station (West) |  | 2019-04-19 | 2019-05-09 11:49 | 20 | 2019-03-19 22:44 | Electrical - Lighting | 500 |  | Material | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | CRL/__ have notified __ that there is a condition set within the Code-1 accepted CRL-MCR-003536, which states that the adaptable boxes shall not be used for emergency lighting or life safety systems. CRL/__ note that these boxes have been used extensively throughout the installation for emergency lighting, FA, and PA/VA systems, and are not in a position to identify why CEG have placed this restriction on the boxes, as life safety systems are wired in fire rated cabling and the boxes provide the same level of protection as the trunking / conduit systems. CRL/__ don’t consider that any terminals are installed in them that would require a higher level of protection, however since the __ installation has progressed against the currently set MCR condition, CRL/__ requested __ to raise a NCR in order to further investigate this matter which could potentially rectify this statement on the CRL-MCR-003536.
| 02SL - Stations (LUL) | Cxxx-NCR-002973 | NCR | MEP - ETH - Level -7 - [Cxxx-ELEC-ESDEX2J] - No lighting provided in maintenance area / gantry |  | Contr | __ | FAR - Farringdon Station (West) |  | 2019-07-12 | 2019-07-15 10:24 | 3 | 2019-05-07 20:49 | Electrical - Lighting | 2000 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | CRL/__ notified __ that during a PAC joint-inspection for ETH Level -7 Small Power and Lighting CommLot (Cxxx-ELEC-ESDWX2J), they noted that no lighting has been provided at the UPE, behind the ESS Stairs (refer to area highlighted on drawing, within attached CRL e-mail notification). CRL/__ noted that according to the referenced drawing, the requirement of lighting within the walkway is still in abeyance. CR/__ note that according to their viewpoint, lighting is required as this area should be treated consistently against similar risers at the station. CRL/__ have requested __ to raise a NCR to further investigate this potential non-compliance.
| 02SL - Stations (LUL) | Cxxx-NCR-002974 | NCR | MEP - WTH - Level -4/-5 - Pin Rack Installation in Circular Shaft Trunking |  | Contr | __ | FAR - Farringdon Station (West) |  | 2019-05-24 | 2019-10-11 15:33 | 140 | 2019-04-16 20:18 | Electrical - Cable Management | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | CRL/__ notified __ that they consider that the installation of Pin Racks in the Comms Compartment Trunking (refer to attachment - the image was taken in the WTH Level -5 Circular shaft when coming down the stairs from WTH Level -4.) impedes the capacity of the trunking. CRL/__ noted that the relevant installation does not comply with the associated accepted quality benchmark. CRL/__ requested that __ raise a NCR to further investigate this issue.
| 02SL - Stations (LUL) | Cxxx-NCR-002975 | NCR | MEP - WTH - Levels 0/+2 - [Cxxx-ELEC-ESDWX2A, Cxxx-ELEC-ESDWX2C, Cxxx-FIPC-FADWX1B] - Materials not suitable for the enviroment in which they are installed |  | Contr | __ | FAR - Farringdon Station (West) |  | 2019-07-26 | 2019-10-14 13:00 | 80 | 2019-06-04 14:58 | Electrical - Power Distribution | 3000 |  | Material | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | CRL/__ notified __ (refer to attachment) that according to the Cxxx MEP Corrosion report, the WTH Level+0 Service Yard and Level+2 Chiller external areas have a corrosion classification category "3", which requires equipment to be hot dip galvanized. CRL/__ noticed that certain MEP services used in the afore-mentioned areas are pre-galvanised and also not IP rated for external environment. Following a __ survey the following services have been identified as non-compliant: - Adaptable boxes; - Fire Alarm & Detection conduits; - Comms CMS. CRL/__ requested that __ raise an NCR to address this non-compliance.
| 02SL - Stations (LUL) | Cxxx-NCR-002976 | NCR | Energised DC cabs 10mm earth cable has been removed |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2019-04-18 | 2019-09-12 12:27 | 147 | 2019-03-26 07:59 | Electrical - Earthing & Bonding | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | 10mm E&B cable has been removed from all energised Cxxx DC cabs. DC1, 3, 4, 5, 6, 7, 8 13, 14, & 15
| 02SL - Stations (LUL) | Cxxx-NCR-002977 | NCR | Damaged External Camera |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2019-04-09 | 2019-04-15 07:48 | 6 | 2019-03-26 17:05 | Communications and Control Systems - CCTV | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | 3 x Damaged External CCTV. The following camera requires replacement. 1) FAR-00-CAM-0158 L76261-MFL0507-V4320FDW-DN - BLK 2) FAR-00-CAM-0155 L76261-MFL0507-V4320FDW-DN - BLK 3) FAR-00-CAM-0153 L76261-MFL0507-V4320FDW-DN - BLK
| 02SL - Stations (LUL) | Cxxx-NCR-002978 | NCR | Misplaced RHP Cable Drum |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2019-04-26 | 2019-04-15 07:52 | -11 | 2019-03-29 15:56 | Communications and Control Systems - Telephony | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Cable drum misplaced - New cable drum is required to be procured.
| 02SL - Stations (LUL) | Cxxx-NCR-002979 | NCR | WTH – Urban Realm – __ HST3 mechanical anchor failure (NAL socket installation) |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2019-06-28 | 2019-06-21 16:29 | -7 | 2019-04-02 16:45 | Civil - Civil Engineering General | 5000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | On Cowcross Street in front of Farringdon Station, the south-East anchor which is one of the 4 No. __ HST3 mechanical anchors that were installed to secure the NAL RS168 socket has failed. The socket is bolted to the recess of the Eastern lighting column reinforced concrete foundation, in which the Eastern lighting column will be installed. The location of the failed anchor is highlighted on the attached drawing ‘Cxxx--S-DDD-M123_1-70001’. The attached photographs show the current hole created by the failure of the anchor. The depth of the irregular hole is 160mm and its dimensions are approximately 50mm by 35mm (max).
| 02SL - Stations (LUL) | Cxxx-NCR-002980 | NCR | Radio connectors |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2019-04-30 | 2019-04-24 13:10 | -6 | 2019-04-02 13:54 | Communications and Control Systems - Radio | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The following connectors are required; 716FLCF12 x 25 716FLCF78 x 25 716MRSCF12 x 50 716MRLCF12 x 50 NMSCF12 x 25 NMRSCF12 x 25
| 02SL - Stations (LUL) | Cxxx-NCR-002981 | NCR | 20 x Directional ANTENNAS - Colour Code RAL9011 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2019-04-17 | 2019-06-05 09:39 | 49 | 2019-04-03 15:09 | Communications and Control Systems - Radio | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | 20 x Directional Antennas are required which are required to be installed with the colour code RAL9011.
| 02SL - Stations (LUL) | Cxxx-NCR-002982 | NCR | MEP - WTH - Level +2 - [Cxxx-ELEC-CMSXX10] - Use of BZP Drop Rods in areas exposed to atmospheric conditions |  | Contr | __ | FAR - Farringdon Station (West) |  | 2019-06-28 | 2019-06-14 10:29 | -14 | 2019-04-29 13:10 | Electrical - Cable Management | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | As scope for Cxxx-NCR-002798 was limited on the WTH Level 0 Loading Bay area, as agreed in the Quality meeting, a new NCR needed to be raised in order to cover the WTH Level +2 areas for the similar issue. __ raises this NCR to cover afore-mentioned agreement.
| 02SL - Stations (LUL) | Cxxx-NCR-002983 | NCR | Damaged Radio Cable |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2019-05-02 | 2019-04-24 13:06 | -8 | 2019-04-04 14:23 | Communications and Control Systems - Radio | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Damaged radio cables. No proven causes. Cable IDs and length shown below. Please see attached for cable ID, location and length.
| 02SL - Stations (LUL) | Cxxx-NCR-002984 | NCR | MEP - WTH - Level -5 - [Cxxx-ELEC-ESDWX2H] - Lighting within "FAN1 Draught Relief Damper EB" area |  | Contr | __ | FAR - Farringdon Station (West) |  | 2019-05-31 | 2019-08-09 14:43 | 70 | 2019-04-06 16:59 | Electrical - Lighting | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | CRL/__ notified __ that the lighting in the WTH Level -5 "FAN1 Draught Relief Damper EB" area (refer to attachment, extract from drawing: Cxxx--E-DDA-M123_6-75313 [C03]), although installed as per the accepted design, it is un-maintainable. CRL/__ believe that, subject to confirmation from __ designers, permanent lighting could be omitted and there is no need for provision of power via 110 volt sockets for task lighting either, as there is no equipment within that area that require maintenance - refer to attached e-mail communication. CRL/__ requested that __ raise this as a non-compliance against the design and confirm remedial actions via FCD, prior to implementation.
| 02SL - Stations (LUL) | Cxxx-NCR-002985 | NCR | MEP - WTH - Level +1 - [Cxxx-ELEC-ESDWX2B] - Missing lighting in "Ladder Access Room" area |  | Contr | __ | FAR - Farringdon Station (West) |  | 2019-06-28 | 2019-10-14 11:13 | 108 | 2019-04-06 19:22 | Electrical - Lighting | 5000 |  | Design | Repair | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | CRL/__ notified __ that the there is neither lighting provision in the LAR Ladder Access Room Void at WTH Level +1 (refer to drawing Cxxx--E-DDA-M123_A-75304), nor 110V maintenance socket provision for task lighting, within the accepted design ((refer to drawings Cxxx--E-DDA-M123_A-75304 [C01], Cxxx--E-DDA-M123_A-75402 [C01]). CRL/__ believe that either permanent lighting or a 110V maintenance socket needs to be provided at this area - refer to attached e-mail communication. CRL/__ requested that __ raise this as a non-compliance against the design and confirm remedial actions via FCD, prior to implementation.
| 02SL - Stations (LUL) | Cxxx-NCR-002986 | NCR | WTH - Package H - Missing Quality Control & Assurance Documentation |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2019-05-03 | 2019-05-03 20:23 | 0 | 2019-04-11 13:18 | Civil - Civil Engineering General | 2500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | 1. The construction of all WTH plinths and upstands is covered under Package H (Cxxx--C-CER-M123-50209). There are records for several plinths identified within ITP Records Cxxx--C-LRC-M123-51135 which cannot be located. 2.On the 27/09/2016 the level +1 plinth (ID 64 within Cxxx--C-LRC-M123-51135) was poured. The cubes taken during this pour have subsequently been misplaced with no record of cube tests being carried out.
| 02SL - Stations (LUL) | Cxxx-NCR-002987 | NCR | MEP - STW - [Cxxx-ELEC-ESD*X1] - Discrepancies between PAC Submain Cable Test Reports and Site Installation |  | Contr | __ | FAR - Farringdon Station (West) |  | 2019-08-02 | 2019-07-15 11:01 | -18 | 2019-05-07 19:57 | Electrical - Power Distribution | 5000 |  | Documentation and Records | Repair | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | CRL/__ notified __ that they have noticed discrepancies between the Sub-main Cable Test Reports that form part of the PAC sign off and the Site Installation. Specifically, CRL/__ noted that they have noticed a number of times that either the test reports indicate CPCs as installed and on site there is no CPC installed, or there are different sizes of CPC shown on test reports and the CPC installed on site. CRL/__ are of the opinion that a check needs to be performed between test reports and the installed site conditions - refer to attached notification. CRL/__ have requested __ to raise an NCR, in order to investigate this further and correct as appropriate.
| 02SL - Stations (LUL) | Cxxx-NCR-002988 | NCR | WTH - Package H - Non-Compliances with BS EN:206 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2019-05-03 | 2019-05-03 20:09 | 0 | 2019-04-12 11:54 | Civil - Civil Engineering General | 2500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Not Defined | Completed |  | have reviewed cube results for all pour relevant for Package H (Cxxx--C-CER-M123-50209) and there are 3 pours which do not comply with one of the compliance criteria set out in BS EN:206. The criteria is as follow: 1 BS EN 206 B.2(4) – The difference between the two 28 day cube strengths divided by their mean must be less than or equal to 15% otherwise the test result shall be deemed invalid 2 BS EN 206 Table B1 – Criterion 1 – The mean of groups of 6 non overlapping 28 Day Test Results must be greater than or equal to the Characteristic Strength Plus 2 = 62 N/mm2 3 BS EN 206 Table B1 – Criterion 2 – Any 28 Day Test Result should not be less than Characteristic Strength Minus 4 = 56N/mm2 The following pours do not comply with Criterion 2: -30/06/2016 W5W7 mix (Page 3 & 4) -28/02/2017 C1/C2 mix (2 locations) (Page 5,6 & 7) -31/08/2018 SL4 mix (Page 1 & 2) Pages stated above are from "NCR location marked-up" attachment. Please see attached cube results from these 3 pours and BS EN 206 compliance sheet.
| 02SL - Stations (LUL) | Cxxx-NCR-002989 | NCR | ANT installed in wrong location |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2019-04-26 | 2019-04-24 13:12 | -2 | 2019-04-12 12:30 | Communications and Control Systems - Radio | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | ANT 30007 & 007 installed in wrong location (cable reference FD3026 & 3024)
| 02SL - Stations (LUL) | Cxxx-NCR-002990 | NCR | ETH - Reduced Capacity Firestopping at Level -4 UMC & LER |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2019-07-26 | 2019-08-09 08:31 | 14 | 2019-05-02 13:48 | Architectural - General | 5000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | During a walkaround site, it was identified that a number of lids provided to firestopping penetrations were not of the suitable size to provide future capacity requirements. The lids provided are too small in comparison to the ladder racks in the UMC and LER rooms at Level -4 in the Eastern Ticket Hall. Please see attached photos and relevant drawing Cxxx--X-DWG-M123-54646 of these two penetrations. This means that the firestopping will need to be broken out (hard and soft compound), correct size lids provided and the openings firestopped again using both hard and soft compounds
| 02SL - Stations (LUL) | Cxxx-NCR-002991 | NCR | WTH – Internal Cladding – Crack to Fire Extinguisher Frame |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2019-07-26 | 2019-10-25 13:52 | 91 | 2019-05-03 13:34 | Architectural - General | 500 |  | Manufacturing Defect | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The Fire Extinguisher Cabinet frame situated on Elevation B WTH FOH has two minor cracks within. See attached markup of ATK F1 drawings showing locations - Cxxx--A-DDA-M123_2-76210 Markupx & Cxxx--A-DDC-M123_Z-76012 Markup. DGL F2 drawing is Cxxx--X-DWG-M123-53312 for details. This defect has been raised to the fabrication and installation sub-contractor __. With the photos attached sent as evidence.
| 02SL - Stations (LUL) | Cxxx-NCR-002992 | NCR | MEP - ETH - Level +0.5 - [Cxxx-ELEC-ESDEX2B] - Missing lighting within the Discharge Air Plenum (ATK-E085) area |  | Contr | __ | FAR - Farringdon Station (West) |  | 2019-06-28 | 2019-08-05 09:56 | 38 | 2019-05-07 22:32 | Electrical - Lighting | 5000 |  | Design | Repair | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | CRL/__ have notified __ that during a joint site inspection as part of ETH Level 0 "Small Power and Lighting" PAC, they have noticed that there was no lighting provided in the ETH Level +0.5 discharge plenum room (refer to images within the attached e-mail notification), although there is Cxxx equipment and cable tray that feed the ETH Level 0 celling. CRL/__ are of the opinion that lighting should be provided. CRL/__ have requested __ to raise an NCR in order to address this non-compliance.
| 02SL - Stations (LUL) | Cxxx-NCR-002993 | NCR | ETH Barbican - Incorrect Isolation joint width in the blockwork |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2019-06-21 | 2019-06-21 14:02 | 0 | 2019-05-17 12:01 | Civil - Civil Engineering General | 4250 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | have reinstated platform 3 on the Barbican station. During a joint /CRL site inspection it was discovered that the Isolation joint between the existing blockwork and newly built platform blockwork was 60mm wide instead of the designed 25mm (See attached mark up drawing Cxxx--S-DDA-M123_3-41232 illustrating location of joint). Refer to site photo taken during the joint /CRL site inspection.
| 02SL - Stations (LUL) | Cxxx-NCR-002994 | NCR | WTH - Package H - __ and cavity wall channel missing records |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2019-05-31 | 2019-05-15 15:23 | -16 | 2019-05-13 10:25 | Architectural - General | 2000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | Inspection and Test Plan Cxxx--C-ITP-M123-40241 Rev.3.0 states that checksheet Cxxx-50241-001 will be provided as a deliverable record for the following ITP activities: - Channel Installation and Post Pour Checks [ITP activities 24, 25, 26 & 27] - Installation of __ (including surface preparation) [ITP activities 30 & 31] During preparation of WTH Package H ITP records (Cxxx--C-LRC-M123-51135 Rev.1.0), it was realised that records for the following items cannot be found: A) __ installation on wall 6 as per Cxxx-SWN-S-DDD-M123_Z-00111 Detail 5. B) Cavity Wall Channel construction in all the upstands highlighted in light blue in the attached sketches.
| 02SL - Stations (LUL) | Cxxx-NCR-002995 | NCR | MEP - STW - [Cxxx-ELEC-ESD*X2] - Use of the "FP 200 Gold MultiCore" cables without accepted MCR |  | Contr | __ | FAR - Farringdon Station (West) |  | 2020-05-01 | 2020-05-29 07:49 | 28 | 2019-06-04 16:05 | Electrical - Lighting | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | __ have installed the "FP 200 Gold MultiCore" cables without having an Code-1 accepted MCR in place.
| 02SL - Stations (LUL) | Cxxx-NCR-002996 | NCR | MEP - PAVA Cable H1000 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2019-06-14 | 2019-06-05 13:41 | -9 | 2019-05-15 15:23 | Communications and Control Systems - Public Address Systems | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | New PAVA H1000 cable required as a new route from the Station Announcement Point to the Whip antenna has been determined. 200 meters of cable is required.
| 02SL - Stations (LUL) | Cxxx-NCR-002997 | NCR | ETH- Welding on Sliding gate without approved documentation |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2019-08-09 | 2019-08-07 14:37 | -2 | 2019-05-17 14:49 | Civil - Civil Engineering General | 3000 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Stiffeners are being welded on the ETH sliding gate at L0without the approved required documentation in order to avoid delay to programmed. The documents have been prepared but are yet to be formally submitted and accepted.
| 02SL - Stations (LUL) | Cxxx-NCR-002998 | NCR | MEP - ETH - [Cxxx-ELEC-ESDEX2*] - Missing concession for escalator luminaire heigths |  | Contr | __ | FAR - Farringdon Station (West) |  | 2019-08-16 | 2020-02-24 15:51 | 192 | 2019-06-04 16:41 | Electrical - Lighting | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Although the luminaires in the ETH Escalators 7/8/9 Equipment Room have been raised to as high as possible as requested by CRL and __, due to the height restriction from __ equipment and protective panels, they still fall short of the required minimum mounting height of 2000mm AFFL, in accordance with the accepted design specification. __ have raised Cxxx-FCD-003636 to formalise current installation, but CRL have notified __ that a concession will also need to be raised to document this type of deviation against the baseline standard requirements. CRL/__ have requested that a NCR is raised to document this procedural non-compliance, as (in order to meet program constraints and in liaison with CRL/__) installation works have progressed prior to formally accepting the deviation from the accepted design via the PTR/FCD and the Concession process.
| 02SL - Stations (LUL) | Cxxx-NCR-002999 | NCR | STW - Missing MCRs before commencing Firestopping using QF1 and __ HS |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2019-06-14 | 2019-06-04 14:42 | -10 | 2019-05-22 14:15 | Architectural - General | 1000 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | QF1 and __ High Strength have been used by the firestopping subcontractor on-site. However, MCRs for these materials were not accepted prior to use on site as per the Works Information.
| 02SL - Stations (LUL) | Cxxx-NCR-003000 | NCR | Cxxx -MEP Cxxx Missing label Assetrs |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2019-09-06 | 2019-10-15 08:00 | 39 | 2019-05-28 14:11 | Communications and Control Systems | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The following labels have been missing; M123-DAT-00215 00216 00217 01632 01545 01372 01135 01134
| 02SL - Stations (LUL) | Cxxx-NCR-003001 | NCR | Drilling hole into cabinet without adequate protection |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2019-06-13 | 2019-07-31 08:19 | 48 | 2019-05-30 10:33 | Communications and Control Systems | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | To allow for cable entry, hole had to be enlarged to allow for a larger gland. Adequate protection was not used.
| 02SL - Stations (LUL) | Cxxx-NCR-003002 | NCR | MEP - WTH - Level -1 - [Cxxx-ELEC-ESDWX1D] - Spare capacity of DB42/W/-1/A not accordance with specification |  | Contr | __ | FAR - Farringdon Station (West) |  | 2019-08-23 | 2020-03-31 07:49 | 221 | 2019-06-04 21:03 | Electrical - Power Distribution | 1000 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | CRL/__ noted that the actual spare capacity of DB42/W/-1/A (14%) was not in accordance with accepted design specification requirement (minimum 25%). CRL/__ requested __ to raise a NCR, in order to investigate this issue further and determine appropriate actions if/where necessary/required.
| 02SL - Stations (LUL) | Cxxx-NCR-003003 | NCR | MEP - STW - [Cxxx-ELEC-ESDWX1D, Cxxx-ELEC-ESDEX1H] - Assurance documentation for Emergency Switchboards |  | Contr | __ | FAR - Farringdon Station (West) |  | 2019-07-26 | 2020-02-07 11:38 | 196 | 2019-06-13 06:17 | Electrical - Power Distribution | 1000 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | CRL/__ have notified __ that no joint inspection has occurred and no ITP assurance documentation has been provided in relation the ETH/WTH emergency switchboards for Lighting / Comms, during the relevant IRN Handovers. CRL/__ requested that __ raise a NCR, in order to address this.
| 02SL - Stations (LUL) | Cxxx-NCR-003004 | NCR | MEP - ETH - [Cxxx-ELEC-ESDEX3] - Maintainability of Lighting Control Modules for Escalators |  | Contr | __ | FAR - Farringdon Station (West) |  | 2019-09-20 | 2019-11-07 15:04 | 48 | 2019-09-04 08:21 | Electrical - Lighting | 5000 |  | Design | Repair | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | __ installed escalator lighting control equipment in the Upper Machine Control rooms (UMC) but Crossrail wanted these re-located as gaining access into __/__ rooms was difficult.
| 02SL - Stations (LUL) | Cxxx-NCR-003005 | NCR | ETH-Clash between sliding gates 1-ED38/ 1-ED39 and C690 manual gates. |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2019-07-12 | 2019-10-21 12:45 | 101 | 2019-06-26 16:41 | Architectural - Doors | 10000 |  | Design | Rework | 2 (6-60k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | Approved code 1 drawings Cxxx--X-DWG-M123-53250 P01 and Cxxx--X-DWG-M123-53251 P01 refers to sliding gates 1-ED38 and 1-ED39 design. These drawings show the handle protruding from the internal face of both gates . It has been identified that these handles are clashing with the C690 manual gates when the sliding gate are operated to close and open the station. Please refer to drawing Cxxx--A-DDA-M123_1-26200 P33. Rhino mechanisation system solution which is being currently installed as a prototype for the sliding gates will additionally increase the effect of this clash.
| 02SL - Stations (LUL) | Cxxx-NCR-003006 | NCR | ETH Moorgate Spur Trench Water Ingress |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2019-07-26 | 2019-07-18 07:42 | -8 | 2019-07-09 15:33 | Civil - Civil Engineering General | 5000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Previous Construction - Problems based on previous construction errors | Completed |  | poured Level -2 slab on the 17/06/2017 (See attached Mark up of Cxxx-SWN-S-DDA-M123_3-29201) as part of Sub-Construction Certificate - Farringdon Station Eastern Ticket Hall Trapezoidal Shaft - Sub Package 40 - Moorgate Spur slab Level -2 + raised slab and dwarf wall (GL 6-7) Cxxx--C-CER-M123-50167 Rev.1.0 have just finished installing the water-proofing detail at L-2 which consists of water-proofing of the trench that spans east to west and a concrete topping slab above this RC slab. During these works water was observed to be seeping into the bottom of the trench at both ends of the trench (See attached Moorgate Spur water-proofing remedial proposal for water ingress Page 1 ). This is preventing the installation of the P-12 waterproofing
| 02SL - Stations (LUL) | Cxxx-NCR-003007 | NCR | MEP - ETH - [Cxxx-ELEC-ESDEX2I, RAD-FAR-RAD00-07007] - ESS2 head height |  | Contr | __ | FAR - Farringdon Station (West) |  | 2019-11-15 | 2019-11-07 16:32 | -8 | 2019-11-01 09:42 | Electrical - Cable Management | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | CRL/__ have notified __ that during a site visit on the 04/07/2019, it was noted that due to the existing conduit (lighting) & tray (radio) installation, the head height clearance in the ESS2 stairway was not deemed sufficient by them. __ measured the tray height at approximately 1.8m at the lowest point. __ will need to revisit current design and installation against "clear-height" requirements. CRL/__ have requested that __ raise a non-compliance, in order to formally investigate this matter.
| 02SL - Stations (LUL) | Cxxx-NCR-003008 | NCR | ETH Moorgate Spur Concrete defects |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2019-07-26 | 2019-07-19 10:19 | -7 | 2019-07-08 16:17 | Civil - Civil Engineering General | 3500 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Personnel Error - Inattention to detail | Completed |  | poured the 100mm protection slab in the Moorgate Spur on the 06/07/2019. In the trench section did not follow Cxxx-FCD-003720 for the position of the shutter. installed the shutter flush with the edge of the trench on all sides, as opposed to the agreed position on the SSL, as per Cxxx-FCD-003720 (See page 5 in the attached report showing the detail).This has led to a voided area and poorly finished concrete as seen in pictures on page 7 and 8 of the attached report.
| 02SL - Stations (LUL) | Cxxx-NCR-003010 | NCR | MEP - Pipework sealed in staircase without sleeves |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2020-01-31 | 2020-01-31 10:55 | 0 | 2019-08-05 09:46 | Mechanical - Piping | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The fire main and domestic pipework travelling down the ETH north and south staircases have been sealed in without correct sleeves. __ sleeves have been installed with prior agreement with CRL. In one location the coupler has been sealed in with the pipes.
| 02SL - Stations (LUL) | Cxxx-NCR-003011 | NCR | WTH- Farringdon Road Works - Missing Cube Results |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2019-09-20 | 2019-09-13 15:32 | -7 | 2019-08-30 16:34 | Civil - Civil Engineering General | 2500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | On 23/10/2018 the __ Vehicle heavy duty slab was poured. The cubes taken during this pour have subsequently been misplaced by __ with no record of cube tests being carried out. See attached highlighted location sketch of the pour area. This slab is designed by __. Please note that this NCR is similar to Cxxx-NCR-002484, Cxxx-NCR-002766, Cxxx-NCR-002808, Cxxx-NCR-002861, Cxxx-NCR-002918, Cxxx-NCR-002920 and Cxxx-NCR-002986. Also, having reviewed recent concrete cube results for the C1C2 (10mm) mix, have noticed that attached extract from the C1/C2 graph shows that this pour doesn’t satisfy testing criteria 3, with a 28 strength result of 47.8 N/mm^2. The 28 day result for the pour on the 24/08/2018 is 46.2 N/mm2. If the 90 day cube result is used in this instance (56.1 N/mm2) the pour is compliant.
| 02SL - Stations (LUL) | Cxxx-NCR-003012 | NCR | MEP - STW - [Cxxx-FIPC-FADWX1A, Cxxx-FIPC-FADEX1A] - Missing Assurance for Fire Alarm & Detection assets of Gas Suppression Systems |  | Contr | __ | FAR - Farringdon Station (West) |  | 2019-10-11 | 2019-10-25 10:54 | 14 | 2019-07-16 14:21 | Fire - Detection | 500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | CRL/__ notified __ that they have not received the Assurance Documentation associated with the Fire Alarm & Detection Assets supporting the operation of the Gas Suppression systems of the station, although all systems have already been handed over via the IRN process and no relevant Outstanding Works have been identified to date. CRL/__ requested that a NCR is raised to formally address this issue.
| 02SL - Stations (LUL) | Cxxx-NCR-003013 | NCR | MEP - Comms - [CAB-FAR-MISC0-11014, CAB-FAR-MISC0-11020, CAB-FAR-MISC0-11024, CAB-FAR-MISC0-11025] - Non Compliance relating to earthing of the RTU HVSR & OHLE |  | Contr | __ | FAR - Farringdon Station (West) |  | 2019-09-20 | 2019-12-02 09:17 | 73 | 2019-07-22 08:42 | Communications and Control Systems | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | The following RTU cabinets were required to be earthed with a 10mm2 Earth Cable -6.1-36.6-120-Grn/Yel; WTH OHLE - FAR-05-CAB-6763U1 ETH OHLE - FAR-06-CAB-7762U1 WTH HVSR - FAR-07-CAB-8669U1 ETH HVSR - FAR-07-CAB-8664U1 This NCR is also to cover the earthing of the following: LEER Lift 6 (WTH-2) - FAR-03-CAB-3131U1 LEER Lift 7 (ETH -1) - FAR-01-CAB-2152U1 LEER Lift 8 (ETH -4) - FAR-04-CAB-5151U1 LEER Lift 9 (ETH0) - FAR-00-CAB-1131U1 DC1 - FAR-06-CAB-7ATKP010U1 DC2 - FAR-05-CAB-6662U1 DC3 - FAR-04-CAB-075AU1 DC4 - FAR-07-CAB-ATKE080U1 DC5 - FAR-01-CAB-1SARU1 DC6 - FAR-03-CAB-4E4041U1 DC7 - FAR-00-CAB-1072U1 DC8 - FAR-01-CAB-2026U1 DC13 - FAR-06-CAB-7ECWU1 DC14 - FAR-06-CAB-7ECEU1 DC15 - FAR-06-CAB-7ATKP010U1 __ cab by DC7 - FAR-00-CAB-1072U2
| 02SL - Stations (LUL) | Cxxx-NCR-003014 | NCR | MEP - WTH - [Cxxx-MECC-HCVWN2A] - DRACAS Non Compliance relating to the Chillers |  | Contr | __ | FAR - Farringdon Station (West) |  | 2019-11-07 | 2019-12-12 10:36 | 35 | 2019-10-24 12:32 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Equipment Breakdown | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Issues with the Chillers at WTH and differential pressure valves. Chiller No1 WTH • Description of the defect – Control Valve stuck in the open position. • Age at time of defect – Two Months. • Symptom – Will not function. • How the defect was detected – By __. • Impact of the defect – Chiller will operate but will not change over. Chiller No2 WTH • Description of the defect – Chiller goes into fault. • Age at time of defect – Straight after commissioning – 6 months • Symptom – Inlet and outlet pressure are crossed. Sensor re-calibrated. • How the defect was detected – Chiller went into fault. Re-set by a number of Carrier engineers. • Impact of the defect – Unable to operate chiller.
| 02SL - Stations (LUL) | Cxxx-NCR-003015 | NCR | MEP - Comms - [__-FAR-__00-10004] - Correct procedure not followed for re-installation of SCADA cable for door 1ED03A |  | Contr | __ | FAR - Farringdon Station (West) |  | 2019-08-09 | 2019-09-05 12:49 | 27 | 2019-07-25 09:09 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | NCR relates to the following instruction to __/__: "The intruder detection system was removed as per the PMI (Cxxx-PMI-01122) whereby the door 1ED03A had to be removed due to adjustment of the floor level. This resulted in the SCADA connection being disconnected to allow for the to be removed cable number (M123-CCC-00373). The door has now been reinstalled and the contact cable from the door can now be re-connected." __-FAR-__00-10004 IRNs have been handed over however, did not follow the correct process for dealing with this issue. Quote from __ (__) below from NCR Email notification attached: "Following a brief discussion with __ and __ it became clear that neither __, __ nor __/__ where aware of the removal of this door contact prior to the works being carried out. Knowing that the WAD procedure had not been followed, __ and I went out to investigate. We found that the junction box and some secondary containment had been removed, and the cable left coiled up with exposed ends. (see photos attached) We tested the ends finding them to be live, so gained access to DC7 and isolated/disconnected the cable from the supply."
| 02SL - Stations (LUL) | Cxxx-NCR-003016 | NCR | ETH- Absence of panic Hardware on door 4-ED02 and 4-ED13 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2019-10-30 | 2019-11-22 14:05 | 23 | 2019-08-01 11:28 | Architectural - Doors | 2000 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | would like to formalise the agreement reached on Cxxx-FCD-003722 and Cxxx-FCD-003723. This NCR is to capture the change of door 4-ED02 and the modiciation of door 4-ED13 Ironmongery. Door 4-ED02 and 4-ED13 is currently installed without a push bar as per the approved design however the absence of panic hardware on an emergency escape door is a Non-conformity. The following was agreed in the Cxxx-FCD-003722 regarding Door 4-ED02 1. The removal of the SR3 security rating requirement for door 4-ED02 as this is superfluous and would hinder the flow of passengers in an emergency. 2. To replace door 4-ED02 with an equivalent that incorporates a push bar. The following was agreed in the Cxxx-FCD-003723 regarding Door 4-ED13 1. Install a panic push pad onto the active leaf (Escalator lobby side) and a lever handle on the other side (lift 9 lobby side). 2. Suitably fill/cover and redudant holes on the door frame. 3. Maintain the fire rating or fire insulation integrity of the doorset Further to the FCD agreement instructed __ to design replacement door 4-ED02 and to procure the additional ironmongery required on door 4-ED13 This design has been reviewed and approved by the designer and have instructed fabrication of the replacement door to mitigate lead time delays. This change to the approved design will have cost and time implications. The typical door lead time is 8 weeks. Please find attached. 1. FCD for door 4-ED02 - Cxxx-FCD-003722 and FCD for door 4-ED13 - Cxxx-FCD-003723 2. Current approved and installed door design - Cxxx--X-DWG-M123-58661 (P03) 3. Updated door 4-ED02 drawings - Cxxx--X-DWG-M123-58661 (C03) 4. Email from designer to confirm that the updated design drawings have addressed all outstanding comments 5. Updated door 4-ED13 drawings - Cxxx--X-DWG-M123-58663 (C03)
| 02SL - Stations (LUL) | Cxxx-NCR-003017 | NCR | ETH – Moorgate Spur Protection Slab - C1/C2 Concrete Mix Design 28 day Strength Not Achieved |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2019-08-09 | 2019-08-08 08:25 | -1 | 2019-08-07 10:23 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Not Defined | Completed |  | poured the 100mm protection slab (as detailed on Cxxx design drawing Cxxx-SWN-S-DDA-M123_3-29201.) in the Moorgate Spur on the 06/07/2019. C1/C2 (S4) concrete was used in this pour – a C50/60 mix - as agreed under Cxxx-FCD-002573. After the 28 day result it was discovered that the design concrete strength was not achieved (See attached concrete cube result and BSEN 2062013 spreadsheet).
| 02SL - Stations (LUL) | Cxxx-NCR-003018 | NCR | MEP - Damage to Comms cable sheathing |  | Contr | __ | FAR - Farringdon Station (West) |  | 2019-09-05 | 2019-09-03 12:23 | -2 | 2019-08-22 12:58 | Communications and Control Systems | 0 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Within the trunking at ETH L-1 outside the UMC room, evidence of damage to comms cabling caused during cable pulling was noted. Cable Asset ID: M123-DAT-02631
| 02SL - Stations (LUL) | Cxxx-NCR-003019 | NCR | Radio cable damaged FD062 |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2019-09-10 | 2019-12-02 09:37 | 83 | 2019-08-27 12:54 | Communications and Control Systems - Radio | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Radio cable FD062 damaged WTH-5 lift lobby. to test cable and if test are good a sheathing repair kit can be used. Please see photos below and have the scaffold taken down or re-erected and ask the scaffolder not to put his tube so close to the radio cables.
| 02SL - Stations (LUL) | Cxxx-NCR-003020 | NCR | MEP - STW - [Cxxx-ELEC-ESD*X3] - Lighting Control for Circulation areas (Back of House) |  | Contr | __ | FAR - Farringdon Station (West) |  | 2019-09-27 | 2019-11-06 16:28 | 40 | 2019-08-29 12:39 | Electrical - Lighting | 5000 |  | Design | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | All Back of House circulation areas shall be controlled by PIR light sensors. It has been identified that some areas have been installed with manual switching instead of PIR light sensors. The Lighting Control Description of Operation confirms PIRs and not switches are the method of lighting control in circulation areas.
| 02SL - Stations (LUL) | Cxxx-NCR-003021 | NCR | MEP - Cxxx - Damage to Radio Cables, WTH Front of House Antenna |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2019-11-25 | 2020-01-31 08:42 | 67 | 2019-09-30 08:00 | Communications and Control Systems - Radio | 1000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Cables FD3056 and FD055 are damaged and need replacing. The damaged is by the antenna where the cable is bent at 90 degrees and the bend radius is not met. the cable is kink on the inside of the bend and stretched on the out side of the bend. The cables have also lost their shape due to issues surrounding the bracketry in this location. The cables connect to antenna 3019 LUL and 019 CRL. NCR is linked to CRL-OBS-28435 .
| 02SL - Stations (LUL) | Cxxx-NCR-003022 | NCR | MEP - STW - [Cxxx-ELEC-LIPXX10] - AN Wallis Lightning Protection materials |  | Contr | __ | FAR - Farringdon Station (West) |  | 2019-10-18 | 2020-01-07 10:28 | 81 | 2019-09-04 09:02 | Electrical - Electrical Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | AN Wallis Lightning Protection materials installed on site without approved MCR.
| 02SL - Stations (LUL) | Cxxx-NCR-003023 | NCR | MEP - Deflection Report - Outstanding Works |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2020-07-31 | 2020-12-01 08:53 | 123 | 2020-01-23 11:41 | Mechanical - Mechanical Engineering General | 3000 |  | Design | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | __ issued the Deflection Report (Cxxx--O7-RGN-M123-50001) identifying the impact on the MEP services and the measures needed to address these such as flexible connections, location of fixings etc. There is a matrix within the report identifying in detail each location where these measures need to be incorporated.
| 02SL - Stations (LUL) | Cxxx-NCR-003024 | NCR | MEP - Comms - Damage to Speakers in Zones 25 & 30 |  | Contr | __ | FAR - Farringdon Station (West) |  | 2019-09-24 | 2019-10-01 15:38 | 7 | 2019-09-10 10:39 | Communications and Control Systems | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | Damage has occurred to the following speakers post installation on site: - Z25 A11 (WTH Level -1) - Z25 A63 (WTH Level 0) - Z25 B66 (WTH Level +2) - Z30 A9 (WTH Level -6) - Z30 B4 (WTH Level -6)
| 02SL - Stations (LUL) | Cxxx-NCR-003025 | NCR | MEP - Comms - Damage to Fibre cables within Platform Inverts |  | Contr | __ | FAR - Farringdon Station (West) |  | 2020-05-29 | 2020-06-18 12:06 | 20 | 2019-09-10 15:18 | Communications and Control Systems | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Damage to sheathing has been found on the following Fibre cables within the Platform Inverts: Run lengths 597m Product code GUSL824 - M123-DAT-00190 - M123-DAT-00196 - M123-DAT-02633 Run length 531m Product code GUSL812 - M123-DAT-00201
| 02SL - Stations (LUL) | Cxxx-NCR-003026 | NCR | MEP - Comms - Damage to Radio cables ETH Level -7 |  | Contr | __ | FAR - Farringdon Station (West) |  | 2019-09-27 | 2019-09-24 11:23 | -3 | 2019-09-12 13:42 | Communications and Control Systems - Radio | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Damage has occurred to the following radio cables on ETH Level -7: - FD312 (runs between CPR-063 and ANT-139) - FD3314 (runs between SPL-3111 and ANT-3139)
| 02SL - Stations (LUL) | Cxxx-NCR-003027 | NCR | MEP - STW - [Cxxx-ELEC] - Volt Free Contacts for SCADA to be installed on ATS's |  | Contr | __ | FAR - Farringdon Station (West) |  | 2019-11-21 | 2019-11-14 12:19 | -7 | 2019-11-07 09:30 | Electrical - Switchgear | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The ATS's serving the PES doors / Cxxx equipment do not have volt free contacts as required by Cxxx specification.
| 02SL - Stations (LUL) | Cxxx-NCR-003028 | NCR | MEP - STW - [Cxxx-FIPC-FAD] - __ SCP-DPS Call Points installed without approved MCR |  | Contr | __ | FAR - Farringdon Station (West) |  | 2019-10-31 | 2019-10-07 14:52 | -24 | 2019-09-24 09:33 | Fire - Detection | 0 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | It would appear that there is no approved MCR for the __ SCP-DPS call points. Approved CRL-MCR-003961 was submitted for the __ HCP-E(SCI) units, however, Cxxx-RFI-004764 was raised after the __ fire engineer recommended replacing the HCP-E(SCI) units with the SCP-DPS type. The response to the RFI confirmed that the units should be changed and that an NCR raised. The call points were changed but the NCR never raised. We now have materials used extensively throughout site without an approved MCR, therefore an NCR shall be raised and an MCR for the __ SCP-DPS units submitted for approval.
| 02SL - Stations (LUL) | Cxxx-NCR-003029 | NCR | WTH - Water Ingress Into L0 Unallocated Space Next to Service Yard & WTH L-1 Lower Apse Ceiling |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2020-07-17 | 2021-05-07 14:26 | 294 | 2020-06-03 16:33 | Civil - Civil Engineering General | 30000 |  | Damaged | Repair | 2 (6-60k) | Complete | Previous Construction - Problems based on previous construction errors | Completed |  | A. Cxxx-NCR-002868 was raised in 2018 regarding 4no. damp patches identified during the repair works to the WTH L-1 Lower Apse Concrete Ceiling. The repairs carried out as part of that NCR have not been successful, so any further remedial works will now be covered by this NCR. B. Furthermore, in mid-2019 it was observed that there was also water ingress into the Level 0 Unallocated Space, adjacent to the Service Yard. Note that the unallocated space is the only area at L0 within the vicinity with no screed, only SSL with a paint finish, so water ingress was visible though the gap between the screed and the SSL, west of the door opening. Refer to attached plan which illustrates both these areas. This NCR will deal with the works required to address the water ingress in both these areas.
| 02SL - Stations (LUL) | Cxxx-NCR-003030 | NCR | MEP - WTH - [Cxxx-FIPC-FISWW1A] - IP rating of Watermist Panels |  | Contr | __ | FAR - Farringdon Station (West) |  | 2020-02-07 | 2020-03-13 15:26 | 35 | 2019-11-21 15:18 | Fire - Suppression | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | __: "The design and installation of the Low Pressure Water Mist fire protection system is based on the VsD 4001 standards for a Minifog EconAua Water Mist system. The original accepted CRL-MCR-005591 selected a IP 54 rated MiniMax control panel with supporting VsD assurance documentation. The panel was then replaced to a IP51 rated __ control panel (CRL-MCR-007537) CRL question the suitability of the IP 51 control panel that is located in the WTH plant room 1/782 which is protected by multiple sprinklers heads as detailed on the system schematic drawing Cxxx--P-DDE-M123_Z-75004. CRL require assurance and supporting evidence that activation of the sprinklers will not compromise the system integrity and the panel would survive the requisite 30 minutes."
| 02SL - Stations (LUL) | Cxxx-NCR-003031 | NCR | MEP - WTH - [Cxxx-ELEC-ESDWX2J] - 25% spare capacity not being achieved for DB13/W/-7/B |  | Contr | __ | FAR - Farringdon Station (West) |  | 2019-10-18 | 2019-10-21 09:02 | 3 | 2019-10-04 14:49 | Electrical - Power Distribution | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | DB13/W/-7/B is currently not meeting the requirements for 25% spare capacity for circuitry.
| 02SL - Stations (LUL) | Cxxx-NCR-003032 | NCR | MEP - ETH - [Cxxx-MECC-HCVEN2A] - Chilled Water Pump No.2 pump motor failure |  | Contr | __ | FAR - Farringdon Station (West) |  | 2019-10-25 | 2019-11-07 13:04 | 13 | 2019-10-11 09:44 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | System Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Pump motor failure for Chilled Water Pump No.2, found to be tight to turn and reportedly catching fire.
| 02SL - Stations (LUL) | Cxxx-NCR-003033 | NCR | MEP - STW - [Cxxx-ELEC] - Removal of Verified electrical asset labels |  | Contr | __ | FAR - Farringdon Station (West) |  | 2019-11-29 | 2019-11-06 09:23 | -23 | 2019-10-16 15:25 | Electrical - General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Verified electrical asset labels have been removed/replaced without acknowledging asset team, thus creating discrepancies within AIMS database.
| 02SL - Stations (LUL) | Cxxx-NCR-003034 | NCR | MEP - ETH - [Cxxx-MECC-HCVEN2A] - Fan coil No. 3: Chilled water coil leaking |  | Contr | __ | FAR - Farringdon Station (West) |  | 2019-11-01 | 2019-11-26 09:38 | 25 | 2019-10-18 08:46 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | System Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | The chilled water coil header on FCU 04/03 had a leak which has since been repaired by __, see report within assurance file under Cxxx-PWK-02036. NCR raised for assurance purposes only and relates to CRL-DRA-000551.
| 02SL - Stations (LUL) | Cxxx-NCR-003035 | NCR | MEP - Damaged radio antenna |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2019-10-31 | 2020-01-31 08:45 | 92 | 2019-10-17 15:40 | Communications and Control Systems - Radio | 2000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Personnel Error - Inadequate work environment | Completed |  | 8 Antenna has been damaged. ant 3117, 143, 173, 3173, 3143 3029 & 029.
| 02SL - Stations (LUL) | Cxxx-NCR-003036 | NCR | MEP Radio antennas not installed as per Cxxx-ATK-A-XSK-CRG02-50048 |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2020-02-28 | 2020-01-17 10:45 | -42 | 2019-10-28 12:13 | Communications and Control Systems - Radio | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Please see photos below, It doesn’t look like the antennas have been installed to the Cxxx-ATK-A-XSK-CRG02-50048 design. It looks like the metal back plate of the antenna is in contact with the metal of the antenna housing bracket. It also look like the fly lead of the antenna has not been passed through the cut out on the top of the antenna housing which means that the antenna can not sit flush. I also notice there is no grub screw to lock the antenna in position. These antennas are FAR-06-ANT-0058, FAR-06-ANT-3058, FAR-06-ANT-0122, FAR-06-ANT-3122 on the WTH -6 & ETH-6 back wall in the CP. Please also see OMI antennas installation in lighting booms in CP's -6. This NCR is also for all directional antennas installed on PES EB & WB
| 02SL - Stations (LUL) | Cxxx-NCR-003037 | NCR | MEP - STW - [Cxxx-FIPC-FADEX1B, Cxxx-FIPC-FADWX1A] - Call Points within Transformer Rooms |  | Contr | __ | FAR - Farringdon Station (West) |  | 2019-12-13 | 2020-03-20 17:04 | 98 | 2019-10-31 13:19 | Fire - Detection | 2000 |  | Material | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The product submitted against CRL-MCR-005391 is not acceptable for use. We have installed and commissioned this product. CRL request that we use STI type call points for the Gas Suppression Systems.
| 02SL - Stations (LUL) | Cxxx-NCR-003038 | NCR | MEP - ETH - [Cxxx-MECC-HCVEN2A] - Chiller malfunction related to CRL-DRA-000707 |  | Contr | __ | FAR - Farringdon Station (West) |  | 2019-11-15 | 2019-11-26 09:35 | 11 | 2019-11-01 08:41 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Chiller ETH No.1 had a Touch Pilot controller with a 'life expired' fault which caused the controller not to function. The controller has since been replaced by Carrier. This NCR is for assurance purposes only and is related to CRL-DRA-000707
| 02SL - Stations (LUL) | Cxxx-NCR-003039 | NCR | MEP - STW - [Cxxx-ELEC-ESDEX1K, Cxxx-ELEC-ESDWX1K] - LV Battery charger FATs missing from IRNs |  | Contr | __ | FAR - Farringdon Station (West) |  | 2019-11-18 | 2019-11-29 10:12 | 11 | 2019-11-04 13:59 | Electrical - LV Equipment | 500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | There is a line item on the Cxxx Electrical ITP for FATs. There seems to have been an oversight in the submission of the LV battery Charger FATs, as these have not been included within the IRN ITP records for the applicable Sub-Mains distribution packages.
| 02SL - Stations (LUL) | Cxxx-NCR-003040 | NCR | MEP - STW - [Cxxx-ELEC-CMSXX10] - Fire Alarms & Detection Secondary CMS fixings |  | Contr | __ | FAR - Farringdon Station (West) |  | 2020-03-20 | 2020-03-12 09:59 | -8 | 2020-02-21 12:40 | Fire - Detection | 5000 |  | Material | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | Wall plugs and screws have been used to fix secondary CMS serving Fire Alarms & Detection equipment. This method of fixing has not been listed within the Demonstration of Fire Compliance for the Station’s Cable Management Support Systems document (Cxxx--O-RGN-M123-50014).
| 02SL - Stations (LUL) | Cxxx-NCR-003041 | NCR | MEP - ETH - [Cxxx-ELEC-ESDEX2F] - Incorrect installation of CCC luminaires |  | Contr | __ | FAR - Farringdon Station (West) |  | 2020-01-31 | 2020-03-31 08:02 | 60 | 2019-11-27 08:32 | Electrical - Lighting | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The installed recessed type CCC luminaires on ETH Level -3 have been rejected because they cannot be re-lamped or have their LED drivers replaced without the removal of the GFRC ceiling panels. This is unacceptable as special lifting equipment and scaffolding is required to remove the ceiling panels which may not be able to be achieved during Engineering hours. Trained personnel will also be required to remove the ceiling panels. The installed luminaires also have a clear glass diffusers which produce excessive glare.
| 02SL - Stations (LUL) | Cxxx-NCR-003042 | NCR | MEP - STW - [Cxxx-ELEC-ESDWX1K, Cxxx-ELEC-ESDEX1K] - Compliance of the busbar support system |  | Contr | __ | FAR - Farringdon Station (West) |  | 2020-01-03 | 2019-12-19 16:44 | -15 | 2019-11-27 09:28 | Electrical - LV Equipment | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | The LV busbar has not been securely fixed using manufacturers fixings across horizontal runs. Without the correct fixings, the forces on the busbar under fault conditions have the potential to cause significant damage and is a potential risk to operatives working in the vicinity. The following has also been noted by CRL: - A number of horizontal clips are not installed as per manufacturers guidelines i.e. not all on outside edges - All vertical clips are not installed as per manufacturers guidelines - Confirmation is required that supports provided for cast resin are as per manufacturers guidelines
| 02SL - Stations (LUL) | Cxxx-NCR-003043 | NCR | TUN - SCL - Inaccessible Grout Injection Hose Boxes in PTW / PL2 |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2020-01-10 | 2020-01-16 14:02 | 6 | 2019-11-27 13:03 | Tunnelling - Linings - In-situ Concrete | 3000 |  | Design | Repair | 4 (0.5-3k) | Complete | Previous Construction - Interfacing issues | Completed |  | Following a site walkaround, two grout injection boxes were identified as being installed in locations which are inaccessible within Platform Tunnel West (PTW), please see attached photo. It is noted that the easternmost box has had the tile infront partially removed to enable access. This is not currently an agreed solution to this issue. The location of this is Chainage -0.7 as identified within page 117 of the document Cxxx--C4-LRC-M123-50489 Rev 3.0, Reinjectable Grout Hose User Manual and As Built Records. The affected boxes are Box 1 and 2 on this drawing. In the case of water ingress into the tunnels, the end user would need to remove tiles in the location to inject grout. Access is also frustrated due to the positioning of the fire hydrant as shown in the picture. This is Non Compliant to the Works Information
| 02SL - Stations (LUL) | Cxxx-NCR-003044 | NCR | ETH - Moorgate Spur to -1 Steps - Works started without approved documentation in place. |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2020-01-17 | 2020-01-28 14:58 | 11 | 2019-12-13 15:01 | Architectural - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Work on installation of the architectural items at the Moorgate steps has started without an approved ITP being in place. The documents have been prepared but are yet to be formally submitted and accepted.
| 02SL - Stations (LUL) | Cxxx-NCR-003046 | NCR | WTH – Farringdon Rd Inlet Main Clash with OSD Cladding |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2020-06-26 | 2020-06-01 11:39 | -25 | 2020-01-08 17:20 | Architectural - General | 10000 |  | Design | Rework | 2 (6-60k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | Two fire inlet mains have been installed on the WTH Farringdon Rd Elevation in line with drawing Cxxx--A-DDC-M123_1-76251. HBR have detailed their Farringdon Rd Cladding in line with GA drawing Cxxx--A-DDA-M123_1-76200. The fire inlet mains positions on drawing Cxxx--A-DDC-M123_1-76251 & Cxxx--A-DDA-M123_1-76200 do not align, therefore there would be a clash between fire inlet mains and OSD cladding.
| 02SL - Stations (LUL) | Cxxx-NCR-003047 | NCR | MEP - ETH - [Cxxx-MECC-HCVEN2A] - ETH Fan Coil No. 1 Malfunction |  | Contr | __ | FAR - Farringdon Station (West) |  | 2020-01-29 | 2020-01-21 09:20 | -8 | 2020-01-15 11:17 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Error by manufacturer in shipping or marking | Completed |  | There was a fault with Fan Coil No.1 (FAR/E/FCU-01) which has now been replaced as per __ report attached. NCR raised for assurance / monitoring purposes only.
| 02SL - Stations (LUL) | Cxxx-NCR-003048 | NCR | ETH - Untidy blockwork openings for new fire hydrants |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2020-06-19 | 2020-06-17 14:15 | -2 | 2020-01-17 16:23 | Architectural - Brickworks/Blockworks | 5000 |  | Supervision/Management | Repair | 3 (3-6k) | Complete | Management Problem - Inadequate supervision | Completed |  | Temporary 200x200mm blockwork openings have been created on ETH L-6 (1no) and ETH L-7 (2no) to expedite the install of the new fire hydrants. The temporary openings have been created incorrectly by knocking blocks out, leaving an extremely untidy finish. The requirement for temporary holes was due to insufficient planning and sequencing of works, not allowing for the blockwork contractor to make the correct holes before the fire mains installation began. SCCs involved: Arch-ETH-2 ETH Architectural Works - Blockwork from Level -7 to Level -1 Cxxx--A-CER-M123-50062 Arch-ETH-8 ETH Architectural Works – Firestopping of penetrations including smoke barriers Cxxx--A-CER-M123-50069
| 02SL - Stations (LUL) | Cxxx-NCR-003049 | NCR | MEP - 2 Hour Fire Rating of __ Cabling Route Not Met |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2020-06-17 | 2020-06-22 10:16 | 5 | 2020-04-09 15:59 | Mechanical - Lifts | 5000 |  | Material | Rework | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | The cable systems from the machine rooms to fire fighting lifts 6 and 9 are required to have 120min fire resistance. Currently the cable system installed can only withstand 60min.
| 02SL - Stations (LUL) | Cxxx-NCR-003050 | NCR | MEP - __ Escalators 1-11 skirt lighting LED drivers DALI compatibility |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2020-03-23 | 2020-02-04 15:10 | -48 | 2020-01-27 10:29 | Electrical - Lighting | 5000 |  | System Defect | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | The following details have been provided by the site team, showing the lead up to the NCR. This NCR has been rasied as there is a compatability issue between the escalator skirting lights and Escalator Drivers. This NCR has been raised in agreement to close the associated PAC for the works. • Cxxx __ team reported Escalators Skirt Lighting system 57 DAL Dimmer unit is successfully addressed, but 107 units could not be addressed due to product compatibility. • Wednesday 2nd October 14:00 a site meeting with / CEG/ __/ __ took place where __ engineer demonstrated the addressing issues. __ (CEG) informed that the supplier and installer Cxxx/ __ to resolve this issue. • Wednesday 02nd October Cxxx/__ interface meeting discussed __ site management could not progress without instruction, the action was taken by __ (CRL) to discuss with __ and __ senior management as this issue is systemwide. • Tuesday 15/10/2019 __ () issued Cxxx-EWN-02814 to CRL. • Wednesday 12/11/2019 Cxxx/__ interface meeting. The issue was discussed and noted that there's been no update from CRL-__ senior management. • Tuesday 17/12/2019 __ (__) confirmed __/__ had replaced a sample of new drivers. __ attendance was requested to address the units. __ informed __ was allocated to other stations, • Monday 06/01/2020 /__/__ site meeting was arranged to confirm the new drivers were addressed and are DALI compatible. • Tuesday 07/01/2020 __ engineer __ issued screen graphic report to /__, __ (__) confirmed __ new drivers delivery will be made by Friday 10/01/2020 • Monday 13/01/2020 __ (__) confirmed replacement works were progress, __ team were also on site addressing and testing new units. • Thursday 23/01/2020 __ engineer __ issued screen graphic report to /__ showing 3 drivers could not be addressed. __ are working to rectify this. __ () on-site inspection with __ engineers confirmed the faulty units are replaced. __'s __ has confirmed a team allocation for Monday 27th and Tuesday 28th January to close out the addressing issues.
| 02SL - Stations (LUL) | Cxxx-NCR-003051 | NCR | WTH Service Yard Level 0 - Installation of IP54 Cable Trunking without an approved MCR |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2020-05-01 | 2020-04-24 08:18 | -7 | 2020-02-21 12:26 | Electrical - Cable Management | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | Following an inspection on site, it was found that the __ IP54 cable trunking installed in the service yard of WTH Level 0, was installed without an approved MCR
| 02SL - Stations (LUL) | Cxxx-NCR-003052 | NCR | WTH - Disabled Toilet Basin With Exposed Trap |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2020-02-25 | 2020-02-27 15:54 | 2 | 2020-02-11 17:24 | Architectural - Sanitary Fittings | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | The disabled toilet basin with exposed trap was raised as an issue in the security notes issued to Cxxx on Cxxx-PMC-15056 following a visit from the CRL security. Previously Cxxx-FCD-003577 was raised to implement semi-pedestals over the exposed traps in the male, female and baby changing areas, but this did not cover the basin in the disabled toilet area.
| 02SL - Stations (LUL) | Cxxx-NCR-003053 | NCR | MEP - STW - [Cxxx-ELEC] - Cable Asset Naming Changes |  | Contr | __ | FAR - Farringdon Station (West) |  | 2020-02-28 | 2020-03-17 16:10 | 18 | 2020-02-14 13:55 | Electrical - Cable Management | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | CRL Asset Identification Standard require 4 lines text for the cable label using capitalised letters. This not always possible due to some label names /description being too long and reducing the text will make them illegible. To improve readability of the label, 5 lines or/and lower case letters will be used for cable label description. See attached photos as an example.
| 02SL - Stations (LUL) | Cxxx-NCR-003054 | NCR | WTH- Metalworks - Missing Pull Test Certs |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2020-04-17 | 2020-04-02 10:06 | -15 | 2020-04-01 16:09 | Architectural - General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | Inspection and Test Plan Cxxx--A-ITP-M123-50008, Activity 3.1.5,3.2.5,.3.3.5,3.4.5,3.5.5,3.6.5,3.6.5,3.7.5,3.8.5,3.11.5,3.12.6,3.15.8 and 3.15.6 .includes a requirement for pull tests to be carried out for anchors installed by __. During the compilation of ITP Records for the WTH Metalwork it has been identified that there are missing Pull test certificates for Metalwork package for the following items: Miscellaneous Metalwork ( Cxxx--A-LRC-M123-50345) • Mesh Panel (item 182) No pull tests carried out – no access due to installation methodology • Sump pump ladders (item 204) No pull tests carried out – due to restricted access and the installation methodology • Parapet capping steelwork (item 233) No pull tests carried out – unable to pull test anchor fixings specified • Fire hydrant balustrade (item 250) No pull tests carried out – due to finished floor finishes / extended bolt lengths prevented pull test equipment being used • Undercroft sump pump grilles (item 252) No pull tests carried out – due to restricted access and the installation methodology • Earthing bar doors (item 269) No pull tests carried out – due to restricted access and the installation methodology LVS/LVU/MSR/SOAR Risers ( Cxxx--A-LRC-M123-50311) • LVS/LVU/LV-B Risers(Item 99-102): No pull tests carried out – no access due to installation methodology • SR1 Risers(Item 103-104): No pull tests carried out – no access due to installation methodology • MSR Risers(Item 94-98): No pull tests carried out – no access due to installation methodology BS8539_2012 – Code of practice for anchors states: Page 42 : “these tests only required when the strength or precise nature of base material is unknown” – However in this case the base material is known, therefore it is not a requirement for the anchors to be tested. Page 41 : “ testing of anchors required : after installation when a sample of all anchors may be proof tested to validate the quality of installation” and from page 42 : “ These tests should be carried out on a sample of working anchors on every safety-critical application (unless approved anchors have been installed by trained operatives working under supervision)”. Cxxx-FCD-002869 states that the pull out tests were carried out by “trained operatives under supervision”. Page 57: “These tests are usually carried out on the installed anchors to show that they have been installed correctly and are not intended to prove suitability.” – The anchors have been installed by “trained operatives” who have installed anchors in other areas which the pull tests have been carried out and passed. Therefore in conclusion: The missing pull tests are still acceptable because the criteria for pull tests requirement of the BS 8539_2012 have been met.
| 02SL - Stations (LUL) | Cxxx-NCR-003055 | NCR | WTH - Metalworks-Missing Sample/benchmarks |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2020-04-17 | 2020-04-03 15:42 | -14 | 2020-04-02 16:37 | Architectural - General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | Inspection and Test Plan Cxxx--A-ITP-M123-50008 Rev 7.0, Item 2.2 includes a requirement for sample and benchmark documents to be provided for some of the items installed by __ on the metalworks package. Also Cxxx-FCD-002406 was raised which lists all the items installed that required sample/benchmarks for this package. However these documents were not produced for the following items: -Grid flooring (Main Service Riser) – Sample and benchmark documents -Stainless steel mesh partition and hand railing (ESS01 and INS01) – sample, prototype and benchmark documents - Balustrades and Handrails for Precast stairs – sample, prototype and benchmark documents - Metal stairs and balustrade - Stairs (sample and benchmark) and for balustrade just benchmark document. Ladders and walkways – sample and benchmark and for handrail only benchmark document Guard rail to ramps - Handrails – sample, prototype and benchmark documents Internal balustrades – Benchmark document Stainless steel weave mesh – Sample, prototype and benchmark documents
| 02SL - Stations (LUL) | Cxxx-NCR-003056 | NCR | STW – __ Welding Assurance Documentation Not As Per Accepted ITP |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2020-04-29 | 2020-04-16 15:05 | -13 | 2020-04-15 15:22 | Architectural - General | 1000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | __ document ‘Inspection and Test Plan - Fabrication and Surface Preparation of Architectural and Structural Steelwork for the WTH and ETH’ - Cxxx--A-ITP-M123-50009 Rev 4.0 sections 3.1 – 3.3b state the requirements for N__ of welds on site. However the weld testing documentation provided by __ in the ITP records within SCCs listed below have not been in line with the ITP requirements: Cxxx--A-CER-M123-50031 - WTH Architectural Works - Metalwork - Metal Staircases and Balustrades (MNS03A, MNS03B, MNS14, MNS15, MNS02) - Cxxx--A-LRC-M123-50319 Cxxx--A-CER-M123-50032 - WTH Architectural Works - Metalwork - Miscellaneous Items – (Fixing to precast stairs, Handrails, Balustrade posts, ramp guardrail, Mesh Louvres) - Cxxx--A-LRC-M123-50338 - Cxxx--A-LRC-M123-50339 - Cxxx--A-LRC-M123-50340 - Cxxx--A-LRC-M123-50341 - Cxxx--A-LRC-M123-50342 - Cxxx--A-LRC-M123-50344 Cxxx--A-CER-M123-50074 - ETH Architectural Works - Metalwork - All other scope (Cat ladders, Handrails, Grid flooring, Signage truss, Hatches etc) - Cxxx--A-LRC-M123-50379 - Cxxx--A-LRC-M123-50380 - Cxxx--A-LRC-M123-50381 - Cxxx--A-LRC-M123-50382 - Cxxx--A-LRC-M123-50383 - Cxxx--A-LRC-M123-50384 - Cxxx--A-LRC-M123-50385 - Cxxx--A-LRC-M123-50394 Cxxx--A-CER-M123-50075 - ETH Architectural Works - Metalwork - General - Cxxx--A-LRC-M123-50328
| 02SL - Stations (LUL) | Cxxx-NCR-003058 | NCR | ETH - Metalworks-Missing Sample/benchmarks |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2020-05-01 | 2020-04-22 13:40 | -9 | 2020-04-17 11:51 | Architectural - General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | Inspection and Test Plan Cxxx--A-ITP-M123-50008 Rev 7.0, Item 2.2 includes a requirement for sample and benchmark documents to be provided for some of the items installed by __ on the metalworks package. Also Cxxx-FCD-002414 was raised which removes the requirement to provide samples and prototypes for all items excluding: 1. Stainless steel weave mesh and 2. Horizontal truss and fabricated beam that form the support to the rain screen cladding and signage band. However these benchmarks/prototypes/sample documents were not produced for these items either.
| 02SL - Stations (LUL) | Cxxx-NCR-003059 | NCR | MEP - WTH - [Cxxx-FIPC-FISWW1A] - DRACAS Record - Sticking LPWM Non Return Valve Watermist. |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2020-05-07 | 2020-04-29 11:46 | -8 | 2020-04-23 10:23 | Fire - Suppression | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | During Commissioning of the LPWM system the delivery side non return valve was sticking on the 80mm main (Clack sticking)
| 02SL - Stations (LUL) | Cxxx-NCR-003060 | NCR | MEP - STW - RAM - Lack of Manufacturers Failure Rate data to verify Availability Criteria |  | Contr | __ | FAR - Farringdon Station (West) |  | 2020-05-29 | 2020-06-22 11:49 | 24 | 2020-05-05 22:26 | Systems - Systems Engineering General | 5000 |  | Documentation and Records | Rework | 3 (3-6k) | Complete | Personnel Error - Other human error | Completed |  | CRL RAM Team have notified __ that further mitigation needs to be applied to the RAM Calculations included within the Code-1 accepted document "RAM ANALYSIS REPORT" (Cxxx--O8-RGN-M123-50001 [8.0]), in order to ensure that the lack of certain Manufacturers' Failure Rate data do not impact on the project's availability results in a manner that the project's RAM Targets could not be met. Following a __/CRL RAM workshop, it was decided that a NCR is raised in order to formally assess the afore-mentioned impact and define corrective actions as appropriate.
| 02SL - Stations (LUL) | Cxxx-NCR-003061 | NCR | ETH - Damage to -3 Lift Lobby Corner Panel |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2020-08-23 | 2020-08-26 09:18 | 3 | 2020-06-26 15:17 | Architectural - General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | The corner panel at the level -3 lift lobby has been found to have been damaged. The panel will require replacing.
| 02SL - Stations (LUL) | Cxxx-NCR-003062 | NCR | TUN/WTH – LP2/WTH Water Ingress |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2020-09-11 | 2020-11-23 14:28 | 73 | 2020-08-12 16:50 | Civil - Tunnelling | 10000 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Previous Construction - Interfacing issues | Completed |  | Cxxx-NCR-002251 identified a leak within the connection of LP2 and WTH station box (SH-W2 shaft). Cxxx-FCD-003149 & Cxxx-FCD-003339 proposed a series of remedial which were implemented at the end of 2018 as part of this NCR. These have been successful in controlling the water ingress to the trackside section of the tunnel. However, the water ingress highlighted in Cxxx-NCR-002251 is still present and since June 2020 has been noticed to be causing damage to the following areas of the BOH station side of the tunnel: - Blockwork to top of separation wall is saturated and stained (215mm wall shown on Cxxx--X-DWG-M123_7-54101) - Ductwork and support system is corroded - Tunnel lining has been stained
| 02SL - Stations (LUL) | Cxxx-NCR-003063 | NCR | ETH- Barbican Lift lobby - Use of non-approved drawing for construction |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2020-09-18 | 2020-09-28 10:47 | 10 | 2020-08-19 08:36 | Architectural - Walls | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The skirting details on barbican Lift Lobby in ETH level -1 has been constructed to drawing Cxxx--X-DWG-M123-56338 Rev C01. The drawing was not formally issued to CRL to be accepted prior to construction commencement. While the drawing has been review and approved by __ it appears that the installed high level skirting trim is different to what had been agreed on-site in October 2019 by , __ and __. are liaising with __ and __ to revise the drawing and to carry out the corrective site works. Please find attached 1.Drawing Cxxx--X-DWG-M123-56338 Rev C01 2.Email from __ following site workshop in October 2019
| 02SL - Stations (LUL) | Cxxx-NCR-003066 | NCR | Cable Fault |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2020-12-11 | 2021-01-04 09:01 | 24 | 2020-09-23 11:03 | Communications and Control Systems - CCTV | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Personnel Error - Not Defined | Completed |  | It has become apparent that the brown pair on the cable serving Camera 0242 from DC15 is down. __ engineers changed the broken to another pair and the camera is now working. However as per guideline all pairs from the cat 6 cable should be working so cable should be replaced
| 02SL - Stations (LUL) | Cxxx-NCR-003067 | NCR | PLT Service Boom Glass Kite-mark |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2020-10-07 | 2020-10-09 16:35 | 2 | 2020-10-02 14:26 | Architectural - General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | The kite marks of the service boom glass is present as indicated by the Kite Glass’ ‘Batch Check Sheets (see ITP records, Cxxx--A-LRC-M123-50285. The kite marks have since been obscured by the frame, fritting and other components.
| 02SL - Stations (LUL) | Cxxx-NCR-003068 | NCR | Damaged Radio Cable |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2020-12-24 | 2021-01-04 09:38 | 11 | 2020-10-03 07:45 | Communications and Control Systems - Radio | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Personnel Error - Not Defined | Completed |  | PPM team found damaged radio cables during routine PPM
| 02SL - Stations (LUL) | Cxxx-NCR-003070 | NCR | MEP - Power Factor Correction Units Commissioning |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2021-01-28 | 2021-01-22 15:05 | -6 | 2020-12-14 09:51 | Electrical - General | 500 |  | Incomplete Works | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The PFC cabinets were installed without the final commissioning being carried out. (East & West) The Factory Acceptance Tests were carried out in April 2017. The FAT Document Cxxx--E-LRC-M123-50430 has only just been issued. 01/12/2020.
| 02SL - Stations (LUL) | Cxxx-NCR-003071 | NCR | MEP Advertising Panels Power Circuit Discrimination |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2020-11-30 | 2020-12-16 16:21 | 16 | 2020-11-18 11:29 | Electrical - General | 0 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Due to the upstream MCCB rating on the Lighting and Power DBs the maximum __ rating to the advertising DBs is restricted to 32A Type C __s. As a consequence the advertising final circuit __s will not achieve full discrimination with the advertising DB supply 32A Type C __. 1. Provide evidence of the as installed circuit arrangement. Schematics, DB Schedules, cable calculations and discrimination graphs. Discrimination graphs were provided with the RFI. 2. Email from LU stating their acceptance of the installed circuit arrangement. An email from __ Global Lead Engineer, representing TfL, was attached with the RFI stating TfL acceptance. 3. Provide evidence that the __s are rated correctly for the load currents and the inrush currents. I have got a copy of an email I sent to and Exterion Media with the changes we needed to make to the ratings of the __s to cater for inrush currents dated 28052019. 4.Provide an explanation of the earth gapping and how the R2 value has calculated ant the effect on the circuit impedance and fault current. I will get this from __. 5. The discrimination issue is also to be captured within the Tier1 project risk register. I have already tried to get this issue on the Risk Register but without success.
| 02SL - Stations (LUL) | Cxxx-NCR-003072 | NCR | STW – In Situ Testing of Fire Stopping Installation Works Not Carried Out As Per Specification |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2020-11-27 | 2020-11-23 16:38 | -4 | 2020-11-10 17:48 | Architectural - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | As found in the Completion Readiness Assessment Framework Cxxx--O4-STP-M123-53007, the specification Cxxx--A-RSP-M123-50057 JP10.2202 states that 10% of all penetration seals should be tested. During installation of the firestopping elements, a 10% check of penetration seals has not taken place.
| 02SL - Stations (LUL) | Cxxx-NCR-003073 | NCR | MEP - [Cxxx-MECC] - Installation of materials prior to MCR acceptance |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2021-03-31 | 2021-03-08 14:02 | -23 | 2021-01-13 13:30 | Mechanical - Mechanical Engineering General | 15000 |  | Supervision/Management | Repair | 2 (6-60k) | Complete | Personnel Error - Inattention to detail | Completed |  | The materials included within the scope of below MCRs have been installed prior to the acceptance of these MCRs. 1. CRL-MCR-006307 - __ - Isoflex Multi Layer Seals and Expansion Joints 2. CRL-MCR-008528 - __ - Acoustic Products - Jackets - Acoustic Fan Jackets 3. CRL-MCR-008922 - __ - Multiflag R & Original
| 02SL - Stations (LUL) | Cxxx-NCR-003074 | NCR | STW - Back of House Fire Signs Manufactured Without Approved MCR |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2021-01-29 | 2021-01-25 18:16 | -4 | 2020-12-10 11:39 | Architectural - Signage | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | The static back of house fire signs have been manufactured without an approved MCR. The MCR data has been reviewed by the nominated the Cxxx Fire Engineer, but the MCR did not get uploaded to eB for formal confirmation. NCR has been raised on the back of this.
| 02SL - Stations (LUL) | Cxxx-NCR-003075 | NCR | MEP – [Cxxx-ELEC] STW – No Fault Reporting for the __ __ Luminaires |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2021-06-25 | 2021-07-09 11:43 | 14 | 2021-01-21 14:58 | Electrical - Lighting | 40000 |  | Incorrect Installation | Rework | 2 (6-60k) | Complete | Material/Preservation Problems - Other | Completed |  | There is no evidence that during the testing and commissioning of the DALI lighting control system that the __ luminaires were tested for fault reporting. Two elements are monitored on DALI. 1. A ballast fault, which could indicate, loss of supply, loss of DALI connections or ballast failure. 2. A lamp failure. There are reports from other stations that the __ Easi tube versions are unable to communicate with DALI for ballast and lamp failures.
| 02SL - Stations (LUL) | Cxxx-NCR-003076 | NCR | TUN - Platform Floor Hatch Supporting brackets Installed with Design Issues |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2021-06-25 | 2021-06-25 12:01 | 0 | 2021-02-15 10:44 | Architectural - Flooring | 27500 |  | Manufacturing Defect | Repair | 2 (6-60k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The current installed brackets installed on the floor hatch at platform level do not have an approved fixing detail. These brackets support the crossmembers below the hatch lids as detailed in drawing listed below and supported by calculations report from __/__ Cxxx--X-XCL-M123-56003 Rev 4.0 Cxxx--X-DWG-M123-56001 Rev P06 Cxxx--X-DWG-M123-56002 Rev P02 Cxxx--X-DWG-M123-56003 Rev P09 Cxxx--X-DWG-M123-56300 Rev P02 Cxxx--X-DWG-M123-56301 Rev P02 Cxxx--X-DWG-M123-56302 Rev P02 Cxxx--X-DWG-M123-56303 Rev P02 Cxxx--X-DWG-M123-56304 Rev P02 Cxxx--X-DWG-M123-56305 Rev P02 Cxxx--X-DWG-M123-56306 Rev P02 Cxxx--X-DWG-M123-56307 Rev P02 Cxxx--X-DWG-M123-56309 Rev P03 Cxxx--X-DWG-M123-56311 Rev P03 Cxxx--X-DWG-M123-56318 Rev P02 Cxxx--X-DWG-M123-56319 Rev P02 Cxxx--X-DWG-M123-56321 Rev P02 Cxxx--X-DWG-M123-56322 Rev P02 Cxxx--X-DWG-M123-56335 Rev P02 This is related to 53 hatches on the platform. marked-up General Arrangement drawings attached. The design calulations was reviewed by Cxxx __ structural engineer and a number of queries were raised with respect to the fixing. The response from the supplier was not adequete in clarifying the issue and directed __ to redesign a compliant bracket.
| 02SL - Stations (LUL) | Cxxx-NCR-003077 | NCR | STW: Non Compliant Installation of Asset Labels In Front House Areas |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2021-04-16 | 2021-04-07 12:13 | -9 | 2021-03-31 16:41 | Information Management - Asset Information | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | During VAP 10 (as documented in Cxxx-XRL-Z3-RGN-M123-50005), it was found that asset labels in the toilet areas have been installed in the toilet areas in non compliant locations which are visible to members of the public. Specifically, this is a non compliance against the requirements set out in CRL1-XRL-Z3-GUI-CR001-50071. No relaxation of requirements had been applied for in advance. Specifically: Doors - CRL1-XRL-Z3-GUI-CR001-50071 section 4.26 states that labels should not be installed to the public facing leaf and only the back of house leaf. Some of the doors in the toilet areas have both leaves facing public areas. MEP Equipment - CRL1-XRL-Z3-GUI-CR001-50071 states that "On all components Assets, equipment labels shall be hidden from public view and placed inside equipment housing or behind the equipment’s enclosure, next to the Manufacturer’s label where possible or else in a consistent position". For the assets in the public toilets, this is not possible due to the finishes incorporated. This NCR has been raised to capture this issue.
| 02SL - Stations (LUL) | Cxxx-NCR-003078 | NCR | STW - Assignment of Barrier Gates L Class to Door PFU |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2021-04-27 | 2021-04-26 16:30 | -1 | 2021-04-13 17:13 | Information Management - Asset Information | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | Certain Barrier Gates L4412 have been allocated to the Door System PFU001, which is non allowable configuration state. Typically, Architectural barrier gates should be allocated to the Furniture PFU. This affects the following asset tags: M123-BAF-09879 to M123-BAF-09882 - Sliding Gate at the Eastern Ticket Hall M123-BAF-09883 and M123-BAF-09884 - Transformer Room Sliding Doors M123-BAF-09885 - Service Yard Gate at WTH M123-BAF-09886 to M123-BAF-09888 - 3 __ Gates at the WTH
| 02SL - Stations (LUL) | Cxxx-NCR-003079 | NCR | MEP - Errors on Fire Schematic Identified Following Crossrail Fire Print Out Panel Check |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2021-05-28 | 2021-06-15 17:24 | 18 | 2021-04-16 16:27 | Fire - Detection | 1000 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | Following the Crossrail asset team checks to the Fire Panel Print Out, the following issues were identified: M123-FDA-01134 - mismatch between schematic and asset data against the FPPO M123-FDA-00412 - mismatch between asset data against the schematics and FPPO As a result of investigation, it was found that the following changes needed to made to the asset data and schematics: M123-FDA-01134 - asset to be changed to SID code 1/518. Schematic to be updated M123-FDA-00412 - asset to be changed to SID code 5/514 As a result, this NCR captured the remedial work required for drawing Cxxx--E-DDE-M123_Z-25587 which is already at AB status. This drawing will need to be amended and resubmitted to be correct. Additionally, the following assets were found to be needing to be updated on the Fire Panels which were handed over on the 5th of March: M123-FDA-01134 L18/D86 SID code mismatch with FPPO LU says 2/521 FPPO to be updated to 1/518 for this asset M123-FDA-01181 L22/D76 SID code mismatch with FPPO LU says 7/043 FPPO to be updated to 7/051 for this asset M123-FDA-01160 L26/D59 SID code mismatch with FPPO LU says 7/626 FPPO to be updated to 8/831 for this asset M123-FDA-00747 L29/D08 SID code mismatch with FPPO LU says 1/048 FPPO to be updated to 1/070 for this asset M123-FDA-00447 L29/D108 SID code mismatch with FPPO LU says A/880 FPPO to be updated to A/611 for this asset M123-FDA-00448 L29/D109 SID code mismatch with FPPO LU says A/880 FPPO to be updated to A/610 for this asset M123-FDA-00178 L31/D17 SID code mismatch with FPPO LU says 2/913 FPPO to be updated to 3/070 for this asset As these assets are already handed over to LU and the panel modified during the intergration, (LU's maintainer) will need to undertake the above changes.
| 02SL - Stations (LUL) | Cxxx-NCR-003080 | NCR | MEP - Station TVS/Dali System - Electromagnetic Interference Testing issues |  | Contr | __ | FAR - Farringdon Station (West) |  | 2021-08-31 | 2021-09-22 09:38 | 22 | 2021-04-20 15:45 | Electrical - Electro Magnetic Compatibility | 40000 |  | Design | Repair | 2 (6-60k) | Complete | Design Problem - Other | Completed |  | On 12 February 2021, Cxxx-PMI-01259 was issued to __ Ltd (__) with the instruction to support CRL in undertaking EMC testing between the Cxxx DALI system and the Cxxx Tunnel Ventilation System (TVS). As required within CRL1-XRL-E-GUI-CR001-50006 [1.0] (provided within the aforementioned PMI), __ have prepared a station-specific Test Plan (Cxxx--E-RGN-M123-50939) and issued this on 30 March 2021. This was essentially a two (2) Stage Plan, with Stage [1] being to identify any interference to the DALI system and any further Stage [2] testing to be undertaken to any DALI circuits which failed during the Stage [1] testing process. Following the tests that were carried out, it was discovered that there was interference on a number of the lighting DALI circuits. Specifically, 1. __ carried Stage [1] tests on a day shift on 23 March. This identified that when the tunnel vent fans were running that there was some interference with 5 no. DALI Buswire circuits and that these would have to be investigated further through a Stage 2 test. These 5 no. circuits were as follows: 1.1. East Ticket Hall (ETH): LCM 01-B, LCM 08-A and LCM 30-A 1.2. West Ticket Hall (WTH): LCM 43-A and LCM-53-A 2. It was identified, that the variable speed drives (VSD’s) of the Cxxx Tunnel Ventilation fans were the source of the electromagnetic interference. As per process, __ decided that it was necessary to ensure that an NCR was initiated and, hence, the current NCR was issued on 20 April. 3. On a night shift on 26 May 2021, the Stage [2] test was successfully completed. The findings were as follows: 3.1. With the WTH tunnel vent fans running LCM’s 43 and 53 both lost communications to a large number of light fittings. This was as per the results of the previous tests carried out and __ were confident that no other LCM’s were affected. 3.2. As a sample check, two (2) of the affected fittings were off prior to the fans running. These fittings defaulted to 100% on once the fans started. This demonstrated that the system fails safe, when the fans cause the interference. 3.3. When measuring the level of EMI at each of the affected DALI Buswire circuits, it was found that isolating the supply __’s and removing the Neutrals of the 230V circuits to the effected light fittings reduced the interference enough to be within the required tolerances. In the case of LCM 53 the reduction was close to 90%.
| 02SL - Stations (LUL) | Cxxx-NCR-003081 | NCR | STW - Sample Prototype Benchmark Requirements Not Met |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2021-05-14 | 2021-05-17 13:36 | 3 | 2021-04-27 07:51 | Architectural - General | 1000 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | The Sample / Benchmark / Prototype Table - Cxxx--A-TSC-M123-50027 - has been produced to demonstrate compliance against the Architectural Specification - Cxxx--A-RSP-M123-50057 - for Samples, Benchmarks and Prototypes to be approved by Crossrail prior to works commencing on site. The latest version of the table, revision 5, was last submitted on the 22nd of March 2018 for acceptance. Although the Contractor worked proactively with Crossrail throughout the duration of the contract to agree the exact requirements for samples prototypes and benchmarks, programme restraints in meant these were not always formally recorded and, as a result, some have also been missed since Cxxx--A-TSC-M123-50027 Rev.5.0 was issued in 2018. As a result, this NCR has been raised. The items not formally recorded are shown on the attached excel file - Sample Benchmark Prototype table.xlsx - attached to this NCR. It is noted that this NCR is only for Benchmarks and Samples, all Prototypes and Mockups have been captured correctly via FCDs and records.
| 02SL - Stations (LUL) | Cxxx-NCR-003082 | NCR | ETH - Butchers Ramp missing MCRs |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2021-05-28 | 2021-06-18 16:12 | 21 | 2021-04-27 15:44 | Civil - Civil Engineering General | 3000 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | During the construction of Butchers Ramp, The below MCRs were not raised prior to commencement of works. This NCR is to cover the missing MCRs and can be closed once they are produced. Hardwood door and Frame - Travis Perkins C32/40 Polypropylene fiber mix concrete
| 02SL - Stations (LUL) | Cxxx-NCR-003083 | NCR | TUN - Leaks Through Sprayed Concrete Lining in WTH Escalator Barrel ES1 |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2021-07-30 | 2021-08-27 20:30 | 28 | 2021-06-21 11:51 | Tunnelling - Linings - Sprayed Concrete | 30000 |  | System Defect | Repair | 2 (6-60k) | Complete | External Phenomenon - Not Defined | Completed |  | There have been historic issues with water ingress in Escalator Barrel ES1 - comprising the sprayed waterproofing/sprayed concrete lining forming Escalator Barrel ES1 - dating back to 2017 (SCL works were completed as part of Sub-Packages Cxxx--C4-CER-M123-50070 Rev.1.0 and Cxxx--C4-CER-M123-50086 Rev.3.0, referenced below). Mass-fill concrete steps - onto which Esc.4,5&6 are supported - were cast in ES1 and shaft SH-W3 as part of Sub-Package Cxxx--C-CER-M123-50198 Rev.1.0). This latest leak was observed in January 2021, on the ES1 SCL crown, adjacent to the area of a previous repair. (This was first raised under CRL-OBS-35118 'WTH & PLT Water Ingress Issues' item 3). The exhaustive list of the key communications is appended. Refer to: Cxxx-XRL-V2-LLG-M123-50004 Rev.2.0 'TUN-SCL WTH SH-W3 ES1 Water Ingress Communications/Reports,etc.' -------------------------------------------------------------------------------------------------------------------------------------------------------- Below is a high-level summary of ES1 water ingress/water management: • At the interface between the WTH SH-W3(escalator shaft) and the ES1 tunnel, a drip tray was installed as part of the initial construction back in 2017. o This has pipes on both north and south sides of the tunnel which carry any water collected into the existing gullies at the pit at the base of escalators 4, 5 and 6 (L-6 platform level). o Note: pit was screeded so as to drive water into the gullies (refer to Cxxx-RFI-004443). 1. January 2017: Water ingress through finished SCL walls on both north and south of escalator barrel first recorded above the mass-fill steps (refer to Cxxx-RFI-004341). o May 2017: First round of injenction works in ES1 reinjectable grout hoses carried out to remedy this issue (refer to Cxxx--C4-RGN-M123-51262 Rev.2.0). o June 2017: Second round of injenction works in ES1 reinjectable grout hoses carried out (refer to Cxxx--C4-RGN-M123-51263 Rev.2.0). o July 2017: Further water ingress through finished SCL walls, post-completion of injection works above (refer to Cxxx-NCR-002629). o August 2017: SHW3/ES1 water management system implemented, as injection works were unsuccessful in fully dealing with water ingress (refer to Cxxx-FCD-002868 and Cxxx-NCR-002589). This system includes a 30mm wide x 30mm deep drainage channel constructed within the mass fill stepped ramp on which the escalators sit, which collects any residual water ingress through the SCL. 2. January 2019: New leak through SCL identified at crown of ES1 (refer to Cxxx-EWN-02701). o June 2019: Surface repairs to area of SCL experiencing leak completed using __, as agreed in Cxxx-FCD-003616, and as documented in Cxxx--C4-RGN-M123-51266 Rev.1.0. 3. January 2021: Further leak, adjacent to area previously repaired with __ in June 2019, identified (refer to Cxxx-ENW-02924 and Cxxx-PMC-15341). o In order to mitigate this new, minor leak at the crown of ES1 a second, it was agreed between Cxxx and CRL that a second drip tray be installed – in lieu of any further injection of grout hoses, surface repairs, etc, which have not been entirely successful in the past. - in accordance with the following design drawings: Cxxx--Y-DWG-M123-51675 C03 Escalator West ES1 / Escalator East ES2: Details Drip Tray (__) Cxxx--Y-DWG-M123-51676 C02 Escalator West ES1 / Escalator East ES2: Details Drip Tray (__ - GFRC Panels) o Any water collected is to be directed to the pit at the base of escalators 4, 5 and 6 (L-6 platform level). Based on what has been observed in the past, the water tends to dry out in the channels formed in the mass-fill steps, before it has even had a chance to travel down into the pit. o March 2021: As advised by the Contractor’s site team, CRL are of the understanding that there may be a second area of water ingress through the SCL at the base of the escalator barrel, which is to be verified by the Contractor (refer to Cxxx-PMC-15341) and addressed as part of this NCR, if required. -------------------------------------------------------------------------------------------------------------------------------------------------------- Refer to attached document for sketches and site photos illustrating the issues encountered to date: Cxxx-XRL-V2-LLG-M123-50005 Rev.2.0 'ES1 Summary of Leaks & Site Photos'.
| 02SL - Stations (LUL) | Cxxx-NCR-003084 | NCR | STW - Asset Labels Not Installed In Accordance with Crossrail Standards |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2021-08-05 | 2021-07-30 06:11 | -6 | 2021-07-22 10:16 | Information Management - Asset Information | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | Two issues are identified as outstanding on the Cxxx VAP Report: 1) Circuit Numbers are not provided on asset labels as these were not available at the time of installation 2) Assets with Duplicate DAAIDs on the printed label These are not in accordance with the Crossrail asset labelling standards. Affected labels as follows from the Cxxx VAP: 1) M123-LVD-05609 & M123-LVD-05618 2) M123-HVA-06212
| 02SL - Stations (LUL) | Cxxx-NCR-003085 | NCR | STW - Quality Issues Arising from Asset Checks |  | Contr | BFK | FAR - Farringdon Station (West) |  | 2021-09-10 | 2021-09-06 09:58 | -4 | 2021-08-26 15:43 | Information Management - Asset Information | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | The following two issues have arisen following final asset quality checks on the Cxxx data: 1) The following two assets are named "FILTRATION UNIT XXX" whereas the naming convention should be "DIRT SEPARATOR XXX". Labels have been installed on site using the FILTRATION UNIT XXX code. Assets are: M123-HVA-00348 M123-HVA-00350 2) The Steel Beam and Steel Columns which form the Windposts at multiple levels within the station are currently non compliant. The naming convention requires the pattern used to include a Grid Reference which has not been provided in the Cxxx data.
| 02SL - Stations (LUL) | Cxxx-NCR-003086 | NCR | STW - asset data - Diameter (Millimetres) attribute not populated on 823 tags |  | Crossrail | PDP | FAR - Farringdon Station (West) |  | 2021-09-24 | 2021-09-17 09:28 | -7 | 2021-09-16 17:10 | Information Management - Asset Information | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | "Diameter (Millimetres)" was not populated for 823 tags across five different asset classes which are part of LU FAR MEPA asset data scope. Affected asset classes are: L539121 - Anti-Vibration Mounts L711353 - Expansion Vessel L746211 - Wiring cables L746291 - Control Cables L7662 - Fibre Optic Cable This was discussed with LU and confirmed that LU is not loading "Diameter (Millimetres)" attribute into their asset data management system for five above referenced asset classes. Proposed to leave data as is.
| 02SL - Stations (LUL) | Cxxx-NCR-003087 | NCR | FAR WTH Service Yard Hatch (1-WFH01) Leak |  | Crossrail | XRL | FAR - Farringdon Station (West) |  | 2023-03-03 |  | -25 | 2022-03-03 15:01 | Architectural - Flooring | 30000 |  | System Defect | Repair | 2 (6-60k) | Open | Discipline/Workmanship - Defective construction | IMPLEMENTATION |  | The Project Manager was made aware in December 2021 that the leak at the WTH Service Yard Hatch (WFH-01) has re-surfaced (raised by LU as a Defect, under CRL-NDF-00178). Refer to attached site photos at both Service Yard level and Level -1 Plant Room (space 2/793). Below is also a summary of the two PWKs that detailed the works the Contractor carried out to remedy this prior to Contract Completion: Cxxx-PWK-02885 WTH - Service Yard Hatch Water Ingress (1-WFH01) Closed on 13/09/2021 on the basis of evidence provided by the Contractor, following which it was discovered that that sealing works had not been fully completed, as specified under Cxxx-FCD-004021. Cxxx-PWK-02884 STW - Ceiling Hatches Opening Mechanism & WTH - Service Yard Hatch (1-WFH01) Waterproofing Works Closed on 13/10/2021, further to completion of Cxxx-FCD-004021 mastic works and additional application of Bituthene tape installed around the hatch joints in order to prevent further water ingress into the plant room. The sealing/patching works carried out have proven to be insufficient, even in the short-term. --------------------------------------------------------------------------------------------------------------------------- Note: this issue has already been previously communicated to the Contractor under the following eB communications: Cxxx-PMC-15437 GEN - WTH Service Yard Hatch Defect Cxxx-SND-00137 WTH Service Yard Hatch (1-WFH01) Leak
|  | Cxxx-NCR-000002 | NCR | Omission of flat square washers |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2020-11-20 | 2020-12-23 11:42 | 33 | 2020-11-13 11:18 | Electrical - Cable Management | 0 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Insufficient information made available to the worker. | Completed |  | Specification JY90 - Fixing to Building Fabric, clause JY90.3208 Fixing to Concrete, sub-clause e) states 'Use flat square washers when fixing through slotted holes.' Flat square washers have not been installed in multiple locations throughout the station. NB. This NCR is raised against 'Electrical - Cable Management' as the largest area of scope; this issue is also present across all disciplines.
|  | Cxxx-NCR-000003 | NCR | WTH Vent Shaft - Filling of slipform climber tube voids |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2020-12-03 | 2021-03-05 17:15 | 92 | 2020-11-19 11:55 | Structural Engineering - Grouting | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | Cxxx-RFI-001953 was raised and agreed the casting-in of slipform climbing tubes into the RC walls of the WTH vent shaft to enable the slipform rig to slide vertically. A month later Cxxx-FCD-000228 was raised and agreed the removal of slipform climbing tubes from the RC walls as work progressed. This FCD agreed that the climbing tube voids would be filled with __ __ GP free flow, non-shrink, cementitious grout. Cxxx's response to this FCD requested the review of the grout application method statement. On 13/11/20 __, () requested a site inspection of the vent shaft voids with __, (CRL). As a result of this inspection and further investigation the following issues have been identified: 1. Not all of the slipform climbing tube voids are accessible. See attachment 'Cxxx-NCR-000003 Attachment – Accessible-Non Accessible WTH Vent Shaft Climbing Tubes.' 2. We put a garden hose down one of the open climbing tube voids from the roof. The hose went down 12m's before it was unable to progress further. This is not the full height of the WTH vent shaft slipform. It is not known why the nose stopped at 12m's. 3. A Method Statement has not been provided for the grout works. 4. Not confirmed if the RFI or FCD approach was followed, or if a combination of the RFI and FCD were followed, or what quantity of RFI/FCD combination is built in the WTH vent shaft slipform structure.
|  | Cxxx-NCR-000004 | NCR | Previously installed radio cable has failed its installation test |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2020-12-18 | 2021-05-13 07:24 | 146 | 2020-12-04 06:48 | Communications and Control Systems - Radio | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | __ have carried out an installation test post termination of feeder cable FD3196
|  | Cxxx-NCR-000005 | NCR | Platform DC cabinets/Poor workmanship |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2021-04-30 | 2021-05-14 13:09 | 14 | 2020-12-22 09:53 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The DC cabinet lids/covers on the platforms are malfunctioning due to the bolt holes fixing them to the main body being misaligned this appears to be caused by poor workmanship on the lids.
|  | Cxxx-NCR-000006 | NCR | SWA cable sheath damage to circuit DB-E-LVB09/2 within ETH L-5 Switchroom IV (6/681) |  | Contr | COF | BOS - Bond Street Station (West) |  | 2021-04-30 | 2021-12-03 18:12 | 217 | 2020-12-23 12:17 | Electrical - General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The outer sheath of the 10mm SWA cable supplying 110V Platform socket (DB-E-LVB09/2) out has been damaged exposing the armouring of the cable. Refer to attached report Cxxx-NCR-000006 SAP Report for the location of the damaged sheathing.
|  | Cxxx-NCR-000007 | NCR | Damaged __ Adaptable Box Located on ETH ESS 7 & 8 Level -4 to -3 - Circuit DB-E-B07/4L1 |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2021-02-16 | 2021-02-26 16:54 | 10 | 2021-02-02 12:21 | Electrical - Lighting | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The __ adaptable box on circuit DB-E-B07/4L1 has been damaged and requires replacing. The adaptable box is located on ETH ESS 7 & 8 Level -4 to -3.
|  | Cxxx-NCR-000009 | NCR | Primary & Secondary Earth Mat Cables Terminated to Incorrect Location on Main Earth Bar MEB-E-B5-01 |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2021-03-05 | 2021-02-16 10:56 | -17 | 2021-02-12 14:42 | Electrical - Earthing & Bonding | 0 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | ETH Primary & Secondary Earth Mats should be installed to MEB MEB-E-B5-01 as detailed on Cxxx-SKC-E-DDE-Cxxx-16000 P17 as follows: ETH Primary Earth Mat terminated to the left hand side (of the drawing) of the normally-closed link of MEB-E-B5-01. This side of the MEB is then connected MEB-E-B4-01 via 2 x independent normally-closed earth links. ETH Secondary Earth Mat terminated to the right hand side (of the drawing) of the normally-closed link of MEB-E-B5-01. This side of the MEB is then connected MEB-E-B4-02 via 2 x independent normally-open earth links. HOWEVER, the termination of the cables is as follows (see attached schematic ETH MEB Schematic Cxxx-XRL-E-DDE-Cxxx-16001 X02 DRAFT.pdf): ETH Primary Earth Mat terminated to the RIGHT hand side (of the drawing) of the normally-closed link of MEB-E-B5-01. This side of the MEB is then connected MEB-E-B4-02 via 2 x independent normally-open earth links. ETH Secondary Earth Mat terminated to the LEFT hand side (of the drawing) of the normally-closed link of MEB-E-B5-01. This side of the MEB is then connected MEB-E-B4-02 via 2 x independent normally-closed earth links.
|  | Cxxx-NCR-000010 | NCR | E031 BOS/UPS/E02 By-Pass incorrectly connected to BOS/LV/E/A should be connected to BOS/LV/E/B |  | Contr | COF | BOS - Bond Street Station (West) |  | 2021-05-03 | 2021-04-23 16:09 | -10 | 2021-04-08 09:16 | Electrical - Power Distribution | 10000 |  | Design | Rework | 2 (6-60k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | E031 - BOS/UPS/E02 External By-Pass is incorrectly installed from Level -3 Emergency Switch Room to Level -4 BOS/LV/E/A 5/668. As per CRL1-XRL-E-RGN-CR001-50010 UPS Neutral Switch Arrangement all external By-Pass supplies should be fed from the B switchbaord. 6.2 The Q2 Neutral Switch Arrangement After detailed assessments of the various operational and maintenance scenarios by all those present at the workshop it was determined that a Neutral Switch, designated Q2, was required to ensure that the neutral connection to the UPS was not broken during LV system isolations or maintenance activities. There followed a discussion about the optimum design for this switch, including it’s switching sequences, location, mounting position and housing. The Q2 Neutral Switch connects the neutrals from either LV Switchboard A or B to the UPS output neutral. The UPS system is also connected to an External Maintenance Bypass (EMB) Switch (fed by LV Switchboard B) and an Automatic Transfer Switch (ATS) which provides the A&B dual power supplies to the UPS, refer to Fig.1.
|  | Cxxx-NCR-000011 | NCR | Cxxx-NCR-001246 Advice Not Followed |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2021-03-08 | 2021-02-23 11:28 | -13 | 2021-02-22 14:11 | Civil - Civil Engineering General | 0 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | I carried out a pre-pour inspection for Cxxx-NCR-001246 on 19/02/21. Cxxx's advice in Cxxx-NCR-001246 has not been followed. __'s advice given in Cxxx-RFI-000098 has been followed instead. This is not following NCR procedure. Further to the recent email exchange and conversation can Cxxx please review the attached pre-pour inspection photos and Cxxx-RFI-000098 response and confirm it is ok to build this detail as Cxxx-RFI-000098 response. Linked are the waterproofing detail drawings and photos showing the adjacent complete waterproofing works to the upstands. Internally the upstands will be further protected by floor finishes.
|  | Cxxx-NCR-000012 | NCR | WTH Main Earth Bars SEB-W-B1-08 & SEB-W-B1-09 Installed Within Incorrect Risers |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2021-03-05 | 2021-02-26 17:25 | -7 | 2021-02-24 11:04 | Electrical - Earthing & Bonding | 0 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Upon site inspection it was found that: SEB-W-B1-08 is installed within WTH Electrical Riser 'B' 680, whereas it it is specified to be installed within WTH Electrical Riser 'A' 681. Cxxx-SKC-E-DDE-Cxxx-16000 for the specified location of the MEB. SEB-W-B1-09 is installed within WTH Electrical Riser 'A' 681, whereas it it is specified to be installed within WTH Electrical Riser 'B' 680. Cxxx-SKC-E-DDE-Cxxx-16000 for the specified location of the MEB.
|  | Cxxx-NCR-000013 | NCR | Nuts Loose on WTH Main Earth Bar SEB-W-B1-04 within TV-FCR (2/763) |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2021-03-10 | 2021-02-26 17:17 | -12 | 2021-02-24 15:53 | Electrical - Earthing & Bonding | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | Upon a verification inspection on Cxxx-PWK-00085 (SC1 MEB Pack 7) it was found that the following nuts and bolts where loose: 4 nuts loose on MET Links; 1 nut and bolt on top 300mm 1C cable. NOTE: This MEB was previously inspected during the IRF inspection for Code 1 IRN Cxxx-SKC-E-NOX-Cxxx-50427.
|  | Cxxx-NCR-000014 | NCR | Comms Adaptable Box Installed on Trunking Lid Impeding Fitting of IP4X Wraparound - WTH ESS5 L-4 |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2021-03-10 | 2021-02-26 16:55 | -12 | 2021-02-24 16:17 | Communications and Control Systems - General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | A adaptable box for the Comms System has been install to the trunking lid which will impede the installation of IP4X Wraparound. See attached report 'WTH ESS5 L-4 Issue with Comms Adaptable Box'.
|  | Cxxx-NCR-000015 | NCR | WTH 300mm Earth Cable LUE01 cable lug not fully crimped at MEB-W-B5-01 within WTH SR LV A (6/673) |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2021-04-30 | 2021-05-07 10:19 | 7 | 2021-03-02 15:06 | Electrical - Earthing & Bonding | 1000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Upon inspection it was found that the 3 x crimps to the cable lug of LUE01 was insufficient i.e. the indentation insufficient. The crimping tool used was a __ M18 Force __HCCT-201C Hydraulic Cable Crimper which crimp at 53kN. The cable lug used is a __ A60 style lug. __ recommend the use of a __ 130kN Crimping Tool with a __ ME60-C die set for 3 crimps. __ recommend that 5 crimps be carried out if a 50kN Crimping Tool is being used.
|  | Cxxx-NCR-000016 | NCR | Cable W071 - Brown Phase Conductor Damaged within ATS Lift 8 |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2021-04-01 | 2021-03-19 12:21 | -13 | 2021-03-18 13:16 | Electrical - General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Cable W071; During an inspection on Submain Cable W071, minor damage to inner the insulation of the L1 brown phase conductor was found within ATS Lift 8 (WTH).
|  | Cxxx-NCR-000017 | NCR | Incorrect Cable size used on circuit DB-W-EL02/3L3 |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2021-07-08 | 2021-07-08 08:24 | 0 | 2021-06-24 07:56 | Electrical - Power Distribution | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | On inspection of circuit DB-W-EL02/3L3 it was noticed that the interlinking cables between each light fitting have been wired in 6mm cable instead of the specified 4mm.
|  | Cxxx-NCR-000018 | NCR | WTH General Extract Damper GE-W-FD090 Size |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-04-27 | 2022-04-18 14:55 | -9 | 2022-04-13 16:08 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Incomplete Works | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | This Fire damper missing on site - replaced with 450x500 (instead of 450x450) See also Redline issued for this system: Cxxx-XRL-M-DDA-Cxxx-11123 WTH Ductwork Layout Level-2 Sheet 3 of 4
|  | Cxxx-NCR-000019 | NCR | __ Support Bracket Slotted Holes Cut - DB-E-A05/3L123, DB-E-A05/4L123 & DB-E-B05/3L123 |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2021-05-07 | 2021-06-23 14:34 | 47 | 2021-04-23 12:08 | Consents - General | 2000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During a site inspection on DB-E-A05/3L123, DB-E-A05/4L123 & DB-E-B05/3L123; it was raised that the unistrut support have been cut through the slotted holes. As a means of fixing, the solid edge of the unistrut bracket has also been drilled which may comporomise the structural integrity of bracket.
|  | Cxxx-NCR-000021 | NCR | ETH, level-2, foul sump room 3/772 - Missing water tank plinths |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-06-21 16:48 | -75 | 2021-05-17 08:16 | Civil - Civil Engineering General | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | Further to Cxxx-RFI-005892, two RC plinths should have been built to support two water tanks in room 3/772 at level-2 in the ETH. These got missed. The area has since been screeded and the tanks sit directly on the screed and covering. No resin applied to floor. There is no requirement for these plinths from any discipline other than possibly Structural. If the plinths are required, the tanks will have to be removed and replaced onto plinths or steel spreader plates which impacts __ pipework connections. 1. The location of these plinths can be seen attachment 'SK-MEP-793 - ETH 3-772 Foul Pump Equipment Coordination Review Rev1' (which is an extract of Cxxx-RFI-005892). 2. The north tank (the Cat 5 cold water tank) = 1540kg 3. The south tank (the potable cold water tank) = 1060kg 4. The tanks are supported by 3mm steel rims that run around the perimeter base of the tanks (see pic 1 attached showing the rim, on a tank at another location). The load is transferred through this 3mm thick rim onto the screed. Our mechanical team preference is to use as is because the tanks have been installed and connected (see Pic 2). 5. The applicable slab RC, floor loading and screed drawings are linked. 6. The screed specification is linked. It is not clear if the two water tanks overload the screed construction. Can Cxxx review and advise if it is acceptable to use as is, if not can these tanks be lifted and placed on steel spreader plates or are the RC plinths necessary? If steel spreader plates can be used then can Cxxx please specify these.
|  | Cxxx-NCR-000023 | NCR | Damaged Insulation of 110v cable, Circuit D.B/LVA05/8L1/2 |  | Contr | COF | BOS - Bond Street Station (West) |  | 2021-06-10 | 2021-12-08 12:13 | 181 | 2021-05-27 12:37 | Electrical - LV Equipment | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Upon inspection of 110v circuits installed historically by another sub contractor, it has been noted that the insulation on a live conductor has been damaged. There is no damage to the copper itself. (please see photo attached)
|  | Cxxx-NCR-000024 | NCR | WTH - Damaged Cable PES Lighting - Cxxx-SKA-E-NOX-Cxxx-50369 |  | Contr | COF | BOS - Bond Street Station (West) |  | 2021-06-23 | 2021-07-22 11:51 | 29 | 2021-06-09 12:43 | Electrical - Lighting | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Whist removing trunking lid an electrical A.P came across a live cable with damaged insulation which subsequently came into contact with the CMS causing circuit EL06 1L3 to trip.
|  | Cxxx-NCR-000025 | NCR | Damaged Sub-main cable - W027 - DB-W-A11 |  | Contr | COF | BOS - Bond Street Station (West) |  | 2021-06-24 | 2021-06-11 15:04 | -13 | 2021-06-10 10:57 | Electrical - General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Upon inspection of sub-main W027 cable for D.B-W-A11 it would appear that the brown core of the cable has been damaged. The damage looks to have happened during the glanding of the cable as it is a very thin split, possible caused by the a stripping tool. IRN Cxxx-SKC-E-NOX-Cxxx-50220
|  | Cxxx-NCR-000026 | NCR | Large Acoustic Door - W-01-792-D01 - Damage to paint work on face of door |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2021-06-24 | 2021-10-28 13:46 | 126 | 2021-06-10 13:02 | Architectural - Doors | 10000 |  | Damaged | Repair | 2 (6-60k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Large Acoustic Door - W-01-792-D01 - Damage to paint work on face of door leaf
|  | Cxxx-NCR-000027 | NCR | Short Supply Cable - D.B-W-A05 3L1-Platforms and Tunnels |  | Contr | COF | BOS - Bond Street Station (West) |  | 2021-06-28 | 2021-07-08 15:16 | 10 | 2021-06-14 10:35 | Electrical - General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The SWA supply cable D.B-W-A05 3L1 which feeds CP5 Lighting is too short.
|  | Cxxx-NCR-000030 | NCR | Damaged Neutral Cable DB-W-EL07-2L1 |  | Contr | COF | BOS - Bond Street Station (West) |  | 2021-07-14 | 2021-06-30 18:54 | -14 | 2021-06-30 14:28 | Electrical - General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The sheathing on the Neutral cable on Circuit DB-W-ELO7-2L1 has been found to be damaged. There is no damage to the copper core itself. Please see image attached. The Insulation damage appears to be a friction burn.
|  | Cxxx-NCR-000031 | NCR | Asset Labelling - DAAID Used for Luminaires |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2021-12-23 | 2021-09-14 15:16 | -100 | 2021-06-29 16:01 | Electrical - General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | Design Alternative Asset IDs (DAAIDs) that do not appear on drawings or other design documentation. Please see "Cxxx-EML-01034 - DAAID.jpg" in the "Attachments" section and the relevant drawing "Cxxx-SKC-E-DDA-Cxxx-31140" in the Reference Documents section, as an example. The DAAIDs used follow the format of "Circuit No./Luminaire's position within the circuit", i.e.: "W-EL04/1L3/3". Based on the current Data for BOS, 1533 assets are affected.
|  | Cxxx-NCR-000032 | NCR | Cable Labels - Text Line Three |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2021-12-22 | 2021-11-23 09:47 | -29 | 2021-06-30 09:48 | Electrical - General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | 1. Several asset labels installed do not conform the Asset Identification Standard as the requirement for text line 3 has not been complied with. Additional details (cable size and type) have been added on to the Text Line 3, which are not allowable by the Asset Identification Standard. Below are the records that could be tracked on this matter: Cxxx-RFI-004355 - Asset Labels - Wiring Response to the RFI: “The Contractors proposal to add the cable size to the asset label is not accepted and should not be included on the label.” However, the CCM the subsequent PMC confirm acceptance “to introduce the cable type and size onto the asset label adjacent to the Designers unique reference number”. Cxxx-CCM-02747 - Value Engineering - Cable Labels Cxxx-PMC-02873 - Value Engineering - Cable Labels Important to note that although the above refer to refers to the aspect of the physical labels, it is not clarified how this deviation should be handled in the database. During the meeting on the 9th of June 2021, Crossrail’s Asset Information Team clarified that they have not been made aware of the CCM/PMC agreement, but confirmed that this is a deviation from the requirements and would be raised as a negative observation during a Verification Activity Plan (VAP). 2. Besides the additional detail on the labels, a number of labels do not follow the Convention for the Cable Type on Text Line Three: - Instead of the "CABLE-P:", required by the Standard, "CABLE P -" has been used. - Instead of the "CABLE-E:", "CABLE-E" or "CABLE E" have been used.
|  | Cxxx-NCR-000033 | NCR | Damaged Cables DB-W-LVA05 |  | Contr | COF | BOS - Bond Street Station (West) |  | 2021-07-21 | 2021-07-08 15:13 | -13 | 2021-07-07 10:54 | Electrical - General | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The insulation on a cable in DB-W-LVA05-Way 1 and DB-W-LVA05-Way 6 has been damaged. The internal copper of the circuit cable has not been damaged.
|  | Cxxx-NCR-000034 | NCR | Non Complient Pin Racks installed in Trunking |  | Contr | COF | BOS - Bond Street Station (West) |  | 2021-07-21 | 2021-10-05 14:33 | 76 | 2021-07-07 10:28 | Electrical - Cable Management | 2000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Non Compliant Pin Racks have been installed in the Riser areas WTH and ETH.
|  | Cxxx-NCR-000035 | NCR | DB-W-A06-7L1,7L2,7L3 - WTH - Damaged outer sheathing of SWA |  | Contr | COF | BOS - Bond Street Station (West) |  | 2021-07-29 | 2021-07-16 14:28 | -13 | 2021-07-15 13:12 | Electrical - General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The Outer Sheathing of the SWA cable DB-W-A06-7L1,7L2,7L3 in the WTH tunnel invert level -6 has been damaged during installation, no internal cores have been damaged.
|  | Cxxx-NCR-000036 | NCR | LVB02 Circuit 3 - Damaged 110v Cable |  | Contr | COF | BOS - Bond Street Station (West) |  | 2021-07-30 | 2021-07-22 11:54 | -8 | 2021-07-16 07:20 | Electrical - General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The sheathing on 110v Circuit LVB02 way 3, has been damaged whilst pulling cables through conduits, on level-1 KD8. The inner core on the cables has not been damaged.
|  | Cxxx-NCR-000038 | NCR | DB-W-EL02 2L1 |  | Contr | COF | BOS - Bond Street Station (West) |  | 2021-07-30 | 2021-07-30 15:58 | 0 | 2021-07-16 16:03 | Electrical - General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | It was noted that in the intervening period between completion of dead testing and IRN submission (Cxxx-XRL-E-NOX-Cxxx-50020) an additional luminaire had been added to DB-W-EL02 2L1 in 2/908 increasing the no. of points from 7no. to 8no. Cxxx-XRL-Z-LRG-Cxxx-50016 specified this inclusion. The circuit was only ever energised after dead retesting was performed, to take account of the extended installation. This is evident in the attached revised test certification were the R1+R2 and R1-Rn values have increased from 0.78 ohms to 1.00 ohms.
|  | Cxxx-NCR-000039 | NCR | E053 - Non Fire Rated Cable Installed |  | Contr | COF | BOS - Bond Street Station (West) |  | 2021-08-05 | 2021-10-07 13:55 | 63 | 2021-07-22 13:27 | Electrical - General | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | QA have gone to inspect the previously installed installation and have found the B supply to the ATS within the Watermist Room 5/398 is the incorrect type of cable. It is Non fire rated when it should be fire rated.
|  | Cxxx-NCR-000040 | NCR | DB-W-B02 IRN Test Certification |  | Contr | COF | BOS - Bond Street Station (West) |  | 2021-08-05 | 2021-08-03 09:46 | -2 | 2021-07-22 19:01 | Electrical - General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | The contractor notifies the client that the incorrect electrical test certification was submitted with the IRN SAF (Site Assurance File) Cxxx-XRL-E-LRC-Cxxx-50019. The certificate provided did not capture design changes associated with CCT 2L1 (Cxxx-FCD-000095) and CCT 5L2 (Cxxx-FCD-000094). The contractor confirms all other relevant information pertaining to the associated FCD's were identified in the SAF and refer the client to page 76 where each FCD's are denoted. The contractor confirms both circuits were retested after design changes were implemented and point to the dead testing dates which occurred after each respective FCD was raised. The no. of points (6no.) for each now align with the drawings submitted in the IRN SAF - DB-W-B02 (Dead Test Verified) SC2.PPC.pdf The contractor notes that when both circuits were retested lower than desired IR readings were recorded and associated Cxxx-PWK-00331 has been raised to identify/monitor/rectify. #Update 28/07/2021# The test sheets incorrectly denoted 5no. of points instead of 6no. for both CCT 2L1 & 5L2. This has since been correctly updated in DB-W-B02 (Dead Test Verified) SC2.PPC.pdf. Note - the resistance readings never changed as the values for each were always reflective of 6no. points as installed however, a retest before IRN submission noted a change in the IR readings. Cxxx-PWK-00331 was not raised at IRN submission stage as incorrect certification had been provided.
|  | Cxxx-NCR-000041 | NCR | DB LVB09-2 Damaged SWA sheaving |  | Contr | COF | BOS - Bond Street Station (West) |  | 2021-08-06 | 2021-07-26 11:39 | -11 | 2021-07-23 13:09 | Electrical - General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Upon inspection an SWA cable installed by previous contractors __ has been found to be damaged. The cable is part of circuit DB LVB09 way 2, the damage to the cable can be found to in room 6/681. The outer sheaving of the cable has split the internal cores and SWA remain intact.
|  | Cxxx-NCR-000042 | NCR | DB-E-EL02 Insufficent Slack to facilitate future maintainance. |  | Contr | COF | BOS - Bond Street Station (West) |  | 2021-08-06 | 2021-07-28 10:24 | -9 | 2021-07-23 14:40 | Electrical - Cable Management | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Colonnade Lighting supplies fed from DB-E-EL02 7L3,8L1,8L2,8L3,9L1,9L2, do not have enough slack to facilitate future maintenance of D.B as required by ITP.
|  | Cxxx-NCR-000043 | NCR | DB-W-EL02 4L1 |  | Contr | COF | BOS - Bond Street Station (West) |  | 2021-08-29 | 2021-08-17 12:54 | -12 | 2021-08-15 22:24 | Electrical - General | 3000 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | It was noted post IRN acceptance (Cxxx-XRL-E-NOX-Cxxx-50020) that the installation had not captured required design changes specified in Cxxx-FCD-000116. The installation has been modified to incorporate 1no. additional luminaire, increasing the total no. of points from 7no. to 8no. QA inspection sheets and electrical test certification (dead/live) have been produced to provide the necessary assurance evidence. The contractor intends on submitting the attached DB-W-EL02 (Dead Tested Verified) SC2_PCC_REV3.pdf at PCC stage, noting it covers the full scope of the as installed condition.
|  | Cxxx-NCR-000044 | NCR | DB-W-B03 1L2 |  | Contr | COF | BOS - Bond Street Station (West) |  | 2021-08-24 | 2021-08-16 07:43 | -8 | 2021-08-10 08:59 | Electrical - General | 2000 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | It was noted post IRN acceptance (Cxxx-XRL-E-NOX-Cxxx-50113) that the installation had not captured required design changes specified in Cxxx-FCD-000078. The installation has been modified to incorporate the additional 2no. luminaires, increasing the total no. of points from 6no. to 8no. QA inspection sheets, electrical test certification (dead/live) have updated redline Cxxx-XRL-E-DDA-Cxxx-31120 X03.pdf have been produced to provide the necessary assurance evidence. The contractor intends on submitting the attached DB-W-B03 Dead_Live_Tested 09.08.2021.pdf at PCC stage, noting it covers the full scope of the as installed condition.
|  | Cxxx-NCR-000045 | NCR | WTH, Level +3/4 Intake/Extract Louvres - RC Structural Opening Expansion |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2021-08-13 | 2021-09-23 17:11 | 41 | 2021-07-30 14:02 | Civil - Structural Engineering | 3000 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | The installation of the platform intake/extract louvre (WTH L+3/4, Gridline A, between Gridlines 2 & 3) was unsuccessful due to the structural opening not being large enough to accept the louvre and the fixing brackets. A survey undertaken on the assembled louvre vs the structural opening prior to lifting it into place revealed that an additional 15mm around the full perimeter of the structural opening is required in order to install the louvre. Please refer to attached marked up drawing 'Louvre Location' and referenced drawings Cxxx-SKC-S-DWG-Cxxx-50419, Cxxx-SKC-S-DWG-Cxxx-50424 & Cxxx-SKC-S-DWG-Cxxx-50436 for further details of the RC structure & reinforcement detail.
|  | Cxxx-NCR-000047 | NCR | Exist sign restricts maintenance activity access to Fire Damper __ Actuator |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-08-27 | 2022-07-22 12:07 | -36 | 2022-06-28 09:51 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Previous Construction - Not Defined | Completed |  | The current light fitting / way out sign installation restricts access to the __ Actuator for future maintenance activities. refer attached 2x photographs. -
|  | Cxxx-NCR-000048 | NCR | Diverse Fibre PLC Safety Critical Cable Route Compromised |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-02-11 | 2022-01-28 17:16 | -14 | 2022-01-28 16:00 | Communications and Control Systems - Fibre Optic Network | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Non-compliance to the specification Cxxx-SKC-M-RSP-Cxxx-50039 MEP Specification – JW60- central Control/Building Management (BMS/Scada) - JW60.1302: under clause JW60.1302 TCP/IP Network item b. Refer to C443-ELE-O8-DWG-Cxxx-50020 and Surveillance report attachedCxxx-XRL-O4-RGN-Cxxx-50004 Rev 1.0
|  | Cxxx-NCR-000049 | NCR | Labelling - Auto Transfer Switches and associated wiring cables |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-07-15 15:11 | -51 | 2021-08-06 13:04 | Information Management - Asset Information | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | A number of labels installed for Auto Transfer Switches and associated wiring cables have been confirmed as being incorrect, containing incorrect text lines or inconsistent information across the labels of linear (wiring cables) and point assets (ATSs).
|  | Cxxx-NCR-000051 | NCR | ETH, Level 0, Incorrect Earth Pit Construction |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2021-09-17 | 2021-09-14 12:37 | -3 | 2021-09-03 10:04 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | It has been found that the ETH earth pits installed at level 0 around the perimeter of the ticket hall have had their drainage pipes infilled with grout. It is thought that the OSD Contractor did this when carrying out their floor finish works in these areas as the pre and post pour inspections did not pick this issue up at the time.
|  | Cxxx-NCR-000052 | NCR | ETH - Incorrect fixings, __ Channel Cast |  | Contr | COF | BOS - Bond Street Station (West) |  | 2021-09-15 | 2021-10-01 14:09 | 16 | 2021-09-01 13:57 | Electrical - General | 3000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The wrong type of fixings have been used in Eastern ticket hall coffer __ channel cast. It has been found that the fixing’s used in the ETH Coffer channels casts are normal 10mm Channel nuts. These nuts are not fit for purpose as the do not turn properly in the channel, causing them not to bite. The fixings required for this type of channel is a Xylan coated __ fixing. It is currently in an unsafe state as the majority of the fixings are not even biting in the channel. Please note: This installation was carried out by .
|  | Cxxx-NCR-000053 | NCR | DB-W-A02 4L1 |  | Contr | COF | BOS - Bond Street Station (West) |  | 2021-08-29 | 2021-08-26 08:16 | -3 | 2021-08-24 06:28 | Electrical - General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | It was noted post IRN acceptance (Cxxx-XRL-E-NOX-Cxxx-50018), the redline included within the SAF pack (Cxxx-XRL-E-LRC-Cxxx-50018) associated with it, captures Circuit 4L1 with only 3 points instead of 6 points (as installed and captured by T&C within the test sheet) The T&C contractor confirms that the documentation submitted and signed off at PCC stage (Phase 2.2) reflects correct installation. Redline Cxxx-XRL-E-DDA-Cxxx-31100 X03 to be attached to this NCR for close-out.
|  | Cxxx-NCR-000054 | NCR | Toilet Extract Fire Damper TE-W-FD010 access blocked by CMS - Cxxx-IRN-50034 __-00269 |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-11-16 17:22 | 73 | 2021-08-27 14:12 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | Toilet Extract Fire Damper TE-W-FD010 on toilet extract ductwork running through Ancillary Ventilation Room FAN II 2/767 (to disabled toilet area in Lobby 2/085) has its access blocked by CMS installed beneath it. See attached photos
|  | Cxxx-NCR-000055 | NCR | WTH, Level-4 Buildersworks - Cxxx-RFI-003462 advice not followed |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2021-09-09 | 2022-04-08 13:30 | 211 | 2021-08-26 16:28 | Civil - Civil Engineering General | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | I was asked to carry out a post core inspection for Cxxx-RFI-003462 on 25/08/21. We Feroscanned the west elevation of the wall and it was determined that we had cut several horizontal reinforcement bars. This is not in alignment with Cxxx-RFI-003462 direction. No vertical bars detected as being cut. Unable to inspect cored surfaces as grout had been applied to them. * Photos attached were taken of the west elevation of the wall on 25/08/21. * Material Compliance Records attached for possible remedial work solutions.
|  | Cxxx-NCR-000057 | NCR | Incorrect Drawing in SAF Pack |  | Contr | COF | BOS - Bond Street Station (West) |  | 2021-09-16 | 2021-09-02 14:35 | -14 | 2021-09-02 08:11 | Electrical - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The DWG included in the IRN SAF (Cxxx-XRL-E-LRC-Cxxx-50132) does not reflect changes as per Cxxx-XRL-E-DDA-Cxxx-72120 listed in RIR Cxxx-XRL-Z-LRG-Cxxx-50006. The physical installation at time of the IRN reflect the changes as outlined in dwg Cxxx-XRL-E-DDA-Cxxx-72120 and was tested and inspected in this condition. Please note testing was repeated post IRN as part of the close out evidence for closure to PWK Cxxx-PWK-00284.
|  | Cxxx-NCR-000058 | NCR | Post IRN Design Change |  | Contr | COF | BOS - Bond Street Station (West) |  | 2021-09-24 | 2021-09-30 10:53 | 6 | 2021-09-10 08:41 | Electrical - General | 2000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | An additional FCU has been installed for an LCM post IRN on circuit D.B-E-B05/9L1. Cxxx-FCD-000145 has been raised which details these works.
|  | Cxxx-NCR-000059 | NCR | Fire door clash/Design has not been not fully coordinated |  | Contr | COF | BOS - Bond Street Station (West) |  | 2021-09-24 | 2022-04-08 14:25 | 196 | 2021-09-10 13:10 | Electrical - General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Due to the need to facilitate the Air release system, the fire doors have been repositioned, causing them to clash with the adjacent light fittings. These changes are captured on Cxxx-FCD-000134. The Lights affected by these changes are fed from Circuit DB-W-EL07/2L3.
|  | Cxxx-NCR-000060 | NCR | Post IRN & PCC Design change DB-W-EL04 1L3 & 6L1 |  | Contr | COF | BOS - Bond Street Station (West) |  | 2021-09-27 | 2022-04-22 14:49 | 207 | 2021-09-13 12:07 | Electrical - General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | This NCR has been raised to capture the assurance of the electrical works as this design change has been made post IRN & PCC. The affected lighting circuits for this design change are DB-W-EL04 1L3 & 6L1.
|  | Cxxx-NCR-000061 | NCR | L/LVA07/5 - Damaged Cable |  | Contr | COF | BOS - Bond Street Station (West) |  | 2021-12-22 | 2021-12-22 14:36 | 0 | 2021-12-08 12:58 | Electrical - General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Upon inspection of circuit W/LVA07/05 the outer sheaving of one of the cables was found to be damaged. The integrity of internal copper remains intact. The leg that is damaged goes into TXB, in order to replace we would require an isolation of the transformer room and possibly the erecting of permanent scaffold to install the cable.
|  | Cxxx-NCR-000062 | NCR | Water Damaged CMS - WTH Level -1 |  | Contr | COF | BOS - Bond Street Station (West) |  | 2021-09-28 | 2022-01-12 12:20 | 106 | 2021-09-14 12:39 | Electrical - Cable Management | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | External Phenomenon - Weather or ambient condition | Completed |  | The CMS at the bottom of ESS 3 Level -1 has been found to have water damage. The riser had not been made water tight prior to CMS Installation.
|  | Cxxx-NCR-000063 | NCR | Damage to sub main cable W016 |  | Contr | COF | BOS - Bond Street Station (West) |  | 2021-09-30 | 2021-09-20 10:02 | -10 | 2021-09-16 10:19 | Electrical - General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The outer sheaving on a Sub-Main cable W016 located on Level +1 Rm B/776 has been damaged. The internal Sheaving and copper of the cable has not been damaged.
|  | Cxxx-NCR-000064 | NCR | DB-W-EL04 6L2 Post IRN/PCC Design Change |  | Contr | COF | BOS - Bond Street Station (West) |  | 2021-09-30 | 2022-01-25 11:18 | 117 | 2021-09-16 14:21 | Electrical - Lighting | 3000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | This NCR has been raised to capture the assurance of the electrical works as this design change has been made post IRN & PCC. These design changes have been captured on Cxxx-FCD-000141. The affected lighting circuit for this design change is DB-W-EL04 6L2.
|  | Cxxx-NCR-000065 | NCR | Post IRN/PCC Design Change Circuit DB-W-A04 1L3 |  | Contr | COF | BOS - Bond Street Station (West) |  | 2021-11-15 | 2021-11-09 09:28 | -6 | 2021-11-01 14:11 | Electrical - General | 3000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | Due to relocation of the fire fighting lobby doors a design change has had to be made to the lighting layout post IRN/PCC stage. This change is to avoid a clash between the doors and adjacent lights. This design change been captured on Cxxx-FCD-000144 and affects Circuit DB-W-A04 1L3. This NCR will capture the assurance documentation, dead/live testing and associated Red line drawings.
|  | Cxxx-NCR-000066 | NCR | Lift 8 - Level -2 - __ Drainage Channel too high |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2021-10-06 | 2021-10-21 11:09 | 15 | 2021-09-22 14:00 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Due to installer error, the cast-in blucher drainage channel has been installed approximately 10mm too high outside of lift 8 level -2. Due to this, the falls in the location would allow water to flow back towards the lift itself, and the channel would not function as per its intended use.
|  | Cxxx-NCR-000067 | NCR | Western Ticket Hall - Lightning Protection - Unable to find earth cable at DC 8 connecting to down pile |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2021-09-28 | 2022-04-01 10:54 | 185 | 2021-09-21 10:16 | Electrical - General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Location: WTH, Ground 0 DC number: DC 8 Details: Civils have made aware to the Electrical team that the DC 8 Earth cable from DC8 earth pit to the down pile cannot be found. Civils have progressed works in the expectation that DC 8 up conductor can be connected to either DC 7 or DC 9 to ensure continuous continuity to the Earth Mat for DC 8. A suitable furse 3 way connection point will need to be housed within the adjacent DC's either 7 or 9.
|  | Cxxx-NCR-000068 | NCR | WTH Vent Shaft __ Door Scabbling |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2021-10-05 | 2022-06-01 13:55 | 239 | 2021-09-21 12:40 | Civil - Civil Engineering General | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | Shown attached are the areas required for localised scabbling around the L+0 vent shaft doors. __ gate steelwork is clashing with the concrete structure and as such needs to be broken back to allow for works to continue. 15-17mm is required to be removed and 2-5mm __ ST05 reapplied to provide sufficient cover.
|  | Cxxx-NCR-000069 | NCR | Damaged Sheaving Brown Cable - D.B-E-B02 1L2 |  | Contr | COF | BOS - Bond Street Station (West) |  | 2021-10-11 | 2021-09-30 11:18 | -11 | 2021-09-27 13:30 | Electrical - General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Whilst replacing lid onto a live trunking the brown cable on circuit D.B-E-B02 1L2 was damaged, causing the circuit to trip. There is no damage to the copper just the outer sheathing.
|  | Cxxx-NCR-000070 | NCR | P&T - CP7 blocked rodding eyes L-5 (Cxxx-PWK-01063) |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-03-11 | 2022-05-27 12:12 | 77 | 2022-02-25 14:32 | Civil - Drainage | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Contamination | Completed |  | Following CCTV surveys undertaken to close out Cxxx-PWK-01063, there are two evaporation drains which require rectification works in order to clear obstructions within them. These drainage runs are both in CP7 and are referenced RE13-CP7 & RE14-CP7 in the CCTV report & videos included with Cxxx-PWK-01063. RE13-CP7 is blocked by what appears to be cementitious debris, and RE14-CP7 contains what appears to be a cementitious slurry in the bottom of the pipe which is reducing the cross section by 10-15%.
|  | Cxxx-NCR-000071 | NCR | Incomplete QA for ETH Earthing Pits |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2021-10-18 | 2021-11-01 10:50 | 14 | 2021-10-04 06:43 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | During the compilation of the existing records for the record pack relating to the ETH Earthing pits it has been noted that there isn't enough information for the earth pits to satisfy the Quality Assurance requirements. Missing records include Pre & post pours for some of the earth pits and no cube results for any of the earth pits. Additionally there are post pour comments were there is no evidence for the issues raised were closed out and inspected. Please refer to attachment 'Earthing Pits QA - Overview' for more information.
|  | Cxxx-NCR-000072 | NCR | Rain Water Damaged to CMS - WTH OSD to Level -1 ESS3 and Interchange Level -3 |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2021-10-22 | 2022-01-07 15:24 | 77 | 2021-10-05 16:37 | Electrical - Cable Management | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Route cause of rain water ingress: The design of the permanent works does not effectively manage storm weather events on the WTH, level+1 slab. The temporary drainage system installed under Cxxx-RFI-000026 was not sufficient to deal with last nights weather event. Electrical Systems affected / areas : - ESS3 staircase Level 0 to Level -1 and lobby areas 1/579 at -1 CMS/ electrical accessories LT02 - Vertical CMS within switch room 1/661 CMS/ electrical accessories LT01 - Interchange lobby 4/083 CMS/ electrical accessories - Interchange lobby 4/071 in long corridor leading to L7 CMS/ electrical accessories PDF mark ups attached as LT1, LT2, LT3.
|  | Cxxx-NCR-000073 | NCR | Traction bond to DB-W-A09 found cut |  | Contr | COF | BOS - Bond Street Station (West) |  | 2021-10-20 | 2021-10-08 09:54 | -12 | 2021-10-06 13:59 | Electrical - Earthing & Bonding | 1000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | External Phenomenon - Theft, tampering, sabotage, or vandalism | Completed |  | Whilst preparing to live test DB-W-A09 SC3 Circuits, T & C team found that the traction earth bond from SEB-W-B5-03 had been 'cut' by others before AP team were to energise.
|  | Cxxx-NCR-000074 | NCR | DB-E-B01/4L1 Damaged Neutral Cable |  | Contr | COF | BOS - Bond Street Station (West) |  | 2021-10-21 | 2021-11-03 15:24 | 13 | 2021-10-07 12:08 | Electrical - General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Whilst the T & C team were carrying out their dead tests 2 faults were found on the same Neutral cable on circuit DB-E-B01/4L1. The damaged cable is located on level +0.5 A072 and Ground floor 1/821 in both instances the outer sheaving of the cable has been damaged, however there is no damage to the inner copper cable itself.
|  | Cxxx-NCR-000075 | NCR | Damage to main door for HV Room 6/674. |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2021-10-25 | 2022-02-21 14:38 | 119 | 2021-10-11 11:38 | Architectural - Doors | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Personnel Error - Other human error | Completed |  | Whilst on an inspection for earthing within room 6/674 it was noticed that the right hand door, low level, has a large dent to the bottom section. Pictures attach to this NCR along with a PDF mark up show the location and extent of damage. This damage has also been made aware to __ on the 11/10/2021 and it was concluded that I will raise this via an NCR.
|  | Cxxx-NCR-000076 | NCR | Damaged Cable circuit DB-W-B05 2L2 |  | Contr | COF | BOS - Bond Street Station (West) |  | 2021-10-26 | 2021-10-18 09:56 | -8 | 2021-10-12 12:18 | Electrical - Lighting | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | A cable on lighting circuit DB-W-B05 2L2 has been found damaged in the WTH level -5 CP1 & CP2 area. The T & C team were preparing to live test and the damaged cable caused the circuit to trip. Upon further inspection it was found that the insulation on the cable had been damaged however the internal core of the cable remains in tact.
|  | Cxxx-NCR-000077 | NCR | Incorrect AMP Isolator Installed for Fire Alarm Supply Panel |  | Contr | COF | BOS - Bond Street Station (West) |  | 2021-10-28 | 2021-10-18 11:56 | -10 | 2021-10-14 08:49 | Electrical - LV Equipment | 1000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During the witnessing of the Live Testing on circuit W029C Fire Alarm Panel supply the CRL FAE noticed that the Isolator installed for the panel was a 25A Cxxx. The associated Drawing Cxxx-SKC-E-DDA-Cxxx--21150 and Cxxx-FCD-000166 states that the Isolator installed should in fact be a 40Amp Cxxx. This panel is located on level -5 6/787 WTH
|  | Cxxx-NCR-000078 | NCR | Partially removed insulation on GE Plenum ETH -5 for IRN-M-50045 |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2021-11-01 | 2022-02-23 16:41 | 114 | 2021-10-18 08:35 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Insulation around Extract Plenum in the doorway between ETH -5 room 6/902 and Corridor 6/229 has had it's insulation partially removed to gain access to Comms junction box, compromising the full thickness of the fire-protection in a small area.
|  | Cxxx-NCR-000079 | NCR | Incorrect Isolation device installed for __ BMS CE |  | Contr | COF | BOS - Bond Street Station (West) |  | 2021-11-02 | 2021-10-22 15:32 | -11 | 2021-10-19 07:38 | Electrical - LV Equipment | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | 2 x __ BMS Control Enclosures have had 25Amp Isolators installed where the design states FCUs are to be installed. The first panel is located in the ETH, Level -5 LCR room, 6/778, and the second is located in the ETH, Level -5, Unallocated 6/902.
|  | Cxxx-NCR-000080 | NCR | DB-E-UPS03/8L1,L2,L3 - Damage to __ gate supply cables |  | Contr | COF | BOS - Bond Street Station (West) |  | 2021-11-02 | 2021-10-28 14:23 | -5 | 2021-10-19 08:43 | Electrical - General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | All 3 phases of the supply cable DB-E-UPS03/8L1,L2,L3 have been damaged whilst running in the final part of the Circuit. The damage is what I would describe as scuffing, and has occurred on the outer sheaving of the cables only. There is no damage to the inner cable protection.
|  | Cxxx-NCR-000082 | NCR | P&T - Discolouration of Granazzo Cem Floor Tiling in Certain Areas of the Platforms - LEVEL -5 |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-05-27 | 2022-05-05 09:50 | -22 | 2021-10-29 15:10 | Architectural - Flooring | 500 |  | System Defect | Repair | 4 (0.5-3k) | Complete | External Phenomenon - Not Defined | Completed |  | The Granazzo Cem floor tiling was laid in 2018 and then covered with a layer of ply/cordex protection until 2020 when the protection was removed. Following this, the platform and AP corridor floor tiling was thoroughly cleaned in March & April and signed off as acceptable by CRL architects. During the first week of June, patches of discoloured tiling were noted on the Eastbound platform between CP5 and 7. Various cleaning trials have been carried out on certain areas and laboratory testing carried out with results to follow.
|  | Cxxx-NCR-000084 | NCR | Western Ticket Hall - LPS - Earth Matt Inspection Pits - Unknown copper tape connection - Room 6/673 , 6/664. |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2021-11-29 | 2022-02-28 14:58 | 91 | 2021-11-15 15:10 | Electrical - Earthing & Bonding | 500 |  | Incomplete Works | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Details of Defect: Whilst on a formal inspection for other works within room 6/673 and 6/664 it was noticed by FAE (Electrical) __ that 2 earth pits (1 pit in each room) was not sitting correctly in the housing and as a result was causing a trip hazard. Upon further investigation when the lids got lifted it was found that there are 1x earth copper tape within each pit that appears to have no connection to the single copper tape that comes from the main earthing system earth bar. There are 2 PDFs attached to this NCR. NCR 6.664 pdf and NCR 6.673 pdf. Within these PDFs shows the unknown tapes.
|  | Cxxx-NCR-000086 | NCR | DB-E-LVA06 Post IRN Design change |  | Contr | COF | BOS - Bond Street Station (West) |  | 2021-11-22 | 2021-11-15 14:18 | -7 | 2021-11-08 13:36 | Electrical - General | 3000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | The test results for circuit DB-E-LVA06/3 indicate the max permissible volt drop has been exceeded. The original design specified the circuit length at 35mtr however it is actually 120mtr. Unfortunately this error was only identified post-IRN.
|  | Cxxx-NCR-000087 | NCR | Damaged cables found during trunking upgrade. |  | Contr | COF | BOS - Bond Street Station (West) |  | 2021-11-23 | 2022-01-13 16:26 | 51 | 2021-11-09 09:41 | Electrical - General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Whilst carrying out the CMS upgrade specified in Cxxx-FCD-000180 a number of damaged cables have been found within the trunking. The damage has occurred on cables EL04/6L1 Live, 5L3 Live, 2L2 Live & 3L3 Neutral. The damage is to the insulation only the fire rating has not been affected. The location of the trunking upgrade is DB-W-EL04 to circ area 5/072.
|  | Cxxx-NCR-000088 | NCR | Circuit E-EL07/6L1 Omitted in error |  | Contr | COF | BOS - Bond Street Station (West) |  | 2021-11-25 | 2021-11-16 12:49 | -9 | 2021-11-11 10:55 | Electrical - General | 5000 |  | Planning | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | After reading Cxxx-RFI-004681 It was thought that Circuit E-EL07/6L1 which supplies illuminated signage level -5 was to be omitted, however there was only meant to be 1 point that was removed from the circuit (non Illuminated Sign above PHPs) the other 2 points were to remain. The D.B has now been IRN'ed without a circuit which is still required.
|  | Cxxx-NCR-000089 | NCR | MCC-E-03 - Failed earth lug crimp at A-End for AHU Electric Heater in MCC Panel |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2021-11-29 | 2022-02-01 09:36 | 64 | 2021-11-15 14:18 | Electrical - Switchgear | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | It has been identified that within the A end AHU Electric heater termination section of the MCC-E-03 panel there was an incorrect crimping of a Earth lug to the main MET section within that cubical. The lug itself appeared to be under crimped and not of the usual __ type lug and crimper die. Due to no place holder on Eb for IRN I have linked to Cxxx SAF and IRN until there is a place holder under C443 contract for MCC-E-03. Request sent to Cxxx on 15/11/2021.
|  | Cxxx-NCR-000090 | NCR | Damaged Cable - Circuit DB-E-B01/2L1,L2,L3 |  | Contr | COF | BOS - Bond Street Station (West) |  | 2021-11-29 | 2021-11-16 16:35 | -13 | 2021-11-15 10:00 | Electrical - General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Post Installation of 3rd party winch cabling, the associated circuit was re-dead tested and identified an insulation resistance fault between L3 and CMS (A/072). Inspection also noted further insulation damage at circuit Z end isolator. The integrity of the inner cable remains intact.
|  | Cxxx-NCR-000091 | NCR | Post IRN Design Change WTH-FCR 2/763, MCC 2/777, LCR 2/907. |  | Contr | COF | BOS - Bond Street Station (West) |  | 2021-12-09 | 2022-03-04 14:41 | 85 | 2021-11-25 15:26 | Electrical - Lighting | 5000 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | RIR Cxxx-XRL-Z-RGN-Cxxx-50022 1.0 on eB which makes changes to the lighting layout on circuits DB-W-A02/2L1 and DB-W-EL02/2L2 which affects rooms FCR 2/763, MCC 2/777, LCR 2/907. These circuits have already been IRN’d and PCC’d therefore the assurance for these circuits will need to be redone and recorded on this NCR.
|  | Cxxx-NCR-000092 | NCR | DB-E-EL02 - Incorrect circuit cable sizes |  | Contr | COF | BOS - Bond Street Station (West) |  | 2021-12-02 | 2021-11-23 15:15 | -9 | 2021-11-18 14:21 | Electrical - Lighting | 5000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Whilst Testing DB-E-EL02 the T & C team discovered that circuits 2L1, 2L2, 2L3, 3L1, 3L2 & 3L3, have been wired in 4mm cable where the __ states the circuits should be wired in 2.5mm.
|  | Cxxx-NCR-000093 | NCR | ETH Material Surveillance check |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2021-12-02 | 2022-05-13 14:37 | 162 | 2021-11-18 15:18 | Electrical - Cable Management | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | On a routine surveillance check on the ETH Chiller room ( Level 1 AKA ground floor) it was identified that the support bracket had no stamp markings on whereas other brackets carried the imprinted UNISTRUT logo. The FAE believes that these non stamped unistrut plates are not from the manufacturer of __ and thus will require evidence that these unistrut accessories carry an approved MCR. An email will be raised to ***( see attached in attachment section) to provide evidence of the MCR approved accessories.
|  | Cxxx-NCR-000094 | NCR | Water Damage to Totem |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-07-21 11:42 | -45 | 2021-11-19 12:38 | Electrical - General | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Optilight have raised an issue with water damage when replacing some of the Totem light LEDs level -5. It would seem that the water has blown the drivers for the LEDs.
|  | Cxxx-NCR-000095 | NCR | Light fitting installed on incorrect circuit |  | Contr | COF | BOS - Bond Street Station (West) |  | 2021-12-03 | 2021-11-24 09:44 | -9 | 2021-11-19 16:36 | Electrical - General | 3000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | As explained in Cxxx-FCD-000009 a light was to be added to circuit DB-W-EL03/1L2, unfortunately the site team installed the light on circuit DB-W-ELO3/1L3.
|  | Cxxx-NCR-000096 | NCR | Proof Load testing has not been carried out by UKAS accredited Contractor |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2021-12-29 | 2022-04-08 15:00 | 100 | 2021-11-19 16:05 | Architectural - Doors | 0 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not qualified | Completed |  | A planned surveillance was carried out on the installation and Assurance of Doors by Cxxx. During a review of ITP deliverables it was noted that Bramley Engineering Ltd who carried out the pull testing, were not UKAS accredited. UKAS accreditation is a Works Information requirement and is referenced in Cxxx-COF-A-ITP-Cxxx-*50009 (Rev 2) Inspection Number 2.6.
|  | Cxxx-NCR-000097 | NCR | Testing Off-Site ‘Wind Resistance Testing’ has not been carried out as required in the the Architectural Specifications. |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2022-01-03 | 2022-01-24 16:00 | 21 | 2021-11-24 16:29 | Architectural - Doors | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | A surveillance was carried out on the compliance of fire doors installed in Tunnel Vent Shaft (TVS) locations. A noise and pressure report were issued by Cxxx ‘Internal Noise and Pressure Requirements Cxxx-__-H-RGN-CRG03-50035 (rev 4). On checking the compliance of the Installed doors at Bond Street Station, the Material Compliance Record (MCR) ‘__ __ door’ Cxxx-SKC-A-LRC-Cxxx-50203 (Rev 3), it was found that the MCR contained calculations for 3Kpa pressure rating, but did not contain testing evidence to validate the calculations. Which is a requirement of the Bond Street Architectural Specification.
|  | Cxxx-NCR-000098 | NCR | Non MCR approved material installed - exit maglock supplies |  | Contr | COF | BOS - Bond Street Station (West) |  | 2021-12-10 | 2022-02-02 12:57 | 54 | 2021-11-26 10:54 | Electrical - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | The materials used to facilitate the installation of the north façade exit maglock supplies do not have an approved MCR. However the materials that have been used are in line with Cxxx-FCD-000229. MCR approval for the below materials has now been submitted. • CRL-MCR-009538 - A9C22112 iCT 16A 230V Contactor • CRL-MCR-009539 - Acti9 A9A15218 iTR 230V/24V Safety Transformer • CRL-MCR-009540 - SEA9DE16 Acti9 Isobar A 8 Way Enclosure
|  | Cxxx-NCR-000100 | NCR | PES 110v Maintainance Sockets not installed to design. |  | Contr | COF | BOS - Bond Street Station (West) |  | 2021-12-13 | 2021-12-03 16:27 | -10 | 2021-11-29 13:20 | Electrical - General | 0 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The Eastbound and westbound PES currently has a number 110v sockets installed at high level for the purpose of cleaning the platform smoke extract duct. One of the sockets on circuit DB-W-LVA05/6 has not been was not installed and a number of sockets fed from DB-W-LVA05, DB-E-LVA08, DB-E-LVB09 have been installed in a different location to what is shown on the original design layout drawings.However there are adequate available sockets to facilitate the cleaning range in either direction across each access hatch on the platform smoke duct. This NCR is to supersede previously raised Cxxx-NCR-000083.
|  | Cxxx-NCR-000101 | NCR | Use of plastic plug and screw in door frame to blockwork abutment fixing |  | Contr | SWN | BOS - Bond Street Station (West) |  | 2021-12-13 | 2022-01-25 15:47 | 43 | 2021-11-29 12:19 | Architectural - Doors | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | Plastic plug was used with screw to secure door frame to blockwork abutment . Use of plastic plugs not in accordance with approved Cxxx-SKC-A-LRC-Cxxx-50249 rev 2.0 JCP Concrete Screw MCR nor __ Door shop drawings . It is not known how many plastic plugs where used throughout BOS .
|  | Cxxx-NCR-000103 | NCR | DB-E-LVA08/3 Incorrect cable size installed |  | Contr | COF | BOS - Bond Street Station (West) |  | 2021-12-16 | 2021-12-04 09:03 | -12 | 2021-12-02 16:42 | Electrical - General | 0 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The cable size for circuit DB-E-LVA08/3 stated in Cxxx-FCD-000221 is 10m cable. However the cable insatlled on site is 6mm.
|  | Cxxx-NCR-000105 | NCR | Non-certified spreader box installed for castel Supplies |  | Contr | COF | BOS - Bond Street Station (West) |  | 2021-12-20 | 2022-01-06 09:54 | 17 | 2021-12-06 14:53 | Electrical - General | 5000 |  | Material | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | __ have requested that the __ Supply Submain W019/W082 WTH ECR 2/174 & __ Supply Submain E019 /E057 ETH ECR 2/173 have a spreader box fitted to each. The ESD team have installed a site made header trunking which has been inspected and signed off by a CRL FAE. However __ will not accept the install as the I.P rating of the header trunking cannot be certified.
|  | Cxxx-NCR-000106 | NCR | Water Mist Plant Room ATS IP Rating |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2021-12-15 | 2022-02-23 10:44 | 70 | 2021-12-08 01:40 | Electrical - Switchgear | 20000 |  | Design | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Other | Completed |  | The installed ATS units in West Ticket Hall level -4 Water Mist Fire Suppression Plant Room 5/397 and East Ticket Hall level -4 Water Mist Fire Suppression Plant Room 5/398 have Ingress Protection ratings of IP31 as Cxxx-SKC-E-DWG-Cxxx-50623, however as both of these plant rooms have fire water mist suppression, a rating of IP54 (Protection against the ingress of dust and water spray) is required as Cxxx-SKC-M-RSP-Cxxx-50030 (JV20 LV Distribution) JV20.1307 – section f).
|  | Cxxx-NCR-000110 | NCR | WTH Level -3 Interchange Ceiling Light fitting support bracket connection not installed to design. |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-06-23 08:21 | -73 | 2021-12-08 12:21 | Electrical - Lighting | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | WTH Level -3 Interchange Ceiling Light fitting support bracket connection not installed to design Cxxx-XRL-E-LRG-Cxxx-50023 lighting circuits DB-W-A03 4L1, DB-W-B03 4L1 & DB-W-EL03 4L1
|  | Cxxx-NCR-000111 | NCR | WTH level -3 lobby 4/083 two light fittings have been removed from circuit DB-W-EL03 11L1 that have previously been signed off in an IRN. |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2021-12-22 | 2022-05-06 14:06 | 135 | 2021-12-08 12:43 | Electrical - Lighting | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | WTH level -3 lobby 4/083 two J1/E light fittings have been removed from circuit DB-W-EL03 11L1 that have previously been signed off in an IRN.
|  | Cxxx-NCR-000112 | NCR | Protective Device Rating – Submain W020 |  | Contr | COF | BOS - Bond Street Station (West) |  | 2021-12-23 | 2021-12-09 11:43 | -14 | 2021-12-09 09:23 | Electrical - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | Protective device rating is incorrectly shown on LV schematic Cxxx-XRL-E-DDE-Cxxx-16100 P04. Drawing should reference “Circuit Breaker Frame Rating” kept as 250A and “Circuit Breaker Trip Unit Rating” changed to 160A as installed on site and shown in the __.
|  | Cxxx-NCR-000114 | NCR | DB-W-LVA03/9-110V Socket not installed to design. |  | Contr | COF | BOS - Bond Street Station (West) |  | 2021-12-24 | 2021-12-17 13:42 | -7 | 2021-12-10 11:05 | Electrical - General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | Cxxx-FCD-000015 states that a 110v socket outlet be added to Circuit DB-W-LVA03/8. The site team have not followed the FCD and have installed the socket on its own new circuit, DB-W-LVA03/9.
|  | Cxxx-NCR-000115 | NCR | Lack of proper protection to Wall cladding in WTH Level -3 / LU Link |  | Contr | SWN | BOS - Bond Street Station (West) |  | 2021-12-23 | 2022-05-19 07:24 | 147 | 2021-12-09 12:00 | Architectural - Walls | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Not Defined | Completed |  | Precast wall cladding panels are not properly protected , materials and equipment is being leaned against panels which resulted in damage and scoff marking of the surface in other areas . Protection and Cleaning not as Cxxx-ATK-N2-RSP-CR002-00001 clause JH40.3906
|  | Cxxx-NCR-000117 | NCR | DB-W-B05/7l2 - Post IRN Design Change |  | Contr | COF | BOS - Bond Street Station (West) |  | 2021-12-24 | 2022-01-06 16:10 | 13 | 2021-12-10 11:07 | Electrical - General | 2000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Due to the wrong earth potential, Damper Panels 134(CLR III 6/415) currently supplied from NCR DB-W-B05/7L2 is required to be removed and resupplied from DB-W-B07/4L3 as per Cxxx-FCD-000116.
|  | Cxxx-NCR-000118 | NCR | DB-W-A07/14L3 - Socket Outlet not installed to design |  | Contr | COF | BOS - Bond Street Station (West) |  | 2021-12-24 | 2021-12-17 13:38 | -7 | 2021-12-10 14:49 | Electrical - General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Due to a high level CMS clashes a 230v socket outlet installed in SR/LV/B has not been installed to design.
|  | Cxxx-NCR-000119 | NCR | DB-W-LVA07/8 - Socket Outlet not installed to design |  | Contr | COF | BOS - Bond Street Station (West) |  | 2021-12-24 | 2021-12-17 15:22 | -7 | 2021-12-10 15:42 | Electrical - General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | DB-W-LVA07/8 110v Socket outlet in SR/LV/B has not been installed as per design & Cxxx-FCD-000086.
|  | Cxxx-NCR-000120 | NCR | Light fittings not installed to FCD |  | Contr | COF | BOS - Bond Street Station (West) |  | 2021-12-29 | 2021-12-17 15:36 | -12 | 2021-12-15 11:12 | Electrical - General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | Following a site inspection it has come apparent that Cxxx-FCD-000121 which dictates the layout of the light fittings located in service riser 4/790 Mez level-2 has not been followed correctly. There are 2 lights in this area wired on 2 different circuits (W-B03/1L3 & W-EL03/11L1), each circuits has been wired to the incorrect point. Cxxx-FCD-000121 also covers the lighting layout in riser 4/790 Level-3, which again has not been followed. The FCD states that the 2 lights in this area be installed on 2 different circuits (W-B03/1L3 & W-EL03/11L1) unfortunately both lights have been installed on circuit W-EL03/11L1.
|  | Cxxx-NCR-000121 | NCR | DB-W-B07/9L1 & 14L1 - Small Power Accessories Not Installed As Per FCD |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-01-04 | 2021-12-21 12:41 | -14 | 2021-12-21 09:36 | Electrical - General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | Following the site inspection of DB-W-B07 (SC3 Circuits), it has been raised that circuits DB-W-B07/9L1 & 14L1 small power accessories have not been installed to the location as shown in Cxxx-FCD-000116 (markup shown on Cxxx-SKC-E-DDA-Cxxx-21150). As shown in drawing Cxxx-COF-E3-DWG-Cxxx-50019 (attached), circuit DB-W-B07/14L1 has been installed to the location shown on the fire alarm layout and circuit DB-W-B07/9L1 has been installed within close proximity to the adjacent north wall. This NCR is seeking acceptance of these changes under a 'Use As-Is' disposition.
|  | Cxxx-NCR-000122 | NCR | DB-W-EL09 - Post IRN Design change |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-01-18 | 2022-01-21 16:21 | 3 | 2022-01-04 14:15 | Electrical - General | 5000 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | __ have requested an additional 6no isolators in the WTH Escalator Control Room ECR I 2/174. The isolators are required to provide a point of isolation and demarcation for the escalator tread lighting on the following circuits: DB-W-EL09/1L2, DB-W-EL09/1L3, DB-W-EL09/2L2, DB-W-EL09/2L3, DB-W-EL09/3L1, DB-W-EL09/3L2. These works are detailed in Cxxx-FCD-000200. The circuits listed above have been IRN'd this NCR will capture the assurance documentation for these works.
|  | Cxxx-NCR-000123 | NCR | CMS installation to Western Ticket Hall, Escape Stairs. |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-01-27 | 2022-01-13 15:16 | -14 | 2022-01-13 08:03 | Consents - General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Following a site inspection, it has been identified that sections of the installed CMS, within Western Ticket Hall Escape Stairs 1+2, has not been installed as per RIR Cxxx-XRL-E-LRG-Cxxx-50018, Of the Changes that deviate from the Design, Not all Have been captured Through the FCD Process either. The changes can be seen within the appended Marked up Drawings.
|  | Cxxx-NCR-000124 | NCR | DB-W-A03 7L2 - Damaged Cable |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-01-26 | 2022-01-17 12:16 | -9 | 2022-01-12 15:47 | Electrical - General | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Whilst lidding a section of trunking a cable was damaged on circuit DB-W-A03 7L2 WTH level -3. The damage caused the circuit to trip out. Fortunately due to the location of the damage and the slack left on the cable the operatives were able to utilise the slack and re-terminate the cable into the DB. No repair was required. Unfortunately there is no photographic evidence of the damage.
|  | Cxxx-NCR-000125 | NCR | Damaged/faulty ATS switch supplying fire fighting lift DB-W-FFL (W010) WTH 3/133 LCC (LER) LU Level 3 |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-01-26 | 2022-01-17 12:27 | -9 | 2022-01-12 11:16 | Electrical - Switchgear | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The ATS switch supplying fire fighting lift DB-W-FFL (W010) WTH 3/133 LCC (LER) LU Level 3 has a damaged/faulty terminal screw on brown phase (L1) the screw is unable to tighten. ATS supplied from sub-main cables W012 & W071.
|  | Cxxx-NCR-000126 | NCR | Clash with Bostwick Gate - panels and __ substructure |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-01-27 | 2022-03-08 12:39 | 40 | 2022-01-13 12:54 | Architectural - Doors | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | The AP1 Bostwick gate is clashing with the panels and __ substructure - see attached photos
|  | Cxxx-NCR-000127 | NCR | CMS Installation WTH Escape Stairs 4 |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-02-18 | 2022-02-07 14:31 | -11 | 2022-02-04 11:22 | Electrical - General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Following a site inspection, it has been identified that sections of the installed CMS, within Western Ticket Hall Escape Stair 4, has not been installed as per RIR Cxxx-XRL-E-LRG-Cxxx-50002, Of the Changes that deviate from the Design, Not all Have been captured Through the FCD Process either. The changes can be seen within the appended Marked up Drawings.
|  | Cxxx-NCR-000128 | NCR | CMS Installation WTH Escape Stairs 5 |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-02-18 | 2022-02-07 14:43 | -11 | 2022-02-04 13:48 | Electrical - General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Following a site inspection, it has been identified that sections of the installed CMS, within Western Ticket Hall Escape Stair 5, has not been installed as per RIR Cxxx-XRL-E-LRG-Cxxx-50002, Of the Changes that deviate from the Design, Not all Have been captured Through the FCD Process either. The changes can be seen within the appended Marked up Drawings.
|  | Cxxx-NCR-000129 | NCR | CMS Rework Female Toilet 2/419 |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-02-01 | 2022-02-01 16:07 | 0 | 2022-01-18 10:40 | Electrical - General | 5000 |  | Design | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Due to clashes between existing conduits and the new ceiling tile supports and frame work in Rm 2/419, it was decided that a 4 compartment trunking should be installed via Riser 2/925 to alleviate the problem. These reworks will affect previously IRN'd circuits B03/8L3, B03/6L2, A03/2L2, EL03/1L3, B03/7L3, A03/1L1 in room 2/419 and B03/7L1 in Riser B03/7L1.
|  | Cxxx-NCR-000130 | NCR | DB.W.A01-Twisted Supply Cable - W017 |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-02-01 | 2022-01-24 16:14 | -8 | 2022-01-18 13:11 | Electrical - General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Upon Inspection it has been found that the inner cores of supply Cable W017 have become twisted. The twist on the cable has caused strain on the insulation of the inner cores and in one case it has split.
|  | Cxxx-NCR-000131 | NCR | CMS installation to ETH, Escape Stairs 7+8 |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-02-11 | 2022-01-31 12:03 | -11 | 2022-01-28 15:00 | Electrical - General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Following a site inspection, it has been identified that sections of the installed CMS, within Eastern Ticket Hall Escape Stairs 7+8, has not been installed as per RIR Cxxx-XRL-E-LRG-Cxxx-50024 , Of the Changes that deviate from the Design, Not all Have been captured Through the FCD Process either. The changes can be seen within the appended Marked up Drawings
|  | Cxxx-NCR-000132 | NCR | WTH Level 0 - 110v Socket outlets. |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-02-02 | 2022-02-01 10:34 | -1 | 2022-01-19 11:08 | Electrical - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | Cxxx-FCD-000119 has been raised to capture changes to 110v socket outlets, allocated circuits. The FCD states that the new circuit reference should be DB-W-LVB02/6 however this circuit reference has already been allocated to different 110v sockets via Cxxx-FCD-00187. The site team have not followed Cxxx-FCD-000119 for this reason and the circuit has now been installed on DB-W-LVB02/7. Also due to site clashes one of the sockets has been installed on the adjacent wall, as indicated on marked up drawing attached.
|  | Cxxx-NCR-000133 | NCR | Relocation of 110v Sockets WTH Level - 1 |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-02-03 | 2022-01-21 12:04 | -13 | 2022-01-20 12:48 | Electrical - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | A number of 110v socket outlets have been installed in different locations to design. The socket outlets remain in the same vicinity but due to site constraints and high level CMS clashes with conduit drops the final locations have been altered. Marked up drawing attached.
|  | Cxxx-NCR-000134 | NCR | CMS Installation WTH Level - 3 4/212 AP1 Interchange Link to LU Station |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-02-04 | 2022-01-24 11:41 | -11 | 2022-01-21 14:48 | Electrical - General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Following a site inspection, it has been identified that sections of the installed CMS, within Western Ticket Hall Level -3, 4/212 AP1 Interchange Link to LU Station, has not been installed as per the Latest IFC drawings: Cxxx-SKC-E-DDA-Cxxx-11232 P14, Cxxx-SKC-E-DDA-Cxxx-11130 P07, Cxxx-SKC-E-DDB-Cxxx-00001 P07. Of the Changes that deviate from the Design, Not all Have been captured Through the FCD Process either. The changes can be seen within the appended Marked up Drawing.
|  | Cxxx-NCR-000135 | NCR | OPCD Size Change for lighting circuits. |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-02-03 | 2022-01-26 14:30 | -8 | 2022-01-20 15:03 | Electrical - General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Each of the following circuits, fed via C type 10A __'s as per design, have been identified as exceeding the maximum permissible earth fault loop impedance when fed via the UPS system. • E-EL05/1L3 • E-EL05/4L2 • E-EL05/6L1 • E-EL07/13L3
|  | Cxxx-NCR-000136 | NCR | CMS Installtion WTH Level -3 |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-02-07 | 2022-01-24 12:05 | -14 | 2022-01-24 10:42 | Electrical - General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Following a site inspection, it has been identified that sections of the installed CMS, within Western Ticket Hall Level -3, All Areas (Excluding 4/212 AP1 Interchange Link to LU Station), has not been installed as per the Latest IFC drawings: Cxxx-SKC-E-DDA-Cxxx-11232 P14, Cxxx-SKC-E-DDA-Cxxx-11234 P06, Of the Changes that deviate from the Design, Not all Have been captured Through the FCD Process either. The changes can be seen within the appended Marked up Drawing.
|  | Cxxx-NCR-000137 | NCR | No Assurance provided for Sump Pump Panel Isolator at ETH -2/SP001 |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2022-02-04 | 2022-01-24 15:07 | -11 | 2022-01-21 10:09 | Electrical - General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The assurance check sheets for the load Isolator including redlines was not included within the SAF pack for the IRN for ETH -2/SP001.
|  | Cxxx-NCR-000138 | NCR | Westbound Platform leak in SCL between CP10 and AP3 |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-02-07 | 2022-02-18 12:53 | 11 | 2022-01-24 16:11 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Leak discovered in the SCL between Cp10 and AP3. Previous resin injection works have taken place in this area and have failed. Water is leaking onto the back of installed GFRC panel.
|  | Cxxx-NCR-000139 | NCR | No Access to Video Wall Isolators Installed behind Cladding at West Ticket Hall L0 |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-08-19 17:15 | -16 | 2022-01-25 13:09 | Electrical - Power Distribution | 1000 |  | Design | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | No access is provided to the Advertising Video Wall Isolators currently installed behind the cladding system at West Ticket Hall L0 (see attached photos). See attached drawings for specific locations. The affected circuits which have already been IRN'd/PCC'd are: DB-W-A10/5L1, W-A10/6L1, W-A10/7L1, W-A10/7L3, W-A10/8L3, W-A10/9L3
|  | Cxxx-NCR-000140 | NCR | WTH Urban Realm, Weighhouse street - MH02 partially blocked |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2022-02-09 | 2022-05-27 12:16 | 107 | 2022-01-26 16:39 | Civil - Drainage | 2000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | WTH Urban Realm, Weighhouse street - MH02 is partially blocked. This is due to grout making its way from outside the footprint of the MH, in to the MH through a gap between the MH biscuit and rings. See email and photos attached.
|  | Cxxx-NCR-000142 | NCR | DB-W-B02 5L2 - Damaged Cable |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-02-15 | 2022-02-11 11:07 | -4 | 2022-02-01 13:45 | Electrical - General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A Damaged single core brown Cable has been found on Circuit DB-W-B02 5L2, the damage has caused the circuit to trip out. The damaged cable is located in KD 8 Level -1. It looks as though the cable has crossed over the divider clip when Wired, so potentially any pressure applied to lid would crush the cable causing the damage.
|  | Cxxx-NCR-000143 | NCR | Circuit DB-W-EL02/1L2 - Incorrect Cable Size |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-02-17 | 2022-02-03 14:46 | -14 | 2022-02-03 13:43 | Electrical - General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Circuit DB-W-EL02/1L2 should have be wired in 2.5mm cable, however in error it has been wired in 4mm cable.
|  | Cxxx-NCR-000144 | NCR | WTH L-3 Dust Sealing (RC Walls) |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-02-17 | 2022-02-04 14:48 | -13 | 2022-02-03 09:55 | Architectural - General | 500 |  | Incomplete Works | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The architectural cladding has been installed to the RC walls within the WTH L-3 interchange area. Historical records cannot be found to evidence that the dust sealing has been carried out to the areas referenced in Cxxx-PWK-01318. It is now not feasible to verify if all these RC walls have had dust sealer applied to the RC walls.
|  | Cxxx-NCR-000145 | NCR | CMS installation to Western Ticket Hall, Levels +1 & +2, (Excluding KD7+8) All Disciplines. |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-02-17 | 2022-02-04 11:30 | -13 | 2022-02-03 15:18 | Electrical - General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Following a site inspection, it has been identified that sections of the installed CMS, within Western Ticket Hall, Levels +1 & +2, (Excluding KD7+8), has not been installed as per RIR Cxxx-XRL-E-LRG-Cxxx-50005 + RIR Cxxx-XRL-E-LRG-Cxxx-50014 , Of the Changes that deviate from the Design, Not all Have been captured Through the FCD Process either. The changes can be seen within the appended Marked up Drawings.
|  | Cxxx-NCR-000146 | NCR | CMS installation to Western Ticket Hall, Levels +0.5 |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-02-21 | 2022-02-08 16:49 | -13 | 2022-02-07 15:34 | Electrical - General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Following a site inspection, it has been identified that sections of the installed CMS, within Western Ticket Hall, Levels +0.5, (Excluding KD7+8), has not been installed as per The Latest IFC CMS Drawing , Of the Changes that deviate from the Design, Not all Have been captured Through the FCD Process either. The changes can be seen within the appended Marked up Drawings.
|  | Cxxx-NCR-000148 | NCR | Non Compliant Cable (SY Cable) found on site (WTH -4 Outside 5/087) |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-02-18 | 2022-02-28 15:26 | 10 | 2022-02-04 14:13 | Electrical - Power Distribution | 500 |  | Material | Reject | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | Non compliant cable found on site (see attached photos). SY cables are not MCR approved and should not be used on site.
|  | Cxxx-NCR-000149 | NCR | Battery heater / control miss match |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-08-19 07:17 | -16 | 2022-02-04 14:12 | Mechanical - Heating Ventilation & Air Conditioning | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Insufficient surveillance of subcontractors | Completed |  | The battery heater circuit is smaller rated than the actual heater
|  | Cxxx-NCR-000150 | NCR | AHU / MCC Control of thyristor circuit |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-06-17 13:14 | -79 | 2022-02-04 14:18 | Mechanical - Heating Ventilation & Air Conditioning | 4000 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | The thyristor circuit has been duplicated in both the MCC panel and the AHU unit and only one is required so modifications are required to enable the units to function
|  | Cxxx-NCR-000151 | NCR | Cable sized to big for terminals |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-07-21 01:18 | -45 | 2022-02-04 14:23 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | The cable run to the battery heater is sized at 2.5mm but the terminals on the PCB for the battery heater supply will not accept cables of this size
|  | Cxxx-NCR-000152 | NCR | AHU internal pipe colours crossed |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-08-14 13:42 | -21 | 2022-02-04 14:29 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Insufficient surveillance of subcontractors | Completed |  | The pipe work internal to the AHU unit should be coloured Blue for negative pressure and red for positive pressure, this has been piped the wrong way round within the unit causing the outside of the unit to be piped incorrectly as they have followed the same coding
|  | Cxxx-NCR-000153 | NCR | Cxxx - - BoH Ceilings - Non-coordinated Design - First Fix / Luminaire Housing Clashes |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-02-18 | 2022-05-20 14:33 | 91 | 2022-02-04 15:32 | Architectural - Ceilings & Soffits | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | As part of the design scope, were required to provide a 600x600mm clear opening to accommodate the luminaires present within the ceiling make up. were provided the product reference and data sheets for these luminaires (Type J - Antares 598 x 598), which detailed the housing/shroud of the luminaire. This showed that the it projected above the finished ceiling level. This housing clashes with the primary sub-frame (CD Profil and cross connections - see drawing Cxxx-SKC-A-DWG-Cxxx-52009) in most locations, requiring rework to enable their install. This clash was not captured during the design phase, nor within the first fix element of the works. The issue discovered during the MEP second fix. The NCR has required rework by both , and rework by the electrical team, in order for the ceiling to accommodate the luminaire housing/shroud. Overview of works required; - Removal of installed tiling - Removal of adjacent secondary fix - Removal and refixing of clashing primary sub-structure where minor adjustments cannot be facilitated) - Reinstatement of all above items. - Reinstatement of luminaire (by others) The above works have now enabled the luminaire installation in all rooms. Rooms affected: >WTH 2/423 2/424 2/318 2/319 2/406 2/331 4/084 6/316 6/317 6/047 6/416 >ETH 2/418 2/419
|  | Cxxx-NCR-000155 | NCR | Cxxx - - BoH Ceilings - __ Perimeter Boards [Incomplete Finish] |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-02-18 | 2022-05-16 13:26 | 87 | 2022-02-04 16:04 | Architectural - Ceilings & Soffits | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | As per specification references JK10.1206 / JK40.1206 , it is stated that the ceiling perimeter plasterboard should be 'taped and jointed suitable to receive applied paint finishes'. At sign off, the perimeter boards have not been taped and jointed, and are not currently in a position to receive applied paint finishes. At the time of writing, this applies to the following rooms (04/02/22): >WTH 6/316 6/317 6/417 6/047 2/423 2/424 >ETH 2/418 2/419 It is noted that are not required to provide the painting works, as per their drawings.
|  | Cxxx-NCR-000156 | NCR | CMS installation to Eastern Ticket Hall, Level 0 |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-02-23 | 2022-02-14 14:30 | -9 | 2022-02-09 08:10 | Electrical - General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Following a site inspection, it has been identified that sections of the installed CMS, within Eastern Ticket Hall Level 0 , has not been installed as per The Latest IFC Drawing , Of the Changes that deviate from the Design, Not all Have been captured Through the FCD Process either. The changes can be seen within the appended Marked up Drawings.
|  | Cxxx-NCR-000157 | NCR | Cxxx - - BoH Ceilings - ETH 2/418 - Incorrect Primary Beam Installation |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-02-24 | 2022-04-03 10:53 | 38 | 2022-02-10 15:06 | Architectural - Ceilings & Soffits | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | In room 2/418, the primary beams have been set out to the incorrect spacings, leading to clashes with the follow on MEP second fix. The current spacing does not correspond with any of the following; - Primary beams to be placed in line with the joints of the tiles (Architectural Specification Reference: JA.6512) - Ceiling to be co-ordinated with MEP assets (Architectural Specification Reference: JK40.1205) - The approved F2 designs [Cxxx-SKC-A-DWG-Cxxx-52037 {C02}] CRL request that this the beam setting out is returned to a beam spacing arrangement that is both in line with tiles, and accommodating of the MEP assets. This will require a rework of a significant part of the 2/418 ceiling - requiring 70% to be removed and reinstated in the correct location. It is also causing delays to the MEP second fix, who cannot install due to the clashing beams.
|  | Cxxx-NCR-000158 | NCR | DB-W-A02 - Isolators Installed in wrong Locations. |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-03-01 | 2022-02-15 12:04 | -14 | 2022-02-15 11:05 | Electrical - General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | A 63 amp isolator on Circuit DB-W-A02/8L2, located in the rubbish store 2/402 has been moved to adjacent wall. The orientation of the 32amp isolators located in local cooling room has been rearranged between circuits DB-W-A02/7L1,2,3 & 14L1,2,3 and DB-W-B02/7L1,2,3 & 14L1,2,3 as shown attached red line drawing. Neither change has had an FCD produced.
|  | Cxxx-NCR-000159 | NCR | CMS installation to Eastern Ticket Hall, Level -4 |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-03-03 | 2022-02-21 16:44 | -10 | 2022-02-17 11:19 | Electrical - General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Following a site inspection, it has been identified that sections of the installed CMS, within Eastern Ticket Hall Level -4 , has not been installed as per The Latest IFC Drawing , Of the Changes that deviate from the Design, Not all Have been captured Through the FCD Process either. The changes can be seen within the appended Marked up Drawings.
|  | Cxxx-NCR-000160 | NCR | Damaged HV Ladder Rack at WTH 6/797 |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-08-30 14:10 | -5 | 2022-02-14 16:00 | Electrical - Cable Management | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The HV ladder rack at WTH 6/797 has been found as damaged (see attached photo).
|  | Cxxx-NCR-000161 | NCR | DB-W-EL02 - OPCD Size Change for lighting circuits |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-05-25 | 2022-05-13 15:31 | -12 | 2022-05-11 12:24 | Electrical - Lighting | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Each of the following circuits, fed via C type 10A __'s as per design, have been identified as exceeding the maximum permissible earth fault loop impedance when fed via the UPS system. DB-W-EL02/5L2 DB-W-EL02/5L3 DB-W-EL02/10L1 DB-W-EL02/2L1 DB-W-EL02/2L2
|  | Cxxx-NCR-000162 | NCR | DB-W-B02/1L3 - OCPD Size Change for lighting circuit |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-05-25 | 2022-05-13 15:33 | -12 | 2022-05-11 12:41 | Electrical - General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | As a result of a discrepancy between the design and installation lengths, circuit DB-W-B02/1L3 has been identified as exceeding the maximum permissible earth faut loop impedance when fed via the UPS system.
|  | Cxxx-NCR-000163 | NCR | CMS installation to Eastern Ticket Hall, Level -1 |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-03-10 | 2022-02-28 10:14 | -10 | 2022-02-24 13:09 | Electrical - General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Following a site inspection, it has been identified that sections of the installed CMS, within Eastern Ticket Hall Level -1 , has not been installed as per The Latest IFC Drawing , Of the Changes that deviate from the Design, Not all Have been captured Through the FCD Process either. The changes can be seen within the appended Marked up Drawings.
|  | Cxxx-NCR-000164 | NCR | P&T, CH2 - Leak in SCL above totem |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2022-03-31 | 2022-03-02 14:30 | -29 | 2022-02-17 16:35 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | We have attempted to seal a leak in the CH2 roof via resin injection on several occasions, (see C445-PMI-00002, C445-PWK-00010, C445-PWK-00011). The leak persists. The leak is emanating from a crack about 200mm back from the face of some unistrut installed to support the cable tray and conduits here. Its leaking on to the back of the cable tray then dripping on to the totem below.
|  | Cxxx-NCR-000165 | NCR | Access door required on Chilled Water CCUs for completion of connections and insulation |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-04-27 | 2022-06-06 15:35 | 40 | 2022-04-13 15:44 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | Access is required to complete __'s CHW connections in the __ Units necessitates an access panel/door to be cut-in to the lower body section to allow completion of the insulation and sealing to the main cooler above." NB: Insulation on these internal sections of Flow/return pipework and condensate drain pipe is to be in Nitrile Armourflex (blue foam) rather than __.
|  | Cxxx-NCR-000166 | NCR | Contractor was unable to provide evidence of all Quality Benchmarks being completed |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2022-04-12 | 2022-03-18 14:26 | -25 | 2022-02-23 12:13 | Architectural - Signage | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Not Defined | Completed |  | A planned Signage Surveillance. On request the Contractor was only able to provide evidence for ‘Totem Quality Benchmark’ Cxxx-SKC-A-LRC-Cxxx-50940 (Rev 1) Code 2 (04/02/2020) and ‘Platform Curved Glazed Signage Benchmark’ Cxxx-SKC-A-LRC-Cxxx-50756 (Rev 2) Code 1, being completed and accepted by CRL Architect. No further evidence was available for, Suspended, Wall projected, Platform Edge Screen (PES) signage and Wall Mounted signage.
|  | Cxxx-NCR-000167 | NCR | Torque Wrench was out of Calibration at time of use |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2022-04-12 | 2022-03-18 14:32 | -25 | 2022-02-23 12:21 | Architectural - Signage | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | During a planned Signage Surveillance the Contractor submitted Torque Wrench calibration certification on checking it was found the it was 10 days out of date at the time use.
|  | Cxxx-NCR-000168 | NCR | Torqueing and Proof Loading of fixings not referenced in Firestopping Installation ITP |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-07-21 14:58 | -45 | 2022-02-23 13:04 | Fire - Compartmentation | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Lack of procedure | Completed |  | During a planned Firestopping Surveillance, the ITP ‘Fireproofing Installation to Service Penetration Walls’ Cxxx-COF-A-ITP-Cxxx-50004 (Rev 1) was found that Torqueing and Proof Loading of fixings were not referenced
|  | Cxxx-NCR-000169 | NCR | Design has been changed and implemented without formal acceptance |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-07-06 09:26 | -60 | 2022-02-24 13:42 | Architectural - Signage | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | A planned Signage surveillance was undertaken at Bond Street, during a desk top review It was also noted that the washers on the wall bracket appear to be too small for the slotted holes, drawing ‘USN 202 Revised first fix’ C474-WWI-A-DWG-Cxxx-50013 (C01) Code 1 does not detail size of washer, also the drawing does not detail slotted holes.
|  | Cxxx-NCR-000170 | NCR | CMS Installation ETH Level -3 |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-03-15 | 2022-03-09 15:07 | -6 | 2022-03-01 15:40 | Electrical - General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Following a site inspection, it has been identified that sections of the installed CMS, within Eastern Ticket Hall Level -3 , has not been installed as per The Latest IFC Drawing , Of the Changes that deviate from the Design, Not all Have been captured Through the FCD Process either. The changes can be seen within the appended Marked up Drawings.
|  | Cxxx-NCR-000171 | NCR | Non-conformant labels for MCC Load cables |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-11-16 20:27 | 73 | 2022-02-25 09:39 | Electrical - Cable Management | 5000 |  | Workmanship | Rework | 3 (3-6k) | Complete | Procedure Problem - Other | Completed |  | Non-compliant labels (estimate of 300), where Alternative Asset IDs used do not reflect the Cable Reference/Circuit number, have been installed on some of the MCC load cables – please see "Non-compliant cable label" example in the "Attachments" section.
|  | Cxxx-NCR-000172 | NCR | ETH - Side Gate Floor Sockets |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-03-31 | 2022-04-22 13:08 | 22 | 2022-02-25 15:11 | Architectural - Flooring | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | On the side gates there are floor sockets that are resined into the granite tiles to lock the door. Unfortunately some of the floor sockets have been cored out in the incorrect position so they are unfit for purpose.
|  | Cxxx-NCR-000173 | NCR | Relocation of LV conduits to allow installation of the new false ceiling in ETH 6/412 |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-03-16 | 2022-03-15 11:02 | -1 | 2022-03-02 11:57 | Electrical - General | 5000 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | 2No. installed LV conduits need to be modified and extended to allow for the new false ceiling void in 6/412 to be classified as a sterile area so that the Fire detection and water suppression does not need to be installed. The conduits contain circuits: Emergency lighting E-EL06/3L3 and LV supply to DCP E-B06/11L1. These changes have been made via Cxxx-FCD-000274 this NCR has been raised to capture the assurance for these works.
|  | Cxxx-NCR-000175 | NCR | ETH Level 0 Ground CMS - limited access and maintenance |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-03-22 | 2022-04-08 10:13 | 17 | 2022-03-08 11:47 | Electrical - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Access and maintenance for future works etc are achievable via maintenance windows (unrestricted sections of CMS), rodding points etc. The obstruction (luminaries) causes particular sections of CMS to be inaccessible.(captured within Observations 5 & 7) Within the Chiller room its advisable that a fixed scaffold would be required to access a section of high level CMS to the right hand side of the room as per observation 13.
|  | Cxxx-NCR-000179 | NCR | ETH Level -1 CMS - Linited access and maintenance |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-09-20 14:26 | 16 | 2022-03-07 11:34 | Electrical - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | 1.Access and maintenance for future works etc are achievable via maintenance windows (unrestricted sections of CMS), rodding points etc. The obstruction (luminaries or unistruts) causes particular sections of CMS to be out of reach whilst using safe means of access equipment 2.Severe obstruction to access and maintain CMS routes. The obstruction (ie: mechanical pipe work eg: access issue 3 within attachment) causes sections of CMS to be completely out of reach whilst using safe means of access equipment A SAP report has been produced and attached in conjunction with marked up CMS layout drawings to identify the areas which require mitigation for adequate A & M. There are no areas of concern identified in relation to 25% spare capacity however, if it so happens that the areas which cannot be accessed due to other disciplines installation (like in access issue No.3), then the proposed mitigation of further CMS will mitigate both A&M and lack of 25% spare capacity. See attached files "ETH -1 2 of 6 Mitigation" & "ethlevel-1aandmcloseout" for additional areas found post inspection.
|  | Cxxx-NCR-000182 | NCR | W-01-633-D01 and W-01-411-D01 incorrect fabrication size |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-03-16 | 2022-05-31 14:57 | 76 | 2022-03-02 12:31 | Architectural - Doors | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Under Cxxx - For W01-633-D01 - W-01-633-D01 has been fabricated incorrectly (see Cxxx-SKC-A-DWG-Cxxx-52440 C01) to the structural opening size given in the door schedule at the time of manufacture (Rev 26) as opposed to the drawing reviewed and accepted by __ (Cxxx-SKC-A-DWG-Cxxx-52440 P03). The fabricated door frame width for W-01-633-D01 is 970mm and the __’s design intent for this door (Cxxx-SKC-A-DDD-Cxxx-40423 P05) calls for a door frame with an overall width of 962mm. For W-01-411-D01 - W-01-411-D01 has been fabricated incorrectly (see Cxxx-SKC-A-DWG-Cxxx-51744 C01) to the structural opening size given in the door schedule at the time of manufacture (Cxxx-SKC-A-TSC-Cxxx-50001 Rev 26) as opposed to the drawing reviewed and accepted by __ (Cxxx-SKC-A-DWG-Cxxx-51744 P02). The fabricated door frame width for W-01-411-D01 is 965mm and the __’s design intent for this door (Cxxx-SKC-A-DDD-Cxxx-40422 P05) calls for a door frame with an overall width of 1040mm.
|  | Cxxx-NCR-000183 | NCR | CMS installation to ETH, Risers 683+927. Levels +0.5 to -4, All Disciplines. |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-03-29 | 2022-03-24 15:14 | -5 | 2022-03-15 09:12 | Electrical - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Following a site inspection, it has been identified that sections of the installed CMS, within Eastern Ticket Hall Level 0 , has not been installed as per The Latest IFC Drawings , Of the Changes that deviate from the Design, Not all Have been captured Through the FCD Process either. The changes can be seen within the appended Marked up Drawings.
|  | Cxxx-NCR-000184 | NCR | WTH, level 0, External Flood Chamber MH snags |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-10-01 07:43 | 27 | 2022-03-02 16:53 | Civil - Drainage | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | I carried out an inspection of the external Flood Chamber MH, (FCMH) at ground level in the WTH. A number of issues were found that need to be rectified: External FCMH - 1. Installed steps difficult and unsafe for access. 2. Riser pipe not restrained to wall and wobbles about. 3. Incoming pipe does not have a 90 degree down pipe as shown in section 2, drawing Cxxx-SKC-P-DDD-Cxxx-25115. 4. Flap valve damaged. 5. Non-Return valve not installed in outflow pipe. 6. Top of riser pipe is higher than the I.L. of the LV duct. 7. Small amount of grout in the bottom of the outflow pipe
|  | Cxxx-NCR-000185 | NCR | WTH TVS LVL +6 RC Upstand around pipework - Incomplete QA |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-03-17 | 2022-03-03 17:23 | -14 | 2022-03-03 16:18 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Incomplete QA for WTH TVS LVL +6 RC Upstand around pipework. Missing items listed below. - In-process concreting check sheet - Post Pour Inspection check sheet - 28 Day Cube Test results To address this issue Schmidt hammer tests have been carried out on this upstand. The test report is included in the attached Record Pack Cxxx-COF-C-LRC-Cxxx-50010 Rev1.0
|  | Cxxx-NCR-000186 | NCR | Bostwick gate top track width |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2022-03-18 | 2022-05-16 13:30 | 59 | 2022-03-04 14:33 | Architectural - Doors | 500 |  | Manufacturing Defect | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | The AP1 Bostwick gate fabricated has been fabricated with a top track of width of 60mm instead of 57mm. The gate was fabricated under Cxxx and installed under Cxxx.
|  | Cxxx-NCR-000188 | NCR | CMS Installation ETH Risers 912,919,920. |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-05-19 | 2022-05-06 09:37 | -13 | 2022-05-05 09:26 | Electrical - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Following a site inspection, it has been identified that sections of the installed CMS, within Eastern Ticket Hall, Risers 912,919+920. Levels -2 to -4, has not been installed as per The Latest IFC Drawings , Of the Changes that deviate from the Design, Not all Have been captured Through the FCD Process either. The changes can be seen within the appended Marked up Drawings.
|  | Cxxx-NCR-000189 | NCR | DB-E-A08 - Circuit no longer required. |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-03-21 | 2022-03-15 16:40 | -6 | 2022-03-07 15:53 | Electrical - General | 5000 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | Due to access and maintenance constraints associated with the existing location of assets a revised design has been issued (Cxxx-FCD-000258). As a direct result, DB-E-A08 – 8L1/L2/L3 is no longer required to supply the asset which has been relocated and re-supplied from another Distribution Board. (Cxxx-NCR-000192.)
|  | Cxxx-NCR-000190 | NCR | Eastern Ticket Hall (ETH) - GLAP Glass Door |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-07-06 09:23 | -60 | 2022-03-07 11:07 | Architectural - Doors | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | Swarf from drilling has accumulated between the glass panes of the GLAP door, see attached photographs.
|  | Cxxx-NCR-000191 | NCR | WTH, level 0, Internal Flood Chamber MH snags |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-08-16 14:19 | -19 | 2022-03-07 14:32 | Civil - Drainage | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | I carried out an inspection of the internal Flood Chamber MH, (FCMH) at ground level in the WTH. A number of issues were found that need to be rectified: Internal FCMH - 1 - Ply installed on the RC wall. 2 - Drainage pipe sleeve not sealed against water leakage. 3 - At least 8xDividag cones not removed and the voids not infilled in the RC walls. 4 - At least 10xsteel scaffold sockets still embedded in the MH biscuit opening.
|  | Cxxx-NCR-000192 | NCR | DB-E-A07 - Post IRN Design change - Westbound Invert |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-04-06 | 2022-06-01 14:59 | 56 | 2022-03-23 08:26 | Electrical - General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | A new circuit has been added to this DB post IRN. The circuit reference is DB-E-A07/18L1,2,3. This change has been captured via Cxxx-FCD-000258. This NCR will capture the assurance for the additional circuit.
|  | Cxxx-NCR-000193 | NCR | DB-E-B08/7L1,L2,L3 - Circuit no longer required |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-03-22 | 2022-03-15 16:44 | -7 | 2022-03-08 10:43 | Electrical - General | 5000 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | Due to access and maintenance constraints associated with the existing location of assets a revised design has been issued (Cxxx-FCD-000258). As a direct result, DB-E-B08 – 7L1/L2/L3 is no longer required to supply the asset which has been relocated and re-supplied from another Distribution Board. (Cxxx-NCR-000194.)
|  | Cxxx-NCR-000194 | NCR | DB-E-A07 - Post IRN Design change - Escalator sump |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-04-06 | 2022-06-01 15:18 | 56 | 2022-03-23 08:46 | Electrical - General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | A new circuit has been added to this DB post IRN. The circuit reference is DB-E-A07-19L1,2,3 This change has been captured via Cxxx-FCD-000258. This NCR will capture the assurance for the additional circuit.
|  | Cxxx-NCR-000195 | NCR | DB-W-A05 - 2 x Circuits no longer required. |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-03-22 | 2022-03-15 16:51 | -7 | 2022-03-08 15:12 | Electrical - General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Due to access and maintenance constraints associated with the existing location of assets a revised design has been issued (Cxxx-FCD-000262). As a direct result, DB-W-A05-7L1,2,3 & 8L1,2,3 are no longer required to supply the assets which have been relocated and re-supplied from other Distribution Boards. (Cxxx-NCR-000196) & (Cxxx-NCR-000197)
|  | Cxxx-NCR-000196 | NCR | DB-W-A07 - Post IRN Design Change. |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-04-06 | 2022-05-19 16:04 | 43 | 2022-03-23 09:06 | Electrical - General | 5000 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | A new circuit has been added to this DB post IRN. The circuit reference is DB-W-A07/23L1,2,3 This change has been captured via Cxxx-FCD-000262. This NCR will capture the assurance for the additional circuit.
|  | Cxxx-NCR-000197 | NCR | DB-W-B07-5L1,2,3 - Post IRN Design change |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-04-06 | 2022-06-16 12:15 | 71 | 2022-03-23 09:15 | Electrical - General | 5000 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | A new circuit has been added to this DB post IRN. The circuit reference is DB-W-B07/5L1,2,3 This change has been captured via Cxxx-FCD-000262. This NCR will capture the assurance for the additional circuit.
|  | Cxxx-NCR-000198 | NCR | BS8519 Bracketry Calculations do not match Site Installation |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-08-24 16:04 | -11 | 2022-03-08 16:50 | Electrical - Cable Management | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The details in the current BS8519 Bracketry Calculations (see related references) does not match what has actually been installed on site. For example, The HUS3-I fixing size used in the BS8519 Bracketry Calculations does not match the fixing size that has been installed on site. The calculations are based on a 55mm (embedment depth) however a 35mm (embedment depth) has been installed. Also following a site visit with __ on 21/03/22, it was found that in WTH circulation area 5/071 outside the emergency switch room, Crofton have done a bracket calculation for this area however their calculation does not match the as built site bracket. Crofton calculations show 4No. __ HUS3-PL6 been fixed into the above concrete slab and 3No. __ HUS3-PL6 been used to fix a bracket to the wall. The bracket on site uses a __ HUS3-I 6 fixing with a 10mm stud dropping either side of the CMS. The height of the drop is approximately 2.5 to the lowest bracket. The spacing between support brackets is 1000mm. Additional CMS(tray, trunking and conduit) has been added to this bracket arrangement on top of what Crofton allowed for in their calculations. Crofton calculated that the total applied load was 2.67kN this is without the additional CMS that has been added to it. However the 35mm __ HUS3-I fixing has a design resistance of 1.3kN as per __ data sheet.
|  | Cxxx-NCR-000200 | NCR | Chilled Water Sleeve sizes not campatible with pipe insulation, vapour barrier and/or fire stopping requirements |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-07-29 14:21 | -37 | 2022-03-09 15:42 | Mechanical - Piping | 15000 |  | Design | Repair | 2 (6-60k) | Complete | Design Problem - Inadequate or defective design | Completed |  | There are a number of compartment walls across the station where the Chilled Water Pipework passing through does not have a suitable sleeve fitted to allow adequate insulation, vapour barrier and/or fire stopping.
|  | Cxxx-NCR-000202 | NCR | WTH L-1, L-2 and L-4 Cavity Drainage |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-09-30 15:33 | 26 | 2022-03-21 13:31 | Civil - Drainage | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Further to Cxxx-RFI-000021, it has been discovered that the perimeter cavity drainage outlets at the WTH have not been constructed as required by the design, (see Cxxx-SKC-P-DDD-Cxxx-35150).
|  | Cxxx-NCR-000203 | NCR | CMS installation to ETH, Level -5, AP3 6-229 + Public Escape Route 6-230 |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-04-19 | 2022-04-05 12:26 | -14 | 2022-04-05 09:20 | Electrical - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Following a site inspection, it has been identified that sections of the installed CMS, within Eastern Ticket Hall Level -5, AP3 6-229 + Public Escape Route 6-230 , has not been installed as per The Latest IFC Drawing , Of the Changes that deviate from the Design, Not all Have been captured Through the FCD Process either. The changes can be seen within the appended Marked up Drawings.
|  | Cxxx-NCR-000204 | NCR | CMS installation to Eastern Ticket Hall. Level -2 |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-03-30 | 2022-03-18 10:36 | -12 | 2022-03-16 12:31 | Electrical - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Following a site inspection, it has been identified that sections of the installed CMS, within Eastern Ticket Hall Level -2 , has not been installed as per The Latest IFC Drawings , Of the Changes that deviate from the Design, Not all Have been captured Through the FCD Process either. The changes can be seen within the appended Marked up Drawings.
|  | Cxxx-NCR-000205 | NCR | CMS installation to WTH, Level -5, AP2 6-219 + Public Escape Route 6-088 |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-04-19 | 2022-04-05 14:02 | -14 | 2022-04-05 10:01 | Electrical - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Following a site inspection, it has been identified that sections of the installed CMS, within Western Ticket Hall Level -5, AP2 6-219 + Public Escape Route 6-088, has not been installed as per The Latest IFC Drawing , Of the Changes that deviate from the Design, Not all Have been captured Through the FCD Process either. The changes can be seen within the appended Marked up Drawings.
|  | Cxxx-NCR-000206 | NCR | DB-E-A04 - Booster Pump Set- Post IRN Design |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-03-28 | 2022-03-28 15:45 | 0 | 2022-03-14 14:03 | Electrical - General | 5000 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | A new Design has been Submitted for the Pump set & BMS booster supplies post IRN via Cxxx-FCD-000219. This NCR has been raised to capture the assurance documentation. The circuits affected by these works are DB-E-A04/16L1,2,3 (asset relocated) and DB-E-A04/14L3 (new Supply).
|  | Cxxx-NCR-000207 | NCR | DB-E-B04 - Booster pump set - Post IRN Design Change |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-03-31 | 2022-03-28 15:49 | -3 | 2022-03-17 13:04 | Electrical - General | 5000 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | A new Design has been Submitted for the Pump set & BMS booster supplies post IRN via Cxxx-FCD-000219. This NCR has been raised to capture the assurance documentation. The circuits affected by these works are DB-E-B04/5L1,2,3 (asset relocated) and DB-E-B04/8L3 (new Supply).
|  | Cxxx-NCR-000208 | NCR | P&T - Excessive Finger Gap between GFRC Panel & Adjacent Plate at Top of Escalator ES2 (LHS) (/__) |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-08-12 13:25 | -23 | 2022-04-04 14:35 | Architectural - Walls | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | It was noted after the installation of the LHS GFRC panel at the top of the ES2 Escalator at LEVEL 0, there is an excessive finger gap between the back of the GFRC panel and stainless steel strip behind the panel.
|  | Cxxx-NCR-000210 | NCR | WTH Level 0.5 Limited access & Maintenance |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-07-07 14:17 | -59 | 2022-03-16 13:09 | Electrical - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | WTH Level +0.5 is a relatively small area in comparison to other floors. The SAP report attached consists of 5 observations, 4 of which slightly restrict A&M. Observation 5 identifies that a fixed scaffold would be the safest means of access to the high level trunking in one particular section (identified on attached drawings). Please refer to the attached SAP report and associated marked up drawings for further information
|  | Cxxx-NCR-000211 | NCR | Pipework in WTH Lobby 6/088 failing pressure test - affects IRNs -D-50002 & 50013 |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-07-15 | 2022-07-20 09:06 | 5 | 2022-03-21 08:48 | Civil - Sewage/Water services | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | After connecting new Station Pumped Drainage pipework to cast-in pipework for Sump Pump -6/SP005 testing from Service riser 6/790 to the Sump below Circ. area 6/072, it was concluded that the pipework cannot hold pressure. It was determined that there is a leaking joint somewhere within the cast in section.
|  | Cxxx-NCR-000213 | NCR | CMS installation to ETH, Level +0.5, All Disciplines. |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-04-06 | 2022-03-25 14:13 | -12 | 2022-03-23 14:10 | Electrical - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Following a site inspection, it has been identified that sections of the installed CMS, within Eastern Ticket Hall Level +0.5 , has not been installed as per The Latest IFC Drawing , Of the Changes that deviate from the Design, Not all Have been captured Through the FCD Process either. The changes can be seen within the appended Marked up Drawings.
|  | Cxxx-NCR-000214 | NCR | CMS installation to Platform and Tunnels, CP1,2,3,3,4,7,8,9 +CP10 |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-04-04 | 2022-03-23 10:46 | -12 | 2022-03-21 14:53 | Electrical - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Following a site inspection, it has been identified that sections of the installed CMS, within Platform and Tunnels, CP1,2,3,3,4,7,8,9 +CP10, has not been installed as per The Latest IFC Drawing , Of the Changes that deviate from the Design, Not all Have been captured Through the FCD Process either. The changes can be seen within the appended Marked up Drawings.
|  | Cxxx-NCR-000215 | NCR | DB-E-A09/7L1,L2,L3 - Circuit no longer required |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-06-08 | 2022-05-27 11:21 | -12 | 2022-05-25 07:44 | Electrical - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Due to access and maintenance constraints associated with the existing location of assets a revised design has been issued (Cxxx-FCD-000258). As a direct result, DB-E-A09 – 7L1/L2/L3 is no longer required to supply the asset which has been relocated and re-supplied from another Distribution Board. (Cxxx-NCR-000216.)
|  | Cxxx-NCR-000216 | NCR | DB-E-B07/14L1,L2,L3 - Post IRN Design Change, Sump Pump |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-05-10 | 2022-06-01 15:32 | 22 | 2022-04-26 08:39 | Electrical - General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | A new circuit has been added to this DB post IRN. The circuit reference is DB-E-B07-14L1,2,3 This change has been captured via Cxxx-FCD-000258. This NCR will capture the assurance for the additional circuit.
|  | Cxxx-NCR-000217 | NCR | ETH Level 0.5-CMS Limited access and maintenance |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-06-17 07:57 | -79 | 2022-03-22 11:10 | Electrical - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | 1)Access and maintenance for future works etc are achievable via maintenance windows (unrestricted sections of CMS), rodding points etc. The obstruction (luminaries) cause particular sections of CMS to be out of reach whilst using safe means of access equipment. The restrictions are identified in observations 1 and 11 on the attached SAP report and located on the attached layout drawings. 2)Out of reach access to sections of CMS. The restriction is identified in observation 13 & 14 on the attached SAP report and located on the attached layout drawings. 3) Observation number 5 shows tiered trunkings within close proximity potentially making it difficult to use a standard screwdriver. The SAP report also provides assurance that all other areas have adequate access to maintain and/or install further services at a later date (observations 2-10 & 12,)
|  | Cxxx-NCR-000221 | NCR | DB-W-A07 - DB Circuits Post IRN Design Change |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-04-06 | 2022-05-20 09:10 | 44 | 2022-03-23 13:14 | Electrical - General | 5000 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | Cxxx-FCD-000262 requires 2 changes to be made to DB-W-A07 Post IRN. Currently DB-W-A07/6L1 supplies the 110V DB LVA07 this is to be moved to DB-W-A07/5L1 which is currently spare. This then allows 6L1,L2,L3 to be used for the new 3 phase supply for the Eastbound Invert Sump.
|  | Cxxx-NCR-000222 | NCR | Damaged WTH CHW Chiller Units 002 & 003 casings - IRN-M-50016 |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-08-02 08:48 | -33 | 2022-04-13 15:45 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper handling of material | Completed |  | Chiller Panels have been bent upon an un-authorised lift being carried out.
|  | Cxxx-NCR-000223 | NCR | CMS installation to WTH. Level 0 and -1, KD7+8, All Disciplines. |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-04-13 | 2022-04-01 10:40 | -12 | 2022-03-30 08:18 | Electrical - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Following a site inspection, it has been identified that sections of the installed CMS, within Western Ticket Hall, Levels 0 and -1, has not been installed as per The Latest IFC Drawings , Of the Changes that deviate from the Design, Not all Have been captured Through the FCD Process either. The changes can be seen within the appended Marked up Drawings.
|  | Cxxx-NCR-000224 | NCR | CMS installation to Eastbound and Westbound Inverts. Level -6, All Disciplines. |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-04-26 | 2022-04-12 15:41 | -14 | 2022-04-12 09:59 | Electrical - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Following a site inspection, it has been identified that sections of the installed CMS, within the Eastbound and Westbound Inverts. Level -6, has not been installed as per The Latest IFC Drawings , Of the Changes that deviate from the Design, Not all Have been captured Through the FCD Process either. The changes can be seen within the appended Marked up Drawings.
|  | Cxxx-NCR-000226 | NCR | WTH Level 0 - Lightning protection |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-04-14 | 2022-04-01 08:54 | -13 | 2022-03-31 14:02 | Electrical - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The Lightning protection earth tape and earth pits have not been installed as per design Cxxx-SKC-E-DDA-Cxxx-11502.
|  | Cxxx-NCR-000227 | NCR | Corduroy Tiles on Public Area Escape Stairs |  | Contr | SWN | BOS - Bond Street Station (West) |  | 2022-05-27 | 2022-05-27 12:13 | 0 | 2022-04-01 14:16 | Architectural - Flooring | 8000 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Other | Completed |  | During LU / CRL inspection and reported by LU SIR 757 - Corduroy tactiles had been installed at various levels of Public Escape not in accordance with Building Regulations Part M , Lu S1133 and BS 8300. LU S1133 states that the escape stairs a public when in use , then a corduroy tactile should be at the bottom of the stair and at the top, not on any intermediate landings- nor on BOH stairs . Cl 3.2.6 A corduroy hazard warning surface shall be installed in accordance with the Approved Document Part M of the Building Regulations and the Department for Transport Guidance on the use of tactile paving surfaces. For the purposes of compliance with Building Regulations , public stairs in the London Underground environment are considered to be external ' stepped access ' and as such required a corduroy hazard warning surface at the top and bottom landing of a series of flights. Staff , escape and maintenance stairs do not require a warning surface. Please refer to attached drawings for the as-built condition.
|  | Cxxx-NCR-000228 | NCR | Platform Inverts CMS (Eastbound & Westbound)Limited access and maintenance. |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-04-13 | 2022-05-20 09:31 | 37 | 2022-03-30 14:02 | Electrical - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Throughout the length of both the Eastbound and Westbound inverts there are no constraints in accessing or maintaining the straight CMS runs. However, in multiple locations in which the trunking and trays ‘T’ off in adjacent directions to pick up cross passages and access passages the maintainer would be constrained in gaining access to short lengths of CMS (these sections are identified on the marked up drawings attached and typical photos showing the extent of the constraint in the associated SAP report)
|  | Cxxx-NCR-000229 | NCR | Westbound & Eastbound Inverts - CMS Poor Workmanship |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-04-26 | 2022-05-20 09:38 | 24 | 2022-04-12 11:47 | Electrical - General | 500 |  | Incomplete Works | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During a site inspection of historic CMS installed in the Westbound & Eastbound Inverts, it has been found that there are a two cases of poor workmanship that are deemed too high risk to replace/repair. These examples have been captured via the attached SAP.
|  | Cxxx-NCR-000230 | NCR | WTH Room 6-408 Drainage Pipework Issues |  | Contr | PDP | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-07-14 14:07 | -52 | 2022-04-01 09:30 | Mechanical - Public Health Engineering | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Drainage pipework as detailed on drawing Cxxx-SKC-P-DDA-Cxxx-21154-P17 cannot be installed as __ have installed drainage pipework in room 6-047 different to the detailed design. This has resulted in the drainage pipework from the cleaners sink being unable to be installed.
|  | Cxxx-NCR-000231 | NCR | Level -1 2/777 No visible tray lid through penertration |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-04-15 | 2022-04-06 11:29 | -9 | 2022-04-01 14:56 | Electrical - General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The low level tray that penetrates from RM 2/777 does not have any visible tray lid installed to segregate the cables from the firestopping. This is indicated on observation 1 on the attached SAP report.
|  | Cxxx-NCR-000232 | NCR | Emergency Escape from UPE |  | Contr | SWN | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-07-29 14:45 | -37 | 2022-04-21 07:50 | Architectural - Doors | 3000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | (1)The UPE Doors between Services and Extract Corridor are lever handle operated from Service Corridor and key locked from the Extract Corridor. P (2)The doors to the West Bound access stairs MNS17 & MNS18 are key locked from the Sump Room side which prevents the stairs located there from being used for escape. (3)Escape from East Bound UPE is only possible via floor hatches to Platform above.
|  | Cxxx-NCR-000233 | NCR | WTH 2/777 - Non conformence in fire stopping detail. |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-09-20 07:40 | 16 | 2022-04-05 14:57 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | Please see observation 1 of the attached SAP report. The fire stopping has been undertaken prior to the completion of the CMS. The submain cables are now embedded within the firestopping compound as there is no physical barrier in place for segregation.
|  | Cxxx-NCR-000235 | NCR | CMS installation to ESS 3, WTH Levels 0 to -1 CMS Layout |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-04-25 | 2022-04-13 09:48 | -12 | 2022-04-11 10:49 | Electrical - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Following a site inspection, it has been identified that sections of the installed CMS, within the Western Ticket Hall, ESS 3. Levels 0 to -1, Also WTH Level-1 CMS Layout Sheet 2 of 4, has not been installed as per RIR (Cxxx-XRL-E-LRG-Cxxx-50001 for ESS3) and The Latest IFC Drawings , Of the Changes that deviate from the Design, Not all Have been captured Through the FCD Process either. The changes can be seen within the appended Marked up Drawings.
|  | Cxxx-NCR-000236 | NCR | DB-W-EL01/1L1 - Luminaires Not Installed as Per Cxxx-FCD-000307 |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-04-21 | 2022-04-07 15:40 | -14 | 2022-04-07 13:57 | Electrical - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Following a site inspection on DB-W-EL01/1L1, it has been raised that 1no. additional 'D/E' fitting has been installed within room 1/790 which is not shown on Cxxx-FCD-000307. Although the fitting is shown on Cxxx-SKC-E-DDA-Cxxx-31100 (P10), it was incorrectly omitted on Cxxx-FCD-000307.
|  | Cxxx-NCR-000237 | NCR | WTH to ETH Inverts - Water damaged CMS |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-08-04 22:10 | -31 | 2022-04-08 08:53 | Electrical - General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Contamination | Completed |  | During an IRN CMS Inspection it has been noted that areas of CMS have received water damage. The damage that has been caused is due to the area not being watertight.
|  | Cxxx-NCR-000238 | NCR | CMS installation to WTH Level 0 all areas. |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-05-05 | 2022-04-22 13:24 | -13 | 2022-04-21 14:39 | Electrical - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Following a site inspection, it has been identified that sections of the installed CMS, within the Western Ticket Hall, Level 0, has not been installed as per the The Latest IFC Drawings, and the Redesign RIRs (Cxxx-OVE-Z-LRG-Cxxx-50002 for SRLV III 1/661 + Cxxx-OVE-A-XPA-Cxxx-50002 Tech Wall), Of the Changes that deviate from the Design, Not all Have been captured Through the FCD Process either. The changes can be seen within the appended Marked up Drawings.
|  | Cxxx-NCR-000239 | NCR | Installation of GRP CMS without Approved MCR |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-08-25 09:16 | -10 | 2022-04-08 10:37 | Electrical - Cable Management | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | In AP2 and AP3 Level -5 the Tier 1 Contractor has installed GRP CMS without an approved MCR. CRL-MCR-005763 has been cancelled on the assumption that CRL-MCR-005272 supersedes all requirements although the latter only captures Ladder Rack and not trunking or tray.
|  | Cxxx-NCR-000240 | NCR | PES Design Plan Light Fitting Seals |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-06-17 11:03 | -79 | 2022-04-08 11:44 | Electrical - Lighting | 500 |  | Equipment Breakdown | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | It has been highlighted during site walks that a number of Design Plan light fittings along the platforms above the PSDs have internal seals hanging down within the diffusers.
|  | Cxxx-NCR-000241 | NCR | Fire Dampers blocked by grilles (ETH) |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-07-12 | 2022-07-13 15:33 | 1 | 2022-06-28 09:54 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Blade Dampers are clashing grilles preventing full open/closure.
|  | Cxxx-NCR-000242 | NCR | WTH - 1/790 & 1/579 - Clash between blockwork and Door 1/633 Steelwork |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-07-12 15:27 | -54 | 2022-04-08 12:43 | Architectural - General | 1500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | A clash has been identified between the blockwork design for the boundary wall between 1/790 and 1/579 and the door support steelwork for door 1/633. The steelwork projects through the blockwork (as per approved details on drawings: Cxxx-COF-A-DWG-Cxxx-50571 and Cxxx-COF-A-DWG-Cxxx-50677, and is also visible on the intent drawing Cxxx-SKC-S-DDD-Cxxx_1-50400). In order for this steel to be installed, the blockwork must be removed. This will require the temporary detachment of the MEP services installed on the wall, and a new blockwork design in this location.
|  | Cxxx-NCR-000243 | NCR | DB-E-B03/3L3 - Damaged Cable. |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-04-22 | 2022-04-14 15:10 | -8 | 2022-04-08 14:31 | Electrical - General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | It was raised, that one of the Escalator Up lights circuits had tripped at DB-E-B03 Circuit 3L3. Upon investigation the damage was found in ETH ECR 2/173 directly above the isolators the circuit is feeding.
|  | Cxxx-NCR-000244 | NCR | Panic escape from UPE doors |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-06-29 13:21 | -67 | 2022-04-08 15:57 | Architectural - Doors | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Panic escape from the UPE in current arrangement is not possible.
|  | Cxxx-NCR-000245 | NCR | WTH Level 2 (-1) Mess Room - LV power and CMS installed to superseded drawings |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-10-11 13:23 | 37 | 2022-04-11 12:12 | Electrical - General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | This NCR is to highlight the electrical installation in 2/331 Mess room has been installed to an old drawing Cxxx-SKC-E-DDA-Cxxx-21110 whereas the FF&E layouts have changed and should have been installed to Cxxx-XRL-E-DDA-Cxxx-21110 X03.
|  | Cxxx-NCR-000246 | NCR | DB-W-A01/10L3 - Additional 25A Isolator Installed |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-04-27 | 2022-04-13 12:08 | -14 | 2022-04-13 10:05 | Electrical - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Following a site inspection on DB-W-A01/10L3, it has been raised that an additional 25A __ isolator has been installed before the unswitched fused spur which then protects the TFL Network Cabinet. The final location of the 25A isolator is along the southern wall of 1/781 as per drawing. This NCR is seeking approval that the use of the 25A __ isolator can be installed in addition to the unswitched fused spur in the location as shown on the attached redline. Circuit DB-W-A01/10L3 has been QA assured, dead tested & the __ calculations verify the proposal.
|  | Cxxx-NCR-000247 | NCR | WTH Stairwell 3 CMS - Limited access and maintenance |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-04-26 | 2022-04-13 11:07 | -13 | 2022-04-12 14:56 | Electrical - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | During a CRL IRF inspection it was identified that a particular section of CMS (identified in observation 1 & 2 of the attached SAP report) would be difficult to access for future maintenance. The said section is at high level on the half landing of WTH Stairwell 3
|  | Cxxx-NCR-000248 | NCR | DB-W-B01/6L3 - Circuit Zs exceeding limit on __ |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-04-27 | 2022-04-14 13:50 | -13 | 2022-04-13 12:45 | Electrical - General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Due to the cable length that has been installed on site cable being longer that what was originally calculated on __, the Zs for the circuit no longer falls within the maximum Zs value.
|  | Cxxx-NCR-000249 | NCR | Additional light installed on circuit DB-W-B01 4L2 in room 1/790. |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-04-28 | 2022-04-14 14:02 | -14 | 2022-04-14 13:25 | Electrical - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Following a site inspection on DB-W-B01/4L2, it has been raised that 1no. additional 'D/E' fitting has been installed within room 1/790 which is not shown on code 1 drawing Cxxx-SKC-E-DDA-Cxxx-31100.
|  | Cxxx-NCR-000251 | NCR | WTH Level 0 CMS - Limited Access and Maintenance |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-07-01 08:57 | -65 | 2022-04-20 07:53 | Electrical - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | 1.Access and maintenance for future works etc are achievable via maintenance windows (unrestricted sections of CMS), rodding points etc. The obstruction (luminaries, conduits, etc) causes particular sections of CMS to be out of reach whilst using safe means of access equipment. Please refer to observations 1, 3 & 11 within the SAP report attached 2.Obstruction to access and maintain CMS routes. The obstruction (ie; luminaries, unistruts, other types of CMS) causes sections of CMS to be out of reach whilst using safe means of access equipment. Please refer to observations 14, 15 & 16 within SAP report attached. These observations refer to areas which will require assets to be removed to facilitate access The attached SAP report also captures areas in which there is no access and maintenance issue but have been recorded to give assurance that a comprehensive check has been undertaken (observations 2, 4, 5, 7, 8, 9, 10, 12, 13 & 18) *Note – Observation no.6 refers to high level CMS which is already captured within Cxxx-NCR-000210 ‘WTH Level +0.5 CMS A&M’ (observation 5 within attached SAP) in which the close out is to demonstrate access can be achieved via fixed scaffold if necessary.
|  | Cxxx-NCR-000253 | NCR | CMS installation to WTH Level -4 |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-05-11 | 2022-04-28 07:14 | -13 | 2022-04-27 13:30 | Electrical - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | Following a site inspection, it has been identified that sections of the installed CMS, within the Western Ticket Hall, Level -4, has not been installed as per the The Latest IFC Drawings, Of the Changes that deviate from the Design, Not all Have been captured Through the FCD Process either. The changes can be seen within the appended Marked up Drawings.
|  | Cxxx-NCR-000254 | NCR | WTH L-3 AP1 Link Passage Sumps SP1 and SP2 isolators |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-05-19 | 2022-05-01 09:34 | -18 | 2022-04-21 11:25 | Electrical - General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Limited access to top screws on SP1 and SP2 isolators when fixed access panels are installed
|  | Cxxx-NCR-000255 | NCR | L-5 PES Grill Anti Lift Cleats - Anti Lift Cleat Fixings Damaged |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-05-05 | 2022-05-20 07:22 | 15 | 2022-04-21 14:34 | Architectural - General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | It has been identified that the some of the fixings which secure the anti-lift cleats above the architectural grills at each end of the platforms are unable to be removed. The M5 button head fixings are spinning when attempts are made to remove them. As such the grills are unable to be removed - currently there are various trades who need to access behind these grills to undertake surveys to progress design on other works. Please refer to the attached drawings and photographs of the grills in question.
|  | Cxxx-NCR-000257 | NCR | CMS installation to WTH Level -2. |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-05-27 | 2022-05-13 14:09 | -14 | 2022-05-13 11:43 | Electrical - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Following a site inspection, it has been identified that sections of the installed CMS, within the Western Ticket Hall, Level -2, has not been installed as per the The Latest IFC Drawings, Of the Changes that deviate from the Design, Not all Have been captured Through the FCD Process either. The changes can be seen within the appended Marked up Drawings.
|  | Cxxx-NCR-000259 | NCR | CMS installation to WTH Risers 680+681 |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-05-20 | 2022-05-08 15:30 | -12 | 2022-05-06 15:21 | Electrical - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Following a site inspection, it has been identified that sections of the installed CMS, within the Western Ticket Hall, Risers 680+681, has not been installed as per the The Latest IFC Drawings, Of the Changes that deviate from the Design, Not all Have been captured Through the FCD Process either. The changes can be seen within the appended Marked up Drawings.
|  | Cxxx-NCR-000263 | NCR | Stainless steel J.Bs installed without MCR |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-07-21 12:24 | -45 | 2022-04-28 12:10 | Electrical - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | Following a site inspection a number of stainless-steel JBs, manufactured by Rittal have been installed station wide without an approved MCR.
|  | Cxxx-NCR-000265 | NCR | UPS switchboards do not comply with BS EN 62305-4 |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-08-19 15:04 | -16 | 2022-05-04 07:53 | Electrical - Earthing & Bonding | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The lightning protection Level (LPL) has been calculated as level II therefore the LPL classification is class II. In addition to the lightning protection classification the level of protection required for the Electrical and Electronic equipment has also been calculated. Electrical and Electronic equipment is protected against both direct and indirect lightning strikes to the structure and connected services, with a LEMP Protection Measures System (LPMS). For both the Eastern and Western station boxes and OSD’s the following measures will be required: Electrical and Electronic Systems: In addition to the lightning protection classification the level of protection required for the Electrical and Electronic equipment has also been calculated. Electrical and Electronic equipment is protected against both direct and indirect lightning strikes to the structure and connected services, with a LEMP Protection Measures System (LPMS). For both the Eastern and Western station boxes and OSD’s the following measures will be required: • 25kA standard equipotential bonding Type 1 SPD to protect line 1 (400v) at its entrance to the structure in accordance with BS EN 62305-3. Protection will be provided on the incoming side of the main ACB’S at both ‘A’ and ‘B’ main switch boards. • Mains transient overvoltage Type 2 and Type 3 SPD’s at all sub-distribution boards and at equipment level for critical equipment in accordance with BS EN 62305-4. Protection will be provided on the incoming supplies to the UPS switch boards and CER distribution boards. • 2.5kA (per pair) standard equipotential bonding Type 1 SPD to protect line 2 (telecoms) at its entrance to the structure in accordance with BS EN 62305-3. It should be noted that during construction of the OSD additional measures will be required for all mains power and telecom lines entering or leaving the building. Additional allowance should be made for, but not limited to: • Roof mounted plant equipment with cables entering the building • Fire alarm cabling • Security and CCTV • External Lighting • Mains power or telecoms/data cabling entering a neighbouring building from the OSD
|  | Cxxx-NCR-000268 | NCR | Cannot access WTH Sump Extract Damper SE-W-FD002 - IRN-M-50035 __-00269 |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-07-12 | 2022-11-16 17:20 | 127 | 2022-06-28 10:00 | Mechanical - Heating Ventilation & Air Conditioning | 0 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | Access for maintenance to WTH Sump Extract System Fire Damper SE-W-FD002 in the corner of room 5/397 is prevented by other systems' CMS and bracketry. see drawing Cxxx-XRL-M-DDA-Cxxx-11143_P01
|  | Cxxx-NCR-000269 | NCR | Missing benchmark for stair nosings and corduroy tactiles |  | Contr | SWN | BOS - Bond Street Station (West) |  | 2022-05-23 | 2022-06-10 11:59 | 18 | 2022-05-09 15:21 | Architectural - Flooring | 500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | Escape stair nosings and corduroy tiles were installed on site without a benchmark being established as required by Architectural Specification JA 4011 ; JL30 2105. Subsequent site inspection by LU SIR 757 had also identified misinterpretation by designers of BS8300, Part M and LU S1133 which has lead to corduroys being installed where these are not required or 400mm wide instead of 800mm wide band. Cxxx-NCR-000227 was raised for corrections to be implemented .
|  | Cxxx-NCR-000271 | NCR | ESC Pits CMS - Installation of Stainless Steel Trunking Without Approved MCR |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-08-11 13:18 | -24 | 2022-05-11 08:44 | Electrical - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | Following a site inspection on ESC ETH 11,12,13 & WTH 17,18 & 19 Pits CMS, it has been raised that the stainless-steel trunking has been installed without an approved MCR. The stainless steel trunking has been installed within ETH 7/776 & WTH 7/775
|  | Cxxx-NCR-000272 | NCR | P&T - Lower Concourse & Cross Passage Floor Tiling QA Documentation NOT Signed by CRL Architects |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-06-30 | 2022-05-30 14:36 | -31 | 2022-05-17 10:56 | Architectural - Flooring | 500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Management Problem - Not Defined | Completed |  | Following the completion of the Granazzo Cem Floor Tiling in the Lower Concourse & Cross Passages on LEVEL -5, these areas were inspected and tested by the sub-contractor with only the main contractor present. The Crossrail architects were never invited for any of these inspections or to witness any testing.
|  | Cxxx-NCR-000276 | NCR | ETH Level -5 CMS installation. |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-06-08 | 2022-05-27 11:13 | -12 | 2022-05-25 11:53 | Electrical - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Following a site inspection, it has been identified that sections of the installed CMS, within Eastern Ticket Hall Level -5 has not been installed as per The Latest IFC Drawings , Of the Changes that deviate from the Design, Not all Have been captured Through the FCD Process either. The changes can be seen within the appended Marked up Drawings.
|  | Cxxx-NCR-000279 | NCR | WTH Level -5 CMS Installation |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-06-24 | 2022-06-10 08:59 | -14 | 2022-06-10 07:40 | Electrical - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Following a site inspection, it has been identified that sections of the installed CMS, within the Western Ticket Hall, Level -5, has not been installed as per the The Latest IFC Drawings, Of the Changes that deviate from the Design, Not all Have been captured Through the FCD Process either. The changes can be seen within the appended Marked up Drawings.
|  | Cxxx-NCR-000280 | NCR | Structural opening too large creating a mastic gap above 20mm |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-05-27 | 2022-05-31 15:24 | 4 | 2022-05-13 07:57 | Architectural - Doors | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Below list of doors have mastic gaps up to 27mm- W-04-414-D01 E-01-088-D02 E-03-91-D02
|  | Cxxx-NCR-000281 | NCR | Post IRN Earthing Changes related to Sump Panel Design Changes |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-06-24 11:33 | -72 | 2022-05-16 11:19 | Electrical - Earthing & Bonding | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | As a consequence of the Sump Panel design changes detailed in Cxxx-FCD-000262 and Cxxx-FCD-000258 there were changes made to the earthing design which are also included within the above FCD's. Therefore updated assurance will need to be provided on the earthing works once completed as the related IRN's have been completed.
|  | Cxxx-NCR-000282 | NCR | P&T - AP1 Corridor Floor Tiling QA Documentation NOT Signed by CRL Architects |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-06-30 | 2022-05-25 07:41 | -36 | 2022-05-18 15:01 | Architectural - Flooring | 500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Management Problem - Not Defined | Completed |  | Following the completion of the Granazzo Cem Floor Tiling in the AP1 Corridor on LEVEL -3 under the previous contract, these areas were inspected and tested by the sub-contractor with only the main contractor present. The Crossrail architects were never invited for any of these inspections or to witness any testing.
|  | Cxxx-NCR-000283 | NCR | Records in package listings are not specific to the works |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2022-07-20 | 2022-08-25 16:34 | 36 | 2022-05-18 08:42 | Information Management - General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Other human error | Completed |  | Package listings list latest revisions of documents not the revisions that were followed for construction. One as an example: construction records pack Cxxx-DCC-A-LRC-Cxxx-50037 list following revisions: Cxxx-SKC-A-DDA-Cxxx-03150 C01 Cxxx-SKC-A-DDA-Cxxx-03151 C01 Cxxx-SKC-A-DDA-Cxxx-03152 C01 And package listing Cxxx-XRL-A-CER-Cxxx-50004 lists following Cxxx-SKC-A-DDA-Cxxx-03150 P15 Cxxx-SKC-A-DDA-Cxxx-03151 P12 Cxxx-SKC-A-DDA-Cxxx-03152 P12
|  | Cxxx-NCR-000284 | NCR | Works started without accepted Method Statement |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2022-07-20 | 2022-06-28 08:57 | -22 | 2022-05-18 09:16 | Health & Safety General | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Not Defined | Completed |  | Work has started on site without specific Method Statement (MS) or Task Briefing. Some instances MS gets signed off and not uploaded to eB. Examples of couple of instances found during review of the package listings: 1. __ - Matwell - __ Grout Application (C442-KNB-A-CER-Cxxx-50011) MS listed is for __ Reinforced Concrete - TVS Specific C442-KNB-O1-GMS-Cxxx-50004 and does not cover the works. 2. WTH - Level 0.5 OSD Central Core Openings and Drainage Connection (Cxxx-COF-C-CER-Cxxx-50012) MS listed is Cxxx-SKC-O1-RGN-Cxxx-50293, should have had their own MS to follow, they could not have followed Cxxx MS. Process to be implemented to make sure that no work starts before there is task specific Method Statement in place.
|  | Cxxx-NCR-000285 | NCR | Records generated as part of the inspection are not as per accepted ITP |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-06-28 09:02 | -68 | 2022-05-18 09:35 | Information Management - General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Not Defined | Completed |  | Records to assure the works in ITP record packs are not the ones agreed during ITP acceptance process. Examples of couple of instances found during review of the package listings: 1. Check sheet used in ITP record pack (Cxxx-COF-A-LRC-Cxxx-50082 Cxxx P&T - - AP2 Bullnose Steel Installation Records) is not part of ITP (Cxxx-COF-A-ITP-Cxxx-50002 Cxxx Inspection & Test Plan (ITP) - Site installation of galvanised steel for PES Ends, ES2 barrel support, AP2 and AP3, ES1 Top End, Concourse End). Check sheet used in the record pack is for primary steel, ITP has check sheet for galvanised steel. Has the wrong check sheet or ITP been used? 2. Check sheet used in ITP record pack (Cxxx-COF-C-CER-Cxxx-50012 WTH - Level 0.5 OSD Central Core Openings and Drainage Connection) is not part of ITP (C450-__-M-ITP-Cxxx-50001 Installation & Testing of Public Health Systems (Gravity, Vent & Pumped Drainage Pipework & Fittings)). Missing pull out test and visual inspection, pressure test done on different form/different company and Calibration records not submitted. Process to be implemented to make sure that check sheets that are used to assure the works are the ones attached to accepted ITP.
|  | Cxxx-NCR-000286 | NCR | Redline drawing management process |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-09-12 09:32 | 8 | 2022-05-18 09:54 | Information Management - General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Checking the package listings it was noted that not all the design changes are marked on redline drawings. For example: 1. - AP2 Bullnose Steel Installation (Cxxx-COF-A-CER-Cxxx-50073) * Cxxx-FCD-001385 ‘AP2 - Bullnose Door coordination DAL fitting above’ mentioned on package listing is changing drawing Cxxx-SKC-A-DDC-Cxxx-21600 ‘Proposed additional skirting line to stainless steel’. Who will be redlining Cxxx-SKC-A-DDC-Cxxx-21600? or is there Cxxx revision of this drawing? * Cxxx-FCD-001217 ‘AP3, Level -5, Vertical steelwork goal post braced of the RC back wall revised proposal’. What drawing was amended against this change? 2. WTH - Level 0.5 OSD Central Core Openings and Drainage Connection (Cxxx-COF-C-CER-Cxxx-50012) * Cxxx-SKC-P-DDA-Cxxx-21095 X02 lists PMI (Cxxx-PMI-01425) to remove the sink, but Cxxx-XRL-P-DDA-Cxxx-21095 X01 does not. Why? What drawing should be listed in package listing Cxxx or Cxxx? * Following drawings used for construction but not redlined, why? Cxxx-SKC-P-DDA-Cxxx-21100 Western Ticket Hall, Station Drainage Layout, Level 0 Cxxx-SKC-P-DDA-Cxxx-21112 Western Ticket Hall, Station Drainage Layout, Level -1, Sheet 2 of 4 Cxxx-SKC-P-DDE-Cxxx-56100 Western Ticket Hall, Public Health Services, Station Drainage Schematic There is Cxxx X01, X02 and X03 revisions for drawing Western Ticket Hall, Public Health Services, Station Drainage Schematic (Cxxx-XRL-P-DDE-Cxxx-56100). Should this drawing be listed? Site team noted that they are following Cxxx-XRL-Z-XCS-Cxxx-50003 CANCELLED - Cxxx - MEP Redline Drawing and As Built Process. Process to be implemented to make sure that red line drawings are accurate, record all the changes and all the relevant drawings are listed in package listing and redlined. Redline process to be amended and submitted for approval.
|  | Cxxx-NCR-000287 | NCR | Earth bonding from the local Earth bar not directly connected to the dedicated earthing terminal of the ATS's and MCC Panels |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-07-05 15:34 | -61 | 2022-05-18 10:24 | Electrical - Earthing & Bonding | 2000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The Earth bonding from the local Earth bar is not directly connected to the dedicated earthing terminal of the ATS's and MCC Panels, some have been cross bonded to the copper banjo CPC connection of the SWA cables as they entre the panels. 1. ETH SPR MCC 2. WTH F__ No. 1 MCC
|  | Cxxx-NCR-000288 | NCR | Self Certification process |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-07-06 13:11 | -60 | 2022-05-18 11:18 | Information Management - General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Surveillance Review of 8 random accepted certification packs picked up that not all required data (assurance documents, PTRs, drawings, redlines) is listed in package listings. Please see report Cxxx-XRL-O4-RGN-Cxxx-50021. Process should be improved to make sure all relevant data is recorded, and information given to the person who creates the package listing. Responsibility to put package listing together should be with the person who managed the job (package manager), not the quality team representative who doesn’t have the knowledge what happened on site.
|  | Cxxx-NCR-000290 | NCR | CMS Installation WTH Level -1 |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-07-04 | 2022-06-21 10:10 | -13 | 2022-06-20 14:57 | Electrical - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Following a site inspection, it has been identified that sections of the installed CMS, within the Western Ticket Hall, Level -1, has not been installed as per the The Latest IFC Drawings, Of the Changes that deviate from the Design, Not all Have been captured Through the FCD Process either. The changes can be seen within the appended Marked up Drawings.
|  | Cxxx-NCR-000291 | NCR | Earth Bar (SEB-W-B4-09) within WTH UPS room has Doubled Up Terminations and is at Full Capacity |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-06-23 11:38 | -73 | 2022-05-22 16:24 | Electrical - Earthing & Bonding | 3000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | BOS Electrical VIRS Item 23 - Earth Bar (SEB-W-B4-09) within WTH -4 UPS room has doubled up terminations and is at full capacity. There is space available to install an auxilary earth bar and relocate the doubled up termiations to their own stud.
|  | Cxxx-NCR-000292 | NCR | ETH -5 Burried Earth nest connections have been installed in bare copper |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-06-22 14:10 | -74 | 2022-05-22 17:36 | Electrical - Earthing & Bonding | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | BOS Electrical VIRS Item 31 Earth nest connections have been installed in bare copper. The connections have been covered over with concrete. Please confirm if the terminations have Denso tape or similar to prevent reaction with lime in the concrete. Obtain installation records to confirm if copper tape protection has been used in the concrete. If protection has not been provided then measures to protect the copper tape are to be installed
|  | Cxxx-NCR-000294 | NCR | Earth Bar (SEB-E-B5-11) within ETH -5 PSD room is at Full Capacity however Bonds Needed to be Installed to Sump Pump Panels |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-06-23 16:33 | -73 | 2022-05-27 08:55 | Electrical - Earthing & Bonding | 3000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Earth Bar (SEB-E-B5-11) within ETH -5 PSD room is at full capacity however bonds are required to be installed to the Sump Pump Panels. There is space available to install an auxiliary earth bar on top of the current earth bar and link the two together.
|  | Cxxx-NCR-000297 | NCR | WTH Level -1 CMS installation. |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-07-06 | 2022-06-22 14:19 | -14 | 2022-06-22 13:45 | Electrical - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | "Following a site inspection, it has been identified that sections of the installed CMS, within the Western Ticket Hall, Level -1, has not been installed as per the The Latest IFC Drawings, Of the Changes that deviate from the Design, Not all Have been captured Through the FCD Process either. The changes can be seen within the appended Marked up Drawings. "
|  | Cxxx-NCR-000298 | NCR | Fire Damper actuator access impeded - FD-019 ETH Ancillary - IRN-M-5004 |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-07-12 | 2022-09-29 09:30 | 79 | 2022-06-28 10:01 | Mechanical - Heating Ventilation & Air Conditioning | 0 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Access for maintenance of actuator is compromised due to proximity of BSA Box. Fire Damper FD-019 in room 5/932 ETH Level -4 Also: damper indicator missing.
|  | Cxxx-NCR-000299 | NCR | Access issue to damper FD-042 ETH Ancillary - IRN-M-50044 |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-07-12 | 2022-09-16 09:45 | 66 | 2022-06-28 10:01 | Mechanical - Heating Ventilation & Air Conditioning | 0 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Access for maintenance is compromised due to surrounding equipment/CMS. Fire Damper FD-042 in room 3/097 ETH Level -2
|  | Cxxx-NCR-000300 | NCR | GE-E-FD096 obstructed by a fire junction box - ETH Gen Extract - IRN-M-50041 __-00268 |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-07-12 | 2022-11-16 17:21 | 127 | 2022-06-28 10:05 | Mechanical - Heating Ventilation & Air Conditioning | 0 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | General Extract Fire damper GE-E-FD096 obstructed by a fire junction box in Circulation Area A/071. See attached drawing 52262 & photo
|  | Cxxx-NCR-000301 | NCR | GE VCD serving CER ETH level -4 obstructed by light fitting __ - ETH Gen Extract - IRN-M-50041 |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-07-12 | 2022-09-16 09:52 | 66 | 2022-06-28 10:05 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | ETH General Extract VCD obstructed by light fitting - end-of-corridor/Lobby 5/097 - see attached DWG 52246 and photo.
|  | Cxxx-NCR-000302 | NCR | Fire Defects - VAR Report - Attached to CRL-OBS-36212 |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-06-28 07:59 | -68 | 2022-06-01 09:50 | Fire - Fire Systems & General | 30000 |  | Incorrect Installation | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | Refer to CRL-OBS-36212. Defects as listed on VAR report (photos 1-4).
|  | Cxxx-NCR-000304 | NCR | ETH - Addictional Exit Light installed post IRN |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-06-22 | 2022-06-15 15:58 | -7 | 2022-06-08 08:34 | Electrical - General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Cxxx-FCD-000273 has been raised to capture additional exit lights to be installed, highlighted as a result of a discrepancy identified between the lighting drawings and the fire strategy drawings. This NCR has been raised to capture the assurance for the additional light added to circuit DB-E-EL01/1L1.
|  | Cxxx-NCR-000305 | NCR | Addictional Exit Lights D.B-W-EL03 |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-06-23 21:17 | -73 | 2022-06-09 09:42 | Electrical - General | 3000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | Cxxx-FCD-000273 has been raised to capture additional exit lights to be installed. These lights have been highlighted as a result of a discrepancy identified between the lighting drawings and the fire strategy drawings. This NCR has been raised to capture the assurance for the additional lights added to circuits D.B-W-EL03/3L1 & 8L2.
|  | Cxxx-NCR-000306 | NCR | DB-E-B07/2L2 - Additional Lighting ETH Level -5 room 6-821 |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-06-22 13:20 | -74 | 2022-06-09 12:11 | Electrical - General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Cxxx-FCD-000311 has been raised for the installation of 2 x Light fittings in room 6-821. This NCR has been raised to capture the assurance for 1 of the additional lights on circuit DB-E-B07/2L2.
|  | Cxxx-NCR-000307 | NCR | DB-E-EL07/5L3 - Additional Lighting ETH Level -5 room 6-821 |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-06-22 13:35 | -74 | 2022-06-09 14:00 | Electrical - General | 3000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Cxxx-FCD-000311 has been raised for the installation of 2 x Light fittings in room 6-821. This NCR has been raised to capture the assurance for 1 of the additional lights on circuit DB-E-EL07/5L3 .
|  | Cxxx-NCR-000308 | NCR | CMS installation to WTH Escalators Levels 0 to -5. |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-06-24 | 2022-06-10 10:53 | -14 | 2022-06-10 08:38 | Electrical - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | "Following a site inspection, it has been identified that sections of the installed CMS, within the Western Ticket Hall, Escalators, Levels 0 to -5, has not been installed as per the The Latest IFC Drawings, Of the Changes that deviate from the Design, Not all Have been captured Through the FCD Process either. The changes can be seen within the appended Marked up Drawings. "
|  | Cxxx-NCR-000309 | NCR | WTH - Minor Lighting changes & Red Lines. |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-08-03 13:24 | -32 | 2022-06-10 10:30 | Electrical - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | This NCR needs to cover all the minor changes made to lighting orientation/minor layout changes. The changes that will be picked up do not require any close out paperwork (QA Checksheets or Test sheets) but will require updated redlines for each level.
|  | Cxxx-NCR-000310 | NCR | ETH - Minor Lighting changes & Red Lines. |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-06-24 09:57 | -72 | 2022-06-10 10:29 | Electrical - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | This NCR needs to cover all the minor changes made to lighting orientation/minor layout changes. The changes that will be picked up do not require any close out paperwork (QA Checksheets or Test sheets) but will require updated redlines for each level.
|  | Cxxx-NCR-000311 | NCR | Cat5 & Potable water booster sets incorrect for WTH and ETH Domestic H&C Water - IRNs P-50002 & 50003 |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-07-08 | 2022-07-08 14:55 | 0 | 2022-06-28 10:06 | Mechanical - Hot & Cold Water Supplies | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Water tank booster sets have been mixed up: On ETH smaller tank Booster @0.75 kW needs to change to 0.55 (Booster on Larger tank @1.1 kW is correct) On WTH smaller tank Booster @1.5 kW needs to change to 0.75 On WTH Larger Cat5 tank Booster @0.55 kW needs to change to 1.5 (see also Cxxx-FCD-000346 & 000347 for __ Wiring diagrams)
|  | Cxxx-NCR-000313 | NCR | SY Cable used on ETH & WTH Entrance Gate Motors |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-08-19 11:48 | -16 | 2022-06-10 13:54 | Electrical - General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | Non compliant SY Cable has been installed on the ETH & WTH Entrance Gate Motors (see attached photo).
|  | Cxxx-NCR-000315 | NCR | DB-E-EL07/1L1 - Addictional fitting added to circuit. |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-06-28 09:22 | -68 | 2022-06-13 09:42 | Electrical - General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Cxxx-FCD-000028 has been raised to facilitate the installation of an additional light to DB-E-EL07/1L1. This NCR has been raised to capture the assurance for this fitting.
|  | Cxxx-NCR-000316 | NCR | DB-E-EL08/3L1,3L2,5L2,10L3 - Addictional points added to circuit. |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-09-09 14:12 | 5 | 2022-06-13 14:14 | Electrical - General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Additional points have been added to circuits DB-E-EL08/3L1,3L2,5L2,10L3 post IRN. This NCR has been raised to capture the assurance for these additional points. These changes have been highlighted via Cxxx-FCD-000297.
|  | Cxxx-NCR-000317 | NCR | ETH General Extract Fan GE-E-EF001 |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-08-10 17:09 | -25 | 2022-06-15 16:25 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | On inspection the fan unit was found to have been incorrectly installed back to front and contrary to the design drawings. The unit will need to be mechanically and electrically disconnected and the unit rotated. The unit will need to be reconnected mechanically once rotated but electrical and BMS services will need to be re-worked as the connections will be on the wrong side.
|  | Cxxx-NCR-000318 | NCR | Flexi-conduit blocking access to damper GE-W-FD020 - WTH Gen Ex. ductw. IRN-M-50032 __-00268 |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-07-06 | 2022-11-16 17:20 | 133 | 2022-06-22 14:19 | Mechanical - Heating Ventilation & Air Conditioning | 0 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | Low pressure water mist flexible pipe to the ceiling panel mounted nozzle blocks maintenance access to the Fire damper GE-FD020 on General Extract ductwork at High-level above doorway in Platform Staff/Male Locker room 6/316 WTH Level -5. See drawing Cxxx-XRL-M-DDA-Cxxx-11155_P01
|  | Cxxx-NCR-000319 | NCR | Support rail blocking access to damper AS-W-FD030 - WTH Ancillary ductw. IRN-M-50033 __-00268 |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-07-12 | 2022-11-16 17:21 | 127 | 2022-06-28 10:07 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | Damper AS-W-FD030 access for maintenance is blocked by exit sign conduit and support rail. See drawing Cxxx-XRL-M-DDA-Cxxx-11141_P01
|  | Cxxx-NCR-000320 | NCR | Support rail blocking access to damper GE-W-FD040 - WTH Gen Ex. IRN-M-50032 __-00268 |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-07-12 | 2022-11-16 17:21 | 127 | 2022-06-28 10:07 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Planning | Repair | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | Support rails and drop-rods hinder maintenance access to damper FD040 at high level (above duct/grille) in LV Switch room III 6/674. See drawing Cxxx-XRL-M-DDA-Cxxx-11141_P01
|  | Cxxx-NCR-000321 | NCR | Blocked access to damper AS-W-FD131 - WTH Ancillary ductw. IRN-M-50033 |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-07-12 | 2022-09-16 10:22 | 66 | 2022-06-28 10:08 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | VCD serving Ancillary ductwork in 2/907 and Fire damper FD131 has very difficult access due to __ pipe bracket/drop rod. Could it be cut back to allow access? see Drawing: Cxxx-XRL-M-DDA-Cxxx-11112_P01 Congested area of services hindering maintenance particularly for higher levels.
|  | Cxxx-NCR-000322 | NCR | Blocked access to damper AS-W-FD142 - WTH Ancillary ductw. IRN-M-50033 |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-07-12 | 2022-09-16 10:35 | 66 | 2022-06-28 10:08 | Mechanical - Heating Ventilation & Air Conditioning | 0 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | An earth tray blocks access to two fire dampers. AS-W-FD142 The earth tray needs moving Circulation Area (Corridor)-2/074 see Drawing: Cxxx-XRL-M-DDA-Cxxx-11112_P01 Congested area of services - including 3 sets pipework -hindering maintenance particularly for higher levels.
|  | Cxxx-NCR-000324 | NCR | VCD serving 2/074 has very difficult access - WTH Ancillary ductw. IRN-M-50033 |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-10-19 | 2022-10-05 15:34 | -14 | 2022-10-05 15:28 | Mechanical - Heating Ventilation & Air Conditioning | 0 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | VCD and adjacent grille on Ancillary ductwork in 2/074 have very difficult access due to other services.
|  | Cxxx-NCR-000325 | NCR | VCD serving 2/763 has very difficult access - WTH Ancillary ductw. IRN-M-50033 |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-10-14 | 2022-10-01 13:09 | -13 | 2022-09-30 12:05 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | VCD on Ancillary ductwork in 2/763 has very difficult access due to other services.
|  | Cxxx-NCR-000326 | NCR | VCD serving 2/777 has very difficult access - WTH Ancillary ductw. IRN-M-50033 |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-10-14 | 2022-10-01 12:03 | -13 | 2022-09-30 12:06 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | VCD on Ancillary ductwork in 2/777 has very difficult access due to other services.
|  | Cxxx-NCR-000327 | NCR | VCD serving rooms down stream is very difficult access - WTH Ancillary ductw. IRN-M-50033 |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-10-14 | 2022-10-01 10:43 | -13 | 2022-09-30 12:06 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | VCD on Ancillary ductwork serving rooms downstream from 5/072 corridor has very difficult access due to other services.
|  | Cxxx-NCR-000328 | NCR | DALI - DB-E-B09/5L1 |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-07-06 | 2022-06-24 08:54 | -12 | 2022-06-22 15:14 | Electrical - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | While marking up ETH -5 it has been noticed that Cxxx-FCD-000174- Captures the location change and number of point from DB-E-B09/5L1 as 6x FCUs on the First Rev and 5X FCUs on the second rev. There are actually 7X FCUs installed on the circuit. This is different to the FCD and also Different to the Signed SAF - Cxxx-XRL-E-LRC-Cxxx-50149.
|  | Cxxx-NCR-000329 | NCR | DALI - DB-E-B07/9L1 |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-07-07 | 2022-06-24 13:35 | -13 | 2022-06-23 08:46 | Electrical - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | While marking up ETH -5 it had been noted that Cxxx-FCD-001809 & Cxxx-FCD-000145- Capture the location change and number of points on DB-E-B07/9L1. It shoes 4x FCUs on the on the marked up drawings however there are actually 5X FCUs installed on the circuit. This is different to the FCD and also Different to the Signed SAF - Cxxx-XRL-E-LRC-Cxxx-50110.
|  | Cxxx-NCR-000330 | NCR | Earthing and Bonding updates for Water Mains connections and equipment rooms 3/772 & 6/906 - Cxxx-FCD-000333 |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2022-07-05 | 2022-06-27 15:05 | -8 | 2022-06-21 16:13 | Electrical - Earthing & Bonding | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Assurance documentation and inspection records needed for works related to Cxxx-FCD-000333 - Earthing and Bonding updates for Water Mains connections and equipment rooms 3/772 & 6/906.
|  | Cxxx-NCR-000331 | NCR | WTH -5 LVSRA 2 No Main 300mm Earth connections LOOSE |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2022-07-05 | 2022-06-24 13:30 | -11 | 2022-06-21 16:33 | Electrical - Earthing & Bonding | 500 |  | System Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | WTH -5 LVSRA 2 No Main 300mm Earth connections found loose and torque markings misaligned. Terminations to be tourqued to the manufactures recommendation. The nuts are to be marked. Photographic evidence is to be submitted to confirm work complete. Location: Room 6/673 (LV Switch Room A)
|  | Cxxx-NCR-000332 | NCR | VCD obstructed room 2/763 WTH Gen Extract ductwork -IRN-M-50032 |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-10-14 | 2022-10-01 07:48 | -13 | 2022-09-30 12:07 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | VCD on General Extract ductwork in room 2/763 is obstructed by other services
|  | Cxxx-NCR-000333 | NCR | VCD obstructed room 5/665 WTH Gen Extract ductwork -IRN-M-50032 |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-10-14 | 2022-10-01 06:27 | -13 | 2022-09-30 12:07 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | VCD on General Extract ductwork is obstructed for access by other services (batteries below) in room 5/665
|  | Cxxx-NCR-000334 | NCR | VCD obstructed room 5/674 WTH Gen Extract ductwork -IRN-M-50032 |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-07-06 | 2022-10-20 09:10 | 106 | 2022-06-22 15:19 | Mechanical - Heating Ventilation & Air Conditioning | 300 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | VCD on General Extract ductwork in room 5/674 is obstructed by other services
|  | Cxxx-NCR-000337 | NCR | BMS Head End Server - Alteration to Circuitry on DB-W-UPS04/3L1 |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-07-08 | 2022-07-06 08:13 | -2 | 2022-06-24 08:23 | Electrical - General | 2000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | WTH Level -4 BMS Room 5/746 (Addition of 2 double sockets to circuit DB-W-UPS04/3L1) Due to the BMS field equipment (BMS Computer, Server, Head End) having moulded plugs and the outlets that are provided from distribution board DB-W-UPS04 being fused spurs, ESD are to add 1no double socket to each of the load sides of the 2 no fused connection units within room 5/746. This enables the said BMS equipment to be connected without compromising the warranty of the equipment (avoiding cutting off the moulded plugs) and allows for mobility of the equipment at later dates. Having the sockets connected to the load side of the FCUs ensures the electrical circuit remains protected from nuisance tripping/overloading at the DB should any other unknown equipment be plugged in.
|  | Cxxx-NCR-000338 | NCR | Additional Light Installed Post IRN DB-W-B03 |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-07-22 | 2022-07-13 10:23 | -9 | 2022-07-08 07:59 | Electrical - General | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Additional light installed post IRN to DB-W-B03/2L3 located in WTH -3 (SID 4/414) Additional light installed as per Cxxx-FCD-000312. NCR is to be raised to capture assurance against Cxxx-XRL-E-N0X-Cxxx-50161
|  | Cxxx-NCR-000339 | NCR | Non Compliant Average Lux Calculation in Multiple Areas |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-07-12 | 2022-09-29 08:28 | 79 | 2022-06-28 08:27 | Electrical - Lighting | 10000 |  | Design | Use As-Is | 2 (6-60k) | Complete | Design Problem - Other | Completed |  | There are a number of areas listed below which do not meet the minimum lux value required for 1-066 A2 at 100% output. C40-RFI-000156 has been raised to CRL Design Team seeking confirmation as to the mitigation in each instance and will facilitate the close out of the NCR. ETH - 1/083 - 2/674 - 6/674 - 6/669 - 6/670 - Z/632 WTH - A/974 - 1/089 - 1/401 - 1/932 - 2/088 - 2/964 - 4/780 - 5/925 - 6/771
|  | Cxxx-NCR-000340 | NCR | Bond St Station Roundel - No MCR for the LED strip lighting. |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-08-08 | 2022-10-21 07:58 | 74 | 2022-07-25 09:29 | Electrical - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Elizabeth line roundel signs that are external to both Ticket halls fall in Zone LPZ 0B. This has been risk assessed inline with the requirements of BS EN 62305-4. It was identified that the roundels fell outside the prescribed zone therefore requiring a level of surge protection to be installed to mitigate any transient currents from entering the building in the event of a lightning strike. This detail had not been identified in the original CRL-MCR-007826 as the As built Lighting risk assessment was completed post submission.
|  | Cxxx-NCR-000341 | NCR | DB-W-A04/1L2 - Addictional light fitting added to circuit post IRN |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-07-14 | 2022-07-07 16:05 | -7 | 2022-06-30 11:22 | Electrical - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | While carrying out lighting red lines it has been noticed that in FAN ROOM 5/777 an additional light has been installed on circuit DB-W-A04/1L2. This NCR has been raised to capture the assurance for this additional light.
|  | Cxxx-NCR-000342 | NCR | Redline Drawings to be Produced to Capture Additional Trunking Not Included Within Current CMS Layout Drawings |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-07-14 | 2022-08-24 14:13 | 41 | 2022-06-30 10:13 | Electrical - Cable Management | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Mostly associated to BMS, there are a number of areas throughout the station where trunking has been installed but not included on the CMS redline drawings produced to support the Primary CMS IRNs. Therefore, there is a need to include all trunkings which are directly linked to the primary CMS on the latest as built CMS layout drawings.
|  | Cxxx-NCR-000343 | NCR | ETH -5 Busbar Hold Down Clamps Missing (6/075) |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2022-09-17 | 2022-08-22 13:35 | -26 | 2022-07-01 08:07 | Electrical - Power Distribution | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Busbar installed in lobby 6/075 has missing hold down clamps and it can be seen that the busbar is not fixed to the unistrut (see attached photos). Location: ETH -5 Lobby 6/075
|  | Cxxx-NCR-000344 | NCR | DB-W-EL04/7L1,7L2,L3 - Post IRN Lighting changes |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-07-19 | 2022-07-21 14:38 | 2 | 2022-07-05 09:21 | Electrical - General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The below circuits have found to have been amended post IRN. This NCR will capture the assurance for these changes. DB-W-EL04/7L1- 6x Lights installed. When IRN was completed there was 7x Lights. DB-W-EL04/7L2- 11x Lights installed. When IRN was completed there was 10x Lights. DB-W-EL04/7L3- 9x Lights installed. When IRN was completed there was 8x Lights.
|  | Cxxx-NCR-000345 | NCR | Platforms and Tunnels - Minor Lighting changes & Red Lines. |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-07-19 | 2022-07-15 12:59 | -4 | 2022-07-05 14:35 | Electrical - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | This NCR needs to cover all the minor changes made to lighting orientation/minor layout changes. The changes that will be picked up do not require any close out paperwork (QA Checksheets or Test sheets) but will require updated redlines for these areas.
|  | Cxxx-NCR-000346 | NCR | WTH - Minor Small Power changes & Red Lines |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-07-19 | 2022-08-17 12:00 | 29 | 2022-07-05 15:09 | Electrical - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | This NCR needs to cover all the minor changes made to the Small Power orientation/minor layout changes. The changes that will be picked up do not require any close out paperwork (QA Checksheets or Test sheets) but will require updated redlines for each level
|  | Cxxx-NCR-000347 | NCR | ETH - Minor Small Power changes & Red Lines |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-07-19 | 2022-08-16 15:27 | 28 | 2022-07-05 15:12 | Electrical - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | This NCR needs to cover all the minor changes made to the Small Power orientation/minor layout changes. The changes that will be picked up do not require any close out paperwork (QA Checksheets or Test sheets) but will require updated redlines for each level
|  | Cxxx-NCR-000348 | NCR | ATS functionality FFL Lift 6 |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-07-20 | 2022-08-18 13:02 | 29 | 2022-07-06 08:30 | Electrical - Switchgear | 500 |  | Testing and Commissioning | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The ATS which supplies the FFL lift 6 on the ETH changed Bias before the Main LV Bus Coupler closed. As per works information JY 71 and Subsequent CEC CRL1-CEC-00307 the ATS should be set to 15 secs and the Primary Bus Coupler should maintain the Bias Supply in the event of loss of one of the A OR B supplies.
|  | Cxxx-NCR-000349 | NCR | DB-W-EL03 - Exit sign lighting changes |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-07-20 | 2022-07-15 11:04 | -5 | 2022-07-06 08:40 | Electrical - General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | DB-W-EL03/6L2- Exit light on ESS 4 Landing WTH -3 moved location and is now a Bi-Directional Sign as per Cxxx-FCD-000341 DB-W-EL03/11L1- Exit light in lobby 4/083 WTH -3 moved location to north wall as per Cxxx-FCD-000341 This NCR has been raised to captured the assurance for these works.
|  | Cxxx-NCR-000350 | NCR | Surge Protection Valve incorrect for commissioning of Domestic pipework WTH & ETH - IRNs-P-50002 & 50003 |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-07-22 | 2022-07-28 15:01 | 6 | 2022-07-08 09:37 | Mechanical - Hot & Cold Water Supplies | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | 2x Surge Protection Valves (as marked on Schematic Cxxx-XRL-P-DDE-Cxxx-16100_P03 as part of Booster pump pipework) are incorrect for allowing commissioning flow.
|  | Cxxx-NCR-000351 | NCR | Supply to Sump Pump Panel (WTH/-6/SP004) did not account for Duty & Assist Loads |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2022-07-22 | 2022-09-22 11:36 | 62 | 2022-07-08 13:55 | Electrical - Power Distribution | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | Supply (W060) to Sump Pump Panel (WTH/-6/SP004) did not account for Duty & Assist pumps being run at the same time. The pumps are designed to run duty/assist under emergency scenarios when the backup rod has failed. The LVB breaker tripped during this particular functional test. Location: WTH -5 6/906
|  | Cxxx-NCR-000353 | NCR | ETH Door contacts not installed onto doors |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-07-26 | 2022-09-22 16:19 | 58 | 2022-07-12 21:23 | Communications and Control Systems - SCADA/Central Management System | 3500 |  | Incomplete Works | Rework | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | The following door contacts have not been installed onto the doors: BOS-E-A-581-D01-MD01 / Contacts need to be fitted to Door BOS-E-1-92-D01-MD18 / Contacts need to be fitted to Door BOS-E-1-91-D01-MD17 / Contacts need to be fitted to Door BOS-E-2-91-D02-MD05 / Contacts need to be fitted to Door BOS-E-3-91-D02-MD10 / Contacts need to be fitted to Door BOS-E-4-91-D02-MD03 / Contacts need to be fitted to Door BOS-E-5-91-D02-MD11 / Contacts need to be fitted to Door Only one leaf on the following doors has the contact installed but requires to be both to allow the full testing BOS-E-6-693-D01-MD21 BOS-E-6-77-D01-MD15
|  | Cxxx-NCR-000354 | NCR | Lighting Control - Redundant Marchalling Boxes and Electircal Wiring - Punch Work |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2022-07-27 | 2022-10-13 12:47 | 78 | 2022-07-13 12:50 | Electrical - Lighting | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Various IRN (for LCM's) submitted for CRL acceptance (see attached email). Cxxx-PWK-01088 - Punch Work requires details to be added regarding the removal of redundant marshalling boxes and associated field wiring. 1) Planned date of removal 2) Provision of scope, cost and time to be provided to Project Manager 3) Confirmation of PMI received by Contractor. Also the category (currently cat C) needs to be agreed with CRL FAE and amended as necessary. As of 13/07/2022 IRN's will be accepted by SR with the PWK As-Is. Issues raised in this NCR to be resolved prior to PCC stage. Associated Early Warnings to be similarly resolved prior to PCC stage, as listed below: Cxxx-EWN-00235 Cxxx-EWN-00270
|  | Cxxx-NCR-000355 | NCR | Lighting ammendments - Following an __ and __ requirements |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-07-29 | 2022-08-02 14:37 | 4 | 2022-07-15 06:06 | Electrical - Lighting | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Post IRN design changes have been made to the circuits listed below, these changes are detailed via Cxxx-FCD-000356. Although Cxxx have met the design station requirement of 150 lux in these areas additional lighting is required, this NCR will capture the assurance of the changes once implemented. ETH A/133 • Additional 1 No Point added to DB-E-B01 1L1 ETH 2/173 • Additional 1 No Point added to DB-E-B03 1L1 • Additional 1 No Point added to DB-E-EL10 1L1 WTH 5/171 • Relocation of 1 No point DB-W-EL09 2L1 WTH FFLL 1/083 • 2 No additional points on DB-W-A02 4L1
|  | Cxxx-NCR-000357 | NCR | VIRS Ref 45- Alloy turnbuckles installed on a trunking bends lid (ETH A/073), this is non-compliant with the regulations. |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-08-11 | 2022-07-20 08:23 | -22 | 2022-07-14 12:31 | Electrical - Cable Management | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | A trunking lid that is installed on a trunking bend has alloy turnbuckles fitted to it in circulation area A/073 in the ETH, this is non-compliant with the regulations.
|  | Cxxx-NCR-000358 | NCR | Non-compliant LUX levels at level -5 Escalator 11-13 Threshold and WTH Level -2/3 Escalator 17-19 Threshold |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-08-08 | 2022-09-21 14:42 | 44 | 2022-07-25 14:57 | Electrical - General | 6000 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | During the review of the lighting verification the below location would appear to have a compliant Lux level average due to the overspill of light from CP 7 to CP10 (Cross passages). CRL requested an onsite verification on the areas between the foot of the escalators and the first totem as this area would appear to be under lit. The onsite inspection also indicated lower levels then recorded in the pack and will need to be taken again to confirm there is not a problem. At the foot of the escalators we are showing 3 digit values approx. 300 and above which must be from the site temps installed as the values measured on the CRL inspection were found to be well under this range. Lighting in this area to be turned on so these can be recorded again and fed back into the table to better understand the Lux / Uniformity values. Currently we are failing uniformity here and its not clear where we would be adjusting the Lux values to boost uniformity. The heat map from the lighting calculation report does not hide that there is a potential problem here.
|  | Cxxx-NCR-000359 | NCR | __ Rail & Mabey Bridge - Outstanding Manufacturing Records and Pull Testing Training Records |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-08-22 | 2022-08-12 12:23 | -10 | 2022-08-08 15:56 | Architectural - General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | 1. ITP Cxxx-SKC-A-ITP-Cxxx-50064 REV 3.0 for WTH - __ MONORAIL FABRICATION & INSTALLATION - ITP Ref 2.1 to 2.8 requires Material Delivery Notes, Mill Certificates, Product Certification as verifying documents for all components. __ and __ are unable to provide these records. 2. __ UK are also unable to Provide Pull Tester Training Certificates.
|  | Cxxx-NCR-000361 | NCR | Electrical Cables Crossing Trunking Compartments |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2022-08-05 | 2022-08-09 16:00 | 4 | 2022-07-22 11:09 | Electrical - General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Electrical cables have been found to cross trunking compartments (see attached photo). Location: Unsure of exact location, refer to __ sticker reference which should detail location in fire stopping log. Also been advised this maybe near ETH A/927 +0.5 SOUTH WALL.
|  | Cxxx-NCR-000362 | NCR | Non Compliant Buswire Circuit Lengths & Ohm Readings ( LCM 91' LCM 92, LCM 93 , LCM 94 , LCM 95 & LCM 96 ) |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2023-06-30 |  | -144 | 2022-07-22 12:49 | Electrical - Lighting | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Open |  | INSPECTION |  | During Point to Point Testing it was discovered that there are non compliant buswire circuit lengths & Ohm readings on LCM 91' LCM 92, LCM 93 , LCM 94 , LCM 95 & LCM 96.
|  | Cxxx-NCR-000363 | NCR | Speaker removed and damged from its fixings |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-12-26 | 2022-09-07 09:56 | -110 | 2022-09-07 07:30 | Communications and Control Systems - Public Address Systems | 200 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Speaker was found to be hanging from the copex in A/096
|  | Cxxx-NCR-000364 | NCR | Speaker Z37/40B removed and damaged from its fixings |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-08-09 | 2022-07-29 16:57 | -11 | 2022-07-26 12:20 | Communications and Control Systems - Public Address Systems | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | whilst on a site inspection a horn speaker was found dangling from its fixings in room A/904 I have checked the speaker it has no damage so can be re fitted, someone must of swung off this to remove it from the wall as it has 3 fixings in it.
|  | Cxxx-NCR-000365 | NCR | Sump Extract Fans Differential Pressure Switches |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-08-15 | 2022-08-19 07:21 | 4 | 2022-08-01 14:46 | Mechanical - Heating Ventilation & Air Conditioning | 2500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | Sump Extract Fans are set up in a Duty/Standby arrangement with a differential pressure switch (DPS) serving each fan. The DPS are installed in common ductwork (other side of the Non-Return damper from the fans), which means that when either the Duty or the Standby fan runs, both DPS give a run signal which results in an alarm. This applies to Sump Extract fans on the ETH and WTH. SE-E-EF001 & SE-E-EF002 SE-W-EF001 & SE-W-EF002
|  | Cxxx-NCR-000366 | NCR | Cxxx |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-09-21 | 2022-11-29 11:15 | 69 | 2022-09-07 10:15 | Electrical - Lighting | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Upon inspection of the LCM’s and its CMS we came across a damaged Dali wire in the ETH lobby 6/097 within the CMS on top of the LCM’s which I believe it has been chewed up by the trunking lid. CRL will require this damage cable to be replaced/rectified. Please see the attached photos for your reference.
|  | Cxxx-NCR-000367 | NCR | Illuminated lights on Non Public Platform cages |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2022-08-17 | 2022-09-09 10:16 | 23 | 2022-08-03 11:10 | Electrical - Lighting | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Illuminated signage has been installed on the trace side of the Non Public Platform cages. CRL1-CEC-00703 & CRL1-CEC-00805 were issued for the Contractor to review sign arrangements within the running tunnels and identify signage which is not in conformance with BS544 2013. Signage is to be sized so as to be seen at a minimum of ≥20m and shall include an exit sign affixed to the designated evacuation door (tunnel side) which leads to the relative place of safety.
|  | Cxxx-NCR-000368 | NCR | DB-W-B01/6L3 - Relocation of Charging Point |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-08-18 | 2022-08-10 11:55 | -8 | 2022-08-04 09:42 | Electrical - General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | This NCR has been raised to capture the assurance for the design change stated in Cxxx-FCD-000365.
|  | Cxxx-NCR-000370 | NCR | Water conditioner required on ETH Domestic - IRN-P-50003 |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2023-06-30 |  | -144 | 2022-08-09 07:51 | Mechanical - Public Health Engineering | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Open |  | IMPLEMENTATION |  | 1. Missing DN40 electro-magnetic water conditioner in the ETH MCWS install in the services riser room 2/931. 2. Absence of water conditioner control boxes in both the ETH & WTH MCWS ETH2/931 & WTH 2/402. 3. Absence of MCR for the HY-MAG DN50 installed in the WTH 2/402. MCR-008658 includes DN25, 35, & 40 models but not 50 as fitted WTH.
|  | Cxxx-NCR-000371 | NCR | WTH L-3 / Escalator 14-16 - __ Rail Trolley Clashes with Ceiling Panels |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2023-06-30 |  | -144 | 2022-09-07 10:44 | Architectural - General | 500 |  | Design | Rework | 4 (0.5-3k) | Open |  | IMPLEMENTATION |  | During a running trial of the __ trolley, it was noted that the rail clashes with the ceiling substructure, preventing full and clear operation of the rail. Clashes appear to occur above the foot of Escalator 14/16. It appears the cause is a mixture of the following issues; 1. Minimal clearance, as per design, between the rostek motor and the adjacent CLG-721 architectural ceiling panels. 2. Minor deviations in the rail line itself. 3. Minor deviations in the ceiling (CLG-721).
|  | Cxxx-NCR-000372 | NCR | WTH - LCM 42 Maximum Cable Length Exceeded |  | Contr | COF | BOS - Bond Street Station (West) |  | 2023-06-30 | 2022-12-09 10:02 | -203 | 2022-08-10 10:48 | Electrical - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | LCM 42 for legs B & C both exceed the 300m maximum cable length and maximum resistance of 8ohms readings. However T&C and CRL design have agreed anything within 10% of the maximum does not require any reworks.
|  | Cxxx-NCR-000373 | NCR | Restricted access to damper RE-W-FD001 - WTH Rubbish Extract. IRN-M-50036 __-00269 |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-08-31 | 2022-11-16 16:00 | 77 | 2022-08-11 08:31 | Mechanical - Heating Ventilation & Air Conditioning | 1000 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | Fire damper in south-west corner of 2/767 (RE-W-FD001) has access problems due to PMR tray below it. (also pic 008) Please demonstrate access or move PMR tray.
|  | Cxxx-NCR-000374 | NCR | Domestic Water Booster Pumps communication to BMS |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-09-01 | 2022-10-20 09:50 | 49 | 2022-08-11 08:58 | Mechanical - Pumps | 500 |  | System Defect | Rework | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | Communication system from domestic water booster pumps (Geniebus) to the BMS (BACnet) are different. When the BACnet module was connected this inhibited the pumps. 4no. Pumps are effected: WTH BCWS -1/001 WTH BCWS -1/002 ETH BCWS -2/001 ETH BCWS -2/002.
|  | Cxxx-NCR-000375 | NCR | IP Rating of Equipment/Services not suitable in Areas with Water Mist/Sprinkler Heads |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2022-09-30 | 2022-10-06 15:16 | 6 | 2022-08-16 14:59 | Electrical - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The below locations all have water mist/sprinkler heads installed, however the equipment within these rooms (DALI LCM's, CMS, JB's, comms equipment etc.) are not suitably IP rated for the environment. Locations with water mist/sprinkler heads: 1. WTH L0 - 1/411 Store room 2. WTH L-1 - 2/402 Rubbish Store 3. WTH L-1 - 2/330 LU Drying room 4. WTH L-1 - 2/318 Male Locker room 5. WTH L-1 - 2/319 Female Locker room 6. WTH L-3 - 4/408 Cleaners Store Water Point 7. WTH L-3 - 4/414 Store room 8. WTH L-4 - 5/397 Water Mist room 9. WTH L-5 - 6/408 Cleaner Store 10. WTH L-5 - 6/409 Cleaner Service 11. WTH L-5 - 6/317 Female Locker room 12. WTH L-5 - 6/316 Male Locker room 13. WTH L-5 - 6/410 Cleaner Equipment room 14. WTH L-5 - 6/415 Cleaning Machine room 15. ETH L0 - 1/401 Rubbish Store 16. ETH L-1 - 2/410 Cleaner Equipment room 17. ETH L-1 - 2/408 Cleaning Machine room 18. ETH L-1 - 2/409 Cleaners Store room 19. ETH L-4 - 5/398 Water Mist room 20. ETH L-5 - 6/412 Platform Maintenance Equipment room 21. ETH L-5 - 6/413 Platform Cleaning Machine room 22. ETH L-5 - 6/414 Store room 23. ETH L-5 - 6/914 NR Workshop
|  | Cxxx-NCR-000376 | NCR | Unable to complete Sprayed Concrete Lining Pull-Tests in ETH AP3 & W-bound Draft Relief |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-08-30 | 2022-08-26 15:12 | -4 | 2022-08-16 12:58 | Mechanical - Mechanical Engineering General | 0 |  | Incomplete Works | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Information not detailed | Completed |  | Sub-contractor __ were requested to up-date their Station fixings pull-test report; C450-__-M-XCL-Cxxx-50002 as part of IRN:-Cxxx-XRL-D-NOX-Cxxx-50007 ETH Gravity Drainage Pipework but did not include any Sprayed-concrete lining tests. Punchworked on IRN as: Cxxx-PWK-00885 (This NCR to close this PWK).
|  | Cxxx-NCR-000377 | NCR | DB-W-A10/5L1 - Damaged Cable |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-08-31 | 2022-08-19 17:09 | -12 | 2022-08-17 10:11 | Electrical - General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | While carrying out a retest of Circuit DB-W-A10/5L1 a fault has been found between the Live conductor and CMS. Upon further inspection minor damage has found to have occurred to the insulation of the cable, this damaged looks to have been caused by the cable being trapped between divider and the lid.
|  | Cxxx-NCR-000379 | NCR | WTH - LCM 31 Maximum Cable Length Exceeded |  | Contr | COF | BOS - Bond Street Station (West) |  | 2023-06-30 | 2022-12-09 10:10 | -203 | 2022-08-22 09:42 | Electrical - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | LCM 31 for leg B exceeds the 300m maximum cable length and maximum resistance of 8ohms readings. However T&C and CRL design have agreed anything within 10% of the maximum does not require any reworks.
|  | Cxxx-NCR-000380 | NCR | __ Gates - Loose Bolts on Kick Out Rail |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-09-05 | 2022-10-31 14:22 | 56 | 2022-08-22 15:48 | Architectural - General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Management Problem - Not Defined | Completed |  | Loose bolts were found on the kick-out rail, during an inspection of the cladding install by a follow on contractor. It appears that either the bolts weren't secured during installation, or have come loose during gate operation through vibration.
|  | Cxxx-NCR-000381 | NCR | Signage graphics installed using code 2 (not accepted) drawings |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-09-11 | 2022-09-01 07:01 | -10 | 2022-08-25 10:49 | Architectural - Signage | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Not Defined | Completed |  | Signage graphics have been installed using code 2 'not accepted' drawings. This applies to signs reference USN 005, 042, 106, 108, 508, 512, 523, 534, 708, 712, 723, 734. Drawings are referenced below.
|  | Cxxx-NCR-000383 | NCR | WTH - LCM 15 Maximum Cable Length Exceeded |  | Contr | COF | BOS - Bond Street Station (West) |  | 2022-09-20 | 2022-11-24 22:19 | 65 | 2022-09-06 09:24 | Electrical - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | LCM 15 legs A & C both exceed the 300m maximum cable length and maximum resistance of 8 ohms reading. However T & C and CRL design have agreed anything within 10% of the maximum does not require any reworks.
|  | Cxxx-NCR-000384 | NCR | Outstanding records for __ Gates Installation Record Packs 50001, 50003, 50005, 50007 & 50010. |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-11-16 | 2022-11-25 12:01 | 9 | 2022-11-02 09:39 | Architectural - Doors | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | ETH - Side Gates - Record pack 50001 1.Checksheets partially wet ink signed and no Del team or CRL signatures. Checksheets to be completed in wet ink. Adobe signed checksheets are not acceptable. 2.Pull testing signed off on one of the checksheets. Which bolts were these tests? No pull test report. Need to confirm if completed in error. 3.Provide torque wrench calibration cert for bolts torqued to 30Nm ETH - Main Gates - Record pack 50003 1.No Installation checksheets. Only wet ink signed checksheets are acceptable which must have actual installation dates so the correct torque calibration certs are in the record pack. 2.No pull test records for the Bottom track, Bottom Brackets, and left Jamb both ends. WTH - Side Gates - Record pack 50005 1.No Installation checksheets. Only wet ink signed checksheets are acceptable which must have actual installation dates so the correct torque calibration certs are in the record pack. 2.Pull testing signed off on one of the adobe signed checksheets. Which bolts were these tests? No pull test report. Need to confirm if completed in error. 3.Provide torque wrench calibration cert for bolts torqued to 30Nm WTH - Main Gates - Record pack 50010 1.No Installation checksheets. Only wet ink signed checksheets are acceptable which must have actual installation dates, so the correct torque calibration certs are in the record pack. 2.Pull test report 29440 does not have enough information to identify what was pull tested. Test report to be updated with location and element tested. Please provide more info. WTH - Vent Shaft Facade Gates - Record Pack 50007 1.No Installation checksheets. Only wet ink signed checksheets are acceptable which must have actual installation dates, so the correct torque calibration certs are in the record pack.
|  | Cxxx-NCR-000385 | NCR | Lift 6 & 8 Drainage Channel Grating Damage |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-09-21 | 2022-10-03 08:41 | 12 | 2022-09-07 10:00 | Architectural - General | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | Further to Cxxx-RFI-000158 this NCR has been raised to capture formal approval of the replacement lift gratings. The original grates installed were installed in line with an approved design however were not fit for purpose, and as such have sustained damaged and need to be replaced. The RFI response states that 'the proposed replacement is acceptable if the bespoke replacement grating from __ can be fabricate in thicker material than 5mm...'
|  | Cxxx-NCR-000386 | NCR | Non-Compliant Lighting Uniformity |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-09-26 | 2022-10-05 15:28 | 9 | 2022-09-12 11:53 | Electrical - Lighting | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | There are numerous areas throughout the station of which compliant uniformity values are not met. These are listed within the WTH Lighting Verification Report - Cxxx-XRL-E-RGN-Cxxx-50056 (Comment 52) & ETH Lighting Verification Report - Cxxx-XRL-E-RGN-Cxxx-50057 (Comment 52).
|  | Cxxx-NCR-000387 | NCR | MCRs for __ and __ doors do not include exerted pressure requirements |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2023-01-13 | 2023-01-09 16:10 | -4 | 2022-09-13 15:29 | Architectural - Doors | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | The code 1 MCRs for __ (Cxxx-SKC-A-LRC-Cxxx-50196 Rev 2.0) and __ __ (Cxxx-SKC-A-MCR-Cxxx-50140 Rev 2.0, Cxxx-SKC-A-MCR-Cxxx-50141 rev 3.0 and Cxxx-SKC-A-MCR-Cxxx-50142 rev 2.0) include neither the exerted pressure requirements from the door schedule nor any evidence of pressure performance. This has been detailed in CEG report CRL1-XRL-M-RGN-Cxxx-50003 ‘Bond Street Station - Verification of door pressure ratings in the TVS locations’.
|  | Cxxx-NCR-000388 | NCR | BOS - WTH - Minor Damages to Matwell |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-10-28 | 2022-11-07 13:15 | 10 | 2022-10-14 14:04 | Architectural - General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Management Problem - Not Defined | Completed |  | In the course of opening and closing the matwell at the WTH to facilitate on-site works, minor damages have occurred to the Matwell that must be rectified prior to station handover. These damages may affect long term serviceability and operation if not addressed. The damages appear to have been caused by operatives opening and removing sections of the Matwell to provide access to the sump pits at the SE and NW corners of the WTH entrance Matwell.
|  | Cxxx-NCR-000389 | NCR | MCC Trace Heating Circuits not RCD Protected |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2022-10-11 | 2022-10-05 07:54 | -6 | 2022-09-27 09:06 | Electrical - General | 6000 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | JY24 states that trace heating circuits should be RCD protected. This has not been provided for the circuits listed below. Cxxx-FCD-000353 and Cxxx-FCD-000359 have since been accepted for the additional RCD protection and one new additional circuit. Cxxx-PWK-00838 and Cxxx-PWK-00969 were incorrectly closed to capture these works and updated assurance (IRF, check sheets, test sheets, redlines, etc.). This NCR is to cover the reworks as per the FCD and updated assurance paperwork. MCC Trace Heating Circuits: * MCC-E-01/9L2 * MCC-E-02/4L2 (new circuit) * MCC-W-01/10L1 * MCC-W-01/11L3
|  | Cxxx-NCR-000391 | NCR | WTH -5/SP001 Hydrocarbon Override |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-10-11 | 2022-10-14 11:16 | 3 | 2022-09-27 17:10 | Mechanical - Public Health Engineering | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | In the event that hydrocarbons are detected within the WTH -5/SP001 sump, an inhibit signal is sent to the pumps. However, there is no capacity on the tank to install a 5th “Overflow” rod to override this signal at high level. This means that once hydrocarbons are detected the pumps will remain inhibited regardless of water level, which risks flooding the plant room if the hydrocarbon alarm is not quickly resolved. Proposal: Use the tank as a "common" reference, freeing up the "common" probe which can then be used as the "overflow" probe to override the pump inhibit signal. Note - This proposal supersedes that proposed in Cxxx-FCD-000387 which was deemed unacceptable by CRL T&C, FAE & CEG. The proposal in Cxxx-FCD-000387 resulted in a scenario whereby the pump would operate after powering down the telemetry enclosure, without any water touching the probes. Due to the concern that any power cut out or switch over would result in pumps running dry, this alternate proposal was required.
|  | Cxxx-NCR-000392 | NCR | L-5 Replacing sealed rodding eyes to facilitate drainage |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-10-28 | 2022-11-04 11:43 | 7 | 2022-09-28 11:19 | Mechanical - Public Health Engineering | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Recent CRL Observations (CRL-OBS-36386 & CRL-OBS-36387) have flagged the need for the existing sealed rodding eyes to be changed to open grates to facilitate drainage within 6/409 & 6/415. There is a tap within 6/409 which could potentially flood the room without a drainage point, and there is a sink within 6/415 which needs a discharge point. Additionally, in 6/777 one of the drains has been left with a cast iron pipe protruding from the floor, as opposed to a drainage gully.
|  | Cxxx-NCR-000393 | NCR | __ Gates (C473) - Throw out track fixings missing and not torqued correctly |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-10-19 | 2022-11-07 13:10 | 19 | 2022-10-05 08:38 | Architectural - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | While undertaking torque testing for the throw out track on the WTH Entrance Gate, Crossrail have discovered that several fixings to the primary steel were not fully torqued to the ITP specification, and in one instance a fixing was missing. The ITP details that these fixings must be torqued to 73Nm.
|  | Cxxx-NCR-000394 | NCR | Busbar Sections Not Fire Rated (2 areas at ETH -5) |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2022-11-08 | 2022-10-27 10:36 | -12 | 2022-10-25 12:01 | Electrical - General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | There are 2 busbar sections at the ETH -5 (see attached mark ups) that do not have fire barriers installed (see attached example parts list). Therefore the fire compartmentation to the associated rooms/areas have not been maintained. Location: ETH Level -5 6/097 to 6/094 and 6/094 to 6/914
|  | Cxxx-NCR-000396 | NCR | Busbar Casings have been Drilled to affix the __ Fire Barriers |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2022-11-11 | 2022-11-09 15:14 | -2 | 2022-10-28 14:28 | Electrical - General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The busbar casings have been drilled to affix the durasteel fire barriers. These were retro drilled instead of using the pre-drilled holes. Confirmation is required from the busbar manufacturer that this has not introduced any structural/casing weakness and warranty/performance issues based upon manufacturers supplied performance data.
|  | Cxxx-NCR-000403 | NCR | Energy based Discrimination Errors from __ Model |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2023-04-28 |  | -81 | 2023-01-10 13:45 | Electrical - LV Equipment | 500 |  | Incorrect Installation |  |  | Open |  | REVIEW |  | Energy based Discrimination Errors have been discovered within the __ Model. Remedial proposal works have also been listed to resolve discrimination errors. See attached list for details of errors. For further information please see referenced __ calculation reports Cxxx-XRL-Z-XCL-Cxxx-50001 Cxxx - Bond Street Station Main Works, M&E WTH - __ As-Built Design Calculations Rev 3 Cxxx-XRL-Z-XCL-Cxxx-50002 Cxxx - Bond Street Station Main Works, M&E ETH - __ As-Built Design Calculations Rev 4
|  | Cxxx-NCR-000404 | NCR | Time Current Discrimination Errors from __ Model |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2023-04-28 |  | -81 | 2023-01-10 14:05 | Electrical - LV Equipment | 500 |  | Incorrect Installation |  |  | Open |  | REVIEW |  | Energy based Discrimination Errors have been discovered within the __ Model. Remedial proposal works have also been listed to resolve discrimination errors. See attached list for details of errors. For further information please see referenced __ calculation reports Cxxx-XRL-Z-XCL-Cxxx-50001 Cxxx - Bond Street Station Main Works, M&E WTH - __ As-Built Design Calculations Rev 3 Cxxx-XRL-Z-XCL-Cxxx-50002 Cxxx - Bond Street Station Main Works, M&E ETH - __ As-Built Design Calculations Rev 4
|  | Cxxx-NCR-000405 | NCR | __ 6.0 Ground fault protection discrimination errors |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2023-04-28 |  | -81 | 2023-01-10 15:02 | Electrical - LV Equipment | 500 |  | Incorrect Installation |  |  | Open |  | REVIEW |  | Prior to the advent of staged completion SC1, Cxxx engaged with __ (the Cxxx electrical design team) and identified various earth fault discrimination errors. Crossrail technical specification CRL1-XRL-M-RSP-CR001-50082: JY71.3204 section L determines that earth / ground fault protection is required for all sub-main circuit devices 400A and above. The __ 6.0 ACB’s within the LV panels were replaced with __ 5.0, however the supplies to the Tunnel Ventilation System (TVS) Variable Speed Drives (VSD) were not changed and remained as __ 6.0 NS1000L devices. This has left earth fault only discrimination issues. It has been confirmed with both __ and __ that these devices can be altered effectively facilitating the removal of the ground fault functionality and the devices are then be deemed as their __ 5.0 equivalent. Please see referenced __ calculation reports - Cxxx-XRL-Z-XCL-Cxxx-50001- WTH AMTECH CALCULATIONS REPORT REV 3.0 Cxxx-XRL-Z-XCL-Cxxx-50002- ETH AMTECH CALCULATIONS REPORT REV 4.0 The devices required to be altered protect cables as below East Ticket Hall - E012 - BOS/LV/E/A TVF1 fan VSD (__le A50) - E061 - BOS/LV/E/B TVF2 fan VSD (__le A50) - E016 - BOS/LV/E/A MCC-E-03(__le A15) West Ticket Hall - W011 - BOS/LV/E/A TVF1 fan VSD (__le A48) - W062 - BOS/LV/E/B TVF2 fan VSD (__le A48) The following escalator supply cables also have earth fault discrimination however to route to resolution will require further coordination with the escalator manufacturer as the discrimination errors are due to the protective devices installed within the __ system. - W019 - BOS/LV/W/A (__le A15) - W082 - BOS/LV/W/B (__le A16) - E019 - BOS/LV/E/A (__le A9) - E057 - BOS/LV/E/B (__le A10)
|  | Cxxx-NCR-000002 | NCR | Materials Lost During PC Change Over |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2021-02-16 | 2021-05-12 10:02 | 85 | 2021-02-02 13:36 | Communications and Control Systems - General | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | It has been highlighted by Cxxx in transmittal Cxxx-CCM-00027 that a number of materials have either been thrown out by the previous client or lost by the previous client during the Covid-19 site closure and subsequent PC change over. The missing items which were highlighted are detailed below.. • 4 No Horn Speakers • 5 No Bi-Directional Speakers • 25 No PAVA Junction Boxes • 4 No CCTV cameras Further to additional stock checks on site there are additional items that are required on site. These are detailed below.. • 40 No SCADA Door Contact Junction Boxes
|  | Cxxx-NCR-000003 | NCR | Damage to installed fibre cable within CMS |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2021-03-22 | 2021-03-30 15:22 | 8 | 2021-03-08 11:06 | Communications and Control Systems - Fibre Optic Network | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | It has only just reported to Crossrail that whilst LUL was carrying out Commissioning works in November to the Connect radio system it was found that cable 125-DAT-00204 installed by __s wad damaged so an investigation was needed.
|  | Cxxx-NCR-000004 | NCR | CIS Bos-05-STD-00502 Westbound platform-Faulty |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2021-03-26 | 2022-01-06 14:12 | 286 | 2021-03-12 12:51 | Communications and Control Systems - Customer Information System | 500 |  | Equipment Breakdown | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | At the initial power on stage of the CIS screen BOS-05-STD-00502 took place the unit failed to come online. 230V was tested and present on the load side of the FCU which would indicate an issue with the asset itself.
|  | Cxxx-NCR-000005 | NCR | LEER 8 Cabinet cable entry BOS-02CAB-3131U1 |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2021-04-03 | 2021-04-01 14:31 | -2 | 2021-04-01 11:44 | Communications and Control Systems - General | 0 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Cxxx-PMI-00063 works information was not followed. __s have drilled or enlarged the top of the cabinet to fit 25mm bushes within the newly installed header trunking instead of using the 16mm stuffing glands provided to pass through cables into the cabinet. The works information stated DO NOT drill or enlarge any current holes into the cabinet. It is noted that there is a small dent in the top of the cabinent,
|  | Cxxx-NCR-000006 | NCR | 1/2" Ohm Corrugated Low Loss Coaxial Cable Black |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2021-05-19 | 2021-05-12 12:23 | -7 | 2021-05-05 12:00 | Communications and Control Systems - General | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | 1500m of 1/2" Ohm Corrugated Low Loss Coaxial Cable Black is required to complete radio install at bond street
|  | Cxxx-NCR-000007 | NCR | Damage to Radio cables |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2021-06-09 | 2021-07-29 08:33 | 50 | 2021-05-26 08:21 | Communications and Control Systems - Radio | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | After a survey completed by __ it was found that 2 cables FD3259 & FD265 appear damaged due to 2 small dents in the cable.
|  | Cxxx-NCR-000008 | NCR | Incomplete works |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2021-06-09 | 2021-08-20 07:27 | 72 | 2021-05-26 09:33 | Communications and Control Systems - Radio | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | __ have gone ahead and terminated a radio cable in CP 5 when the tray work has not been finished yet leaving the cable unsupported.
|  | Cxxx-NCR-000009 | NCR | Damaged radio antenna 3081 |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2021-07-19 | 2021-07-27 08:29 | 8 | 2021-07-05 08:48 | Communications and Control Systems - Radio | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Insufficient surveillance of subcontractors | Completed |  | Whilst __ were carrying out testing to the Radio system an antenna 3081 located ETH -1 was found damaged.
|  | Cxxx-NCR-000011 | NCR | Faulty PMR radio cable |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2021-07-28 | 2021-08-10 07:45 | 13 | 2021-07-14 09:09 | Communications and Control Systems - CCTV | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | __ carrying out T & C duties found cable FD182 failing its functuality test
|  | Cxxx-NCR-000012 | NCR | PAVA-Z25 |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-02-10 | 2022-02-03 12:01 | -7 | 2022-01-27 09:48 | Communications and Control Systems - Public Address Systems | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | N/A
|  | Cxxx-NCR-000013 | NCR | PAVA-IMPEDANCE LEVELS |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2021-07-21 | 2021-07-23 13:22 | 2 | 2021-07-16 12:31 | Communications and Control Systems - Public Address Systems | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | A LEG ON ZONE 25 IMPEDANCE OUT WITH 20% TOLERANCE ALLOWED FOR ESCALATOR SPEAKERS. TOTAL SPEAKERS 12X2W EOL2 TOTAL TAPPINGS WATTAGE 26W. CALCULATED IMPEDANCE 384.6 OHMS. MAX PERMITTED 461.5 OHMS MEASURED AT 470 OHMS.
|  | Cxxx-NCR-000014 | NCR | Damaged radio cable FD111 |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2021-08-10 | 2021-08-10 07:42 | 0 | 2021-07-27 07:08 | Communications and Control Systems - Radio | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | WTH -5 Radio Cable FD111 failed the testing process.
|  | Cxxx-NCR-000015 | NCR | Damaged radio antenna 038 |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2021-08-24 | 2021-12-01 08:27 | 99 | 2021-08-10 06:49 | Communications and Control Systems - Radio | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | When terminating and testing __ have found a fly lead to antenna 038 WTH -4
|  | Cxxx-NCR-000016 | NCR | Damaged radio antenna fly lead 3088 ETH -2 |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2021-08-24 | 2021-10-26 05:49 | 63 | 2021-08-10 06:59 | Communications and Control Systems - Radio | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | When __ were carrying out their T & T duties they have found damage to the fly lead of antenna 3088
|  | Cxxx-NCR-000017 | NCR | Damage to Radio cable FD203 |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2021-08-31 | 2021-11-12 08:58 | 73 | 2021-08-17 10:31 | Communications and Control Systems - Radio | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | __ T & C team tested FD203 cable which failed testing.
|  | Cxxx-NCR-000018 | NCR | Damage to radio antenna fly lead 114 ETH -5 |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2021-09-01 | 2021-08-24 09:32 | -8 | 2021-08-18 09:04 | Communications and Control Systems - Radio | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | __ T&C team, when terminating radio cables on ETH -5 have found the fly lead to antenna 114 is damaged.
|  | Cxxx-NCR-000019 | NCR | Damaged Radio Cable FD 3301 |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2021-09-10 | 2021-12-21 10:17 | 102 | 2021-08-27 06:57 | Communications and Control Systems - Radio | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | During the __ radio testing procedures. It was found that cable FD 3301 had failed the testing parameters required. On investigation it was found said cable was kinked.
|  | Cxxx-NCR-000020 | NCR | Damaged Radio Cable FD 3187 ETH -2 |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2021-09-10 | 2021-10-26 05:51 | 46 | 2021-08-27 09:51 | Communications and Control Systems - Radio | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | Damaged Radio cable FD 3187 ETH-2 cause of damage unknown as yet. During __ testing procedures this cable when under test failed the parameters. Viable damage found on cable in the form of a kink
|  | Cxxx-NCR-000021 | NCR | Radio Cable FD193 Damaged ETH -2 |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2021-09-10 | 2021-10-26 05:52 | 46 | 2021-08-27 10:07 | Communications and Control Systems - Radio | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | During Radio cable testing carried out by __. It was found that Cable FD 193 ETH -2 failed to meet the testing parameters. On further inspection a visible 'Kink' to the cable was highlighted as the probable cause. Cable will need to be replaced in its entirety.
|  | Cxxx-NCR-000022 | NCR | Damage to installed and tested Radio PMR assets |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2021-09-21 | 2022-01-25 13:23 | 126 | 2021-09-07 10:02 | Communications and Control Systems - Radio | 5000 |  | Damaged | Rework | 3 (3-6k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Whilst __ were carrying out tests on the installed Radio system they found damage cabling and coupler's on the scaffold in WTH -1. On investigation it appears that __ who are the Fire stopping contractors were the last ones working in that area. Investigation is ongoing. Couplers- CPR 3060,050,3061 & 059 Feeder cables- FD 3173,179,180,3174 Feeder cables
|  | Cxxx-NCR-000023 | NCR | SAP 001 Z17 Fault |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2021-09-23 | 2021-10-26 06:01 | 33 | 2021-09-09 13:27 | Communications and Control Systems - Public Address Systems | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During __ (Cxxx) T&C of Zone 17. It was found that there is a fault to the Station Announcement Point (SAP) Z17/ 001. Email report from __ states they have investigated to try to rule out faulty equipment
|  | Cxxx-NCR-000024 | NCR | Replacement Clock |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2021-09-27 | 2021-09-14 08:41 | -13 | 2021-09-13 11:26 | Communications and Control Systems - Customer Information System | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | During the tier 1 change over at Bond Street the Clock delivered by __ in 2018 was misplaced/lost. This NCR is required to trigger the replacement of this clock by __.
|  | Cxxx-NCR-000025 | NCR | Faulty radio cables |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2021-09-29 | 2021-12-21 10:20 | 83 | 2021-09-15 06:07 | Communications and Control Systems - Radio | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | At T and T stage __ have found that the following cables have failed their functuality tests. FD031, 032, 033, 243 FD3028, 3030, 3236
|  | Cxxx-NCR-000026 | NCR | Radio Cable Fault FD364 |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2021-10-04 | 2021-10-26 05:55 | 22 | 2021-09-20 09:10 | Communications and Control Systems - Radio | 500 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During Cxxx testing cable FD364 ETH -2 failed the functionality parameters
|  | Cxxx-NCR-000027 | NCR | Fire Detection - Use of the __-E VEP system without accepted MCR |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2021-10-18 | 2022-02-03 16:54 | 108 | 2021-09-20 15:22 | Fire - Detection | 0 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | This NCR is raised following the procurement and installation of __-E VEP system prior to an accepted MCR.
|  | Cxxx-NCR-000028 | NCR | Incomplete CMS for Radio cables FD3058B and FD063B |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2021-10-29 | 2021-11-26 13:34 | 28 | 2021-09-29 07:22 | Communications and Control Systems - Radio | 500 |  | Incomplete Works | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Flexi bend attached to tray work needs cutting in to remove lip
|  | Cxxx-NCR-000029 | NCR | FD 3058 and FD3058B damaged radio feeder cables |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2021-10-22 | 2021-11-26 13:37 | 35 | 2021-09-29 07:41 | Communications and Control Systems - Radio | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The following Radio Cables have been damaged by over tightening the Metal Tie Wraps around them.
|  | Cxxx-NCR-000030 | NCR | Procurement of extra Radio connectors |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2021-11-23 | 2021-12-01 08:23 | 8 | 2021-11-09 13:35 | Communications and Control Systems - Radio | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Other | Completed |  | Due to the large number of damaged cables on both the east and west ticket halls at Bond St there is a need for more connectors. This is due to having the replace the damaged cables which requires new connectors. This damage has been caused by various factors which include damage during install, and damage by others on site (unknown who as not reported).
|  | Cxxx-NCR-000031 | NCR | Failed Radio Cable Due to Damage FD3247 |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2021-12-02 | 2022-01-13 12:22 | 42 | 2021-11-18 12:31 | Communications and Control Systems - Radio | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Radio cable FD 3247 ETH -5 has sustained damage since cable was terminated and tested to 'pass' on the 16th Aug 21. Cable was noted as visibly being tampered with as gland was disconnected from coupler 3086. Cable re tested on the 17th Nov 21 and 'Failed' the testing parameters
|  | Cxxx-NCR-000032 | NCR | Damaged Radio Cables FD 047/048/049 3044/3046 |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2021-12-03 | 2022-01-13 12:28 | 41 | 2021-11-19 13:32 | Communications and Control Systems - Radio | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During the testing of Radio Cables 5 x cables failed the testing perimeters to allow a pass. Those cables are FD 047/048/049 & FD3044/3046
|  | Cxxx-NCR-000033 | NCR | Damaged Manual Call Point |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-02-08 | 2022-03-04 08:28 | 24 | 2021-12-13 14:03 | Fire - Fire Systems & General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Manual call point (device number L22/D33 ) has been damaged Unknown by who or when
|  | Cxxx-NCR-000034 | NCR | Fire Detection - Incorrect Position of the VAD in 4/767 |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-02-08 | 2022-03-08 15:03 | 28 | 2022-01-25 18:24 | Fire - Detection | 1000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - NCR excessive closure due to design issue | Completed |  | There is currently no visibility of the beacon (L17/48) from behind the AHU unit and duct work ( See attached photos) In addition, and due to the current lighting configuration, visibility of beacon will be difficult to distinguish in an alarm scenario.
|  | Cxxx-NCR-000037 | NCR | Damaged Radio antenna 3038 |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-02-14 | 2022-02-23 15:42 | 9 | 2022-01-31 11:20 | Communications and Control Systems - Radio | 2000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | Radio antenna 3038 has been found damaged in room WTH 5/397, A RIVO and investigation to be carried out by to determine the route cause.
|  | Cxxx-NCR-000038 | NCR | LPWM-Non Compliant Pipe Support Installation |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-07-01 | 2022-06-29 14:52 | -2 | 2022-04-18 11:08 | Fire - Suppression | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Water mist pipework bracketry cannot be installed in some areas due to heavy congestion of services within the ceiling. To maintain accessibility and maintainability multiservice bracketry was utilised, refer to attached "Bracket report Bond St" for location reference.
|  | Cxxx-NCR-000039 | NCR | LPWM-Water mist pipework installation commenced without accepted ITP |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-02-19 | 2022-05-20 10:44 | 90 | 2022-02-05 15:05 | Fire - Suppression | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Lack of approval Code 1 procedures excessive | Completed |  | __ commenced water mist pipework installation without accepted Code 1 ITP
|  | Cxxx-NCR-000040 | NCR | LPWM-Commencing water mist testing & commissioning activities without accepted CTPs |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-08-25 15:07 | -10 | 2022-02-07 15:06 | Fire - Suppression | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | __ commenced water mist system T&C activities without accepted Commissioning Test Plan (CTP) in place.
|  | Cxxx-NCR-000042 | NCR | Fire Detection-Removal of Multidetector in 1/932, Node 10 Loop 22 |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-02-28 | 2022-05-20 10:47 | 81 | 2022-02-14 17:07 | Fire - Detection | 500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | Multidetector L22/23 in 1/932 has been removed without coordination with the fire team. See attached mark-up
|  | Cxxx-NCR-000043 | NCR | Fire Detection-Damaged conduit in Lobby 4/097, Node 09 Loop 17 |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-03-01 | 2022-03-08 14:52 | 7 | 2022-02-15 15:57 | Fire - Detection | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Conduit and 230v supply between fire dampers AS-E-FD033 and GE-E-FD032 (located in Lobby 4/097 above BAT room 4/779 door) has been cut through. See attached photo and mark up drawing. If the circuit has been energised, it could lead to a major health and safety accident.
|  | Cxxx-NCR-000044 | NCR | WTH level 2 (old level -1) - OPE duct access panel blocked by Fire Damper conduit in Circulation Area 2/074 |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2022-03-31 | 2022-05-08 10:11 | 38 | 2022-02-16 12:32 | Fire - Detection | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | See attachments: A piece of fire damper control cable conduit has recently been placed below an OPE duct access hatch which prevents its removal (CRL CEG/LU have tried to remove the panels). The conduit shall be set down to allow the 100mm thick panel to slide down and out
|  | Cxxx-NCR-000045 | NCR | Fire Detection-DCP 109 Disconnected Terminations, Node 13 Loop 34 |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-03-02 | 2022-05-20 10:48 | 79 | 2022-02-16 16:16 | Fire - Detection | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | External Phenomenon - Theft, tampering, sabotage, or vandalism | Completed |  | Someone a third party has disconnected some of the DCP 109 terminations and removed the din rail connectors. See attached photo. The Damper panel DCP109 located in circulation area 2/075 WTH-1
|  | Cxxx-NCR-000046 | NCR | Damage to Radio antennas 009 & 3009 |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-03-10 | 2022-03-01 12:57 | -9 | 2022-02-24 10:18 | Communications and Control Systems - Radio | 4000 |  | Damaged | Rework | 3 (3-6k) | Complete | Personnel Error - Inattention to detail | Completed |  | Damage found the PMR antennas 009 & 3009 WTH -1
|  | Cxxx-NCR-000047 | NCR | Over Length Cables |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-03-21 | 2022-03-16 15:50 | -5 | 2022-03-07 15:51 | Communications and Control Systems - Public Address Systems | 4000 |  | Documentation and Records | Rework | 3 (3-6k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | There is not enough cable to complete the H1000 install for zone19 as the design length and install lengths are different. Due to changes in CMS routes the cable lengths were longer so more cable was used for each zone. Please see detail below: Estimated - 155m Actual - 205m Required - 285m This delta was due the following: Zone 17 - 28m longer Zone 18 - 58m longer Zone 20 - 2m shorter Zone 24 - 2m longer
|  | Cxxx-NCR-000048 | NCR | Damaged Camera |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-03-31 | 2022-03-18 11:10 | -13 | 2022-03-17 12:32 | Communications and Control Systems - CCTV | 3000 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Damaged heated camera.
|  | Cxxx-NCR-000049 | NCR | ETH LCR 3/967 - speaker conduit blocking access and maintenance area to fire damper |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2022-04-20 | 2022-04-14 11:35 | -6 | 2022-03-21 16:31 | Communications and Control Systems - Public Address Systems | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | A speaker conduit is blocking access and maintenance area to fire damper above the conduit. The fire damper can no longer be accessed using a ladder or platform as planned. The fire damper was once blocked by other electrical services, but these were moved as part of Cxxx-NCR-000989. The speaker conduit has since been added to the room and has caused the same problem. Please see attached photo 'ETH LCR 3-967 - speaker conduit blocking access and maintenance area to fire damper.jpg'.
|  | Cxxx-NCR-000050 | NCR | ETH LCR 3/910 - antenna and support clashing with CCU door openings |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2022-04-20 | 2022-04-11 11:40 | -9 | 2022-03-21 16:43 | Communications and Control Systems - Public Address Systems | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | ETH LCR 3/910 - the doors of the CCUs need to open wider than 90 degrees in order to get the air filters out. At the moment there is an antenna and support that prevent the doors from opening wide enough. The antenna and support needs to be modified to allow the doors to open freely and for filters to be changed. The photos attached show the clash.
|  | Cxxx-NCR-000051 | NCR | Fire Detection-DCP 159 Conduit Drilled Through the Label, Node 09 Loop 18 |  | Contr | XRL | BOS - Bond Street Station (West) |  |  | 2022-05-20 10:52 |  | 2022-03-22 09:57 | Fire - Fire Systems & General | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | CMS labels in Foul Pump Room 3/772 were damaged and covered by the conduit branching off the main trunking into DCP 159. The conduit was drilled and cables wired through the trunking label. See attached photos.
|  | Cxxx-NCR-000052 | NCR | Damaged Whip ANT ETH Lev 0 |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-04-27 | 2022-05-11 12:57 | 14 | 2022-04-13 11:14 | Communications and Control Systems - Public Address Systems | 2000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Personnel Error - Not Defined | Completed |  | Damage caused to Zone 20 Whip Antenna 002 - Replacement unit required
|  | Cxxx-NCR-000053 | NCR | Fire Mic 001 WTH Casing has been drilled |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-04-22 | 2022-06-10 10:15 | 49 | 2022-04-08 07:20 | Communications and Control Systems - Public Address Systems | 0 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Whilst installing, the contractor has drilled cable entry holes into the Fire Mic 001 (EMS01) casing located on Lev0 WTH.This goes against the provided installation guidelines that states the 'appropriate knock outs for cable entry points should be chosen'.
|  | Cxxx-NCR-000054 | NCR | Asset damage |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-05-05 | 2022-05-03 09:55 | -2 | 2022-04-14 11:43 | Communications and Control Systems - Public Address Systems | 2000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | It was reported by site manager that a speaker on zone 19 has been damaged, An investigation is underway to find the cause of the damage.
|  | Cxxx-NCR-000055 | NCR | Door contacts installed on 'non safe side' |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-09-14 07:30 | 10 | 2022-05-23 07:22 | Communications and Control Systems - SCADA/Central Management System | 8000 |  | Incorrect Installation | Rework | 2 (6-60k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The following doors contacts have been installed on the wrong side of the doors. The contacts were installed on the 'non safe side' which is in contravention of the install guidelines and LUL requirements. ETH - MD05 (level -1) - 2/087 to Firefighting lobby MD10 (Level -2) - 3/091 to Firefighting lobby MD03 (Level -3) - 4/101 to Firefighting lobby MD11 (Level -4) - 5/091 to Firefighting lobby WTH - MD04 (Level 0) - 1/083 to Firefighting lobby MD01 (Level -1) - ESS2 to Firefighting lobby MD04 (Level Interchange) - ESS2 to Firefighting lobby MD06 (Level -4) - 5/087 to Lobby to EES5 MD05 (Level -4) ESS4 to Circ Area 5/072
|  | Cxxx-NCR-000056 | NCR | ASD - Non-conformant lift shift design |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-07-07 | 2022-09-05 08:36 | 60 | 2022-06-23 15:18 | Fire - Detection | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | After carrying out the smoke tests in the lift shafts, It was record that the ASD pipe work installed is not functioning as it should be. Also after further investigation it has been noted that the current design does not meet the requirements under BS5839.
|  | Cxxx-NCR-000057 | NCR | Aspirating System Pipework Installation Commenced Without Accepted ITP |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-07-27 | 2022-06-29 12:18 | -28 | 2022-06-29 11:13 | Fire - Detection | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Not Defined | Completed |  | Cxxx-TEW-E3-ITP-Cxxx-50003 rev 1.0 for installation of ASD pipework was submitted on 23/09/2021 and received code 2 on 20/10/2021. The only comment related to lack of space for CRL witness signatures on the check sheets. The ITP has not been revised and resubmitted. Installation is now complete. Check sheets have been signed by CRL witnesses regardless of the lack of dedicated space for this.
|  | Cxxx-NCR-000058 | NCR | Alterations to WTH and ETH LPWM Design and installation |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-09-16 | 2022-09-28 08:41 | 12 | 2022-07-08 12:04 | Fire - Suppression | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | Post inspection of the LPWM system by CRL, it was identified that there are multiplu locations where watermist suppression nozzels have been obscured by other system installed in the vicinity. therfor reducing the dicipation of the mist in allighnment with the design requirements
|  | Cxxx-NCR-000059 | NCR | Fire alarm printout allignment to S1088 Floor levels and respective fire Zones |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-09-12 | 2022-09-05 09:03 | -7 | 2022-07-14 13:05 | Fire - Fire Systems & General | 500 |  | Software | Reject | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | It has been identified that the Fire alarm PCC printouts, specifically Floor levels and fire zones do not allign to the latest S1088 design fire plans. Noting finished floor levels differ from construction Levels
|  | Cxxx-NCR-000060 | NCR | Maglock connector blocks |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-08-26 | 2022-08-08 21:39 | -18 | 2022-07-29 14:19 | Fire - Fire Systems & General | 500 |  | Material | Repair | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | It has been identified that Non conformant connector blocks have been utilised on mag lock connections
|  | Cxxx-NCR-000061 | NCR | Defective Fire Door Mag Locks |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2022-09-22 | 2022-09-13 12:56 | -9 | 2022-08-05 09:26 | Fire - Fire Systems & General | 500 |  | Equipment Breakdown | Rework | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | - Mag Locks procured are not fit for purpose, as the bespoke fire doors are too heavy for the magnets. As a result the doors are having to be opened on multiple occasions by staff and putting undue stress on the plastic housing of the mag locks and causing them to break and the doors to shut uncontrolled, over time. This can not afford to happen post revenue service as the doors are on an escape route and prior to the PRM lift providing wheelchair access. - Approximately 16no. Mag lock (2 per leaf, 8 leafs' in total). Contractor to confirm actual number and locations. - Suggested remedial work - Procure the Vimpex 400n magnetic door holders (replacement item to have approved CRL MCR). - Provide FCD prior to implementation. - Provide approved MCR
|  | Cxxx-NCR-000002 | NCR | P&T - No MCR in Place for Material being Incorporated into PES End CMS Penetrations Prior to Works Commencing |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2021-04-30 | 2021-04-23 12:37 | -7 | 2021-03-19 15:53 | Architectural - Walls | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Following a review of the PES Enclosure Wall design by the project designers __, they notified the contractor very late in the project that additional works needed to be undertaken around the CMS penetrations to mitigate air flow through the penetrations. The designers proposed the material in question for incorporation into the works not the contractor. The material was NOT approved prior to incorporation into the works.
|  | Cxxx-NCR-000003 | NCR | ETH Matwell - Cube Strength |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2021-12-22 | 2022-01-21 15:25 | 30 | 2021-12-08 16:10 | Architectural - Finishes | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Inspection points not adequate | Completed |  | 28 Day Cube results of the first pour of the ETH Matwell __ Detail did not meet the design strength required
|  | Cxxx-NCR-000004 | NCR | MCR not in place for __ __ HBS and __ Primer |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2022-06-17 | 2022-06-09 14:16 | -8 | 2022-05-18 08:17 | Architectural - Flooring | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Not Defined | Completed |  | 1. MCR for __ __ HBS Cxxx-SKC-O4-QSV-Cxxx-50055 is submitted for concrete repairs, on MCR location in works "Remedial works to damage structural concrete for Cxxx" not for Matwell - __ Grout Application. 2. There is no MCR for __ Primer
|  | Cxxx-NCR-000005 | NCR | Lack of Benchmarks for Firestopping Details Site Wide |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-07-15 | 2022-08-16 14:36 | 32 | 2022-07-01 14:45 | Fire - Compartmentation | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | No samples or benchmarks have been produced/offered to CRL for supplementary firestopping details provided by __.
|  | Cxxx-NCR-000002 | NCR | MCC-E-09 - (FAE Site Inspection) Broken C&D Isolator, Loose Glands & Loose conductor core. |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2021-12-16 | 2022-02-04 10:41 | 50 | 2021-12-02 13:50 | Communications and Control Systems - Power Supplies | 3000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On inspection of MCC-E-09 multiple snags have been identified with the inspection of works. These are as follows: 1. Broken Rotary Switch for a Red C&D isolator. Replacement required. 2. 1 x loose gland was found on the motor control box termination point. All glands to be inspected to ensure they are installed as per the manufactured instructions. 3. Brass glands have not been clamped down correctly on the earth cables supplying the motor control units. Re-inspection on AHU 001 and 002 including VSD's and isolators feeding both motors. 4. 1 x neutral connection was found loose by the FAE inspector and this hadn't been torqued in compliance with the manufactures guidelines. 5. Earth connection points on VSD's have no anti-vibration locking devices installed. 70% of install did have them installed. Please re-arrange another site inspection to capture close out of the NCR issues and snags identified.
|  | Cxxx-NCR-000003 | NCR | AHU' Piteo tubing is the wrong colour to the spesification required |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-11-09 11:36 | 66 | 2022-02-14 14:49 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The AHU units have been piped up in red and blue tubing as per the specification but in the wrong order, red being positive and blue negative. The tubing needs to be changed that has been carried out by ECp to the correct order.
|  | Cxxx-NCR-000004 | NCR | VSD keypads nto supplied with __ drives |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-09-26 07:39 | 22 | 2022-02-14 14:58 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper storage of material | Completed |  | The contractor __ has not provided the keypads required to set up the __ type VSD drives as per the contract specification
|  | Cxxx-NCR-000008 | NCR | __ controls cable used instead of KNX whitestripe for BMS |  | Contr | ELE | BOS - Bond Street Station (West) |  | 2022-03-16 | 2022-03-06 15:10 | -10 | 2022-03-02 13:12 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | The 2pair KNX Whitestripe cable specified in the code 1 C443 BMS CE control cable schedules has been changed to a __ 3 pair cable due to supply issues. C443 have installed the __ cable on all CE panel install work since December 2021. The __ cable has an approved MCR CRL-MCR-008632. The spare cores will be tied to earth.
|  | Cxxx-NCR-000009 | NCR | LV Cable Supplying Fans Does Not Allow For Vibrations (MCC-E-08) |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-06-17 16:10 | -79 | 2022-03-03 18:42 | Electrical - Power Distribution | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The LV cable supplying the fans on MCC-E-08 does not allow for vibrations (see attached photo). This is non-compliant to BS7671 522.7 which states final connections to plant that produces vibration must be designed to accomdate this such as flexible conduit etc. (see technical details).
|  | Cxxx-NCR-000010 | NCR | LV Cable Supplying Fans Does Not Allow For Vibrations (MCC-E-09) |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-09-28 11:46 | 24 | 2022-03-23 10:10 | Electrical - Power Distribution | 3000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The LV cable supplying the fans (x2) on MCC-E-09 does not allow for vibrations (see attached photos). This is non-compliant to BS7671 522.7 which states final connections to plant that produces vibration must be designed to accommodate this (see technical details).
|  | Cxxx-NCR-000013 | NCR | Faulty __ Inverter for CHW-W-PU002 |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-08-03 10:13 | -32 | 2022-04-01 13:37 | Electrical - Electrical Engineering General | 500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Not Defined | Completed |  | During commissioning of WTH Chilled Water Pumps it was found that the frequency converter on Pump CHW-W-PU002 flags a permanent fault on start up, which is an STO fault which prevents the pump from running. See report attached for details. Serial Number: Y2128A00337 __ Model: ACH580
|  | Cxxx-NCR-000014 | NCR | MCC-W-04 Isolator missing internal bush and causing damage to cables |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2022-04-20 | 2022-04-20 07:54 | 0 | 2022-04-06 11:25 | Electrical - General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | No bushes have been installed on the isolators associated with MCC-W-04 which is causing damage to the cables out sheathing from the sharp edges (see attached photos). This is non-compliant to the below BS7671 clauses.
|  | Cxxx-NCR-000016 | NCR | LV Cable Supplying Fans Does Not Allow For Vibrations (MCC-W-05) |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-09-23 15:13 | 19 | 2022-06-13 10:04 | Electrical - Power Distribution | 3000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The LV cable supplying the fans on MCC-W-05 does not allow for vibrations (see attached photo). This is non-compliant to BS7671 522.7 which states final connections to plant that produces vibration must be designed to accommodate this such as flexible conduit etc. (see technical details).
|  | Cxxx-NCR-000017 | NCR | LV Cable Supplying Fans Does Not Allow For Vibrations (MCC-W-09) |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-09-23 14:55 | 19 | 2022-06-13 10:15 | Electrical - Power Distribution | 3000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The LV cable supplying the fans on MCC-W-09 does not allow for vibrations (see attached photo). This is non-compliant to BS7671 522.7 which states final connections to plant that produces vibration must be designed to accommodate this such as flexible conduit etc. (see technical details).
|  | Cxxx-NCR-000018 | NCR | LV Cable Supplying Fans Does Not Allow For Vibrations (MCC-W-06) |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-09-23 15:29 | 19 | 2022-06-13 10:23 | Electrical - Power Distribution | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The LV cable supplying the fans on MCC-W-05 does not allow for vibrations (see attached photo). This is non-compliant to BS7671 522.7 which states final connections to plant that produces vibration must be designed to accommodate this such as flexible conduit etc. (see technical details).
|  | Cxxx-NCR-000019 | NCR | LV Cable Supplying Fans Does Not Allow For Vibrations (MCC-E-05) |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-09-23 15:35 | 19 | 2022-06-13 10:27 | Electrical - Power Distribution | 3000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The LV cable supplying the fans on MCC-E-05 does not allow for vibrations (see attached photo). This is non-compliant to BS7671 522.7 which states final connections to plant that produces vibration must be designed to accommodate this such as flexible conduit etc. (see technical details).
|  | Cxxx-NCR-000020 | NCR | LV Cable Supplying Fans Does Not Allow For Vibrations (MCC-E-06) |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-09-23 14:53 | 19 | 2022-06-13 10:40 | Electrical - Power Distribution | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Previous Construction - Other | Completed |  | The LV cable supplying the fans on MCC-E-06 does not allow for vibrations (see attached photo). This is non-compliant to BS7671 522.7 which states final connections to plant that produces vibration must be designed to accommodate this such as flexible conduit etc. (see technical details).
|  | Cxxx-NCR-000021 | NCR | LV Cable Supplying Fans Does Not Allow For Vibrations (MCC-W-08) |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-07-01 12:01 | -65 | 2022-06-13 10:54 | Electrical - Power Distribution | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The LV cable supplying the fans on MCC-W-08 does not allow for vibrations (see attached photo). This is non-compliant to BS7671 522.7 which states final connections to plant that produces vibration must be designed to accommodate this such as flexible conduit etc. (see technical details).
|  | Cxxx-NCR-000022 | NCR | MCC-E-01 and MCC-E-02 CUBICLE 6 MCCB 5 the mechanism within has stopped working |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-08-15 | 2022-08-03 14:21 | -12 | 2022-08-01 11:04 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Equipment Breakdown | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Information not detailed | Completed |  | Eastern Ticket Hall 1/776 MCC-E-01 & MCC-E-02 __le 6 MCCB 32A isolators for the primary pumps, Isolating selector and mechanism to the isolator within seems to have stopped working as the handles turn but the unit itself stays off.
|  | Cxxx-NCR-000001 | NCR | __ have not provided the __ Mortar Test Cube Reports for Record Pack C444-PYR-A-LRC-Cxxx-50002 |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-12-16 | 2022-12-06 09:15 | -10 | 2022-11-02 16:18 | Architectural - Brickworks/Blockworks | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | __ have not provided the __ Mortar Test Cube Reports for Record Pack C444-PYR-A-LRC-Cxxx-50002. They have only listed the Mortar test Cube Report numbers on the Check sheets so there is no way of knowing if the tests passed or failed. This is a deliverable on the ITP Cxxx-COF-C-ITP-Cxxx-50004 rev 2.0
|  | Cxxx-NCR-000002 | NCR | Sitewide - Cracking to Linear Joint Seals |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2023-06-30 |  | -144 | 2022-10-19 11:07 | Fire - Fire Systems & General | 500 |  | System Defect |  |  | Open |  | PROPOSE ACTION |  | Horizontal __ head joints have been inspected throughout the site and it has been highlighted that the Luff coat has cracked.
|  | Cxxx-NCR-000001 | NCR | Missing Documentation Relating to CK Tech Injection Works Undertaken at Bond Street |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2021-07-13 | 2022-01-27 16:00 | 198 | 2021-06-29 11:57 | Civil - Tunnelling | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | Whist compiling the quality assurance record pack, it was noted that a number of inspection records were missing and/or incomplete therefore, insufficient records to confirm if the works were undertaken.
|  | Cxxx-NCR-000005 | NCR | WTH - L0 Upstands - Incomplete Works, Testing and Inspection |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2021-06-26 | 2021-07-22 12:22 | 26 | 2021-06-12 12:15 | Civil - Civil Engineering General | 0 |  | Incomplete Works | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | WTH - L0 upstands for incomplete works, testing and inspections. Incomplete works - Making good completed by __ Incomplete testing - Cubes misplaced/ lost Incomplete inspections - Missing signatures from Client
|  | Cxxx-NCR-000003 | NCR | Eastern Ticket Hall Eastbound Platform Extract Duct - localised reduced insulation thickness to accomodate Architectuaral panel |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2021-05-14 | 2021-05-07 11:05 | -7 | 2021-04-30 10:47 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | In the Eastern Ticket Hall, Eastbound Platform, the Platform Extract Duct connection has a clash with the new architectural glass panel and brackets. It is the 100mmthick insulation that clashes with the glass panel, not the metal duct itself. The solution is to reduce the insulation thickness to 50mm so that the glass panel and brackets can be fitted into place. See Photo 1, 2 and 3. The PSE duct and insulation has already been signed off under IRN Cxxx-SKC-M-NOX-Cxxx-50019 2.0 Cxxx Installation Release Notice (IRN) - ETH Platform Smoke Extract
|  | Cxxx-NCR-000002 | NCR | Damaged pipes near the AP2 drip tray |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2021-07-22 | 2021-12-06 12:52 | 137 | 2021-05-13 14:12 | Mechanical - Piping | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | During an inspection for C445-PWK-00001 __ noticed that some of the pipework to the SE corner of the AP2 drip tray has suffered some water damage. See pics and location attachment.
|  | Cxxx-NCR-000003 | NCR | Full pressure test required on ETH CHW System - IRN-M-50017 |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-07-20 16:10 | -46 | 2022-04-13 15:47 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Incomplete Works | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Not Defined | Completed |  | ETH Chilled water pipework requires testing of whole system as only partial tests have been carried out excluding By-pass pipework
|  | Cxxx-NCR-000004 | NCR | Full pressure test required on WTH CHW System - IRN-M-50004 |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-04-27 | 2022-06-06 13:16 | 40 | 2022-04-13 15:49 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Incomplete Works | Repair | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | ETH Chilled water pipework requires testing of whole system as only partial tests have been carried out excluding By-pass pipework
|  | Cxxx-NCR-000005 | NCR | Subcontractor did not install to the instructed current drawing - IRN-D-50007 |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-07-28 14:54 | -38 | 2022-04-13 15:50 | Mechanical - Public Health Engineering | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Installation of the header pipework for ETH Gravity Drainage (Cxxx-XRL-D-NOX-Cxxx-50007) has been done from a mixture of the information and routing from Cxxx-SKC-P-DDA-Cxxx-52212_P10 and P13. The IFC/Instructed drawing was P13. Route is as per Redline X01 drawn on P10. Latest drawing is now; Cxxx-XRL-P-DDA-Cxxx-52212_P01 - to be redlined
|  | Cxxx-NCR-000008 | NCR | Chiller Water Pipework Insulation installation 'sealing details' failing - Condensation has saturated rockwall (ETH and WTH) |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2023-06-30 |  | -144 | 2022-09-12 14:29 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Open | Discipline/Workmanship - Defective construction | IMPLEMENTATION |  | This is a site wide issue. The Chiller Water Pipework Insulation installation 'sealing detail' has failed. Condensation has formed on the pipework and ancillaries that have not been vapour sealed and this has saturated large sections of Rockwall behind the out silver tape/covering. Corrosion is also now forming on the CHW components. Puddles or water are forming on the floor or dripping down from pipes that are at high level. Sections of saturated insulation must be removed and refitted with an adequate sealing detail added. Some binder points on the CHW AHUs and in LCRs still need insulating, to be consistent with what __ did in similar rooms. The dosing pots need insulation too as condensation forms on these and drips then causes problems. Insulate with Armaflex. The updated survey pictures showing the incomplete insulation as of 16/11/2022 are attached. Please see 'ETH chilled water pipework and components require insulation completing.msg', and 'WTH chilled water pipework and components require completing.msg'. This NCR now captures snags listed in Cxxx-PWK-01308 - Repair & inspection of damaged insulation WTH Levels +1 & +2 - IRN-M-50030.
|  | Cxxx-NCR-000010 | NCR | New WTH chilled water pipework supports required - As per structural calculation Cxxx-XRL-M-XCL-Cxxx-50003 |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2023-01-13 | 2022-12-18 13:40 | -26 | 2022-11-13 16:18 | Mechanical - Piping | 3000 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Not Defined | Completed |  | The __ works information required loading details to be provided for all fixings. The ETH __ chilled water pipework supports was covered by a __ structural calculation (C450-__-M-XCL-Cxxx-50001), but the WTH was not, as the installation was not complete when the calculation was done, 2020. In the absence of a WTH __ structural calculation, Crossrail (the Employer) instructed the same subcontractor structural engineering firm used by __ (RA) to carry out an assessment of the completed WTH installation, 2022. The findings from the WTH calculation was that the WTH __ chilled water pipework supports required additional fixings. one extra bracket at level +0.5, and one extra bracket at level -4. The details are detailed in Cxxx-XRL-M-XCL-Cxxx-50003. This NCR is for a non compliance to Cxxx-SKC-M-RSP-Cxxx-50004 rev 3.0, MEP Specification - JA - General Requirements for MEP JA.1004, and for the not completing the installation to an acceptable level for it to be assured.
|  | Cxxx-NCR-000011 | NCR | WTH 6/914 RFLI Workshop Pipework labelling |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2022-12-16 | 2022-12-12 10:40 | -4 | 2022-11-15 14:28 | Mechanical - Public Health Engineering | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Provide pipework identification labels for all drainage pipework.
|  | Cxxx-NCR-000013 | NCR | ETH pressurisation unit pipework has service identification and directional labels incorrectly applied |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2022-12-16 | 2022-12-13 12:39 | -3 | 2022-11-13 17:10 | Mechanical - Piping | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not trained for the work being performed | Completed |  | ETH pressurisation unit pipework has service identification and directional labels incorrectly applied, as per CRL-OBS-36299 and its attached photos.
|  | Cxxx-NCR-000017 | NCR | Domestic Tank Insulation |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2022-12-16 | 2022-12-04 18:50 | -12 | 2022-11-15 15:11 | Mechanical - Public Health Engineering | 500 |  | Incomplete Works | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The tanks insulation should be as per this PMI (C450-PMI-00197). All 4 domestic tanks in WTH 2/767 & ETH 3/772 are to be insulated to avoid bacterial growth at certain temperatures.
|  | Cxxx-NCR-000018 | NCR | Installation of Water conditioner |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2022-11-29 | 2022-11-15 15:19 | -14 | 2022-11-15 15:16 | Mechanical - Public Health Engineering | 500 |  | Incomplete Works | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | This NCR has been raised in error.
|  | Cxxx-NCR-000026 | NCR | Water Heaters PRV Discharges |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2022-12-16 | 2022-12-12 10:30 | -4 | 2022-11-18 13:40 | Mechanical - Public Health Engineering | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Water Heaters - General All PRV Discharges are currently terminating inside the tundish. Tundish terminations required an AUK3 type air gap (twice the diameter of the inlet pipe size). Use of the manufacturers supplied tundish will resolve this. Or the terminations will need to be cut back above the level of the current tundishes. Please review and amend all water heaters in all locations.
|  | Cxxx-NCR-000003 | NCR | Incorrect Finish to Front of House Bronze Doors |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2021-08-27 | 2022-02-11 12:31 | 168 | 2021-06-04 11:53 | Architectural - Doors | 500 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | 4no. __ __ Bronze Doorsets listed below have been finished with the incorrect colour and powder coating. E-01-92-D01 W-01-411-D01 W-01-633-D01 W-04-85-D01 The C01 drawings showed the finish colour as "PPC Anodic Bronze Y2214F" whereas the correct colour should have been “Bronze PPC - D1036 SW268JR”. The current finish does not match the bronze panels surrounding the door. The paint is also non compliant with LU Fire Regulations.
|  | Cxxx-NCR-000004 | NCR | Missing COCs for WTH Louver Manufacture (Gilberts) |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-01-27 | 2022-05-20 07:19 | 113 | 2022-01-13 11:07 | Architectural - Finishes | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Not Defined | Completed |  | The Certificate of Conformity (COCs) or the WTH louver manufacture has not been provided
|  | Cxxx-NCR-000005 | NCR | Use of plastic wall plug in ASSA door installation into blockwork (further to Cxxx-NCR-000101) |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-07-12 13:35 | -54 | 2022-04-26 12:40 | Architectural - Doors | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Further to Cxxx-NCR-000101 it has been established that plastic plug wall plugs have been used to secure ASSA door frames to blockwork, not just for levelling of the door frame during installation, but as the permanent fixing for the door frame. See attached photos of E-01-088-D02.
|  | Cxxx-NCR-000006 | NCR | Lack of AIS signature on records |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-05-26 | 2022-06-10 14:30 | 15 | 2022-05-12 16:17 | Architectural - Doors | 0 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | AIS (third party fire assurance) have not signed off on any JJS installed doors since SC1 doors
|  | Cxxx-NCR-000007 | NCR | FD30 Fire Door Stickers installed on replacement doors |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2023-01-13 | 2023-01-10 14:41 | -3 | 2022-05-17 11:26 | Architectural - Doors | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | Following implantation of C451-PMI-00035 and C451-PMI-00043, the Contractor has supplied doors fitted with incorrect Fire Door identification stickers.
|  | Cxxx-NCR-000008 | NCR | E-02-075-D01 - swing direction incorrect |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-05-31 | 2022-06-09 12:02 | 9 | 2022-05-17 15:15 | Architectural - Doors | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | E-02-075-D01 swing direction is not as per approved drawing
|  | Cxxx-NCR-000002 | NCR | WTH Chiller Room Hatches - Size Discrepancy vs Structural Opening |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2021-07-27 | 2021-10-28 13:44 | 93 | 2021-04-28 12:50 | Architectural - General | 500 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | It has been identified that hatches W-A-580-H01, W-B-580-H01 & W-C-580-H01 have been fabricated to dimensions that do not suit the structural openings in the WTH Chiller Room L+0.5, L+1 & L+2 slabs where they are to be installed. The structural openings have been formed correctly to the dimensions on the structural and architectural drawing sets. The structural openings are 1244x1350 in plan dimensions and the hatches have been fabricated to overall dimensions of 1230x1200. As a result the manufactured hatches do not bear on a sufficient area of RC within the structural opening, additionally there would be large gaps between the hatch frame and the RC around the hatch perimeter. Subsequently it has also been discovered that an advisory comment on the hinging arrangement and handles was not taken into consideration before manufacture of the hatches, as such these are also incorrect.
|  | Cxxx-NCR-000003 | NCR | WTH Chiller Room Personnel Doors - Manufactured and Installed Incorrectly |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2021-10-11 | 2021-10-28 07:02 | 17 | 2021-05-21 14:19 | Architectural - Doors | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Verification Problems - Not Defined | Completed |  | The two personnel doors in the WTH Chiller room have been manufactured and installed with the opening direction incorrect.
|  | Cxxx-NCR-000005 | NCR | WTH - Chiller Room Large Doors - Manufacturing Quality Assurance Records |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2021-10-16 | 2021-10-20 12:44 | 4 | 2021-06-17 11:28 | Architectural - Doors | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Other | Completed |  | The Contractor's manufacturing quality assurance records have not been populated during fabrication for the below listed doors thus are unable to submit these documents as part of the manufacturing ITP deliverable record pack. A similar NCR was raised for the WTH - Vent Shaft Large Doors (see Cxxx-NCR-001060). W-B-901-D01 W-B-901-D02 W-C-901-D01 W-C-901-D02
|  | Cxxx-NCR-000006 | NCR | ETH North Facade Doors - Surface Finish |  | Contr | SSM | BOS - Bond Street Station (West) |  | 2021-07-13 | 2021-07-05 10:54 | -8 | 2021-06-29 12:10 | Architectural - Doors | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following the return from surface treatment, the Subcontractor has identified defects on the internal face of doors E-01-74-D03 & E-01-756-D02. The PPC finish has highlighted weld & grind marks in the door skin not previously identified.
|  | Cxxx-NCR-000007 | NCR | E-01-756-D02 - Incorrectly surveyed |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2021-08-02 | 2021-11-23 14:16 | 113 | 2021-07-19 08:52 | Architectural - Doors | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | E-01-756-D02 does not fit the structural opening. It has been fabricated too large for the structural opening because the opening was incorrectly surveyed by __ Ltd.
|  | Cxxx-NCR-000008 | NCR | SR3 Certification on Final Escape Doors |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2021-12-24 | 2022-04-08 09:46 | 105 | 2021-12-10 17:24 | Architectural - Doors | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | SR3 Certification on Final Escape Doors (listed below) is now invalid following removal of the internal astragal - E-01-75-D01 E-01-75-D02 W-01-631-D01 W-01-632-D02 Internal astragal was removed to allow the doors to function correctly. See video of issue showing how the doors will not open correctly with the internal astragal in place.
|  | Cxxx-NCR-000009 | NCR | Damage to ETH L+0 wall winch |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2021-12-29 | 2022-01-07 12:45 | 9 | 2021-12-15 12:11 | Architectural - Doors | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Insufficient information made available to the worker. | Completed |  | The commissioning of the L+0 ETH Large Hatch winches a relay mechanism has been blown during commissioning of winches by the Contractor.
|  | Cxxx-NCR-000010 | NCR | Missing Manufacture Documentation for ETH Large Hatch Winch Posts (L-2) |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-03-08 | 2022-04-04 14:45 | 27 | 2022-02-22 17:21 | Architectural - Doors | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | No manufacturing records or documentation can be provided for the ETH Large Hatch Posts (L-2). See Cxxx-SKC-A-DWG-Cxxx-50044 for original design, with changes captured in Cxxx-FCD-000035 and Cxxx-FCD-000051 for details. Access to area now only available during maintenance shift 23:30 to 05:40 on certain days only.
|  | Cxxx-NCR-000011 | NCR | Missing Manufacture Documentation for ETH Large Hatch Winch Plates (L+0) |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-03-10 | 2022-05-10 13:42 | 61 | 2022-02-24 15:02 | Architectural - Doors | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | No manufacturing records or documentation can be provided for the ETH Large Hatch Plates (L+0).
|  | Cxxx-NCR-000012 | NCR | Lack of MCR for W-03-634-H03 and W-03-635-H02 |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-03-24 | 2022-04-01 14:12 | 8 | 2022-03-10 17:26 | Architectural - Doors | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | W-03-634-H03 and W-03-635-H02 have been installed without an MCR in place. Acceptance of fire certification for these hatches has been accepted under Cxxx see Cxxx-RFI-005729.
|  | Cxxx-NCR-000013 | NCR | No AIS sign-off on WTH Chiller Room Personnel Doors (W-B-580-D01 and W-C-580-D01) |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-03-30 | 2022-03-24 13:57 | -6 | 2022-03-16 17:58 | Architectural - Doors | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Not Defined | Completed |  | AIS sign off on these doors is missing
|  | Cxxx-NCR-000002 | NCR | Busbar Supports Calculations need Updating |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-10-02 11:42 | 28 | 2022-02-14 14:33 | Electrical - Power Distribution | 2000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The busbar support calculations need updating as HUS3-I fixings have been used (refer to Cxxx-NCR-000198). In addition the busbars have been noted as installed at various lengths without adequate support. For example the support design for WTH LVA (Cxxx-SKC-E-DWG-Cxxx-50675) shows a length of 1.8m without any supports (see attached photo). The design also states support spacing of 1m minimum. All other busbar routes should also be checked. WTH -5 corridor area was also identified as having other services being installed off the busbar supports and not being independently supported.
|  | Cxxx-NCR-000003 | NCR | Meters not Installed on the UPS Switchboards for 63A Breakers and Above |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2022-03-01 | 2022-05-03 11:45 | 63 | 2022-02-15 10:29 | Electrical - Switchgear | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During a CEG VAP on 03/02/22 it was found that meters have not been installed on the WTH UPS Switchboards for all 63A breakers and above as required by JV20.1301 (see attached photos). All other Switchboards should be checked for missing meters as per the spec. Location: WTH L-4 UPS Room ETH L-3 UPS Room
|  | Cxxx-NCR-000004 | NCR | Red/Green Buttons on all Switchgear do not Comply with British Standard |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-10-02 15:32 | 28 | 2022-02-15 13:48 | Electrical - Switchgear | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The red/green push buttons on all the Switchgear (see attached example photo) on site currently do not conform to the applicable machinery control standards BS EN 60204:1 and BS EN 60073. The colour of these buttons are required to be black (see attached example from TCR).
|  | Cxxx-NCR-000002 | NCR | Area of defective screed on WTH TVS L+6 (G/780) |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2021-08-31 | 2021-10-29 12:27 | 59 | 2021-08-17 15:00 | Architectural - Flooring | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Supervision - Other | Completed |  | 12m2 localised area of screed placed on 16/07/21 is defective. Area was left partially screeded / unfinished for minimum 2hrs without any protective covering.
|  | Cxxx-NCR-000005 | NCR | P&T - Incorrect Colour of Grout Used for Floor Tiling Infills in AP1 Corridor |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-06-30 | 2022-06-16 10:33 | -14 | 2022-05-27 13:28 | Architectural - Flooring | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | Following the clearing out of various stored materials in the AP1 corridor, it was noted that there were still tiles missing along the line of the central handrail which has now been de-scoped. The incorrect colour grout was used when installing these infill tiles throughout the corridor.
|  | Cxxx-NCR-000006 | NCR | Failure to undertake proof load testing during hatch installations |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-09-30 | 2022-09-08 12:04 | -22 | 2022-07-20 08:41 | Architectural - General | 500 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | No proof load testing undertaken for the fixings used throughout the L-5 hatch installation works as required by the works information.
|  | Cxxx-NCR-000007 | NCR | Poor Workmanship of Installation of BISCO Gasket to LEVEL -5 Floor Skirting on Eastbound Platform |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-09-15 | 2022-09-05 07:24 | -10 | 2022-09-01 08:51 | Architectural - Flooring | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The quality of the gasket recently reworked along the Eastbound platform was of poor quality workmanship so requires additional rework.
|  | Cxxx-NCR-000008 | NCR | L-5 Hatch Bracket Installation - Workmanship Issues |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-08-24 | 2022-10-07 08:05 | 44 | 2022-08-10 12:50 | Architectural - General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | Further to Cxxx-NCR-000006, during the course of opening the hatch covers on L-5 various issues have been discovered as summarised below: 1. E-06-7-H03 - Top left fixing is absent. 2. E-06-7-H07 - Different support plate noted on each side of pit. 3. E-06-7-H09 - Top left fixing is absent. 4. P-06-208-H01 - Top right fixing ends flush with the nut, no protruding thread. 5. P-06-208-H02 - Bottom right fixing ends flush with the nut, no protruding thread. 6. W-06-5-H09 - Only 5no. fixings installed to plate type which elsewhere has 8no. fixings. 7. W-06-5-H05 - Top left fixing absent. 8. W-06-204-H01 - Bottom left fixing absent. 9. W-06-5-H03 – 1no. Fixing cannot be torqued as is spinning in place (west face plate). 1no. fixing is missing from east face plate. 10. W-06-5-H01 - 5 anchors installed in an end plate where elsewhere only 4 fixings used. Spacing is not uniform. 11. W-06-5-H01 - Fixings are offset, not mirrored on the plate centreline. 12. W-06-5-H08 - 1no. Fixing cannot be torqued as is spinning in place. Top right fixing absent. These issues have been referred to __ to determine if acceptable to 'leave-as-is' - refer to Cxxx-RFI-000161. The response from __ is attached to this NCR along with proposed treatments, summarised below: 1. E-06-7-H03 - Baseplate fails. Requires installation of top left anchor. 2. E-06-7-H07 - Accepted as is assuming all required anchors have been installed 3. E-06-7-H09 - Baseplate fails. Requires installation of top left anchor. 4. P-06-208-H01 - Additional fixing required. Note new fixing location must be minimum 65mm away from the defective fixing but no closer than 25mm to the edge of the plate. 5. P-06-208-H02 - Additional fixing required. Note new fixing location must be minimum 65mm away from the defective fixing but no closer than 25mm to the edge of the plate. 6. W-06-5-H09 - Accepted as is. 7. W-06-5-H05 - Accepted as is. 8. W-06-204-H01 - Baseplate fails. Requires installation of bottom left anchor. 9. W-06-5-H03 – Accepted as is. 10. W-06-5-H01 - 5 anchors installed in an end plate where elsewhere only 4 fixings used. Spacing is not uniform. Additional fixing required as shown in the markup. 11. W-06-5-H01 - Fixings are offset, not mirrored on the plate centreline. 2no. additional fixings as shown in the markup. 12. W-06-5-H08 - Accepted as is.
|  | Cxxx-NCR-000009 | NCR | AP3 - Floor Hatches - Missing Bracket Fixings |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-09-16 | 2022-09-30 14:55 | 14 | 2022-09-02 12:56 | Architectural - General | 500 |  | Incomplete Works | Repair | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | During the lifting and reinstatement of hatches in AP3 it has been discovered that there are fixings missing from some of the hatch beam support plates. The hatches applicable are E-06-211-H01, E-06-211-H02, E-06-211-H03 however CRL requests that all the hatches in AP3 are checked to ensure no further fixings are absent. A photographic survey and marked up drawings showing the location of the affected plates should be provided for completeness. Contractor to propose corrective action for CRL & Designer approval.
|  | Cxxx-NCR-000002 | NCR | Esc 11-13 Kickplates too short |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-07-31 | 2022-08-16 08:45 | 16 | 2022-04-01 09:19 | Architectural - Finishes | 4000 |  | System Defect | Repair | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | 2no kick plate at the bottom of Esc 11-13 and 1no kick plate at the top have been altered by the Escalator contractor __ to allow the GFRC panels to be installed in escalator barrel. As a result of this a gap has been created between the GFRC and Skirting.
|  | Cxxx-NCR-000003 | NCR | Esc 14-16 Escalators s/s trim |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-10-10 10:30 | 36 | 2022-06-13 11:49 | Architectural - Finishes | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | The __ stainless steel trim on Escalator 14-16 does not sufficiently interface with the adjacent __ wall cladding. 1.__ are responsible for completing the Subcontract design based on the design intent shown on the Cxxx design drawings, Cxxx Design and Specification and LU Specifications, which form part of Volume 2C of the Subcontract Works Information. 2.As per the Works Information the decking panels are required to be integrated with the adjacent station fabric including wall cladding as stipulated within: •Cxxx Architectural Component Design Specification - Section JX10 Lift Fit-Out and Escalator Finishes Clause JX10.1201 d) Coordinate work at interface with associated works not forming part of this scope: iii) The Station Works wall cladding and lift shaft enclosure Clause JX10.1204 Type ESC-101 Escalator Fit Out G (i) Escalator decking shall also be fitted with an edging strip to stop objects falling over the open side. •Various Cxxx design drawings showing escalator decking being aligned to adjacent cladding with minimal or no gap Cxxx-__-A-DDH-Cxxx-20036 P01 - WTH ESC4, ESC5, ESC6 Upper Escalator Resizing Clearances
|  | Cxxx-NCR-000004 | NCR | Escalator Dipsticks - Defective electrical oil level inspection device |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-08-22 | 2022-10-03 09:56 | 42 | 2022-08-08 08:25 | Mechanical - Escalators | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | This NCR has been raised to record that there are ongoing reliability issues with the electrical oil level devices, which has resulted in the escalators not being in conformance to the following requirements of the Pan TfL technical specification SPC-LAE-301941170: SPC-LAE-301941170 part 2: 16.2.3. A method of determining the oil level shall be provided. This shall also indicate the maximum and minimum permitted levels. A low oil level switch shall be provided (see Part 3, clause 8.3 of this specification). SPC-LAE-301941170 part 3: 8.3. Activation of a ‘gearbox oil level low switch’ while the escalator is running shall not cause the escalator to stop. It shall not be possible to restart the escalator until the oil level is restored to the correct operational level. An appropriate message shall be displayed on the controller screen.
|  | Cxxx-NCR-000005 | NCR | WTH Escalator 14 Additional Top s/s Trim |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-10-07 | 2022-10-17 08:54 | 10 | 2022-09-30 16:30 | Architectural - Finishes | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The __ stainless steel trim at the top of Escalator 14 does not extend to the adjacent the newly installed Anti Climb Bronze Balustrade extension. __ were made aware of the Balustrade/Anti Climb barrier by means of various instructions and interfaces on site. The requirement for __ to provide a stainless-steel trim formed part of their contractual obligation under the following clauses. 1.__ are responsible for completing the Subcontract design based on the design intent shown on the Cxxx design drawings, Cxxx Design and Specification and LU Specifications, which form part of Volume 2C of the Subcontract Works Information. 2.As per the Works Information the decking panels are required to be integrated with the adjacent station fabric including wall cladding as stipulated within: •Cxxx Architectural Component Design Specification - Section JX10 Lift Fit-Out and Escalator Finishes Clause JX10.1201 d) Coordinate work at interface with associated works not forming part of this scope: iii) The Station Works wall cladding and lift shaft enclosure Clause JX10.1204 Type ESC-101 Escalator Fit Out G (i) Escalator decking shall also be fitted with an edging strip to stop objects falling over the open side.
|  | Cxxx-NCR-000006 | NCR | All Stations - Escalator Dipsticks - Defective Electrical Oil Level Inspection Device |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2023-06-30 |  | -144 | 2022-10-20 14:51 | Mechanical - Escalators | 500 |  | Design |  |  | Open |  | REVIEW |  | See C461-NCR-000004 for details (reopened following review, see attached email dated 20/10/2022).
|  | Cxxx-NCR-000002 | NCR | SOP call and send functionality L5 & 7 |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-10-10 10:27 | 36 | 2022-06-08 15:40 | Communications and Control Systems - SCADA/Central Management System | 20000 |  | Incorrect Installation | Rework | 2 (6-60k) | Complete | Design Problem - Not Defined | Completed |  | Missing SOP call and send functionality for the PRM lifts 5 (ETH) and 7 (WTH). Currently all SOP's are installed as COMMS and will need changing to MSOP/ASOPs. (typically includes comms) Lift 5 & 7 both have staff override functionality which is operational however no facility to control lifts by means of the call and send facility. Lift 5 and Lift 7 are to be modified to be call/send type.
|  | Cxxx-NCR-000003 | NCR | Lift 6 - Faulty Load Weighing Unit |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-09-05 | 2022-10-13 13:04 | 38 | 2022-08-22 08:59 | Architectural - General | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | A faulty load weighing unit has been installed in Lift 6 preventing sign off of the Form 54
|  | Cxxx-NCR-000004 | NCR | ETH Lift 6 Ride Quality Issue - Under car sheave LH, entrance side is noisy (ticking, possibly bearing) |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-11-16 | 2022-12-03 07:32 | 17 | 2022-11-02 16:06 | Mechanical - Lifts | 500 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | During the Form 54 inspection carried out on Lift 6, by the LU Lift and Escalator Inspection Engineer, a ticking noise was noticed emanating from the underside of car, this was noted as possibly being form the sheave area and possibly a bearing by the engineers.
|  | Cxxx-NCR-000002 | NCR | Installed Floor Spring System for Side Gates does not match approved design |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2021-06-03 | 2022-03-10 09:48 | 280 | 2021-05-20 08:12 | Architectural - Doors | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Not Defined | Completed |  | Approved designs for ETH side gates and WTH side gates state that a __ BTS80 will be installed for the floor spring system. A __ model has been installed instead.
|  | Cxxx-NCR-000003 | NCR | Works proceeding with manufacture without an Approved Code 1 manufacturing ITP |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2021-09-01 | 2021-10-22 11:18 | 51 | 2021-05-20 08:31 | Architectural - Doors | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Insufficient work planning by the subcontractors | Completed |  | __ Ltd have proceeded with manufacture of the WTH Vent Shaft Façade Gates and the WTH & ETH Main Gate Enclosures without an Approved Code 1 manufacturing ITP.
|  | Cxxx-NCR-000004 | NCR | Isolation gasket not installed for Main Entrance Gate Enclosures |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2021-06-07 | 2021-12-17 06:27 | 193 | 2021-05-24 12:54 | Architectural - Doors | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Main Gate Enclosure panels have been manufactured without an isolation gasket.
|  | Cxxx-NCR-000005 | NCR | Damaged ETH side gate leaf |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2021-06-17 | 2021-12-02 12:23 | 168 | 2021-06-03 08:53 | Architectural - Doors | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | A lifting incident on 11.05.2021 resulted in a __' side gate leaf being dropped and damaged.
|  | Cxxx-NCR-000006 | NCR | ETH Side Gate - Alignment Issues |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2021-08-12 | 2021-12-08 07:55 | 118 | 2021-07-29 09:47 | Architectural - Doors | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The ETH Side Entrance Gate have been installed out of alignment creating uneven spacing between the leaves. Please see attached photos and survey (provided for information only).
|  | Cxxx-NCR-000007 | NCR | Vent Shaft Facade Gate - Hinge material - Stainless steel |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2021-10-23 | 2022-04-05 07:51 | 164 | 2021-10-09 14:00 | Architectural - Doors | 500 |  | Manufacturing Defect | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | __ have fabricated the hinges for the Vent Shaft Facade gates completely in stainless steel as opposed to brass with a stainless steel pin.
|  | Cxxx-NCR-000008 | NCR | Use of non-compliant SUBMINATURE SNAP SWITCH DC2C-C5RB |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2021-11-12 | 2022-05-26 14:20 | 195 | 2021-10-29 08:54 | Architectural - Doors | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | A SUBMINATURE SNAP SWITCH DC2C-C5RB is called for in the current design of the Side and Main gates for monitoring gate positions (for Cxxx door monitoring system and for motor control). The cable to this type of switch cannot be suitably be mechanically protected as a SWA cable referenced in the drawings can not be connected into these proposed switches. The gates affected are - WTH Entrance Gates- Cxxx-SKC-C-LRG-Cxxx-50580 WTH Side Gates- Cxxx-SKC-A-LRG-Cxxx-50344 ETH Entrance Gates- Cxxx-SKC-A-LRG-Cxxx-50345 ETH Side Gates- Cxxx-SKC-A-LRG-Cxxx-50343
|  | Cxxx-NCR-000009 | NCR | Side Gate - Corroding floor spring encasement boxes |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-09-07 07:03 | 3 | 2021-11-01 15:37 | Architectural - Doors | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | The encasement boxes that hold the Side Gate opening/closing floor springs have corroded significantly after minor duration of installation. See attached photos. **Update 04/12/21** __ have installed the ETH Side Gates with corroding floor springs in 3no. (possibly 5no.) locations.
|  | Cxxx-NCR-000010 | NCR | Colour/Hue of Patinated Main Gate Enclosures (ETH and WTH) |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2021-11-19 | 2021-12-24 07:04 | 35 | 2021-11-05 13:16 | Architectural - Doors | 500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | Patinated Main Gate enclosures panels have been fabricated without seeking CRL sample approval of the colour/hue. Colour/hue does not match the surrounding cladding by a significant margin. See attached photos.
|  | Cxxx-NCR-000012 | NCR | Out of tolerance installation of the ETH and WTH Main Gate throwout track brackets and drive socket fixing postion |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2021-11-25 | 2022-05-20 13:43 | 176 | 2021-11-11 18:31 | Architectural - Doors | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | CRL have completed a survey of the ETH and WTH throwout track brackets. Please see attached for info; adjustments will require __ to complete there own survey. Adjustments identified in this survey have found that the below items are out of position and will clash with the surrounding cladding - 1. Position of ETH drive sprocket holes 2. ETH brackets horizontal position 3. WTH brackets horizontal and vertical position. Note - __ have confirmed that they are working with a new top of bracket height of (124325) that accommodated the original as-built position of the Bridge beam stiffener as agreed in Cxxx-FCD-001054.
|  | Cxxx-NCR-000013 | NCR | Vent Shaft Facade Gate - Main, LHS and RHS Jamb Post - Patination colour/hue |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-07-06 10:28 | -60 | 2021-11-13 11:44 | Architectural - Doors | 500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The Central, LHS and RHS Jamb Post Patination colour/hue is incorrect and not as per the agreed benchmark. See attached photo of Central Jamb Post. ***Update 05/01/2022** Gate leaf colour is also not acceptable; see attached photo - FW__Inspection_VSF_Gates.zip **Update 21/04/2022** Gate leaves returned from factory without acceptable patination following repairs (see C473-NCR-000020); see attached photos - 'Patination issues 20.04.2022 - Folder 1.zip' and 'Patination issues 20.04.2022 - Folder 2.zip'
|  | Cxxx-NCR-000014 | NCR | Vent Shaft Gate - LHS Sliding Mullion Top Track __ Fixings |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-06-24 14:06 | -72 | 2021-11-17 11:02 | Architectural - Doors | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Insufficient thread extension to allow full thread engagement of nut with bolt - see attached of 2no. fixing of the Vent Shaft Gate LHS Sliding Mullion Top Track.
|  | Cxxx-NCR-000015 | NCR | SR3 Rating of D07 side gates |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2021-12-13 | 2022-04-19 12:28 | 127 | 2021-11-29 19:19 | Architectural - Doors | 500 |  | Incomplete Works | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | D07 Side Gates has been installed on the ETH without provision of SR3 certification or modification necessary to gain SR3 certification. The same is expected for the WTH once installed.
|  | Cxxx-NCR-000016 | NCR | WTH VSF Gate - Updated Exceptional Loads Report |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-09-02 10:28 | -2 | 2021-11-29 19:32 | Architectural - Doors | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Not Defined | Completed |  | The Contractor has installed the VSF Gates without providing an updated exceptional load report following various design changes to the gate system
|  | Cxxx-NCR-000017 | NCR | No MCR provided for fixings |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-08-16 14:37 | -19 | 2021-12-04 15:24 | Architectural - Doors | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | The Contractor has not provided an MCR for fixings used on any of the works installed by the Contractor (WTH Side, Main, Vent Shaft Façade and ETH, Main gates).
|  | Cxxx-NCR-000018 | NCR | Captive Floor Pieces for ETH Side Gates |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2021-12-18 | 2022-05-20 08:17 | 153 | 2021-12-04 16:06 | Architectural - Doors | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The Contractor has now installed the ETH Side Gates with incorrect dimensioned floor spring cover pieces captive pieces (see attached photos). The cover plates (including captive pieces) were to be enlarged as part of the solution for the out of position floor springs (see C473-NCR-000006).
|  | Cxxx-NCR-000020 | NCR | Damage to Vent Shaft Facade Gates |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-01-03 | 2022-04-29 07:11 | 116 | 2021-12-20 09:13 | Architectural - Doors | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | The Vent Shaft Façade gates have been significantly damaged by __ operatives in three incidents: - the gate was left unsecured and it smashed into equipment - permanent hinges were replaced without packing (C473-NCR-000007) - gates not secured during Eunice Storm event 18/02/2022
|  | Cxxx-NCR-000021 | NCR | Colour/Hue of Patinated WTH Main Gate Enclosures |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-01-21 | 2022-05-20 06:52 | 119 | 2021-12-22 11:48 | Architectural - General | 500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | Patinated WTH Main Gate enclosures panels have been fabricated without seeking CRL sample approval of the colour/hue. Colour/hue does not match the surrounding cladding by a significant margin. See attached photos.
|  | Cxxx-NCR-000022 | NCR | ETH Main Gate Enclosure |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-07-15 17:32 | -51 | 2022-01-17 05:05 | Architectural - Doors | 500 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Due to the weight of the panels and the length cantilever of the folding portion of the enclosure, the leading edge of the enclosure is not plumb, creating a 55mm gap with the fixed panel. See attached photos.
|  | Cxxx-NCR-000023 | NCR | Maglock clash with substructure of the surrounding small infill panel. |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-01-31 | 2022-04-29 07:14 | 88 | 2022-01-17 05:22 | Architectural - Doors | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | The electrical termination glands of the maglocks are larger than indicated in the approved design for the ETH and WTH side gates. As such, these glands clash with the substructure of the __ small infill panels by approx. 10mm. Please see attached photo from the ETH. It is expected that the same clash exists on the WTH side gates and __ substructure.
|  | Cxxx-NCR-000024 | NCR | Clash with large __ door on WTH Vent Shaft and the __' Sliding Mullion |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-02-03 | 2022-03-11 09:03 | 36 | 2022-01-20 07:02 | Architectural - Doors | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | A clash exists between the __ door and the __' RHS sliding mullion on the WTH Vent Shaft L+0 such that the bottom pendent/roller on the __' RHS sliding mullion needs to be removed to allow the doors to be opened. See attached photo.
|  | Cxxx-NCR-000026 | NCR | Split added to Main Gate jamb post flashing |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-03-31 | 2022-04-15 05:54 | 15 | 2022-03-17 11:19 | Architectural - Doors | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | __ have added a split to the jamb post flashing for the Main Gates
|  | Cxxx-NCR-000027 | NCR | Leading Edge Unrestrained on VSF Gates on DP2 and DP4 leaves |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-06-17 10:21 | -79 | 2022-04-21 09:01 | Architectural - Doors | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The leading edge of DP2 and DP4 on the VSF Gates are not restrained by the shoot bolts. As a result, these leaves can be pulled easily outwards. See attached mark-up showing leaves affected.
|  | Cxxx-NCR-000028 | NCR | WTH Enclosure bracket fixing redrilled without supporting calcs or design approval |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-07-01 13:40 | -65 | 2022-05-21 10:56 | Architectural - Doors | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | __ have proceed with drilling a new fixing hole in the WTH Main Gate enclosure bracket without following design approval process
|  | Cxxx-NCR-000029 | NCR | ETH Main Throwout track rollers |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-06-17 14:13 | -79 | 2022-05-31 15:24 | Architectural - Doors | 500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | The Contractor has fabricated the throwout track rollers 20mm too large - see attached email
|  | Cxxx-NCR-000031 | NCR | Main Entrance Gate Top Track Slipping out of alignment |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-07-18 | 2022-07-15 17:34 | -3 | 2022-07-04 16:55 | Architectural - Doors | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The Main Entrance Gate Top Track Slipping out of alignment. The problem was amended on the WTH by introducing another fixing into the web of the main entrance beam. The concern is that this is going to be an ongoing problem, only discovered after the gates have been operation for a period of time.
|  | Cxxx-NCR-000032 | NCR | Key switch |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-09-30 | 2022-09-07 15:25 | -23 | 2022-07-04 17:00 | Architectural - Doors | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The key switch provided by __ projects beyond the line of the cladding and is not accordance with the approved design
|  | Cxxx-NCR-000033 | NCR | Functionality issues on ETH and WTH main gate controls |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-07-21 | 2022-07-29 14:57 | 8 | 2022-07-07 13:51 | Architectural - Doors | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | The ETH and WTH Main Gates have the below functionality issues - 1. Correct LEDs not lighting up 2. Sounder and beacon not functioning correctly 3. Key switch not functioning correctly
|  | Cxxx-NCR-000034 | NCR | WTH/ETH Main Entrance Gates Missing & loose fixings - Lack of torque tests |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-10-19 | 2022-11-14 11:43 | 26 | 2022-10-05 08:13 | Architectural - Doors | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Not Defined | Completed |  | Following an inspection with Crossrail's Architect, to the Main Entrance Gates, a number of fixings were missing, were loose or were not torque tested (attached pictures).
|  | Cxxx-NCR-000035 | NCR | __ - Ticket Hall Main Gates - Enclosure Corrective Works |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-10-25 | 2022-11-11 06:27 | 17 | 2022-10-11 12:50 | Architectural - General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | During works to prepare station main gates for readiness, the following issues were discovered on the enclosure: 1. Internal 'enclosure shut' microswitch did not activate properly with existing bracketry (WTH & ETH) 2. Enclosure did not align with the front panel (WTH & ETH) 3. Ramp piece did not work with the current drop bolt position, requiring refabrication. 4. Ramp piece required redrilling to accommodate the drop bolt. These works were addressed by Contractor's representative (B&F) via the following means: 1. New microswitch bracketry was designed, fabricated and installed by B&F (WTH & ETH - microswitch now activates correctly). 2. WTH: A) New roller installed on the underside of the enclosure panel B) A restraining bracket was installed the pull the warped front panel back into alignment ETH: A) Operatives removed and realigned the closer dampening strips inside the enclosure B) B&F Operatives removed clashing elements projecting into the enclosure swing 3. New ramp pieces were designed, fabricated and installed by B&F 4. B&F operatives drilled the ramps (3) to allow the drop bolts to fully activate.
|  | Cxxx-NCR-000036 | NCR | __ - Station Side Gates - Side Gate Corrective Works |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2023-02-02 | 2023-01-31 14:41 | -2 | 2022-10-14 14:20 | Architectural - General | 3000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | The following issues have been observed with the __ Side Gates during inspection; - All side gate drop bolts do not activate the microswitch in the soffit, preventing a signal being sent back to the SOR that the gates are closed. - 1No Emergency escape side (ETH) will not disengage on the emergency side when handle is turned.
|  | Cxxx-NCR-000037 | NCR | __ - Side Gates - Escape Gate Locking Mechanism Issues (WTH & ETH) |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2023-02-02 | 2023-01-31 14:45 | -2 | 2022-10-20 15:34 | Architectural - General | 5000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | WTH: During operation of the WTH Side Gates, the Easternmost Emergency Escape Side gate has started to jam during operation. On inspection by B&F and Y&Y operatives, it appears to be an issue in the internal mechanism, which will need to be replaced and reinstalled (cannot be addressed on site). ETH: On operation of both the emergency escape doors, it has been noted that the emergency release is not releasing properly once the gate is locked externally. We believe that this has been caused by the internal mechanism being installed on the alternate door - we believe this can be switched on site.
|  | Cxxx-NCR-000038 | NCR | __ - Side Gates - Emergency Gate Handle - Spindle has threaded the socket |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2023-02-02 | 2023-01-31 14:49 | -2 | 2022-11-09 11:19 | Architectural - General | 500 |  | Equipment Breakdown | Rework | 4 (0.5-3k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | Under inspection after the ETH emergency side gate ceased to engage during staff operation, it has been noted that the spindle has threaded its receiving socket (see attached photos). This has been identified as a risk for all emergency escape gates.
|  | Cxxx-NCR-000039 | NCR | __ - Main Gates - Main gate loses alignment (limit shifts) |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-11-30 | 2022-11-18 12:24 | -12 | 2022-11-16 12:51 | Architectural - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | External Phenomenon - Not Defined | Completed |  | A commonly made user error during operation allows the gate to be closed or opened with the locking mechanism engaged. If this happens, the chain jumps, shifting the set limit position on the gate, preventing it from fully opening and closing when subsequently operated. Once the limit has shifted, the gate will not close fully and the lock cannot be engaged, requiring the limits to be reset and recalibrated before this can be achieved. Further training needs to be provided to LU staff to avoid this, and there is a subsequent ongoing cost for the limits to be reset if the error occurs. The O&M Manual should be updated to include how to address this for the maintainer.
|  | Cxxx-NCR-000041 | NCR | ETH Enclosure Not Plumb |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2023-03-18 |  | -40 | 2023-01-16 09:43 | Architectural - General | 500 |  | Incorrect Installation |  |  | Open |  | PROPOSE ACTION |  | It has been found that the ETH front enclosure panel is not plumb by approx. 25mm. This is causing the last gate leaf to clash with the panel when opening and closing the gates. A similar issue was found previously at the WTH prior to handover
|  | Cxxx-NCR-000042 | NCR | ETH Entrance Gate Snags |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2023-03-18 |  | -40 | 2023-01-16 10:53 | Architectural - General | 500 |  | Incorrect Installation |  |  | Open |  | PROPOSE ACTION |  | Two number snags were discovered during the site review carried out by __ 11/01/23 Bushing missing from high level pendant 1st gate leaf clashing with jamb post on bottom section
|  | Cxxx-NCR-000001 | NCR | P&T - Platform Wayfinding Signage Print Issue - Providing Incorrect Temp Vinyl (__) |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-07-22 08:03 | -44 | 2022-01-28 12:40 | Architectural - Signage | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The sub contractor Wood Wood were instructed to supply blanking vinyl to temporarily cover some permanent wayfinding signage for a short duration for a particular stage of the project. However the sub contractor provided blanking vinyl with high tack adhesive not low tack even though they knew the vinyl was only temporary. Following the completion of that stage of the project requiring the blanking vinyl, it was removed peeling away the print of some of the permanent wayfinding signage text as a result of using high tack adhesive vinyl.
|  | Cxxx-NCR-000002 | NCR | USN204 Bracketry Re-Manufacture |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-01-20 | 2022-02-07 16:20 | 18 | 2021-12-23 13:16 | Architectural - Signage | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Bracketry for USN 204 does not align with the fixing studs installed by other trades, Sign bracketry requires remanufacture.
|  | Cxxx-NCR-000003 | NCR | P&T - USN 207 Signage Bracket SS Trim Fabricated Incorrectly |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-02-10 | 2022-02-09 10:00 | -1 | 2022-01-27 09:09 | Architectural - Signage | 500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The stainless steel panel which is installed around the USN 207 projecting sign in AP1 requires an oversized panel aperture to facilitate its installation around the signage bracket. To cover the gap at the bottom of the panel aperture, a stainless steel plate was incorporated into the design of the bracket and should have been welded to the bottom of the main projecting arm. However, upon delivery to site it was noted the SS plate was welded on the top of the bracket arm. This would prevent the installation of the surrounding stainless steel panel. It would need to be rectified.
|  | Cxxx-NCR-000004 | NCR | P&T - USN 402 & 419 Clash between Cable Entry Hole and Rear Support Plate (Wood Wood) |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-04-08 | 2022-04-08 09:43 | 0 | 2022-03-31 16:25 | Architectural - Signage | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | USN 402 & 419 have a similar design - the front signage unit is fixed to a rear support plate which is fixed into the AP2 bullet door structure. These signs are illuminated so require a 20mm cable entry hole in the back of each signage unit to facilitate the cable route. Unfortunately the edge of the rear support plate partially covers the cable entry hole in the signage unit for both USN 402 & 419. A Proposal to trim locally the edge of the rear support plates has been discussed with the sub contractor design team.
|  | Cxxx-NCR-000005 | NCR | P&T - Connection Fixing Holes in USN 207 NOT as Per Design/Drawing (Wood Wood) |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-07-26 08:46 | -40 | 2022-04-04 13:57 | Architectural - Signage | 500 |  | Manufacturing Defect | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | It was noted that the configuration of the connection holes between the bracket and signage unit did not reflect the approved design drawing and clarification is needed from the wayfinding sub contractor designer that the current configuration is acceptable.
|  | Cxxx-NCR-000006 | NCR | Lack of Signed Inspection Checksheets for Torque and Pull-out Testing |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-04-20 | 2022-05-04 08:32 | 14 | 2022-04-06 14:28 | Architectural - Signage | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | Although the pull-out and torque testing were carried out, and with the checksheet signed by the installer (W&W) and tests witnessed by Cxxx (), the testing was not witnessed by CRL Architectural. For avoidance of doubt the torque testing was carried out by the installer (W&W), while the pull-out testing being undertaken by an independent assessor. As the tests were carried out by an independent body we proposed for the items installed to kept and utilised as they are without the requirement of further testing.
|  | Cxxx-NCR-000007 | NCR | WTH L-3 USN 200 - Poor Installation Workmanship |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-09-30 | 2022-10-03 08:43 | 3 | 2022-04-14 12:31 | Architectural - Signage | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | Due to poor installation and workmanship, USN 200 present at WTH L-3 above the lift door has been installed out of tolerance and alignment in relation to the surrounding bronze cladding and stainless-steel lift architraves.
|  | Cxxx-NCR-000008 | NCR | Hanging Signs - insufficient treaded on the support rods |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-08-25 12:41 | -10 | 2022-04-25 09:51 | Architectural - Signage | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | It was observed that on the hanging signs, the treaded rods are generally either flush or short of passing through the nut, whereas industry standards normally call for the thread to protrude. This issue might affect all the hanging signs and it's not limited to USN 005, 104, 400, 401, 1013 & 1014.
|  | Cxxx-NCR-000009 | NCR | Pull Testing to be completed |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-06-30 09:33 | -66 | 2022-05-19 20:12 | Architectural - Signage | 500 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Management Problem - Not Defined | Completed |  | Pull tests are still to be completed on the below installed signs in L-3 WTH - Projecting signs – USN202, 207, 214 and 216 Suspended sign – USN205
|  | Cxxx-NCR-000010 | NCR | P&T - Incorrect Graphic's to PES ENd Wall Signs USN 500 & 700 (Missing Wheelchair Symbol) |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-07-07 | 2022-07-22 08:29 | 15 | 2022-06-23 10:08 | Architectural - Signage | 500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | Incorrect Graphic's to PES End Wall Signs USN 500 & 700 (Missing Wheelchair Symbol)
|  | Cxxx-NCR-000011 | NCR | P&T - Missing Support Angles to Gas Struts of Top Panel of Platform Curved Signage (SGN 205) |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-07-22 14:48 | -44 | 2022-06-13 08:02 | Architectural - Signage | 500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | P&T - It was noted during an inspection of some of the top panels of the USN 205 platform curved signs that the brackets supporting the gas struts were bent, possibly from the opening of the top panel . Upon further inspection of other top panels, it was noted that some gas strut brackets had an additional angle in place which would potentially prevent the gas strut bracket from bending. This detail is NOT clear on the approved design drawing but should be shown on the fabrication drawing which the site team wouldn't have access to. These signs were manufactured by Wood Wood.
|  | Cxxx-NCR-000012 | NCR | P&T - USN 216 Bracket Missing Downstand Plate to Cover Panel Gap in AP1 Corridor (Wood Wood) |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-08-30 | 2022-08-19 10:10 | -11 | 2022-06-29 15:45 | Architectural - Signage | 500 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Similar to USN 207 and 302, there needs to be a gap left under the signage bracket to accommodate the install & removal of the surrounding SS cladding panel. To cover this gap, a stainless downstand plate was designed to be fixed the underside of the signage bracket. Unfortunately, the USN 216 bracket doesn't have any downstand plate in place even though it is clearly shown on the approved WW design drawing.
|  | Cxxx-NCR-000013 | NCR | ETH L-0 USN 006 - Poor Installation Workmanship |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-07-22 | 2022-10-03 07:38 | 73 | 2022-07-08 09:55 | Architectural - Signage | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Due to poor installation and workmanship, USN 006 present at ETH L0 above the lift door has been installed out of tolerance and alignment in relation to the surrounding bronze cladding and stainless-steel lift architraves.
|  | Cxxx-NCR-000014 | NCR | Faulty Drivers - 10Nr. Sitewide |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-09-26 | 2022-11-14 15:22 | 49 | 2022-09-12 13:29 | Architectural - Signage | 500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During commissioning of __ Signage throughout the station, 10Nr. driver failures have occurred.
|  | Cxxx-NCR-000015 | NCR | Incorrect Installation of Poster Case Catches |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-11-15 | 2022-11-10 10:36 | -5 | 2022-11-01 14:25 | Architectural - Signage | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Poster case catches have been secured using 3m tape. During the install of the LU posters by LU operational staff it was found that the catches had debonded from the 3m tape.
|  | Cxxx-NCR-000017 | NCR | Faulty LEDs in ETH Entrance Sign |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-11-15 | 2022-11-10 17:45 | -5 | 2022-11-01 14:30 | Architectural - Signage | 500 |  | System Defect | Repair | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | 3Nr. LED strips have been found to be faulty in the ETH front entrance
|  | Cxxx-NCR-000018 | NCR | Faulty LEDs in USN 202 |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-11-15 | 2022-11-10 17:47 | -5 | 2022-11-01 14:31 | Architectural - Signage | 500 |  | Material | Repair | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | FAulty LED found in USN 202. This LED will need to be replaced
|  | Cxxx-NCR-000009 | NCR | ETH - LIN 409 Precast skirting clash |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-01-26 | 2022-03-10 16:01 | 43 | 2022-01-12 12:14 | Architectural - Finishes | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | There is a stainless steel bracket that sits beneath the LIN 403 Panels to act as a backing plate for the LIN 409 skirting to be installed. Unfortunately either side of the ETH Escalator this bracket originally installed by __ is out by approximately 20mm.
|  | Cxxx-NCR-000010 | NCR | ETH Lift 5 - Panel alignment |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-02-18 | 2022-04-21 08:16 | 62 | 2022-02-03 16:50 | Architectural - Finishes | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | External Phenomenon - Not Defined | Completed |  | The bronze panels that are surrounding the Lift 5 entrance and adjacent the lift architrave are out of alignment. On the left side the gap between the Bronze door and architrave is approximately 15mm where it is designed to be a 5mm nominal gap, along with the bronze door is sitting approx. 15mm further out. Additionally on the right side of the Lift front, the fixed panel doesn't align with the hinged panel beneath nor the cladding panel above.
|  | Cxxx-NCR-000011 | NCR | ETH Northern Facade - Damages to Bronze Panels |  | Contr | XRL | BOS - Bond Street Station (West) |  | 2022-04-30 | 2022-06-09 11:13 | 40 | 2022-02-10 17:01 | Architectural - Finishes | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Contamination | Completed |  | Damages to 4 No's bronze panels were identified on the ETH North Façade (attached pictures and marked drawings)
| 02SL - Stations (LUL) | Cxxx-NCR-000137 | NCR | welded reinforcement of the Pali Radici |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2011-10-17 | 2011-11-17 11:12 | 31 | 2011-10-11 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | C501 failedd to follow the procedure
| 02SL - Stations (LUL) | Cxxx-NCR-000142 | NCR | Tests Cubes made by non UKAS persons |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2011-10-21 | 2011-11-08 22:36 | 18 | 2011-10-17 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed |  | Non UKAS trained or certificated person/s making and storing cubes on site.
| 02SL - Stations (LUL) | Cxxx-NCR-000144 | NCR | Inspection Request form not issued |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2011-10-17 | 2011-11-08 22:41 | 22 | 2011-10-25 | Structural Engineering - Structural Engineering - General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Completed installation of first contiguous mini pile without issuing inspection request form to Crossrail for witness points identified on ITP
| 02SL - Stations (LUL) | Cxxx-NCR-000157 | NCR | Pali Radici |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2011-10-31 | 2011-11-04 19:01 | 4 | 2011-10-28 | Civil - Geotechnical Engineering | 500 |  | System Defect | Use As-Is |  | Complete |  | Completed |  | No records being kept on site for each individual pile reinforcement length Nor drawings kept on site
| 02SL - Stations (LUL) | Cxxx-NCR-000158 | NCR | Check certificate not issued |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2011-11-02 | 2011-11-10 17:35 | 8 | 2011-11-01 | Structural Engineering - Structural Engineering - General | 500 |  | Design | Use As-Is |  | Complete |  | Completed |  | Constructed the piling mat for the Contiguous and pali radice pile installation without a design check certificate issued with the design.
| 02SL - Stations (LUL) | Cxxx-NCR-000163 | NCR | Inspection Request Forms |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2011-11-11 | 2011-11-08 22:38 | -3 | 2011-11-04 | Civil - Geotechnical Engineering | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | The client has not been invited or recieved adequate notice of impending intervention points.
| 02SL - Stations (LUL) | Cxxx-NCR-000166 | NCR | Setting out of hoarding |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2011-11-11 | 2011-12-02 23:25 | 21 | 2011-11-04 | Civil - Civil Engineering General | 500 |  |  | Use As-Is |  | Complete |  | Completed |  | 1 number Timber post exceeds 1500 by 340mm
| 02SL - Stations (LUL) | Cxxx-NCR-000171 | NCR | Working without ITP |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2011-11-22 | 2011-11-17 11:43 | -5 | 2011-11-15 | Utilities Engineering - Water | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | Sub Contractor RGB commenced work prior to the acceptance of ITP for the Relocation of existing Mechanical services withing Moorgate Station
| 02SL - Stations (LUL) | Cxxx-NCR-000181 | NCR | Cover to pile cages |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2011-11-22 | 2011-11-27 22:26 | 5 | 2011-11-21 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Material | Rework |  | Complete |  | Completed |  | Existing pre welded rebar spacers in excess of 50mm
| 02SL - Stations (LUL) | Cxxx-NCR-000183 | NCR | Loss of Auger |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2011-11-28 | 2011-11-30 10:38 | 2 | 2011-11-24 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Equipment Breakdown | Use As-Is |  | Complete |  | Completed |  | Auger section lost whilst augering to required depth. new section added and continue to required depth. It is presumed that the lost section would have been pushed to the front or back of the contiguous wall. If to the front this may cause problems for the D wall construction.
| 02SL - Stations (LUL) | Cxxx-NCR-000184 | NCR | Concrete grout testing |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2011-11-29 | 2011-12-13 22:02 | 14 | 2011-11-24 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Cube samples being transported away from site in buckets or bags and made away from site. Materials appear not to be labelled, or records kept of time taken or when made.
| 02SL - Stations (LUL) | Cxxx-NCR-000204 | NCR | Surveillance on drawing management |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2011-12-22 | 2011-12-19 12:11 | -3 | 2011-12-14 | Communications and Control Systems | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed |  | A third party drawing used for demolition was found not to be on the drawing register.
| 02SL - Stations (LUL) | Cxxx-NCR-000205 | NCR | Late Submission of ITPs |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-01-13 | 2011-12-19 08:29 | -25 | 2011-12-14 | Civil - Civil Engineering General | 500 |  | Planning | Repair |  | Complete |  | Completed |  | ITPs are being submitted with less that 4 weeks before start of work.
| 02SL - Stations (LUL) | Cxxx-NCR-000215 | NCR | Surveillance on hoarding maintenance |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-01-19 | 2012-02-09 16:40 | 21 | 2012-01-12 | Construction Health & Safety - Construction Health & Safety General | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | Not maintained requires Gloss painting in Crossrail blue, addition of top rail and toe board
| 02SL - Stations (LUL) | Cxxx-NCR-000221 | NCR | Support slab for Temporary support to 8-87 |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-02-14 | 2012-02-28 16:53 | 14 | 2012-01-31 | Civil - Structural Engineering | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | No cubes taken
| 02SL - Stations (LUL) | Cxxx-NCR-000222 | NCR | Failure to raise IRF |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-02-07 | 2012-02-14 17:19 | 7 | 2012-01-31 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed |  | Crossrail were not informed that works requiring inspection would take place at the weekend. It was originally notified prior to the weekend that works would be carried out on the Monday.
| 02SL - Stations (LUL) | Cxxx-NCR-000239 | NCR | Mortar Cube failed to reach target strength |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-03-13 | 2012-03-22 14:26 | 9 | 2012-03-06 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Mortar M4 failed to achieve 4N/mm2 at 28 days by 0.1N/mm2 and 0.25N/mm2 respectively for two cubes crushed at this date. No spares remaining.
| 02SL - Stations (LUL) | Cxxx-NCR-000241 | NCR | Failed to submit ITP |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-03-15 | 2012-03-15 08:43 | 0 | 2012-03-07 | Civil - Civil Engineering General | 500 |  | Planning | Use As-Is |  | Complete |  | Completed |  | C501 failed to submit the ITP for the installation of the bentonit silos 4 weeks befor the work start
| 02SL - Stations (LUL) | Cxxx-NCR-000253 | NCR | Ready mix concrete. Incorrectly mixed |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-03-20 | 2012-04-17 22:33 | 28 | 2012-03-19 | Civil - Drainage | 500 |  | Material | Rework |  | Complete |  | Completed |  | Concrete has arrived on site poorly mixed, where the admixture micro silica has collected into lumps. This would mean that the correct dosage of admixture was not entering the structure.
| 02SL - Stations (LUL) | Cxxx-NCR-000261 | NCR | Testing |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-04-11 | 2012-04-17 22:35 | 6 | 2012-03-28 | Civil - Civil Engineering General | 500 |  | Planning | Rework |  | Complete |  | Completed |  | UKAS accredited laboratory __ failed to make cubes for the Moorfields sewer diversion. On the 27/3/12. The technician arrived on time but left site without making cubes. Also __ Ltd carrying out works on the Goswell sewer strenthening project on two occaisions have failed to have __ make cubes, cause being late arrival and failure to arrive.
| 02SL - Stations (LUL) | Cxxx-NCR-000269 | NCR | Sewer Diversion |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-04-23 | 2012-04-17 22:47 | -6 | 2012-04-16 | Civil - Civil Engineering General | 500 |  | Design | Use As-Is |  | Complete |  | Completed |  | Bar mark 26 incorrectly scheduled as too long but cut too short in manufacturing.
| 02SL - Stations (LUL) | Cxxx-NCR-000270 | NCR | Removal of crack inducer |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-04-23 | 2012-05-31 14:21 | 38 | 2012-04-16 | Civil - Sewage/Water services | 500 |  | System Defect | Rework |  | Complete |  | Completed |  | The method did not work, steel formers were left in the pour.
| 02SL - Stations (LUL) | Cxxx-NCR-000272 | NCR | Poor finish to concrete Wall |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-04-23 | 2012-04-27 16:36 | 4 | 2012-04-16 | Civil - Civil Engineering General | 500 |  |  | Repair |  | Complete |  | Completed |  | Air holes and grout loss
| 02SL - Stations (LUL) | Cxxx-NCR-000279 | NCR | Incorrectly formed thrust blocks |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-04-27 | 2012-05-11 08:08 | 14 | 2012-04-20 | Utilities Engineering - Water | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | Thrust blocks are constructed oversize, and encasing components that should not be concreted. This will prevent removal and replacemnt in future.
| 02SL - Stations (LUL) | Cxxx-NCR-000280 | NCR | Pile 8 fill material |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-04-27 | 2012-04-25 23:24 | -2 | 2012-04-20 | Civil - Fill | 500 |  | Material | Repair |  | Complete |  | Completed |  | Cube results failed to reach the expected strength. 0.05N/mm2 was achieved. The cause was an incorrect ratio of Bentonite to concrete. The design required 0.331m3/m3 of soilcrete. Actual volume was 0.5m3/m3 of soilcrete
| 02SL - Stations (LUL) | Cxxx-NCR-000285 | NCR | MH S4 Blinding |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-04-25 | 2012-04-26 10:19 | 1 | 2012-04-24 | Civil - Sewage/Water services | 500 |  | Design | Rework |  | Complete |  | Completed |  | Visqueen was used below blinding to prevent water coming up during concrete placement. During placement the water was trapped beneath and formed pockets of water which reduced the thickness of concrete from the required 75mm.
| 02SL - Stations (LUL) | Cxxx-NCR-000286 | NCR | GRAMM - Subcontractor Approval not Sought |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-05-09 | 2012-05-04 13:03 | -5 | 2012-04-26 | Communications and Control Systems | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | __ began working on the acoustic barrier required for extended hours working prior to approval was received from Crossrail
| 02SL - Stations (LUL) | Cxxx-NCR-000288 | NCR | Use of non approved repair material |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-05-07 | 2012-05-14 08:45 | 7 | 2012-04-30 | Civil - Sewage/Water services | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Failure to raise a MCR for the use of __ 4A with non approved sand cement mix
| 02SL - Stations (LUL) | Cxxx-NCR-000291 | NCR | Box Culvert Base - 28 day test failed |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-05-10 | 2012-05-04 15:26 | -6 | 2012-05-03 | Civil - Structural Engineering | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Mix Design with 55% GGBS 20mm agg was placed in the Box Culvert base. Two cubes were crushed at 28 days for concrete mix design C35/45. One cube passed at 45N/mm and the other failed at 43.5N/mm.
| 02SL - Stations (LUL) | Cxxx-NCR-000305 | NCR | Cube failure |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-06-05 | 2012-07-06 08:37 | 31 | 2012-05-31 | Civil - Drainage | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | A test cube achieved 40N/mm2 at 28 days
| 02SL - Stations (LUL) | Cxxx-NCR-000310 | NCR | Failure of concrete test cubes to attain design strength |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-08-02 | 2012-07-12 09:04 | -21 | 2012-06-21 | Utilities Engineering - Water | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Cubes C501-C0105 and C0106 attained 38.6 and 38.5N/mm respectively.
| 02SL - Stations (LUL) | Cxxx-NCR-000316 | NCR | Goswell Street Sewer - Failure of Concrete Test Cubes to Attain Design Strength |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-10-05 | 2012-09-25 15:38 | -10 | 2012-06-29 | Civil - Sewage/Water services | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | The cube results for pours 8, 11 & 12 were below strength at 54N/mm2, 53N/mm2 & 55.5N/mm2 respectivley.
| 02SL - Stations (LUL) | Cxxx-NCR-000317 | NCR | failure to control and monitor ground movement |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-08-15 | 2012-08-13 23:00 | -2 | 2012-07-01 | Geotechnical Engineering - Settlement | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | On Monday 25th June, whilst sheet piles adjacent to 8 Moorfields were being pulled out using vibration equipment, large cracks in excess of 25mm wide were noticed in the west and south walls of the basement to 8 Moorfields and the north and west walls of the basement to the Globe pub. Data from UCIMS shows that levelling studs in the area of 8 Moorfields have settled by in excess of 30mm. No alerts have been activated by the contractor and no review of data from UCIMS has been carried out or presentation of ground movements. Ground movement has not been controlled within limits stated in the Employers I&M Plan or the Contractor's Action Plan.
| 02SL - Stations (LUL) | Cxxx-NCR-000318 | NCR | Crack at the party wall of No. 8 Moorfields |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-08-31 | 2012-08-27 21:00 | -4 | 2012-07-03 | Geotechnical Engineering - Settlement | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed |  | 1- Three No. of the Sheet piles had been pulled out to a certain level using a vibro hammer which should not happen. 2- When the groundwater is encountered above formation level no injection grouting carried out. 3- The excavation did exceed the formation level.
| 02SL - Stations (LUL) | Cxxx-NCR-000322 | NCR | 28 day cube fails to reach design strength |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-09-17 | 2012-09-17 23:05 | 0 | 2012-07-06 | Civil - Drainage | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Cubes 501-C0170 and 171 attained 38 and 38.5 respectively. Failing to achieve 45M/mm2.
| 02SL - Stations (LUL) | Cxxx-NCR-000330 | NCR | Concrete not reaching design strength |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-08-31 | 2012-07-20 16:26 | -42 | 2012-07-17 | Civil - Drainage | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Cubes C501-CO203 and 0204 attained 33 and 33.4N/mm2. Design strength is 45N/mm2 at 28 days
| 02SL - Stations (LUL) | Cxxx-NCR-000334 | NCR | Test Cube failing to reach design strength at 28 days |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-09-28 | 2012-09-17 23:07 | -11 | 2012-07-23 | Civil - Sewage/Water services | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Test cubes Co216 and 217 achieved 35 and 35.5N/mm2
| 02SL - Stations (LUL) | Cxxx-NCR-000346 | NCR | Goswell Sewer Flexurial tests not carried out |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-10-14 | 2012-09-26 13:30 | -18 | 2012-08-14 | Civil - Sewage/Water services | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Tests carried out on trial panel but not on permanent works.
| 02SL - Stations (LUL) | Cxxx-NCR-000350 | NCR | Failure of Concrete to reach design strength at 28 days |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-10-23 | 2012-10-07 20:51 | -16 | 2012-08-22 | Civil - Drainage | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Cubes numbers 203, 204 achieved 33 and 33.4N/mm2 at 28 days. 205, 206, 207 crushed at 56 days achieved 37.4, 37.4 and 38.2 respectively.
| 02SL - Stations (LUL) | Cxxx-NCR-000364 | NCR | Chlorination of the 250mm water main |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-09-24 | 2012-09-28 16:45 | 4 | 2012-09-20 | Utilities Engineering - Water | 500 |  | Material | Rework |  | Complete |  | Completed |  | Chlorination result came out at 15 ppm
| 02SL - Stations (LUL) | Cxxx-NCR-000406 | NCR | Guide wall tolerance |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-11-20 | 2012-11-12 14:08 | -8 | 2012-11-06 | Shafts - Shafts General | 500 |  | System Defect | Repair |  | Complete |  | Completed |  | Distance between guide walls after construction was measured as 1.2m
| 02SL - Stations (LUL) | Cxxx-NCR-000410 | NCR | reinstatement of utility trench |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-12-21 | 2012-12-12 15:38 | -9 | 2012-11-21 | Civil - Roadworks Formation | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | the trench had been offered for inspection to be ready for concreting , CRL noticed that the existing concrete had not been cleaned and there were some backfilling material on the corners and there were a water valve chamber had not sealed and the concrete may easily going through. please find the attached photos.
| 02SL - Stations (LUL) | Cxxx-NCR-000412 | NCR | D-Wall Guide Wall design line |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-03-15 | 2013-02-11 22:04 | -32 | 2012-11-22 | Structural Engineering - Diaphragm Walls | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | The width and verticality of the guide wall to the east of the southern berrette is out of tolerance. following an asbuilt survey on the top line. A further survey will be carried out once we strike the shutters after the minimum striking time. The guide wall will be scabbled back to design line.
| 02SL - Stations (LUL) | Cxxx-NCR-000425 | NCR | Bentonite Silos Assurance |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-03-31 | 2013-03-15 08:21 | -16 | 2013-01-14 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | No assurance documents have been provided for the manufacturing of the bentonite silos
| 02SL - Stations (LUL) | Cxxx-NCR-000428 | NCR | Concrete cubes not reaching Strength |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-02-04 | 2013-01-25 08:22 | -10 | 2013-01-23 | Utilities Engineering - Utilities General | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Cubes taken for Ropemaker Street on the 19/12/12 No's C0504a and C0505a reached 38.4 and 38.2 respectively. Spare crushed at 34 days reached 39N/mm
| 02SL - Stations (LUL) | Cxxx-NCR-000429 | NCR | No Approved Concrete Supplier & Design Mix |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-02-25 | 2013-01-30 22:42 | -26 | 2013-01-24 | Utilities Engineering - Gas | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | No Approved Concrete Supplier & Design Mix
| 02SL - Stations (LUL) | Cxxx-NCR-000430 | NCR | P22 ‘M’ and P31 Reinforcement Steel Level |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2014-04-01 | 2013-07-04 09:17 | -271 | 2013-06-11 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Due to an error during fabrication of reinforcement cage P22 design case M and P31 the current as built top of steel is ~150mm high. The positional components for the Griptec male couplers were not installed between cage 4 & 5. This has raised all permanent main bars and shear links by ~150mm. The top band within cage 5 is installed to the correct level and all couplers are set out from this point and are at the correct level in relation to the top band. Now that the main bars are welded into position it is now not possible retrospectively introduce the missing components. The consequence of this error will mean that the top of steel and toe of steel level will be ~150mm higher than design while the correct horizontal (slab) coupler levels are maintained.
| 02SL - Stations (LUL) | Cxxx-NCR-000432 | NCR | Diaphragm wall Panel 01 installation |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-03-31 | 2013-03-15 08:29 | -16 | 2013-01-29 | Civil - Excavation | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | Obstruction hit whilst excavating; unable to place reinforcement cage to level. Excavation has been backfilled and panel will be reexcavated.
| 02SL - Stations (LUL) | Cxxx-NCR-000434 | NCR | Reinstatement |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-03-01 | 2013-03-04 10:23 | 3 | 2013-01-30 | Utilities Engineering - Utilities General | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | Crowning of road reinstatement in excess of 10mm causing water to pond in front of pedestrian drop kerb, surround to tactile pavement and existing york stone paving not flush, two areas haveing a trip greater than 6mm
| 02SL - Stations (LUL) | Cxxx-NCR-000435 | NCR | REMOVAL OF PILE 53 PRIOR TO DIAPHRAGM WALLING |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-03-31 | 2013-01-31 23:08 | -59 | 2013-01-30 | Civil - Demolition/Site Clearance | 500 |  |  | Use As-Is |  | Complete |  | Completed |  | none
| 02SL - Stations (LUL) | Cxxx-NCR-000438 | NCR | Damage to CW62 brick work |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-03-31 | 2013-02-22 14:17 | -37 | 2013-02-06 | Civil - Civil Engineering General | 500 |  |  | Repair |  | Complete |  | Completed |  | Outer layer of brick works from the brick arch has delaminated exposing the next layer of bricks underneath. This is not a structural element of the structure but closes off behind the beams.
| 02SL - Stations (LUL) | Cxxx-NCR-000440 | NCR | Road reinstatement failure |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-04-15 | 2013-02-15 08:42 | -59 | 2013-02-12 | Utilities Engineering - Water | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | Road surface adjacent to works requires intervention at the earliest opportunity. Cracking greater than 2.5mm, Exceeds NG2.2.5 Combined Defect – Intervention.
| 02SL - Stations (LUL) | Cxxx-NCR-000442 | NCR | SP002 Piezometer in the South East of the Shaft has been damaged from tracking machines |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-04-30 | 2013-04-19 11:12 | -11 | 2013-02-14 | Geotechnical Engineering - Geotechnical Monitoring | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | A 60m Piezometer pipe has been snapped at the tip and some loose material has got down the pipe creating an obstrumction 27 meters down from PPL.
| 02SL - Stations (LUL) | Cxxx-NCR-000444 | NCR | Failure to take 56 day test cubes |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-05-21 | 2013-02-27 12:35 | -83 | 2013-02-19 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | No cubes taken for 56 day test
| 02SL - Stations (LUL) | Cxxx-NCR-000445 | NCR | Over dig on Panel S05 |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-03-01 | 2013-03-01 14:38 | 0 | 2013-03-01 | Civil - Civil Engineering General | 500 |  | System Defect | Use As-Is |  | Complete |  | Completed |  | Panel over dug by approximately 1m due to difficulty in desanding bentonite depths checks were not able to be performed accurately due to the bentonite being too thick.
| 02SL - Stations (LUL) | Cxxx-NCR-000449 | NCR | Temporary jetty bolt connection |  | Contr | BAM | LIS - Liverpool Street Station (Central) |  | 2014-12-31 | 2014-09-23 10:38 | -99 | 2013-02-27 | Structural Engineering - Bolted Connections | 5000 |  | Material | Rework | 3 (3-6k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | M30 X 110mm Grade 8.8 HSFG Bolts were used to splice the King post
| 02SL - Stations (LUL) | Cxxx-NCR-000452 | NCR | Non UKAS trained person making test cubes |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-04-30 | 2013-03-14 13:56 | -47 | 2013-03-01 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Person not trained by __ as agreed by CRL making test cubes.
| 02SL - Stations (LUL) | Cxxx-NCR-000453 | NCR | Missing Concrete test cube results |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-04-30 | 2013-03-07 15:45 | -54 | 2013-03-04 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | It was noted that on 3 occasions cubes were taken but no results pertaining to pali radici piles 48, 53, 33, 24 and 55 were returned. We have approached __ the sub contractor more than several times asking for these results. We also asked __ and __ the test house if they could release the results directly to __. This has not happened.
| 02SL - Stations (LUL) | Cxxx-NCR-000454 | NCR | Kinked Geothermal pipe |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-04-30 | 2013-03-15 10:56 | -46 | 2013-03-04 | Civil - Geotechnical Engineering | 500 |  | Damaged | Use As-Is |  | Complete |  | Completed |  | Pipe was found to be kinked. Subsequently it was retested and found to hold a test
| 02SL - Stations (LUL) | Cxxx-NCR-000455 | NCR | Missing link in plice section of D-wall Cage |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-04-30 | 2013-04-02 14:22 | -28 | 2013-03-05 | Structural Engineering - Reinforcement | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | 2No links installed in spliced section between cages 4 and 3 spaced 300mm apart
| 02SL - Stations (LUL) | Cxxx-NCR-000457 | NCR | Unable to de-sand bentonite |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2014-01-31 | 2013-06-05 10:34 | -240 | 2013-03-12 | Civil - Geotechnical Engineering | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | During construction of strutting wall S09 on 27-28/02/13, works progressed past Dwall ITP (C501-__-C-STP-C101-50039 Rev5.0) hold point 4.10 despite not meeting the criteria stipulated. Hold point 4.10 requires the bentonite within the panel to have a sand content of 2% prior to proceeding to completion. After a considerable duration of desanding, the bentonite was repeatedly tested and over a period consistently contained a sand content of 4% (higher than the 2% maximum detailed within the ITP for Bentonite Testing, C501-__-C-STP-C101-50031 ). As the strutting walls do not contain any reinforcement and do not resist loads by end bearing, the decision was made to progress with the construction of the panel with a 4% bentonite sand content so that the excavation was not open for longer than necessary and to minimise the risk of delay to this panel, causing the next panel being constructed to be open for longer than necessary. Due to the particular size of fines suspended within the bentonite, the desanding operation durations are far exceeding what was originally envisaged.
| 02SL - Stations (LUL) | Cxxx-NCR-000458 | NCR | Reinforcement Panel P20 |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-04-30 | 2013-03-20 13:56 | -41 | 2013-03-11 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Bar mark 14 is not perpendicular to the cage, therfore is not able to be tack welded to bar 28.
| 02SL - Stations (LUL) | Cxxx-NCR-000459 | NCR | Reinforcement |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-04-30 | 2013-03-15 08:35 | -46 | 2013-03-12 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | 75mm timber bites were used between cages . Bites were positioned on bars allowing potential crushing of spacers. Boxouts were supporting cages instead of bites.
| 02SL - Stations (LUL) | Cxxx-NCR-000461 | NCR | Eldon Street Trial Hole Concrete Below Strength |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-05-31 | 2013-04-11 23:13 | -50 | 2013-03-13 | Utilities Engineering - Water | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | The cube strength results at 28 days are at 27 & 28.2 N/mm2, and have therefore failed to acheieve specified strength of 40N/mm2 at 28 days.
| 02SL - Stations (LUL) | Cxxx-NCR-000464 | NCR | Offered for inspection when non compliant |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-03-31 | 2013-03-28 16:51 | -3 | 2013-03-18 | Human Factors - Human Factors General | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | CRL carried out an inspection of Panel 02 after invitation and it was found that the resevation tube had a 200X200x6mm plate welded to the bottom of the tube. This was rectified within the shift. However __/__ engineers failed to find this fault.
| 02SL - Stations (LUL) | Cxxx-NCR-000469 | NCR | Damaged Geothermal loop |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-05-31 | 2013-04-10 17:07 | -51 | 2013-03-28 | Civil - Civil Engineering General | 500 |  | Damaged | Reject |  | Complete |  | Completed |  | The western most geothermal loop on P21 is not holding pressure following cage installationand was presumable damaged during installation. The loop was tested prior to installation and passed the pressure test
| 02SL - Stations (LUL) | Cxxx-NCR-000471 | NCR | Two Exd Box Lids Found to be Damaged During Inspection |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-05-31 | 2013-04-18 13:17 | -43 | 2013-03-28 | Civil - Sewage/Water services | 500 |  | Damaged | Rework |  | Complete |  | Completed |  | Damaged during installation from tightening up grub screw to high
| 02SL - Stations (LUL) | Cxxx-NCR-000479 | NCR | Failure To raise MCR |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-05-31 | 2013-05-07 22:38 | -24 | 2013-04-10 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | A MCR was raised for the King posts and bolts but the connection plate was missed, it was initially thought that the plates were included in the steel for the King posts. This is not the case. We have tried to gather the information for the plates before using in the works, this has not happened, therefore we are raising the NCR.
| 02SL - Stations (LUL) | Cxxx-NCR-000483 | NCR | Three Further Exd Box Lids Found to be Damaged During Inspection |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-05-31 | 2013-04-18 13:48 | -43 | 2013-04-11 | Civil - Sewage/Water services | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | Damaged during installation, from tightening up grub screw to high.
| 02SL - Stations (LUL) | Cxxx-NCR-000484 | NCR | Failing to address identified snag item at __ for P16 |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-05-31 | 2013-04-16 12:04 | -45 | 2013-04-12 | Civil - Civil Engineering General | 500 |  | System Defect | Use As-Is |  | Complete |  | Completed |  | 4 No's Temporary works raker bars where identified missing at express during initial check but not rectified before delivery. Due to obstruction in the ground, sequence was changed from Panel 22 to Panel 16, with resulted in the final check for completion of snags not fully carried out at Express.
| 02SL - Stations (LUL) | Cxxx-NCR-000485 | NCR | Temporary Works rebar Welding on Site |  | Contr | KIR | LIS - Liverpool Street Station (Central) |  | 2013-09-30 | 2013-09-04 23:00 | -26 | 2013-04-17 | Civil - Civil Engineering General | 500 |  | System Defect | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Lack of procedure | Completed |  | 4 No's TW reinforcement [raking bars for inclined lifting] bars were welded on site [to panel P16] without an approved procedure in place.
| 02SL - Stations (LUL) | Cxxx-NCR-000494 | NCR | Panel P05ii Design case F installed 125mm higher than designed level |  | Contr | BAM | LIS - Liverpool Street Station (Central) |  | 2014-12-31 | 2014-04-01 11:58 | -274 | 2013-04-24 | Civil - Geotechnical Engineering | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Verticallity problems were encountered when digging P05. The cage became wedged within the excavation and would not lower to its design position.
| 02SL - Stations (LUL) | Cxxx-NCR-000495 | NCR | waterstop connection details |  | Crossrail | PDP | LIS - Liverpool Street Station (Central) |  | 2013-09-30 | 2013-09-16 15:42 | -14 | 2013-04-25 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | the joint had been connected using cable tie
| 02SL - Stations (LUL) | Cxxx-NCR-000509 | NCR | Failed pressure test in geothermal loop P04 |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-07-31 | 2013-05-17 15:33 | -75 | 2013-05-08 | Civil - Geotechnical Engineering | 500 |  | Damaged | Reject |  | Complete |  | Completed |  | Loop failed to retain pressure
| 02SL - Stations (LUL) | Cxxx-NCR-000511 | NCR | Failure to submit prelimary integrity testing results within 24 hours |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-07-31 | 2013-06-14 10:54 | -47 | 2013-05-10 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Testing has been carried out several weeks ago and no test results have been received.
| 02SL - Stations (LUL) | Cxxx-NCR-000523 | NCR | P20 accoustic anomailies |  | Contr | BAM | LIS - Liverpool Street Station (Central) |  | 2014-10-31 | 2014-01-28 22:43 | -276 | 2013-05-30 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | The Cross hole sonic logging carried out on panel 20 has accoustic anomolies onthe toe of the panel. __ have flushed and retested with a small improvement. __ propose to reflush and retest.
| 02SL - Stations (LUL) | Cxxx-NCR-000525 | NCR | P31 not poured to guide wall level |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-06-30 | 2013-06-03 08:31 | -27 | 2013-05-31 | Civil - Civil Engineering General | 500 |  | Planning | Use As-Is |  | Complete |  | Completed |  | Unexpected high overconsumption of stone (40-75mm) required to backfill the gap behind the stopend. Once the material available on site was depleted completely, the pour was stopped in order to avoid any quality issues. The C35/45 concrete level on P31 was left at 105.55 mATD (5.3m below guide wall level / 2.9m above COL), not poured to GW level as intended.
| 02SL - Stations (LUL) | Cxxx-NCR-000529 | NCR | Annulas grout strength |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-07-03 | 2013-06-14 09:01 | -19 | 2013-06-05 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | OSD#1 - 56 day cubes were tested but the average strength gain reached only 2.7 N/mm^2.OSD#2 - Cubes were tested only at 28 days with an average strength gain of 2.1 N/mm^2.OSD#3 - Cubes were tested only at 28 days with an average strength gain of 3.0 N/mm^2. The tests carried out on the annulus grout prior to installation were carried out in laboratory conditions and therefore may not represent 'real world' gains. An ambiguity in testing dates and lack of ITP checksheet item meant that 56 day cubes were not taken on 2 of the 3 OSD piles
| 02SL - Stations (LUL) | Cxxx-NCR-000531 | NCR | P23N Cage 5 & 4 Rackers |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-06-21 | 2013-06-10 23:20 | -11 | 2013-06-06 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Drawing C501-__-C-DWG-C101-50223 indicates the arrangement of the these rackers. However on arrival to site they have been installed upside down. The first racker should be fixed to the near face then the far face and so on. However it is in reverse; far face then near face and so on. The arrangement of the rackers being installed in reverse has no affect on the cage during lifting. However it was not picked up until onsite and therefore the process of checking within Neath did not capture the change.
| 02SL - Stations (LUL) | Cxxx-NCR-000537 | NCR | P06 Blocked Sonic tube |  | Contr | BAM | LIS - Liverpool Street Station (Central) |  | 2013-09-30 | 2013-09-02 22:53 | -28 | 2013-06-11 | Civil - Geotechnical Engineering | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete |  | Completed |  | The northwest sonic on Panel 06 was found to be blocked at 28 metres from GW level during flushing with low pressure water. The tube was jetted on 07/06/2013 and the blockage was moved down 31.2m
| 02SL - Stations (LUL) | Cxxx-NCR-000538 | NCR | Drawings used for construction not submitted for review |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-08-31 | 2013-06-26 23:12 | -66 | 2013-06-18 | Civil - Civil Engineering General | 500 |  |  | Use As-Is |  | Complete |  | Completed |  | At the time of inspection/installation (13/06/13), the approved drawings for Panel P24 on eB were: C501-__-C-DWG-C101-50225 C501 __ - Design Case P - Panel P24 __ Rev P06 (CRL Rev 3.0) Date (drawn): 02/01/13 C501-__-C-DWG-C101-50226 C501 __ - Design Case Q - Panel P24 __ Rev P03 (CRL Rev 1.0) Date (drawn): 07/01/13 It was noted from the __ check-sheets (and our own observations) that these drawings were out of date, and that the revisions used for construction were: C501-__-C-DWG-C101-50225 C501 __ - Design Case P - Panel P24 __ Rev P07 Date (drawn): 05/02/13 C501-__-C-DWG-C101-50226 C501 __ - Design Case Q - Panel P24 __ Rev P04 Date (drawn): 30/05/13 We received ‘unofficial’ copies of the latest drawings in order to carry out our inspections, which were then uploaded onto eB on 14/06/13.
| 02SL - Stations (LUL) | Cxxx-NCR-000544 | NCR | Panel 12 Concrete segregation at top section |  | Contr | BAM | LIS - Liverpool Street Station (Central) |  | 2014-09-30 | 2014-04-09 08:38 | -174 | 2013-06-19 | Civil - Civil Engineering General | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Panel P12 was concreted to top of guide wall, however the concrete segregated and bleed water accumalated in the top 400mm of guide wall. Cause Combination of a lack of very fine aggregate, GGBS and retarder in the mix
| 02SL - Stations (LUL) | Cxxx-NCR-000545 | NCR | P12 missing links |  | Contr | BAM | LIS - Liverpool Street Station (Central) |  | 2013-09-30 | 2013-09-02 23:29 | -28 | 2013-06-24 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete |  | Completed |  | P12 loose fit links were not supplied with the P12 delivery on the Friday 14/06/13 night shift.
| 02SL - Stations (LUL) | Cxxx-NCR-000548 | NCR | P07 couplers installed 105mm low |  | Contr | BAM | LIS - Liverpool Street Station (Central) |  | 2014-12-31 | 2014-09-12 16:21 | -110 | 2013-06-27 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | As no levels for the couplers in BX131 were shown on the cage fabrication drawing (C501-__-C-DWG-C101-50209 Revision P06), it was assumed that the levels corresponded to the couplers in the parallel boxout (BX14) which were given in the side elevation. The change in level for the corner slab couplers was not detected in both __ and __'s checks of the fabrication drawing when comparing it to the design intent shown in elevation B of Drawing C501/__/C/DDL/C101/50406 Revision G.
| 02SL - Stations (LUL) | Cxxx-NCR-000549 | NCR | P07 Unable to provide verticality report |  | Contr | BAM | LIS - Liverpool Street Station (Central) |  | 2013-08-31 | 2013-07-24 08:43 | -38 | 2013-06-27 | Civil - Civil Engineering General | 500 |  | Equipment Breakdown | Rework | 4 (0.5-3k) | Complete |  | Completed |  | __ at this moment are unable to recover the file. (file corrupted)
| 02SL - Stations (LUL) | Cxxx-NCR-000550 | NCR | Panel 28 failure to take required number of test cubes |  | Contr | BAM | LIS - Liverpool Street Station (Central) |  | 2013-08-31 | 2013-07-16 23:33 | -46 | 2013-06-27 | Civil - Civil Engineering General | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | __ were advised on the size of the pour and have brought insufficient cubes. 6 sets taken.
| 02SL - Stations (LUL) | Cxxx-NCR-000551 | NCR | P04ii No Vertcality report |  | Contr | BAM | LIS - Liverpool Street Station (Central) |  | 2013-08-31 | 2013-07-24 08:47 | -38 | 2013-06-27 | Civil - Civil Engineering General | 500 |  | Equipment Breakdown | Rework | 4 (0.5-3k) | Complete |  | Completed |  | __ can not provide a verticality print out for Panel 04 ii The __ b-tronic computer system in the Mc64 created a corrupted file
| 02SL - Stations (LUL) | Cxxx-NCR-000555 | NCR | Loop on Panel 21 damaged |  | Contr | KIR | LIS - Liverpool Street Station (Central) |  | 2014-09-30 | 2014-09-25 15:13 | -5 | 2013-07-03 | Civil - Civil Engineering General | 5000 |  | Damaged | Use As-Is | 3 (3-6k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | When attempting to flush P21 geothermal loop a blockage was discovered
| 02SL - Stations (LUL) | Cxxx-NCR-000556 | NCR | P11 Cast level |  | Contr | KIR | LIS - Liverpool Street Station (Central) |  | 2014-12-31 | 2014-06-10 15:59 | -204 | 2013-07-03 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Panel 11 concrete has been poured to approximately 109.550. This is approx 550-750mm below the cut off leel of 109.900. Once exposed there may be a zone of contaminated concrete which will need to be removed.
| 02SL - Stations (LUL) | Cxxx-NCR-000566 | NCR | Flow test Panel 5 |  | Contr | KIR | LIS - Liverpool Street Station (Central) |  | 2014-09-30 | 2014-09-14 21:05 | -16 | 2013-07-15 11:48 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On panel 5, 1 no load (number 43, ticket number 213911) was recorded to have a flow rate of 560. this is outside of the ITP parameter, i.e 590-720 for the C35/45 mix
| 02SL - Stations (LUL) | Cxxx-NCR-000567 | NCR | Flow test -Panel 6 |  | Contr | KIR | LIS - Liverpool Street Station (Central) |  | 2014-09-30 | 2014-09-12 15:40 | -18 | 2013-07-15 12:11 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | On panel 6, 1 no load (number 21, ticket number 21150951) was recorded to have a flow rate of 580. This is outside of the ITP parameters, i.e 590-720 for the C35/45 mix
| 02SL - Stations (LUL) | Cxxx-NCR-000568 | NCR | Panel 14 - FLow test |  | Contr | KIR | LIS - Liverpool Street Station (Central) |  | 2014-09-30 | 2014-04-16 09:57 | -167 | 2013-07-15 13:48 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | On panel 14, 3 no loads (number5: ticket number 225610, number 6 ticket number 225611 and load 17: ticket number 2256624) were recorded to have flow rates of 580. this is outside of the ITP parameters, i.e 590-720 for the C35/45 mix
| 02SL - Stations (LUL) | Cxxx-NCR-000569 | NCR | Flow test Panel 33 |  | Contr | KIR | LIS - Liverpool Street Station (Central) |  | 2014-09-30 | 2014-04-17 10:34 | -166 | 2013-07-16 08:40 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | On panel 33, 2 no loads (number 3:ticket number 3171225686 and number 4 : ticket number 3171225681) were recorded to have flow test of 580. this is outside of the ITP parameters, i.e 590-720 for the C35/45 mix
| 02SL - Stations (LUL) | Cxxx-NCR-000571 | NCR | Flow test - Panel 19 |  | Contr | KIR | LIS - Liverpool Street Station (Central) |  | 2014-09-30 | 2014-09-12 15:38 | -18 | 2013-07-16 08:26 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | On panel 19, 1 no load (number 4:ticket number 21147906) was recorded to have a flow rate of 570. this is outside of the ITP parameters, i.e 590-720 for the c32/45 mix
| 02SL - Stations (LUL) | Cxxx-NCR-000572 | NCR | P16 Falure to generate verticality report |  | Contr | BAM | LIS - Liverpool Street Station (Central) |  | 2013-08-30 | 2013-07-31 11:09 | -30 | 2013-07-18 11:43 | Civil - Civil Engineering General | 500 |  | Equipment Breakdown | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | __ can not provide verticality print out for panel 16 The B-tronic computer system in the MC64 created a corrupted file
| 02SL - Stations (LUL) | Cxxx-NCR-000573 | NCR | Equipment failure Goswell Sewer |  | Contr | BAM | LIS - Liverpool Street Station (Central) |  | 2014-02-28 | 2014-02-16 21:22 | -12 | 2013-07-23 11:01 | Surveying - Instrumentation and Monitoring | 15000 |  | Equipment Breakdown | Repair | 2 (6-60k) | Complete | Material/Preservation Problems - Other | Completed |  | During baseline testing the approximately 90 metres of instruments stopped transmitting data.
| 02SL - Stations (LUL) | Cxxx-NCR-000574 | NCR | Panel B01 failure to submit check sheets |  | Contr | BAM | LIS - Liverpool Street Station (Central) |  | 2013-09-30 | 2013-07-25 16:15 | -67 | 2013-07-23 11:49 | Human Factors - Human Factors General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | __ did not submit off site panel check sheets to __ prior to CRL inspection. Off site or factory Check sheets will highlight completed or outstanding snag items and will be highlighted at inspections.
| 02SL - Stations (LUL) | Cxxx-NCR-000575 | NCR | D-wall Panel 12 - Reservation tube for temporary inclinometer (INT001) |  | Contr | KIR | LIS - Liverpool Street Station (Central) |  | 2014-03-31 | 2014-02-10 21:47 | -49 | 2013-07-24 16:36 | Civil - Civil Engineering General | 5000 |  | Design | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | reservation tube for temporary inclinometer in panel 12 not installed.
| 02SL - Stations (LUL) | Cxxx-NCR-000576 | NCR | Panel S4- concrete temperature not recorded |  | Contr | KIR | LIS - Liverpool Street Station (Central) |  | 2013-09-30 | 2013-09-05 16:16 | -25 | 2013-07-25 13:22 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete |  | Completed |  | Concrete temperature was not recorded on the checksheet for panel S4.
| 02SL - Stations (LUL) | Cxxx-NCR-000577 | NCR | P22 missing Link |  | Contr | BAM | LIS - Liverpool Street Station (Central) |  | 2013-09-30 | 2013-09-03 11:52 | -27 | 2013-07-31 11:57 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A positional coupler was missed from cage 4-5 this led to a link set being missed due to spacing, with a knock on effect on cage 3 moving a trapping band down, again a link set was omitted.
| 02SL - Stations (LUL) | Cxxx-NCR-000578 | NCR | Possible damage to P10 |  | Contr | BAM | LIS - Liverpool Street Station (Central) |  | 2014-12-31 | 2014-09-12 15:31 | -110 | 2013-07-31 12:13 | Civil - Concrete Pavement | 2000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Other | Completed |  | During excavation of S12 on the 500mm nibble against P10 the grab brought up ply and styrofoam indicating damage to the box outs on P10, this will have may have exposed the couplers to concrete or damaged them.
| 02SL - Stations (LUL) | Cxxx-NCR-000579 | NCR | King post in Barrette B06 is out of tolerance |  | Contr | BAM | LIS - Liverpool Street Station (Central) |  | 2014-10-30 | 2014-04-09 11:27 | -204 | 2013-08-16 14:21 | Civil - Civil Engineering General | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The position of the king post in Barrette B06 is outside the tolerance of +/- 25mm. The actual position was +96mm to the Eastings and -66mm to the Northings
| 02SL - Stations (LUL) | Cxxx-NCR-000580 | NCR | Damaged Couplers P10 |  | Contr | KIR | LIS - Liverpool Street Station (Central) |  | 2013-10-31 | 2013-10-01 13:22 | -30 | 2013-08-16 15:24 | Civil - Civil Engineering General | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During the break out of Panel 10 the method was to burst the concrete above trim level and then use a Hydraulic breaker to break out the burst section of concrete and hand breakers down to trim level. However during the break out the hydrualic breaker was used to remove concrete down to trim level and as a result slipped and damaged three couplers intened for starter bars in the capping beam. Attached is a drawing indicating the location of couplers affected.
| 02SL - Stations (LUL) | Cxxx-NCR-000581 | NCR | Trim level quality issues |  | Contr | BAM | LIS - Liverpool Street Station (Central) |  | 2013-11-30 | 2013-11-06 14:00 | -24 | 2013-08-30 11:44 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | On P04-P10 as of 15-8-13 it has been found that there have been occurences of bentonite caking round couplers and that concrete has peeled away from faces of couplers. Foam debonding sleeves have extended past the cut off level and there excessive cover to the stopends. Please see attached photos for better explanation
| 02SL - Stations (LUL) | Cxxx-NCR-000582 | NCR | P25 Sonic reports shows potential flaws |  | Contr | BAM | LIS - Liverpool Street Station (Central) |  | 2013-10-31 | 2013-09-04 13:14 | -57 | 2013-08-16 16:25 | Civil - Civil Engineering General | 3000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Sonic report For P25 shows numerous flaws
| 02SL - Stations (LUL) | Cxxx-NCR-000583 | NCR | P23 Blocked Sonic |  | Contr | BAM | LIS - Liverpool Street Station (Central) |  | 2013-10-31 | 2013-09-04 09:36 | -57 | 2013-08-21 13:14 | Civil - Geotechnical Engineering | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The middlewest sonic Panel 23 was to be blocked at 39.5 metres from GW level during sonic logging testing.
| 02SL - Stations (LUL) | Cxxx-NCR-000584 | NCR | P05 Numerous sonic flaws |  | Contr | BAM | LIS - Liverpool Street Station (Central) |  | 2013-11-30 | 2013-09-09 15:38 | -82 | 2013-08-21 13:39 | Civil - Geotechnical Engineering | 3000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The sonic report for P05 shows numerous flaws in the top 5m of the panel. Investigation of the panel shows evidence of bleed which may of accumlated around the sonic tubes causing anomalous readings
| 02SL - Stations (LUL) | Cxxx-NCR-000585 | NCR | Barrette B01 King post out of tolerance |  | Contr | BAM | LIS - Liverpool Street Station (Central) |  | 2014-12-31 | 2014-09-23 16:28 | -99 | 2013-08-29 11:41 | Civil - Civil Engineering General | 1500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The position of the King post in Barrette B01 is outside the tolerance of +/- 25mm. The actual position was 26mm to the easting and 44mm to the Northing.
| 02SL - Stations (LUL) | Cxxx-NCR-000586 | NCR | King post in Barrette B01 is out of tolerance |  | Contr | BAM | LIS - Liverpool Street Station (Central) |  | 2013-11-30 | 2013-09-17 10:09 | -74 | 2013-08-29 11:56 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The position of the king post in Barrette B01 to the northing is outside the tolerance of +/- 25mm. the actual psition was 46mm to the Northings.
| 02SL - Stations (LUL) | Cxxx-NCR-000587 | NCR | B08 Was delivered to site with insufficeint welds |  | Contr | BAM | LIS - Liverpool Street Station (Central) |  | 2013-11-30 | 2013-09-03 12:21 | -88 | 2013-08-30 10:48 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete |  | Completed |  | Barrette Cage B08 was delivered to site on 10/07/13 with 1 number 160mm on weld between the king post and BM 29 instead of 2 number 100mm welds as per Drawing C501-__-C-DWG-C101-50236 Rev P08.
| 02SL - Stations (LUL) | Cxxx-NCR-000588 | NCR | Missing Concrete tempratures for S08 |  | Contr | BAM | LIS - Liverpool Street Station (Central) |  | 2013-10-31 | 2013-09-09 17:47 | -52 | 2013-08-30 11:03 | Civil - Civil Engineering General | 500 |  | Equipment Breakdown | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Missing some of the concrete temperatures for the S08 concrete pour on 16 July 2013.The thermometer used to measure the concrete temperature stopped working mid-way through the pour. The second, back up thermometer was also not working.
| 02SL - Stations (LUL) | Cxxx-NCR-000589 | NCR | P27 Non UKAS staff carrying out sampling and testing |  | Contr | BAM | LIS - Liverpool Street Station (Central) |  | 2013-10-31 | 2013-09-09 17:55 | -52 | 2013-08-30 11:10 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Due to __ being unable to provide a technician for the duration of the P27 concrete pour (technician left at 22.00 on Tuesday 9th of July), the following NCR's occurred: One of the three sets of cubes taken for the C35/45 structural concrete were not taken at the required intervals according to specification i.e. one set every 50m3. The flow tests carried out after the __ technician had left were done by our Engineers who are not UKAS trained.
| 02SL - Stations (LUL) | Cxxx-NCR-000590 | NCR | Reservation tube grout not obtaining strength |  | Contr | BAM | LIS - Liverpool Street Station (Central) |  | 2013-10-01 | 2013-09-18 09:26 | -13 | 2013-09-02 14:08 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The strength of the sonic reservation tube grout is less than the C40/50 strength quoted in the MCR - see attached
| 02SL - Stations (LUL) | Cxxx-NCR-000591 | NCR | P07 concrete poured 1.0m below guide wall level |  | Contr | BAM | LIS - Liverpool Street Station (Central) |  | 2013-12-31 | 2013-12-03 13:29 | -28 | 2013-09-03 10:22 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The concrete cast level on Panel P07 was approx 1m below the guide wall.
| 02SL - Stations (LUL) | Cxxx-NCR-000592 | NCR | P04 blocked inclinometer |  | Contr | BAM | LIS - Liverpool Street Station (Central) |  | 2014-03-31 | 2014-01-27 18:20 | -63 | 2013-09-03 10:37 | Civil - Civil Engineering General | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | Panel 04 – inclinometer tube has a steel bolt obstruction at the base.
| 02SL - Stations (LUL) | Cxxx-NCR-000593 | NCR | P33 Concrete bleed |  | Contr | BAM | LIS - Liverpool Street Station (Central) |  | 2014-09-30 | 2014-07-08 14:59 | -84 | 2013-09-03 10:55 | Civil - Civil Engineering General | 1000 |  | Material | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | P33 Concrete grout has bled
| 02SL - Stations (LUL) | Cxxx-NCR-000594 | NCR | P11 incomplete temperature recording |  | Contr | BAM | LIS - Liverpool Street Station (Central) |  | 2013-09-17 | 2013-09-18 09:27 | 1 | 2013-09-03 11:59 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Only the first 5 loads of concrete in P11 had their temperatures recorded
| 02SL - Stations (LUL) | Cxxx-NCR-000595 | NCR | P09 discrepancy in concrete volume over size |  | Contr | BAM | LIS - Liverpool Street Station (Central) |  | 2013-10-11 | 2013-09-18 12:16 | -23 | 2013-09-03 14:39 | Civil - Civil Engineering General | 2000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The concrete supplied to Panel P09 indicates an undersupply of 5.5%
| 02SL - Stations (LUL) | Cxxx-NCR-000596 | NCR | P12 blocked Geothermal pipe |  | Contr | BAM | LIS - Liverpool Street Station (Central) |  | 2013-12-31 | 2013-12-02 08:18 | -29 | 2013-09-04 10:56 | Civil - Civil Engineering General | 3000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | After breaking down Panel 12 __ tried to flush the Southern most geothermal pipe. It was found to be blocked.
| 02SL - Stations (LUL) | Cxxx-NCR-000597 | NCR | P26 indicates an undersupply of 7.5%. |  | Contr | BAM | LIS - Liverpool Street Station (Central) |  | 2014-10-01 | 2013-09-24 11:51 | -372 | 2013-09-05 13:58 | Civil - Civil Engineering General | 3000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The concrete supplied to Panel P26 indicates an undersupply of 7.5%.
| 02SL - Stations (LUL) | Cxxx-NCR-000599 | NCR | Panel P16 indicates an undersupply of 8.1%. |  | Contr | BAM | LIS - Liverpool Street Station (Central) |  | 2014-10-30 | 2014-09-12 16:44 | -48 | 2013-09-11 14:02 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The concrete supplied to Panel P16 indicates an undersupply of 8.1%.
| 02SL - Stations (LUL) | Cxxx-NCR-000600 | NCR | Couplers on P13 insufficent cover |  | Contr | BAM | LIS - Liverpool Street Station (Central) |  | 2013-12-10 | 2013-11-06 14:03 | -34 | 2013-09-11 15:14 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | After breakdown of Panel 13 the couplers do not have the required 70mm cover.
| 02SL - Stations (LUL) | Cxxx-NCR-000601 | NCR | Panel 20 indicates a undersupply of concrete |  | Contr | BAM | LIS - Liverpool Street Station (Central) |  | 2014-10-30 | 2014-09-12 14:14 | -48 | 2013-09-13 10:38 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The concrete supplied to Panel P20 indicates an undersupply of 4.1%
| 02SL - Stations (LUL) | Cxxx-NCR-000602 | NCR | S06 unable to find cube results |  | Contr | BAM | LIS - Liverpool Street Station (Central) |  | 2014-09-30 | 2014-07-09 16:11 | -83 | 2013-09-13 10:46 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The 2 No sets of cubes taken from strutting panel S06 and corresponding paperwork can not be located.
| 02SL - Stations (LUL) | Cxxx-NCR-000603 | NCR | Welding on site without an approved Welding Procedure Qualification Record (WPQR) & Welding Procedure Spec (WPS) |  | Contr | BAM | LIS - Liverpool Street Station (Central) |  | 2014-04-30 | 2014-04-11 12:04 | -19 | 2013-09-18 16:53 | Structural Engineering - Welding | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Welding on site was carried out without an approved Welding Procedure Qualification Record (WPQR) & Welding Procedure Spec (WPS) in place.
| 02SL - Stations (LUL) | Cxxx-NCR-000604 | NCR | Panel 1 Bentonite ph level exceeded |  | Contr | BAM | LIS - Liverpool Street Station (Central) |  | 2013-11-30 | 2013-09-24 11:36 | -67 | 2013-09-19 15:51 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The pH of the Bentonite was measured at 12.5 and 12.3 which exceeds the limit of 12 in the ITP
| 02SL - Stations (LUL) | Cxxx-NCR-000605 | NCR | Panel 4 tremmie exceeded permissble seperation |  | Contr | BAM | LIS - Liverpool Street Station (Central) |  | 2013-11-30 | 2013-10-09 14:01 | -52 | 2013-09-19 16:18 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The difference in level measured at each of the 2 tremmie pipes had a difference in level of up to 400mm which is greater than the 250mm allowed within the specification.
| 02SL - Stations (LUL) | Cxxx-NCR-000606 | NCR | Position of cage P09 |  | Contr | KIR | LIS - Liverpool Street Station (Central) |  | 2013-12-31 | 2013-10-14 17:35 | -78 | 2013-09-20 12:53 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Cover to the the reinforcement cage for the d wall panel is to be 75mm NF and 100mm FF. The attcahed photo illustrates that the cage for P09 is twisted resulting in oppositie corners having reduced cover. The longitudual position of the cage is to be +/-75mm (Clause KP10.3212) and although the attached photo is taken from the stop end this also has a positional tolerance which could result in a cumalative effect. The affect on the capping beam reinforcement is that within grid lines 2 - 4 on wall B there is two starter bars less. However between grid lines 2-1 there will be an 2 additional starter bars.
| 02SL - Stations (LUL) | Cxxx-NCR-000607 | NCR | Position P20 + P21 |  | Contr | KIR | LIS - Liverpool Street Station (Central) |  | 2013-12-31 | 2013-10-14 17:37 | -78 | 2013-09-20 13:29 | Civil - Civil Engineering General | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The design cover for the d wall reinforcement is FF 100mm and the NF 75mm. On breaking down to trim level the position of cages P20 and P21 show that they are twisted in plan and have excess cover the front and reduce cover to the back. The position of P21 restricts the current starter bars detailed for the end of the high level capping beam. Currently two starter bars are to sit within a 350mm end wall on wall C after the sloping section, but due to the position of couplers it results in one bar sitting central of the wall and the adjacent couplers positioned half in and half out.
| 02SL - Stations (LUL) | Cxxx-NCR-000608 | NCR | P07 underbreak |  | Contr | BAM | LIS - Liverpool Street Station (Central) |  | 2014-09-01 | 2013-09-24 11:12 | -342 | 2013-09-20 14:39 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The concrete graph submitted in the P07 record shows 5% underbreak and cast to GW level. However the concrete graph saved on the server shows 0% underbreak and cast 1.0m below GW level. The cast level was low as per the NCR raisd (591). It is unclear which record is correct or why they differ.
| 02SL - Stations (LUL) | Cxxx-NCR-000609 | NCR | Panel 21 tremmie differential |  | Contr | BAM | LIS - Liverpool Street Station (Central) |  | 2013-11-30 | 2013-10-09 12:41 | -52 | 2013-09-23 10:06 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The difference measured vertically between the 2 tremmies was up to 500mm which is greater than allowed in the specification.
| 02SL - Stations (LUL) | Cxxx-NCR-000610 | NCR | Panel 27 reinforcement check sheet not completed |  | Contr | BAM | LIS - Liverpool Street Station (Central) |  | 2013-11-30 | 2013-10-01 14:26 | -60 | 2013-09-23 11:46 | Civil - Civil Engineering General | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not trained for the work being performed | Completed |  | Box outs BX 50, 51, 109 167, and 168 not completed correctly
| 02SL - Stations (LUL) | Cxxx-NCR-000611 | NCR | Panel 18 2.3% underbreak |  | Contr | BAM | LIS - Liverpool Street Station (Central) |  | 2014-10-31 | 2013-09-24 11:02 | -402 | 2013-09-23 16:26 | Civil - Civil Engineering General | 500 |  | Equipment Breakdown | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The concrete graph submitted in the Panel records showed a underbreak of 2.3%
| 02SL - Stations (LUL) | Cxxx-NCR-000612 | NCR | P03 3.7% underbreak |  | Contr | BAM | LIS - Liverpool Street Station (Central) |  | 2014-09-01 | 2013-10-01 13:32 | -335 | 2013-09-26 09:22 | Civil - Civil Engineering General | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The Concrete graph submitted for Panel 3 records showed a 3.7% underbreak
| 02SL - Stations (LUL) | Cxxx-NCR-000613 | NCR | P11 3% underbreak |  | Contr | BAM | LIS - Liverpool Street Station (Central) |  | 2014-09-01 | 2013-10-01 11:26 | -335 | 2013-09-26 11:53 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Panel 11 concrete graph indicated a 3% underbreak.
| 02SL - Stations (LUL) | Cxxx-NCR-000614 | NCR | P32, P33, P01, P02, P03 Reduce cover to the near face |  | Contr | KIR | LIS - Liverpool Street Station (Central) |  | 2014-03-31 | 2013-10-18 08:28 | -164 | 2013-09-30 15:02 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The reinforcement cages installed for the d wall are on the skew which reduces cover to the near face and far faces in opposite corners. The cover of the FF should be 100mm and NF 75mm. In some areas there is 40mm NF and 75mm FF.
| 02SL - Stations (LUL) | Cxxx-NCR-000615 | NCR | Failure to submit the Jetty's fabrication ITP |  | Crossrail | PDP | LIS - Liverpool Street Station (Central) |  | 2014-03-31 | 2014-02-11 13:16 | -48 | 2013-10-01 09:18 | Civil - Civil Engineering General | 1000 |  | Planning | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | C501 failed to submit an ITP for our acceptance and not to start work until that acceptance has been gained is a strict requirement of the works information, the structural steel had been fabricated jo
| 02SL - Stations (LUL) | Cxxx-NCR-000616 | NCR | The Jetty steelwork was deemed to be non-compliant |  | Crossrail | PDP | LIS - Liverpool Street Station (Central) |  | 2014-04-30 | 2014-02-12 15:42 | -77 | 2013-10-01 10:48 | Civil - Civil Engineering General | 25000 |  | System Defect | Rework | 2 (6-60k) | Complete | Management Problem - Inadequate administrative control | Completed |  | The jetty steel work was deemed to be non-compliant with the lack of the fabrication DRW, fabrication check sheets and welding test results
| 02SL - Stations (LUL) | Cxxx-NCR-000617 | NCR | Soft material found in West OSD pile, below trim level. |  | Contr | KIR | LIS - Liverpool Street Station (Central) |  | 2013-12-31 | 2013-12-16 15:53 | -15 | 2013-10-02 12:05 | Civil - Civil Engineering General | 500 |  | Material | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Soft material found below cut-off / trim level in the Western OSD pile. The central core of the pile approximately 600mm dia. contains soft grout/Bentonite mixture with no significant strength. This is currently found at 200mm below the trim level. The outer perimeter contains full strength concrete which encases the steel reinforcement.
| 02SL - Stations (LUL) | Cxxx-NCR-000618 | NCR | Barrette B07 ‐ the pH 12.6 is not less than 12 as required by the ITP. |  | Contr | BAM | LIS - Liverpool Street Station (Central) |  | 2014-09-01 | 2013-10-16 16:46 | -320 | 2013-10-07 10:59 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Barrette B07-the pH 12.6 is not less than 12 as required by the ITP.
| 02SL - Stations (LUL) | Cxxx-NCR-000619 | NCR | B07 ‐ Tremmie level difference |  | Contr | BAM | LIS - Liverpool Street Station (Central) |  | 2014-09-01 | 2013-10-24 08:57 | -312 | 2013-10-07 11:08 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | B07 ‐ The difference in level measured at each of the 2 tremmie pipes had a differenc in level of up to 600mm which is greater than the 250mm allowed within the specification.
| 02SL - Stations (LUL) | Cxxx-NCR-000620 | NCR | P31 box out check sheet missing |  | Contr | BAM | LIS - Liverpool Street Station (Central) |  | 2014-09-01 | 2013-10-09 13:32 | -327 | 2013-10-07 11:27 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | P31 ‐ there is no record of checks being done on box outs 159 and 190. No check sheets
| 02SL - Stations (LUL) | Cxxx-NCR-000621 | NCR | B04 Tremmie level |  | Contr | BAM | LIS - Liverpool Street Station (Central) |  | 2014-09-01 | 2013-10-24 09:27 | -312 | 2013-10-07 11:37 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | B04 ‐ The difference in level measured at each of the 2 tremmie pipes had a differenc in level of up to 500mm which is greater than the 250mm allowed within the specification.
| 02SL - Stations (LUL) | Cxxx-NCR-000622 | NCR | Panel P32 ‐ density of the Bentonite |  | Contr | BAM | LIS - Liverpool Street Station (Central) |  | 2014-09-01 | 2013-10-24 14:17 | -312 | 2013-10-07 11:44 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Panel P32 ‐ the density of the Bentonite > 1.15 as required by the ITP. The sand content may be above the 2% allowed by the spec
| 02SL - Stations (LUL) | Cxxx-NCR-000623 | NCR | Missing shear link SE Corner Wall B |  | Contr | KIR | LIS - Liverpool Street Station (Central) |  | 2013-10-22 | 2013-10-18 08:37 | -4 | 2013-10-08 15:19 | Civil - Civil Engineering General | 20 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | It was noticed once the stop end was in place for a concrete pour that there was a missing shear at the foot of the pour. It was not possible to add the shear due to the shutter being installed.
| 02SL - Stations (LUL) | Cxxx-NCR-000624 | NCR | Geo Loop P21 |  | Contr | KIR | LIS - Liverpool Street Station (Central) |  | 2014-02-28 | 2013-12-04 13:47 | -86 | 2013-10-09 19:16 | Civil - Civil Engineering General | 2500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | A piece of rebar was found to be wedge within one of the geo pipes of P21. After trying to remove the bar is was discovered that the bar was bent and had a spike on it which extends out of the pipe. It is unknown how the pipe managed to get into the pipe bent the way it was, but the split extended down past the couplers. Due to the reduce cover on the back of P21 breaking out further concrete and cutting the pipe lower and extending it back up good not be done as there was no room at all.
| 02SL - Stations (LUL) | Cxxx-NCR-000625 | NCR | Bars sceduled incorrectly |  | Contr | KIR | LIS - Liverpool Street Station (Central) |  | 2013-12-31 | 2013-10-30 08:20 | -62 | 2013-10-09 20:14 | Civil - Base Course | 3000 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Although the scedules and drawings are submitted and approved by Motts there was a bar detailed incorrectly and miss. BM 11 was detailed as a shape code 00 but should have been a 15 due to the splay on the capping beam. The bars where bent to the splay onsite and installed at the correct centres.
| 02SL - Stations (LUL) | Cxxx-NCR-000626 | NCR | Height of couplers Wall C SE Corner |  | Contr | KIR | LIS - Liverpool Street Station (Central) |  | 2013-12-31 | 2013-10-30 10:47 | -62 | 2013-10-09 20:44 | Civil - Civil Engineering General | 3000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Due to the construction joint concrete not being sufficiently level across the back in the area of the future 450mm wall where couplers are required. The coupler were post installed and as a result rested on the construction joint, which in turn determined their height. Therefore the height of the couplers vary from +0mm to +20mm.
| 02SL - Stations (LUL) | Cxxx-NCR-000627 | NCR | Un planned construction Joint SE Corner Wall C |  | Contr | KIR | LIS - Liverpool Street Station (Central) |  | 2013-10-23 | 2013-10-14 17:33 | -9 | 2013-10-09 21:07 | Civil - Base Course | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During concreting the second level pour from 112.750 up to 113.700 on the SE corner on Wall C, 2 concrete wagoon turnered up out of spec for a slump of S3. Both wagons were rejected and as a result the C50 mix started to set. The pour was stopped and a construction joint put in. The CJ was prepared and 2 hydruphillic strips installed as requried.
| 02SL - Stations (LUL) | Cxxx-NCR-000628 | NCR | IN 006 Inclinometer tube twisted |  | Contr | BAM | LIS - Liverpool Street Station (Central) |  | 2014-06-30 | 2014-04-15 21:24 | -76 | 2013-10-10 13:21 | Surveying - Instrumentation and Monitoring | 1500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Follow installation od IN06 inclinometer tubing it was found that the key lines had a inconsistancy. Borehole camer revealed that the top tube had rotated off line.
| 02SL - Stations (LUL) | Cxxx-NCR-000629 | NCR | SP02 Blockage at filter tip |  | Contr | BAM | LIS - Liverpool Street Station (Central) |  | 2013-12-31 | 2013-11-07 10:42 | -54 | 2013-10-10 13:38 | Surveying - Instrumentation and Monitoring | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Unable to lower dip meter probe final 3 meters of the 60 m installation
| 02SL - Stations (LUL) | Cxxx-NCR-000630 | NCR | Panel 30 2.8% underbreak |  | Contr | BAM | LIS - Liverpool Street Station (Central) |  | 2014-09-01 | 2013-11-19 12:10 | -286 | 2013-10-22 13:28 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Panel 30 concrete records indicate a possible underbreak of 2.8%
| 02SL - Stations (LUL) | Cxxx-NCR-000632 | NCR | Diaphragm Wall Panel-27: Insufficient concrete cover. |  | Contr | KIR | LIS - Liverpool Street Station (Central) |  | 2013-12-31 | 2013-11-11 13:41 | -50 | 2013-10-23 14:53 | Civil - Civil Engineering General | 3000 |  | System Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Between 101.0mATD and 103.1mATD on the outside face of Diaphragm wall Panel 27, insufficient concrete cover to the reinforcement has been observed. An area of D-wall 2.1m high, 0.6m wide (top), 1.5m wide (bottom) has been found to have insufficient concrete cover. The cover to the reinforcement in this area partially consisted of a soft Bentonite/clay material. This material was found to be 80-90mm thick in places, thus when the soft material was removed, the face of the main vertical 50mm dia. reinforcement was exposed.
| 02SL - Stations (LUL) | Cxxx-NCR-000633 | NCR | OSD Column Starter Bars |  | Contr | KIR | LIS - Liverpool Street Station (Central) |  | 2013-12-31 | 2013-11-24 21:38 | -37 | 2013-11-04 15:37 | Structural Engineering - Reinforcement | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Starter bars for the OSD column not spaced out at 150mm c/c as required on the drawing. This was due to the following factors:- 1) Heavy congestion of the 4No. layers of B40 reinforcement in the top mat, 2) The difference in orientation between the square column and the direction of the main reinforcement, 3) The number of lapped reinforcing bars in the top mat.
| 02SL - Stations (LUL) | Cxxx-NCR-000634 | NCR | Inclinometer beseline readings prior to excavation |  | Contr | BAM | LIS - Liverpool Street Station (Central) |  | 2013-12-31 | 2013-11-27 15:48 | -34 | 2013-11-08 17:07 | Geotechnical Engineering - Geotechnical Monitoring | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | Contractor to obtain 1 week inclinometer baseline readings prior to excavation. __ commenced excavation without obtaining inclinometer baseline readings along 8/87 Moorgate (south side). Excavation level is approx 107.500m ATD and excavated material was made ground thus no movement was expected to happen. Excavation is on hold till baseline reading are obtained.
| 02SL - Stations (LUL) | Cxxx-NCR-000635 | NCR | Reduce to capping beam NE |  | Contr | KIR | LIS - Liverpool Street Station (Central) |  | 2014-09-30 | 2014-07-09 16:10 | -83 | 2013-11-15 16:01 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | After striking the back shutter on the north east ring beam it was discovered that the __ was not pushed fully into the corner. This has resulted on the cover on the corner to be significantly reduced from the proposed 90mm to 15mm worst case. There are also areas on the north which have rippled during the concreting with after a cover survey would also reduce cover to 15mm.
| 02SL - Stations (LUL) | Cxxx-NCR-000636 | NCR | toolbox talk on installtion of waterproofing |  | Contr | KIR | LIS - Liverpool Street Station (Central) |  | 2014-12-31 | 2013-12-03 13:30 | -393 | 2013-11-20 10:21 | Civil - Civil Engineering General | 50 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | Due to the hydrophilic strip being installed incorrectly/ damaged after installation a toolbox talk was required to brief the team on the correct installation. Although it was briefed to the dayshift it wasn't delivered to the nightshift that then went and installed it incorrectly. It was put right by the dayshift but could have been avoided had the toolbox talk been undertaken. It must be noted that the incorrect installation has always been rectified prior to concreting.
| 02SL - Stations (LUL) | Cxxx-NCR-000637 | NCR | Extensometer EX04 Fault |  | Contr | BFK | LIS - Liverpool Street Station (Central) |  | 2014-04-30 | 2014-02-12 14:52 | -77 | 2013-11-21 16:22 | Geotechnical Engineering - Geotechnical Monitoring | 2000 |  | Equipment Breakdown | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | The in shaft extensometer labelled as EX004 is no longer recording information. On inspection the housing pipe has sheared at approximately 5.6m below the current platform level (106.5m) which means we cannot insert the probe beyond this point. We have taken regular readings between 18 September and 14 November 13, which are attached.
| 02SL - Stations (LUL) | Cxxx-NCR-000639 | NCR | Failure to submit an approved Materails compliance record before works commencement |  | Contr | BAM | LIS - Liverpool Street Station (Central) |  | 2014-02-28 | 2014-02-13 23:11 | -15 | 2013-11-28 10:19 | Civil - Civil Engineering General | 1500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | __ failed to submit an approved MCR before concreting the OSD pile cap.
| 02SL - Stations (LUL) | Cxxx-NCR-000640 | NCR | OSD PILE CAP - CONCRETE C35-45 10mm CEM 3 non compliances |  | Contr | BAM | LIS - Liverpool Street Station (Central) |  | 2014-05-31 | 2014-03-10 09:40 | -82 | 2013-11-28 11:47 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | Concrete has been placed to support programme requirements that has subsequently been reviewed and classed as non compliant. All as detailed on informal copy of MCR review sheet C501-__-O4-XCS-C101-50177 1. total cement content exceeds 450kg 2. contained admixtures from two different manufacturers.
| 02SL - Stations (LUL) | Cxxx-NCR-000641 | NCR | Hold point on Rebar not observed for NE capping beam |  | Contr | KIR | LIS - Liverpool Street Station (Central) |  | 2014-11-30 | 2014-10-15 09:25 | -46 | 2013-12-01 18:55 | Civil - Base Course | 500 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Shutters were erected prior to C501 fully inspecting the reinforcement. When the steel was inspected it was found that bars were installed incorrectly and some in the wrong place. This NCR is raised for the process of the ITP not being followed correctly.
| 02SL - Stations (LUL) | Cxxx-NCR-000642 | NCR | Dimension Error Drawing 01302 |  | Contr | KIR | LIS - Liverpool Street Station (Central) |  | 2014-03-30 | 2014-02-13 15:52 | -45 | 2013-12-01 19:27 | Civil - Civil Engineering General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Drawing 01302 had dimensions for the corner of the ring beam which was shown as 2100 from Grid Line D and 2306 up from Grid Line 1. However once the reinforcement was fixed on site it was noticed that there was an issue with he setting out as the back corner of the DRS was 153mm incorrect. It was then raised via email to Motts and a response sketch confirmed an additional dimension of 2218 from Grid line D which altered the setting out around the DRS.
| 02SL - Stations (LUL) | Cxxx-NCR-000643 | NCR | GSHP Damaged Loops P04, P12 & P21 |  | Contr | KIR | LIS - Liverpool Street Station (Central) |  | 2014-03-30 | 2013-12-18 07:36 | -102 | 2013-12-01 19:58 | Civil - Civil Engineering General | 5000 |  | Damaged | Use As-Is | 3 (3-6k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | GSHP have been damaged/blocked during the pile break down of panels P04, P12 & P21. The attached drawings have been updated and submitted of the revised layout.
| 02SL - Stations (LUL) | Cxxx-NCR-000644 | NCR | Water leaking through joint between capping beam and DWall Panel 8 |  | Crossrail | PDP | LIS - Liverpool Street Station (Central) |  | 2014-07-31 | 2014-05-08 10:20 | -84 | 2013-12-04 10:49 | Civil - Civil Engineering General | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On Tuesday 19th November 2014 it was observed that water was leaking through the construction joint between the capping beam and DWall Panel 8 and on subsequent days leaks were observed at other panel locations. The water appeared to be coming up from below the guide wall behind the capping beam as the top of the guide wall was not wet .In the following weeks grout from Cxxxs operations has also been observed.
| 02SL - Stations (LUL) | Cxxx-NCR-000645 | NCR | Inclinometer in D-wall |  | Contr | BAM | LIS - Liverpool Street Station (Central) |  | 2014-05-30 | 2014-05-21 21:40 | -9 | 2013-12-10 18:16 | Surveying - Instrumentation and Monitoring | 2500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | __ will not be able to provide readings for instrument INT004 (panel 31) before start of excavation to lower level due to damage/bend to the access tube. During ring beam/capping beam construction in North West corner of the shaft inclinometer reservation tube and access inclinometer tube were found bend at level approx 106.5m ATD (blinding level). The damage does not allow take any manual readings until the tube is repaired. In the future IPI will be installed in this location. This particular inclinometer is in the area of the D-wall which will be broken out for escalator opening and for column to be casted which will allow to carried out necessary repairs at the lower level (below first ring beam). __ asks for permission to dig to lower level without obtaining readings for INT004 after capping has been beam constructed. Reading had been taken before capping beam construction started and readings will be provided for other inclinometers in this area such as INT003, IN006 (west) and INX001 (manual readings if required) and IN001 (IPI).
| 02SL - Stations (LUL) | Cxxx-NCR-000646 | NCR | Inclinometer INT002 |  | Contr | BAM | LIS - Liverpool Street Station (Central) |  | 2014-04-30 | 2014-02-28 11:06 | -61 | 2013-12-10 18:36 | Surveying - Defects and Condition | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | Access tube for INT002 needs flushing, obstruction was found 7.5m down the tube when run dummy probe. Access tube is extended above finish capping beam level. __ proposes to pour concrete to capping beam as planned and carried out flushing the tube from capping beam level.
| 02SL - Stations (LUL) | Cxxx-NCR-000647 | NCR | Diaphragm Wall Barrette B06 - End Pour Times and Concrete Level Differences |  | Contr | KIR | LIS - Liverpool Street Station (Central) |  | 2014-12-31 | 2014-04-06 23:52 | -269 | 2013-12-16 12:38 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | The pairs of concrete loads with End Pour times of 02:19, 02:50, 03:57, 04:35, 05:03 and 05:35 all have concrete level differences between the two tremies of greater than 0.25m. This is against the Method Statements details.
| 02SL - Stations (LUL) | Cxxx-NCR-000648 | NCR | Instrument in the shaft readings |  | Contr | BAM | LIS - Liverpool Street Station (Central) |  | 2014-04-30 | 2014-02-28 11:20 | -61 | 2014-01-27 16:52 | Geotechnical Engineering - Geotechnical Monitoring | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | C501 __ did not provide weekly readings on magnetic extensometer EX3 in the shaft due blockage at 10m inside tube. There were no readings for 3 weeks (wc 23rd December 2013 to wc 06th January 2014). Instrument was flushed out twice over that period and obstruction was completely removed. Readings have been taken weekly as per spec since 16th January 2014.
| 02SL - Stations (LUL) | Cxxx-NCR-000649 | NCR | Panel 21 Panel 22 inclusions |  | Contr | BAM | LIS - Liverpool Street Station (Central) |  | 2014-05-31 | 2014-04-07 11:58 | -54 | 2014-02-06 12:15 | Civil - Civil Engineering General | 1000 |  | Material | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | An inclusion was found on P21 and P22 above 102.395. After investigation the depth of the inclusion was confirmed to be only 100mm until solid concrete was found.
| 02SL - Stations (LUL) | Cxxx-NCR-000650 | NCR | Scaffold Storage area |  | Contr | BAM | LIS - Liverpool Street Station (Central) |  | 2014-05-31 | 2014-04-13 23:10 | -48 | 2014-02-21 15:32 | Civil - Civil Engineering General | 3000 |  | Planning | Rework | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | A temporary scaffold storage area is being erected in Moorfields south of the shaft area. No Temporary works design or check certificate has been issued to CRL. The Current temporary works register does not contain the works. No Method statement issued. This activity did not appear on the 4 weekly lookahead.
| 02SL - Stations (LUL) | Cxxx-NCR-000651 | NCR | Escalator opening props - 5 Star grout below strength |  | Contr | BAM | LIS - Liverpool Street Station (Central) |  | 2014-05-31 | 2014-04-13 22:57 | -48 | 2014-02-21 16:43 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | The required 5 star grout for filling voids between the Escalator opening props and the ring beam did not reach the required strength of 60N/mm2 at 28 days and that non compliant test moulds were used.,
| 02SL - Stations (LUL) | Cxxx-NCR-000652 | NCR | Surface finish DRS Walls 102.395 - 106.5m |  | Contr | KIR | LIS - Liverpool Street Station (Central) |  | 2014-07-31 | 2014-07-30 10:22 | -1 | 2014-02-24 12:06 | Civil - Civil Engineering General | 10000 |  | Workmanship | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Inadequate/insufficient tooling. | Completed |  | After striking the shutters to the DRS walls it was found that the shutters had moved during the concrete pour. This has resulted in the surface finish being out of specification as stated on drawing Cxxx-MMD-C-DDJ-C101-00011 as +/- 25mm.
| 02SL - Stations (LUL) | Cxxx-NCR-000653 | NCR | Instrumentaton & Monitoring |  | Contr | BAM | LIS - Liverpool Street Station (Central) |  | 2014-04-11 | 2014-03-17 15:46 | -25 | 2014-02-25 14:13 | Surveying - Instrumentation and Monitoring | 5000 |  | Incorrect Installation | Use As-Is | 3 (3-6k) | Complete | Personnel Error - Not Defined | Completed |  | During procedure of replacing IPIs in access tube IN004 instruments dropped inside the tube. C501 recovered most of them but unfortunately lower IPIs wedged at the bottom of the tube. This means down to 59m ATD tube is accessible to install new sensors, but not from 53m ATD as intended to be. __ proposes to use rest of the lenght of the tube and install instruments from 59m ATD to 113.7m ATD
| 02SL - Stations (LUL) | Cxxx-NCR-000654 | NCR | Inclusions in D Wall Panels P05, P21 & P22 |  | Contr | KIR | LIS - Liverpool Street Station (Central) |  | 2014-05-31 | 2014-03-17 15:47 | -75 | 2014-02-28 17:38 | Civil - Civil Engineering General | 500 |  | System Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | There are three inclusions which have been identified within panels P05, P21 & P22. These been addressed as described within the D wall repair Procedure C501-__-C-GMS-C101-50188.
| 02SL - Stations (LUL) | Cxxx-NCR-000655 | NCR | Instrumentation and monitoring |  | Contr | BAM | LIS - Liverpool Street Station (Central) |  | 2014-06-30 | 2014-05-29 13:24 | -32 | 2014-03-13 14:05 | Surveying - Instrumentation and Monitoring | 15000 |  | Damaged | Use As-Is | 2 (6-60k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | One of the Cxxx asset protection instruments installed and monitored by C501 is not working. Instrument which is automated Vibrating Wire Piezometer PV02 is located in the verge along Moorgate in midway of the C501 box (Cxxx drawing Cxxx-OVE-C4-DDA-CR001_Z21585). Instrument consist of three piezometers at different strata levels: Deep piezo is located at 68m ATD, middle piezo at 74.4m ATD, top piezo at 90m ATD Borehole was drilled back in October/November 2011 and instrument was installed on 2 November 2011. Instrument was commissioned in February 2013, and automated readings started streaming to data logger in August 2013. On 3 November 2013 instrument stopped working, area where instrument is located was concreted over to allow for jetty crane access, ducts were protected during concreting but it seems that problem is somewhere below the concrete. Instrument is not accessible anymore and data has not been recorded since November 2013. There are other instruments in this area such as Cxxx inclinometers and extensometers, C501 inclinometers, which means that area is very congested in terms of amount of instruments and utilities within the road and verge. This leads to conclusion that drilling new instrument would be very difficult. Also looking at the progress of work has been achieved so far without data for that particular instrument C501 propose to leave instrument as it is.
| 02SL - Stations (LUL) | Cxxx-NCR-000656 | NCR | Over break of concrete DRS |  | Contr | KIR | LIS - Liverpool Street Station (Central) |  | 2014-11-30 | 2014-09-18 16:36 | -73 | 2014-03-19 20:45 | Civil - Civil Engineering General | 10000 |  | Supervision/Management | Repair | 2 (6-60k) | Complete | Management Problem - Inadequate supervision | Completed |  | In undertaking the remedial works for NCR 652 which required us to break back the out of tolernace concretre finish we have over broken in patches. This has therefore left areas with reduce covers as little as 20mm.
| 02SL - Stations (LUL) | Cxxx-NCR-000657 | NCR | Damaged Seepage pipe |  | Contr | BAM | LIS - Liverpool Street Station (Central) |  | 2014-10-30 | 2014-09-18 16:38 | -42 | 2014-03-28 16:29 | Civil - Drainage | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | A ductile iron Seepage pipe at AP9 lining wall gridline 3 was damaged when the shuttering was struck. Specifically a piece of pipe was broken off limiting the amount of pipe to join onto the next pipe.
| 02SL - Stations (LUL) | Cxxx-NCR-000658 | NCR | Geothermal Loop P22 |  | Contr | BAM | LIS - Liverpool Street Station (Central) |  | 2014-07-31 | 2014-06-18 10:29 | -43 | 2014-03-28 16:45 | Civil - Civil Engineering General | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | A Geothermal loop has been damaged during construction works
| 02SL - Stations (LUL) | Cxxx-NCR-000659 | NCR | Platform +3 to +4 Raking Column A First Pour - Concrete Cubes |  | Contr | KIR | LIS - Liverpool Street Station (Central) |  | 2014-06-30 | 2014-04-29 16:09 | -62 | 2014-04-02 16:00 | Civil - Civil Engineering General | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | 2 No. Concrete cubes was taken for the pour, and 1 of the cubes got damaged. A minimum of 2 No. concrete cubes are required as per the specification.
| 02SL - Stations (LUL) | Cxxx-NCR-000660 | NCR | Cover Issue During Construction of Raking Column C Between Platform +4 to +3 |  | Contr | KIR | LIS - Liverpool Street Station (Central) |  | 2014-07-31 | 2014-05-21 21:43 | -71 | 2014-04-03 16:41 | Civil - Civil Engineering General | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Due to congestion of reinforcement in the Platform +4 ring beam, the raking column C couplers were installed out of position (but in tolerance) which has caused the below coupled reinforcement in the Raking Column C to have minimal concrete cover on the face of the column.
| 02SL - Stations (LUL) | Cxxx-NCR-000661 | NCR | Inclusion in Panel P01 at Platform +3 Level |  | Contr | KIR | LIS - Liverpool Street Station (Central) |  | 2014-08-31 | 2014-07-09 16:03 | -53 | 2014-04-08 09:34 | Civil - Civil Engineering General | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the break out for couplers in panel P01 at Platform +3 level, an inclusion was found that is approximately 700-1000mm deep.
| 02SL - Stations (LUL) | Cxxx-NCR-000662 | NCR | Platform +2 Middle NE Quadrant |  | Contr | KIR | LIS - Liverpool Street Station (Central) |  | 2014-08-31 | 2014-07-09 16:08 | -53 | 2014-06-02 10:08 | Civil - Civil Engineering General | 500 |  | Incomplete Works | Repair | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | Section of PL +2 middle NE quadrant was approx. 2m3 short from being completed as had 1 No. rejected concrete load as outside of specification and batching plant had closed, so unable to get a further load. An area of 6m2 at the back of the ring beam was left approx. 100mm low showing the dummy cage reinforcement.
| 02SL - Stations (LUL) | Cxxx-NCR-000668 | NCR | Platform +4 to Platform +3 Diaphragm Wall Inclusions |  | Contr | KIR | LIS - Liverpool Street Station (Central) |  | 2014-09-30 | 2014-07-09 16:05 | -83 | 2014-06-02 14:24 | Civil - Civil Engineering General | 3000 |  | Material | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Inclusions were found in the diaphragm wall panels between PL+4 to PL+3. See attached Report for further details and photos.
| 02SL - Stations (LUL) | Cxxx-NCR-000669 | NCR | Failure to raise MCR |  | Contr | BAM | LIS - Liverpool Street Station (Central) |  | 2014-09-30 | 2014-06-18 23:01 | -104 | 2014-06-06 14:26 | Materials - Approval | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | PMI 282 instructed foam concrete to be placed against CW62. FCD 572 specified 20mm compressable filler __ or Similar. No MCR was submitted for the Compressable filler
| 02SL - Stations (LUL) | Cxxx-NCR-000670 | NCR | Cube tank Switched off |  | Contr | BAM | LIS - Liverpool Street Station (Central) |  | 2014-09-30 | 2014-07-07 11:59 | -85 | 2014-06-13 09:57 | Civil - Civil Engineering General | 500 |  | System Defect | Repair | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | On a walk round it was noted that the cube storage tank was switched off. There were 3 concrete repair tanks stored in the tank. When the tank was switched on the temperature was noted to be 17.4 degrees. 0.6 degree below the required range of 18-22 C.
| 02SL - Stations (LUL) | Cxxx-NCR-000671 | NCR | Platform +3 to Platform +2 Diaphragm Wall Inclusions |  | Contr | KIR | LIS - Liverpool Street Station (Central) |  | 2014-10-31 | 2014-08-06 13:42 | -86 | 2014-06-19 10:31 | Civil - Civil Engineering General | 3000 |  | Material | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Contamination | Completed |  | Inclusions were found in the diaphragm wall panels between PL+3 to PL+2. See attached Report for further details and photos.
| 02SL - Stations (LUL) | Cxxx-NCR-000672 | NCR | Drawing issued to third party contrary to Document control procedure |  | Contr | BAM | LIS - Liverpool Street Station (Central) |  | 2014-09-30 | 2014-06-29 20:25 | -93 | 2014-06-20 14:52 | Human Factors - Human Factors General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | When carrying out a surveillance on a sub contract Steel fabricator. It was found that a drawing had been issued by email and a receipt request had not been included. The drawing was marked "Prelimery" but the sub contractor had been instructed to proceed by email.
| 02SL - Stations (LUL) | Cxxx-NCR-000673 | NCR | South East Platform +2 middle box-out in ring beam - drying shrinkage cracks |  | Contr | KIR | LIS - Liverpool Street Station (Central) |  | 2014-10-31 | 2014-09-19 15:15 | -42 | 2014-06-26 09:19 | Civil - Civil Engineering General | 1000 |  | System Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | South East Platform +2 middle box-out in ring beam has developed drying shrinkage cracks, as a result of entrapped air/water on the surface of the element.
| 02SL - Stations (LUL) | Cxxx-NCR-000674 | NCR | South West Platform +2 middle ring beam - drying shrinkage cracks |  | Contr | KIR | LIS - Liverpool Street Station (Central) |  | 2014-10-31 | 2014-09-17 11:29 | -44 | 2014-06-26 09:20 | Civil - Civil Engineering General | 1000 |  | System Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | South West Platform +2 middle ring beam has developed drying shrinkage cracks, as a result of entrapped air/water on the surface of the element.
| 02SL - Stations (LUL) | Cxxx-NCR-000676 | NCR | Panel 2 Platform +2 Lower to Platform +1 Inclusion |  | Contr | KIR | LIS - Liverpool Street Station (Central) |  | 2014-08-24 | 2014-08-06 14:12 | -18 | 2014-07-10 07:52 | Civil - Civil Engineering General | 1500 |  | Material | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Inclusion found in the diaphragm wall Panel 2 between Platform +2 Lower to Platform +1. See attached photo.
| 02SL - Stations (LUL) | Cxxx-NCR-000677 | NCR | Panel 23 Platform +2 Lower to Platform +1 Inclusion |  | Contr | KIR | LIS - Liverpool Street Station (Central) |  | 2014-08-24 | 2014-08-06 14:13 | -18 | 2014-07-10 08:00 | Civil - Civil Engineering General | 1500 |  | Material | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Inclusion found in the diaphragm wall Panel 23 between Platform +2 Lower to Platform +1. See attached photo.
| 02SL - Stations (LUL) | Cxxx-NCR-000678 | NCR | Platform +2 Lower to Platform +1 Inclusions |  | Contr | KIR | LIS - Liverpool Street Station (Central) |  | 2014-08-24 | 2014-08-06 14:13 | -18 | 2014-07-10 08:43 | Civil - Civil Engineering General | 500 |  | Material | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Inclusions were found in the diaphragm wall panels between PL+2 Lower to PL+1. See attached photos.
| 02SL - Stations (LUL) | Cxxx-NCR-000679 | NCR | Ring beam strain gauges |  | Contr | BAM | LIS - Liverpool Street Station (Central) |  | 2014-10-31 | 2014-09-23 16:16 | -38 | 2014-07-16 17:23 | Surveying - Instrumentation and Monitoring | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | During the wiring up of the strain gauges on ring beams 4 and 5 (platform +2) it has become apparent thet the following strain gauges and/or cables have become damaged during concrete pour to the point that they are no longer able to provide readings Affected strain gauges SG04-f, SG05-d, SG05-e The strain gauges were working correctly at the point of installation as __ providfed the zero reading for the instruments A solution to the above issue would be to install surface mounted strain gauges at the locations where the instrument are currently positioned (this will require driling in the concrete for gauge anchor)
| 02SL - Stations (LUL) | Cxxx-NCR-000680 | NCR | Works commenced without an approved ITP |  | Contr | BAM | LIS - Liverpool Street Station (Central) |  | 2014-10-31 | 2014-10-22 10:10 | -9 | 2014-07-18 16:10 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | An ITP was returned Code 3. But the works went ahead. Works were to fix pipe brackets to the shaft ring beams so a permanent concrete delivery pipe could be provided.
| 02SL - Stations (LUL) | Cxxx-NCR-000681 | NCR | Angled Additional Bars Missing from South East PL+2 Lower Pour |  | Contr | KIR | LIS - Liverpool Street Station (Central) |  | 2014-11-30 | 2014-09-19 15:09 | -72 | 2014-07-21 16:43 | Civil - Civil Engineering General | 3000 |  | Incomplete Works | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | __ provided a sketch which details bars which were overlooked on the ring beam drawings. However 7 No. 25mm diameter bars were missed from the South East quadrant at Platform +2 Lower. See the marked up sketch attached.
| 02SL - Stations (LUL) | Cxxx-NCR-000682 | NCR | Jetty Bolt failure |  | Contr | KIR | LIS - Liverpool Street Station (Central) |  | 2014-09-08 | 2014-08-27 09:22 | -12 | 2014-07-25 12:22 | Civil - Civil Engineering General | 30000 |  | Workmanship | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Other | Completed |  | During cleaning/tightening process of the Jetty bolts, a jetty splice plate bolt has failed when it was being torqued up. The failure is due to the bolts and nuts being insufficiently cleaned before attempting to tighten them to the required tension. Material stuck within the threads has caused the nut to lock thus putting the bolt into a torque force rather than under tension.
| 02SL - Stations (LUL) | Cxxx-NCR-000683 | NCR | South West ring beam Level 85.4m - Reinforced Bars Installed in wrong place |  | Contr | KIR | LIS - Liverpool Street Station (Central) |  | 2014-11-30 | 2014-09-30 13:01 | -61 | 2014-07-29 09:46 | Civil - Civil Engineering General | 1500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | At South West ring beam Level 85.4m, 14 reinforced bars, BM 71, were installed in wrong place. As per current position there will be clashes between BM 55 and the box out at +2 lower level
| 02SL - Stations (LUL) | Cxxx-NCR-000686 | NCR | AP6 Temp. Prop |  | Contr | KIR | LIS - Liverpool Street Station (Central) |  | 2014-11-30 | 2014-10-01 21:58 | -60 | 2014-08-06 08:35 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Improper resource allocation | Completed |  | AP6 Prop concrete was not filled to the top, leaving rebar exposed in the north side of the prop (see attached photo) due a wrong 'cube up' by the engineer
| 02SL - Stations (LUL) | Cxxx-NCR-000687 | NCR | Cold joint at DRS opening (East side of the opening) |  | Contr | KIR | LIS - Liverpool Street Station (Central) |  | 2014-11-30 | 2014-09-19 15:13 | -72 | 2014-08-06 09:18 | Civil - Civil Engineering General | 500 |  | Planning | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | Cold joint left on the face of the angled slope in the DRS opening at level +1, see attached photo
| 02SL - Stations (LUL) | Cxxx-NCR-000688 | NCR | Void left for concrete pour North East level +2 lower |  | Contr | KIR | LIS - Liverpool Street Station (Central) |  | 2014-11-30 | 2014-09-19 13:47 | -72 | 2014-08-06 09:49 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Void left from concrete pour in the North East level +2 lower at the top of the pour (see attached photo)
| 02SL - Stations (LUL) | Cxxx-NCR-000689 | NCR | Void left from Concrete pour in the South East Level +2 lower |  | Contr | KIR | LIS - Liverpool Street Station (Central) |  | 2014-11-30 | 2014-09-19 14:16 | -72 | 2014-08-06 09:52 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Void left from concrete pour in the South East level +2 lower at the top of the pour (see attached photo)
| 02SL - Stations (LUL) | Cxxx-NCR-000690 | NCR | Out of tolerance concrete dimensions |  | Contr | BAM | LIS - Liverpool Street Station (Central) |  | 2014-11-28 | 2014-09-19 13:29 | -70 | 2014-08-06 16:30 | Civil - Civil Engineering General | 1500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | It was noted that the tolerances of the diaphragm wall (+/-25mm and 1:150) were not in step with the capping beam tolerances (please see RFI 562). The capping beam was therfore built to accomodate the D Wall. Consequentially the capping beam in places is out side the tolerances required. The maximum out of tolerance was one at 50mm. The as built surveys can be found in C501-__-C-LST-C101-50029
| 02SL - Stations (LUL) | Cxxx-NCR-000691 | NCR | Concrete |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2014-11-30 | 2014-10-02 09:09 | -59 | 2014-08-08 11:18 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Lack of procedure | Completed |  | During a CRL led planned surveillance the Contractor was unable to provide any planned arrangements for hot/cold weather concreting. The Contractor stated that KF10 is used for guidance, example; ITP number C501-__-C-ITP-C101-50009 rev 3.0 section 3.13; Check ambient temperature, controlling documents; Specification for Civil Structural Works Cxxx-MMD-C-RSP-C101-00002, Rev. 9.0 KF10-3205 and BS8110 part 1
| 02SL - Stations (LUL) | Cxxx-NCR-000692 | NCR | Panel 23 +1 middle to +1 lower |  | Contr | KIR | LIS - Liverpool Street Station (Central) |  | 2014-11-30 | 2014-08-22 10:55 | -100 | 2014-08-11 17:38 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Inclusion found at panel 23 between the soffit of +1 and +1 lower. The inclusion was broken out and the rebar exposed.
| 02SL - Stations (LUL) | Cxxx-NCR-000693 | NCR | Section of DRS Concrete Out of Tolerance at Platform +1 Level |  | Contr | KIR | LIS - Liverpool Street Station (Central) |  | 2014-11-30 | 2014-08-22 10:52 | -100 | 2014-08-12 10:00 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | It was noticed that a section of the reinforcement in the DRS opening area was installed 35mm out due to an setting out error, and as a result the shutter had to be moved back to ensure adequate cover to the reforcement. Please find attached as-built drawings of teh concreted DRS area at PLatform +2 Lower/Platform +1.
| 02SL - Stations (LUL) | Cxxx-NCR-000695 | NCR | Damaged Stopend at Platform +1 Lower Between Panels P08 & P09 |  | Contr | KIR | LIS - Liverpool Street Station (Central) |  | 2014-11-30 | 2014-09-19 11:33 | -72 | 2014-08-14 12:51 | Civil - Civil Engineering General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | During the breaking out the the Barettes from Platform +1 Level to Platform +1 Middle, the stopend between panels P08 & P09 was damaged.
| 02SL - Stations (LUL) | Cxxx-NCR-000696 | NCR | Additional Jetty Props fabricated prior to endorsement by Responsible Welding Coordinator (RWC) |  | Crossrail | PDP | LIS - Liverpool Street Station (Central) |  | 2014-11-19 | 2014-09-30 10:30 | -50 | 2014-08-21 20:44 | Civil - Structural Engineering | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | The additional props at the top of the crane jetty commenced installation on the 18th August 2014 and had been delivered to site before that date. No report from a RWC was submitted to endorse the required welding documentation, prior to the commencement of fabrication.
| 02SL - Stations (LUL) | Cxxx-NCR-000697 | NCR | Diaphram wall inclusion repair failure |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2014-10-21 | 2014-09-26 13:46 | -25 | 2014-08-22 15:56 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Formwork constructed for d-wall inclusion repair on 21-8-14 nightshift Section of formwork failed and/or not adequately sealed to AP6 downstand. At approx 2:30pm on 22-8-14, pour had partially spilled onto blinding. Pour still wet at time of inspection.
| 02SL - Stations (LUL) | Cxxx-NCR-000699 | NCR | Platform +1 Middle & Lower concrete finish |  | Contr | KIR | LIS - Liverpool Street Station (Central) |  | 2014-11-30 | 2014-09-18 12:07 | -73 | 2014-08-22 21:25 | Civil - Civil Engineering General | 3000 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | During the concreting of Platform +1 Middle & Lower the team where pumping through the top port inlet and with 20mm from the soffit to go the shutter started to fail. The shutter proceeded to move along the horizontal joint of the 2.7m and 900mm shutter pans causing the shutter face to bow vertically. The shutters was supported furtehr and the concrete pour was able to finsh. The NCR is raised for the face being out of tolerance
| 02SL - Stations (LUL) | Cxxx-NCR-000700 | NCR | P23 Cage 1 Inclusion |  | Contr | KIR | LIS - Liverpool Street Station (Central) |  | 2014-11-30 | 2014-09-19 13:48 | -72 | 2014-09-02 08:47 | Civil - Civil Engineering General | 3000 |  | Material | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Inclusion Found in Panel 23
| 02SL - Stations (LUL) | Cxxx-NCR-000701 | NCR | Ring Beam Platform +4 East |  | Contr | __ | LIS - Liverpool Street Station (Central) |  | 2014-11-30 | 2014-10-01 22:02 | -60 | 2014-09-09 16:40 | Civil - Civil Engineering General | 1500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Survey of Ring Beam Platform +4 East- East lining wall, results on a deviation from tolerance in width in range of 27mm to 47 mm in various locations.
| 02SL - Stations (LUL) | Cxxx-NCR-000702 | NCR | Base slab works |  | Contr | __ | LIS - Liverpool Street Station (Central) |  | 2014-10-08 | 2014-09-14 21:40 | -24 | 2014-09-11 14:02 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Base slab works commenced without an accepted ITP ( ITP Reference number C501-__-C-ITP-C101-50033)
| 02SL - Stations (LUL) | Cxxx-NCR-000705 | NCR | Barrette Geo pipes |  | Contr | KIR | LIS - Liverpool Street Station (Central) |  | 2014-11-28 | 2014-10-16 15:01 | -43 | 2014-10-03 16:22 | Civil - Geotechnical Engineering | 3000 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Contamination | Completed |  | Barrette 1, 2 and 8 have blocked Geo pipes and Barrttes 3, 4, 5, 6 and 7 have geo pipes flowing in on direction (east to west)
| 02SL - Stations (LUL) | Cxxx-NCR-000706 | NCR | Option 3 Manhole Position |  | Contr | KIR | LIS - Liverpool Street Station (Central) |  | 2014-12-31 | 2014-12-05 16:58 | -26 | 2014-10-24 13:00 | Communications and Control Systems - Station Management System | 3000 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | During the option 3 drainage works, the manhole had to be positioned out of tolerance due to the adjacent pile caps obstruting __ installing it as per drawing Cxxx-MMD-D-DDA-C101_1-11030 note 7. However __ did not follow the correct process of raising an FCD for the position of the manhole being further out of position than that stated in Note 7 on drawing Cxxx-MMD-D-DDA-C101_1-11030 before the Manhole was constructed. Note: As the manhole has been cast out of position, it is the BM17 (DWG C501-__-C-DDL-C101-50780) which is detailed to cast into the reinstatement slab, which determines the edge of concrete slab. The reinstatement slab has therefore been cast to its minimum point to maintain cover to these bars.
| 02SL - Stations (LUL) | Cxxx-NCR-000707 | NCR | Base Slab Level Inclusions |  | Contr | KIR | LIS - Liverpool Street Station (Central) |  | 2015-01-31 | 2014-12-02 15:43 | -60 | 2014-11-11 11:28 | Civil - Civil Engineering General | 2500 |  | Material | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Contamination | Completed |  | Inclusions were found in the diaphragm wall panels at the base slab level. See attached Report for further details and photos.
| 02SL - Stations (LUL) | Cxxx-NCR-000708 | NCR | Base Slab - Sump - Couplers Cast Out of Position |  | Crossrail | PDP | LIS - Liverpool Street Station (Central) |  | 2014-12-20 | 2014-12-08 10:38 | -12 | 2014-11-20 14:59 | Civil - Civil Engineering General | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Couplers closest to Dwall in the first stage sump concrete - cast out of position.
| 02SL - Stations (LUL) | Cxxx-NCR-000709 | NCR | Base slab concrete finishing levels |  | Contr | __ | LIS - Liverpool Street Station (Central) |  | 2014-12-23 | 2014-12-14 21:56 | -9 | 2014-11-20 17:07 | Civil - Civil Engineering General | 3000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Base Slab Concrete finishing levels out of specified tolerance
| 02SL - Stations (LUL) | Cxxx-NCR-000710 | NCR | AP6 Tunnel couplers |  | Crossrail | PDP | LIS - Liverpool Street Station (Central) |  | 2015-08-31 | 2016-02-24 11:02 | 177 | 2014-12-22 13:14 | Civil - Civil Engineering General | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | Further to RFI 769the couplers on the lower section of AP6 had not been installed, its not shown in the detailed design neither the Red line DRW.
| 02SL - Stations (LUL) | Cxxx-NCR-000711 | NCR | MTH - Couplers incorrectly protruding from Manhole 3 |  | Crossrail | PDP | LIS - Liverpool Street Station (Central) |  | 2015-10-11 | 2015-10-20 08:45 | 9 | 2015-07-13 09:45 | Civil - Civil Engineering General | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | It has been has found that couplers are incorrectly protruding from Manhole 3 (shoul dhave been flush) and have been damaged due to a lack of protection. This defect will have to be amended.
| 02SL - Stations (LUL) | Cxxx-NCR-000713 | NCR | MTH - Lack of cover to the OSD column reinforcement and verticality to the position of couplers |  | Crossrail | PDP | LIS - Liverpool Street Station (Central) |  | 2015-10-11 | 2015-09-22 17:51 | -19 | 2015-07-13 10:52 | Civil - Civil Engineering General | 5000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | MTH - Lack of cover to the OSD column reinforcement and verticality to the position of couplers. It has found that there is a lack of cover to the OSD column reinforcement. This has affected the verticality to the position of couplers. This defect will have to be amended.
| 02SL - Stations (LUL) | Cxxx-NCR-000714 | NCR | MTH - Lack of cover to coupler bars in existing MTH sewer |  | Crossrail | PDP | LIS - Liverpool Street Station (Central) |  | 2015-10-11 | 2015-08-09 22:20 | -63 | 2015-07-13 12:04 | Civil - Civil Engineering General | 6000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | MTH - Lack of cover to coupler bars in existing MTH sewer. On exposing the existing reinforcement couplers on the MTH sewer, it has found that there are several locations where the concrete cover to the coupler is only 25mm (top and bottom mat). This is less than the 45mm required on the reinforcement drawings. Furthermore, there are areas of chipped concrete on the edges of the sewer that will need to be made good prior to concreting the new adjoining slab. Refer to marked up drawing and photo evidence for further information.
| 02SL - Stations (LUL) | Cxxx-NCR-000715 | NCR | Low cover to couplers in ring beam at 79.1m level, in Wall A1 |  | Crossrail | PDP | LIS - Liverpool Street Station (Central) |  | 2016-01-31 | 2016-02-24 10:46 | 24 | 2015-11-02 09:57 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | Cxxx have measured as-built cover to BM 04 in the ring beam at 79.1m level, Wall A1, varying between 70mm and 25mm, as opposed to the required 115mm cover. See attachment.
| 02SL - Stations (LUL) | Cxxx-NCR-000425 | NCR | MP112 incorrect cage installed. |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-11-21 | 2012-11-15 15:08 | -6 | 2012-11-07 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | An A1 type cage was placed. (See As-built sketch). Instead of an A2 type Cage. This occurred because the Foreman thought the pile he was installing was MP113 not MP112.
| 02SL - Stations (LUL) | Cxxx-NCR-000426 | NCR | Pile Type MP - Verticality out of tolerance |  | Contr | LOS | LIS - Liverpool Street Station (Central) |  | 2013-12-31 | 2013-12-15 11:22 | -16 | 2012-11-14 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The piles shown in the attached sketch show which MP piles are out of the specified tolerance. The measurement of the verticality was carried out with an electronic spirit level placed on the inside of the first temporary casing. This is the only verticality measurement that can be carried out due to the piling methodology. (i.e, restricted access rig has no onboard electronic measuring device). The measurements may have been influenced by the shape of the casing and need to be taken with caution. Therefore the piles shown as 'out of tolerance' on the attached sketch may have in fact been installed to the specification requirement.
| 02SL - Stations (LUL) | Cxxx-NCR-000427 | NCR | MP Pile Type - Toe Level out of tolerance |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-06-28 | 2013-03-22 13:12 | -98 | 2012-11-07 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The MP Piles shown in the attached have a Toe Level higher then the 100mAOD design. This is due to the measuring of the pile depth being taken to an accuracy of 0.1m, and the casing level to an accuracy of 0.001. This then only leaves Piles MP002, 006, 054, 118, 120, 121, 125 with a toe level higher than the design. For these piles the depth was taken once the augers had been taken apart from the rig and the cage was ready for installation. The cage levels were not high, thus suggesting that the final toe level was at or lower than the 100mATD design. Therefore there must have been some spoil fallen into the pile to cause a measurement lower than required. This spoil would have compacted under the weight of the cage enabling the cage to be at the correct level.
| 02SL - Stations (LUL) | Cxxx-NCR-000428 | NCR | MP piles - Plan position out of tolerance |  | Contr | LOS | LIS - Liverpool Street Station (Central) |  | 2013-12-30 | 2013-12-13 15:03 | -17 | 2012-11-21 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The 13No piles shown on the attached sketch are out of tolerance of up to 37mm inside the box (MP036 = 37mm, MP037 = 29mm & MP074 = 27mm) and up to 48mm along the line of the contiguous wall. Obstructions were encountered on piles MP081 & 132 The other piles are out of tolerance because the guide wall had to be reset in the appropriate position due to the wrong setting out point provided. More specifically at the junction of the reset guidewall and the next section of the guidewall (MP036 & 037)
| 02SL - Stations (LUL) | Cxxx-NCR-000429 | NCR | MP Piles out of tolerance cage level. |  | Contr | LOS | LIS - Liverpool Street Station (Central) |  | 2014-03-30 | 2013-12-13 13:20 | -107 | 2012-11-21 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The reinforcement cages in the piles listed below are out of the specified tolerance. The deviation listed is the total amount from specified design level. MP004 = -163 MP027 = -118 MP064 = -159 MP081 = -118 MP104 = -115 MP129 = -155
| 02SL - Stations (LUL) | Cxxx-NCR-000431 | NCR | Grout testing |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-12-14 | 2012-12-04 12:30 | -10 | 2012-11-09 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | ITP Cxxx-LAO-C-ITP-C101_WS103-50006 rev 2.0 item 32 Grout Consistency incorrectly identifies the Controlling Document Clause for Concrete Testing. Grout Consistency test results were not available during CRL surveillance of 1st November 2012.
| 02SL - Stations (LUL) | Cxxx-NCR-000432 | NCR | Installing RC without ITP |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-12-24 | 2012-12-04 10:16 | -20 | 2012-11-09 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | The Contractor commenced the installation of a RC base without a valid ITP in place for the works.
| 02SL - Stations (LUL) | Cxxx-NCR-000433 | NCR | Concrete Cube Storage |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-12-28 | 2012-12-04 16:46 | -24 | 2012-11-13 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | The cubes taken from the mini piles have been kept overnight in a site cabin, without temperature controls - with temperatures dropping below the 15 degree minimum.
| 02SL - Stations (LUL) | Cxxx-NCR-000434 | NCR | Imported material chemical properties |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-12-28 | 2012-12-04 13:09 | -24 | 2012-11-13 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Records were not made available for surveillance QS502-02 or thereafter to the date of this NCR to demonstrate implantation of __ 340 clause 3.3 with respect to imported material being free of contaminants.
| 02SL - Stations (LUL) | Cxxx-NCR-000536 | NCR | Verticality MP134 (missed off NCR 426) |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-07-31 | 2013-05-10 12:54 | -82 | 2012-11-21 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Pile MP134 is out of the specified tolerance as shown in the attached site log. It is tilting 10mm/m away from the railway and 7mm/m along. This occured due to an obstruction encoutered whilst drilling. The pile was filled with grout and re-bored to get it closer to the soecified position and verticality,however the final position is as stated above.
| 02SL - Stations (LUL) | Cxxx-NCR-000540 | NCR | Geothermal Loop Installation |  | Crossrail | PDP | LIS - Liverpool Street Station (Central) |  | 2013-12-31 | 2013-10-03 22:52 | -89 | 2012-11-28 | Civil - Civil Engineering General | 500 |  | System Defect | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Piles 117, 115 were concreted and to be left for a minimum of 24hrs (as per KP10 and RFI relaxation) before taking off pressure and burying within the piling mat – I found today that these piles (and P118) were flow tested immediately after concreting – an operation that involves releasing the pressure. This has potentially allowed the plastic to collapse and therefore compromised the loop’s usefulness. During tremmie removal the ball valve was knocked and allowed P112 to lose the pressure during the 24 hr curing period – this may also have compromised the loop.
| 02SL - Stations (LUL) | Cxxx-NCR-000543 | NCR | P119 - Top of cage higher then specified tolerance. |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-03-31 | 2013-03-22 12:48 | -9 | 2012-12-04 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | The cage in pile P119 is at a height of 106.785mATD rather then the design level of 106.415mATD. The cage was placed higher then the design level as it was forethought that some amount of 'settleing would take place during the placement of the cage on the toe of the pile (With cage feet) and the concreting process. The 'settleing' that took place was not the the full amount allowed for. Therefore the cage has remained high.
| 02SL - Stations (LUL) | Cxxx-NCR-000550 | NCR | Pile P120 & P137 - Concrete Cover to Cage |  | Contr | LOS | LIS - Liverpool Street Station (Central) |  | 2013-12-31 | 2013-12-04 13:32 | -27 | 2013-01-07 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Material | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | P120 and P137 were seen to have the top of the cage close to the casing and therefore not allowing 100mm of concrete cover once completed. Details of P120; The top of the cage is 106.545mATD and the cut off level is 105.815mATD. The skid spacers are fixed to the cage at 3m centres; therefore it is only the top 2.2m of the pile which is of concern. The bands of skid spacers were checked before placing the cage and it is believed that either the weight of the cage pushed the cage towards the edge of the casing or the installation of the tremie pipes in such a congested space resulted in the same issue. (P137 has been observed to be in a similar condition) Please find attached the cage drawing, sketch of the dimensions for the pile and a photo of the top of the cage.
| 02SL - Stations (LUL) | Cxxx-NCR-000616 | NCR | Pile P132 Bearing Piling. Out of permitted deviation tolerance. |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-03-31 | 2013-03-23 21:08 | -8 | 2013-01-04 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Pile P132 has a casing verticality of 6mm/m towards the North and 14mm/m towards the East. It also has a position deviation from the design of 32mm towards the South and 41mm towards the West. While drilling on the 3rd Jan an obstruction from piling platform level to 3m below was encountered. The oversized core barrel (900mm diameter) was used, however due to the proximity of the pile and the 1200mm diameter guidewall the tolerance of +-25mm could not be achieved. (The guidewall could not be broken out as there is steel embedded within it). The obstruction was 3m thick, therefore the verticality could not be altered as it followed the uncored (hard) surface of the side of the obstruction.
| 02SL - Stations (LUL) | Cxxx-NCR-000647 | NCR | P124 Cage higher then specified tolerance |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-03-31 | 2013-03-22 13:56 | -9 | 2013-01-18 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The cage in pile P124 is at a height of 106.443mATD rather then the design level of 106.180mATD. The cage was placed higher then the design level, because the cage engineer accidently placed the cage feet longer then required.
| 02SL - Stations (LUL) | Cxxx-NCR-000648 | NCR | P143 - Out of plan poisional tolerance |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-03-31 | 2013-03-22 13:40 | -9 | 2013-02-11 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Pile P143 has a position deviation from the design of 11mm towards the North and 25mm towards the East. (In total 36mm in the North and 50mm in the East direction) While drilling, an obstruction was encountered. (See attached email for description)
| 02SL - Stations (LUL) | Cxxx-NCR-000654 | NCR | PW350 cage connection |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-04-30 | 2013-03-22 16:24 | -39 | 2013-01-23 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | PW350 only has 19No connected at the level of 73.7mATD. One number coupler is not connected in the middle of the outside face of the contiguous wall cage. A B40x2m reinforcement bar is lapped at that location. The coupler was unable to be connected due to the out of alignment between the main bar on the bottom section of cage and the main bar on the middle section of cage. This alignment error was due to the welding of the links onto main bar taking place after the pre-assembling of the cage.
| 02SL - Stations (LUL) | Cxxx-NCR-000659 | NCR | PW357 |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-03-31 | 2013-03-06 13:59 | -25 | 2013-01-25 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | While completing pile PW357 we encountered issues with the concrete delivery; as a result the pile has not been concreted. (See email) In summary; 1) Time taken; start boring 8am 24/01, finish boring 12.30pm 24/01, start concreting 7.52am 26/01, finish concreting 11.10am 26/01 2) Pile drilled deeper by 3.62m (toe level 56.38mATD) 3) Extra cage placed at bottom of original cage (see attached sketch within email) 4) Concrete used was mix A4 not Mix D. (MCR; Cxxx-LAO-O4-XDS-C101_WS103-50008). (n.b, items 2-4 above pre-agreed with CRL) Pile Log attached for full information.
| 02SL - Stations (LUL) | Cxxx-NCR-000803 | NCR | PW352 - Out of Plan positional tolerance |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-06-03 | 2013-03-22 14:38 | -73 | 2013-02-21 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The casing asbuilts for PW352 are as follows: (North = 11mm, East = 33mm) Design; 83355.974, 36243.330 First check; 83356.007, 36243.319 Error; -0.033, 0.011 Second check; 83356.007, 36243.323 Error; -0.033, 0.007 The error is in the East direction, which is along the centre line of the wall. Therefore it is not coming into the box. This occured due to the guidewall scollops not providing the firmness and positioning to ensure the casing does not go outside the tolerance.
| 02SL - Stations (LUL) | Cxxx-NCR-000804 | NCR | Sonic Tube - PW348 |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-04-04 | 2013-03-22 17:07 | -13 | 2013-02-21 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Damaged | Use As-Is |  | Complete |  | Completed |  | 3No sonic tubes. Not 4No as specified. See attached Near Miss details.
| 02SL - Stations (LUL) | Cxxx-NCR-000820 | NCR | PW349 - Concrete admixture change and Tremmie pipe cast in. |  | Contr | LOS | LIS - Liverpool Street Station (Central) |  | 2014-05-31 | 2014-01-19 21:24 | -132 | 2013-02-28 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | - The superplasticiser used was not the __ LTD SP18RM, but was a __ PLC SKY544 (Shown on attached Mix design). The amount used has not changed and the result of acheiving the workability has also not changed. All the flow test results were all within tolerance. This occured becasue the supplier had a delivery of the SPLAS required a day later then needed. - The pile has a section of 9m tremmie pipe cast into the top. Starting approximately 2m below PPL (110.2mATD) and finishing at 99.2mATD. 6m of tremmie will be left below the COL. The pipe is grade S275, 165mm ID, 175mm OD main pipe, 193mm OD at joint. It is full of concrete. This occured during the splitting of the tremmie pipes. The crane lifted the detached tremmies upwards, but the angle the jib was placed caused the tremmies within the keying off fork to move and slip through the fork and into the pile.
| 02SL - Stations (LUL) | Cxxx-NCR-000865 | NCR | Verticality of bearing piles out of tolerance (101,104,129) |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-05-31 | 2013-04-02 14:31 | -59 | 2013-03-22 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Piles P101, P104 & P129 rig instrumentation shows the bore verticality being out of design tolerance. P101 at 19.2m is 15mm North and 138mm West. (Max allowed is 96mm) P104 at 19.4m is 15mm North and 141mm West. (Max allowed is 96mm) P129 at 53.9m is 327mm North and 22mm West. (Max allowed is 270mm) This was due to obstructions in these areas.
| 02SL - Stations (LUL) | Cxxx-NCR-000948 | NCR | Orientation of MP125 slab couplers |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-05-15 | 2013-05-07 17:13 | -8 | 2013-04-04 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | MP125 slab couplers have been exposed and they are found to be facing South East not South West as designed. (See attached photos)
| 02SL - Stations (LUL) | Cxxx-NCR-000974 | NCR | N.West Mini Pile Propping - ST-10 |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-12-31 | 2013-07-09 16:23 | -175 | 2013-04-19 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The end of prop ST-10 does not meet the king post, with a 75mm gap between the prop endplate and kingpost. The end plate is also 25mm off centreline of the king post towards prop ST-11, causing torque of 16.5kNm (see photos and attached calculation sheet).
| 02SL - Stations (LUL) | Cxxx-NCR-000991 | NCR | Blomfield Box - PW366 out of positional tolerence on plan |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2014-04-25 | 2013-07-24 08:25 | -275 | 2013-04-24 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | PW366 has been installed outside of the allowable tolerance on plan position. The plan position of the pile at COL is 14mm in the south west direction outside of the allowable tolerance. Therefore the pile deviates outside of the box. This occured due to an obstruction in the ground as per email sent to CRL on 23/04/13, see below We have encountered obstructions on pile ref. PW366 on the 22/04/13. On Pile PW366 we have encountered a 2m obstruction @ 1.5m below PPL which is more adverse than on the GBR. The obstruction was made of brick wall and concrete and an overall of 2h00 was required to core / break through the obstruction. CRL was informed; however no one was available to attend the coring operation. The pile position had to be broken out with the excavator and subsequently cored in order to penetrate the obstruction. Please note that this resulted in the pile being kicked off position by 10mm towards pile ref. PW365. We will attempt to reset the pile position this morning and will advise of further time spent accordingly. Should you wish us to adopt a different methodology please advice at your earliest opportunity.
| 02SL - Stations (LUL) | Cxxx-NCR-000994 | NCR | ITP for offsite fabrication of temporary propping steelwork |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-08-31 | 2013-07-04 09:55 | -58 | 2013-06-19 | Civil - Civil Engineering General | 500 |  | System Defect | Repair |  | Complete |  | Completed |  | An ITP was not produced by the fabricator, __, and issued to Crossrail on eB for acceptance.
| 02SL - Stations (LUL) | Cxxx-NCR-001010 | NCR | Mini pile propping steel couplers cast in with 18mm recess - 108.5m Level |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-08-30 | 2013-06-28 14:25 | -63 | 2013-04-29 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | To ensure positional tolerance of the couplers during construction, a plywood jig was constructed and fixed to the formwork. This resulted in a recess being formed in concrete face with __ Bolt couplers being cast flush with recess face. This produced the gap of 48mm between waler beam and cast-in coupler face instead of desinged gap of 30mm. As a result, bolts will be subjected to bending forces larger than originally designed and needs to be looked into by TW engineer prior to signing of the permit to load.
| 02SL - Stations (LUL) | Cxxx-NCR-001012 | NCR | NW mini pile props ST10 & ST11 damaged stiffeners |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-08-30 | 2013-07-30 22:35 | -31 | 2013-04-29 | Civil - Civil Engineering General | 3000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During pile break out to expose the King Posts for connection with props, 5 out of 6 stiffener plates on each king post were damaged to an extent making them unsuitable.
| 02SL - Stations (LUL) | Cxxx-NCR-001022 | NCR | oversized holes in waler beam to ST10 & ST11 props- NW minipile propping |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-10-31 | 2013-09-02 13:17 | -59 | 2013-04-30 | Civil - Civil Engineering General | 1000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete |  | Completed |  | When steel waler was fixed to the lining wall, 5no. of 12no. M24 cast-in couplers for prop ST10 (drawing C3229-ENG-TW-0042 , detail 6) were not quite installed flush with concrete face. This created problem during screwing M24 bolts through 26mm dia holes in steel waler beam. Waler beam flange was 40mm thick and did not allow correcting the alignment of bolt though 26mm dia hole. To get the alighnment right so that bolt can be offered into the couplers, holes needed to be enlagred between 3 to 5mm on the side of the hole which clashed with the bolt. Refer to the attached photos.
| 02SL - Stations (LUL) | Cxxx-NCR-001024 | NCR | Steel prop ST10 25mm off line from center of King Post - NW minipile propping |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-09-30 | 2013-09-02 13:18 | -28 | 2013-04-30 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During installation it was found out that Steel prop ST10 is 25mm out of alignment from center of king post. The King Post had predrilled holes which did not match with the holes in prop end plate. The holes needed to be redrilled in King Post flange such that they come in line with the holes in prop end plate.
| 02SL - Stations (LUL) | Cxxx-NCR-001029 | NCR | Obstruction to PW367 |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-07-09 | 2013-05-24 22:03 | -46 | 2013-05-08 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  |  | Rework |  | Complete |  | Completed |  | While drilling pile PW367 on Friday 3/5/13 the rig bucket experienced a hardened layer at 40m below the platform level of 107.000m atd. During drilling through this, the rig was unable to retract the bucket out of the pile and so became stuck. We were unable to extract the bucket out of the pile until Sunday morning 5/5/13 resulting in the pile being open for more than 48 hours. As the pile could not be completed within 60 hours we backfilled the pile with single sized washed gravel as per our contingency plan Cxxx-LAO-O4-GDP-C101_WS103-50001.
| 02SL - Stations (LUL) | Cxxx-NCR-001071 | NCR | Temporary Works Construction Changes to Accepted Design |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-07-31 | 2013-06-28 16:51 | -33 | 2013-06-03 | Civil - Civil Engineering General | 500 |  | System Defect | Use As-Is |  | Complete |  | Completed |  | Alterations to Temporary Works Design during the construction of the temporary proppping to the mini piles as identified in Method Statement "Installation of propping at 108.5m to NE Mini piles", and, "Temporary Works Design Blomfield Box - Mini Piles Props at 108.5m" have not been Approved or Accepted in writing by the Temporary Works Co-ordinator/Designer/Employer. Alterations were approved verbally only.
| 02SL - Stations (LUL) | Cxxx-NCR-001073 | NCR | Blomfield Box - PW360 exceeding vertical/positional tolerance |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2014-04-25 | 2013-07-31 14:42 | -268 | 2013-05-14 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | PW360 has been installed out of the allowable verticality tolerance and therefore the positon of the pile at the soffit of the 73.750 SSL is 100mm out of position on plan. This is in a westerly direction. which is away from the box.
| 02SL - Stations (LUL) | Cxxx-NCR-001074 | NCR | Blomfield Box - PW368 out of positional/vertical tolerance |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-01-31 | 2014-11-17 12:59 | -75 | 2013-05-14 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | PW368 has been installed out of the allowable verticality tolerance and therefore the positon of the pile at the soffit of the 73.750 SSL is 80mm out of position on plan. This is in a south easterly direction which is towards the box.
| 02SL - Stations (LUL) | Cxxx-NCR-001080 | NCR | Blomfield Box - PW367 coupler positions out of tolerence |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-01-31 | 2014-11-17 13:01 | -75 | 2013-05-21 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The cage in pile PW367 is at a height of 106.905mATD which is 105mm above the design level of 106.800mATD and is within the SPERW tolerance but not to the tolerance stated in RFI LIS-CRL-RFI-Cxxx-00746 of +-50mm. The top of the cage had been set within the tolerance to RFI 000746 prior to extracting the casing. Once the casing had been removed the cage was found to have risen to 106.905mATD The couplers therefore in the top section will be 55mm higher than the specified tolerance set out in RFI LIS-CRL-RFI-Cxxx-00335, so 105mm in total above its designed position. Taking into account the coupler connection tolererances the second section will possibly be a maximum of 35mm higher than the specified tolerance, the third section will possibly be 15mm higher than the specified tolerance and the rest of the cages are predicted to be within tolerance. It is also possible that these connection tolerances are not used and the couplers are in fact fully engaged, this would then mean that all the couplers in the 6 cages are 105mm higher than the design level.
| 02SL - Stations (LUL) | Cxxx-NCR-001108 | NCR | Blomfield Box - P502 unable to be completed within 48 hours |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-06-24 | 2013-06-18 23:16 | -6 | 2013-06-10 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Equipment Breakdown | Rework |  | Complete |  | Completed |  | Pile P502 had to be abandoned due to the kelly bar being misaligned/damaged (as per email sent by __ on 07/06/13) which was deemed to be unsafe to proceed its completion. This resulted in the pile not being completed within the 48 hour time frame set by RFI LIS-CRL RFI-Cxxx-00658.
| 02SL - Stations (LUL) | Cxxx-NCR-001150 | NCR | Plunge Column Donut Setting Out Error |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2013-09-30 | 2013-08-30 07:58 | -31 | 2013-06-28 | Civil - Civil Engineering General | 7000 |  | Workmanship | Rework | 2 (6-60k) | Complete |  | Completed |  | Donuts are cast out of position and have been backfilled.
| 02SL - Stations (LUL) | Cxxx-NCR-001156 | NCR | Inclinometer installation failure |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2014-03-31 | 2014-02-11 13:29 | -48 | 2013-07-03 | Geotechnical Engineering - Concrete - Bored Pile | 1000 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On pile PW331 a trial installation of an inclinometer tube took place which failed due to the tube catching on the lining wall bars inside the cage. This resulted in the tube being stressed and the joint to open and allow grout to seep inside of the tube. We believe that this was due to the joint failing while the tube was being plunged allowing for the intake of grout. The grout was dipped inside the tube on 03/07/13 and the level was found to be 100mATD. The fact that the tube filled with grout suggests that there is a potential seggregation to the concrete surrounding the tube compromising its strength.
| 02SL - Stations (LUL) | Cxxx-NCR-001166 | NCR | P201 open more than 24 hours. |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2013-09-30 | 2013-07-31 23:15 | -61 | 2013-07-05 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Due to the unforeseen circumstances the excavation of pile P201 has been open for more than 24 hours. The reinforcement has also been submerged in bentonite.
| 02SL - Stations (LUL) | Cxxx-NCR-001169 | NCR | P201 - Wrong materials delivered for connecting plunge column |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2013-08-12 | 2013-07-31 10:47 | -12 | 2013-07-29 13:57 | Geotechnical Engineering - Concrete - Bored Pile | 1000 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | NB: This NCR was originally raised as a draft prior to the migration to eb/PTR under PTR number LIS-CRL NCR-Cxxx-01168 on the 8th July. As a result of the migration all drafts were cancelled and it is this reason for it now being raised 24 days after the event. On installing the plunge column in pile P201 it was found that the delivered washers were not the correct type specifeid. The specified washers to be used when connecting the plunge column sections with HSFG bolts are the TurnaSure® __I washers grade 10.9. The grade of the delivered washers were 8.8. The plunge column was then removed from the pile and an emergency delivery of the TurnaSure® __I washers grade 10.9 was made allowing the installation to proceed. Only the grade 8.8 bolts and washers is incorporated within the __ ITP
| 02SL - Stations (LUL) | Cxxx-NCR-001170 | NCR | Pile Levels to 300 Diameter Mini Piles |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2013-10-31 | 2013-09-30 11:55 | -31 | 2013-08-02 17:48 | Civil - Civil Engineering General | 1000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A number of the 300 diameter piles have been broken down to below the intended cut off level. The attached PDF gives the details of which piles are low and by how much. The levels given are the lowest levels on the top of the pile. The intended pile cut off level in this area is 109.225.
| 02SL - Stations (LUL) | Cxxx-NCR-001171 | NCR | Lack of Triggers applied to ground movement |  | Crossrail | PDP | LIS - Liverpool Street Station (Central) |  | 2014-02-28 | 2014-02-11 10:43 | -17 | 2013-08-05 11:55 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Graphs of ground movement in the Cxxx zone of influence, prepared by __, have todate not shown the prescribed trigger values from the relevant I&M Plans.
| 02SL - Stations (LUL) | Cxxx-NCR-001172 | NCR | Blomfield Box - Coupler in MP013 damaged |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2013-10-31 | 2013-09-10 08:40 | -51 | 2013-08-12 10:05 | Civil - Excavation | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On exposing the mini piles it was found that a coupler in pile MP013 have been damaged/sheared off thus not allowing of the installation of the male coupler. See attached photo.
| 02SL - Stations (LUL) | Cxxx-NCR-001174 | NCR | Steelwork fabrication commenced without an Accepted ITP |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2013-12-05 | 2013-08-27 16:04 | -100 | 2013-08-27 11:42 | Civil - Structural Engineering | 10000 |  | System Defect | Rework | 2 (6-60k) | Complete |  | Completed |  | __ Ltd started the offsite fabrication of steelwork for Plunge Columns without having an Accepted Inspection and Test Plan. The Inspection and Test Plan in use at the fabrication shop was the standard __ Ltd ITP for fabricating and welding steelwork to the NSSS standard.
| 02SL - Stations (LUL) | Cxxx-NCR-001177 | NCR | Wrong Diameter and Spacing of Links Installed to 500mm section of capping beam |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2013-12-31 | 2013-10-03 23:20 | -89 | 2013-09-18 15:37 | Structural Engineering - Reinforcement | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | To enable easy construction of the stopend (so that it was not located over the middle of a pile) it was moved approximately 480mm to the west. The capping beam is not situated 550mm east of GL6. The reinforcement shear links in the area 1m either side of GL6 are supposed to be B20 at 100mm centres. The location where the links change from B16 to B20 is also the location of the design stopend between pour 3 and pour 4. The reinforcement for pour 3 is detailed on 50055 but the reinforcement in pour 4 is detailed on 50056. When the decision to move the stopend was taken it was assumed that the links would not change and therefore B16 links at 200mm centres were installed. Now looking at drawing 50056 it has become clear that the links in this 480mm long stretch of capping beam (beyond the design stopend location) are wrong.
| 02SL - Stations (LUL) | Cxxx-NCR-001179 | NCR | Blomfiel box - PW469, PW471 & PW473 Steel level exceeding level tolerance |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2013-12-31 | 2013-10-08 11:27 | -84 | 2013-09-27 10:56 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The cage levels in piles PW469, PW471 & PW4730 are at a height of 109.695mATD, 109.690mATD and 109.701mATD respectively meaning that they are 70mm, 65mm and 76mm above the design level of 109.625mATD. This is within the tolerance specified in SPERW Clause B10.4.4 but not to the tolerance stated in RFI LIS-CRL-RFI-Cxxx-00746 of +-50mm. The top of the cages had been set within the tolerance to RFI 000746 prior to extracting the casing. Once the casing had been removed the cage was found to have risen to 109.704mATD. We predict that the cage level has dropped within tolerence over the period of the concrete curing time.
| 02SL - Stations (LUL) | Cxxx-NCR-001180 | NCR | Blomfield box - PW413, PW419 top of steel level exceeding tolerance |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2013-12-31 | 2013-10-18 10:47 | -74 | 2013-09-27 11:10 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The cage levels in piles PW413 & PW419 are at a height of 109.700mATD and 109.715mATD respectively meaning that they are 75mm and 90mm above the design level of 109.625mATD. This is within the tolerance specified in SPERW Clause B10.4.4 but not to the tolerance stated in RFI LIS-CRL-RFI-Cxxx-00746 of +-50mm. The top of the cages had been set within the tolerance to RFI 000746 prior to extracting the casing. Once the casing had been removed the cage was found to have risen. We predict that the cage level has dropped within tolerence over the period of the concrete curing time.
| 02SL - Stations (LUL) | Cxxx-NCR-001181 | NCR | Damaged 50mm Diameter Positional Couplers - Capping Beam Construction in the Grout Box |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2013-12-31 | 2013-10-23 17:54 | -69 | 2013-10-03 13:29 | Civil - Civil Engineering General | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 3 No. 50mm diameter positional couplers were damaged when breaking out the guide wall that surrounded the 900mmm diameter piles within the Grout Box.
| 02SL - Stations (LUL) | Cxxx-NCR-001182 | NCR | Inclined Piezometer 32 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2014-03-31 | 2014-01-20 11:00 | -70 | 2013-10-04 17:07 | Geotechnical Engineering - Geotechnical Monitoring | 5000 |  | Workmanship | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | There has been a setting out error in the installation of Inclined Piezometer 32. This has meant that the lower part of the Piezometer has been struck by the pilot tunnel drive as shown in the attached sketch.
| 02SL - Stations (LUL) | Cxxx-NCR-001183 | NCR | Blomfiel box - PW467 Top of Steel level exceeding allowable tolerance |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2014-10-31 | 2014-02-11 10:15 | -262 | 2013-10-07 10:22 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On completion of breaking down pile PW467 an as-built has been taken on the top of the pile cage. The level taken is at a height of 109.460mATD meaning that it is 165mm below the design level of 109.625mATD and exceeding the allowable tolerence. The top of the cage had been set at 109.663 within the tolerance to RFI 000746.
| 02SL - Stations (LUL) | Cxxx-NCR-001184 | NCR | Blomfield Box - PW407 & PW409 top of steel level exceeding allowable tolerance |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2014-08-31 | 2014-02-11 10:20 | -201 | 2013-10-07 11:46 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On completion of breaking down piles PW407 & PW409 an as-built has been taken on the top of the pile cages. The levels taken are at heights of 109.494mATD and 109.324 respectively meaning that they are 131mm and 301mm below the design level of 109.625mATD exceeding the allowable tolerence. The top of the cage had been set within the tolerance to RFI 000746.
| 02SL - Stations (LUL) | Cxxx-NCR-001186 | NCR | PW417 out of tolerance |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2014-10-31 | 2014-01-13 10:19 | -291 | 2013-10-11 12:53 | Structural Engineering - Concrete Member | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Pile PW417 has been installed out of tolerance. consequently this has obstructed the design thickness off the 250mm thick lining wall- see attached drawing
| 02SL - Stations (LUL) | Cxxx-NCR-001188 | NCR | 8 No. damaged 50mm Diameter Positional Couplers in the Grout Box |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2013-12-31 | 2013-11-05 13:34 | -56 | 2013-10-14 11:00 | Civil - Civil Engineering General | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Whilst the excavator was mucking away materials from site adjacent to the piles it damaged the lips of 8 number 50mm couplers within the piles with its bucket.
| 02SL - Stations (LUL) | Cxxx-NCR-001189 | NCR | Damaged B16 couplers to piles PW473, PW471 and PW469 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2014-03-31 | 2014-01-30 15:18 | -60 | 2013-10-14 11:33 | Civil - Civil Engineering General | 3000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During exposing the B16 couplers withing piles PW473, PW471 and PW469 the heads of the couplers were damaged. This was primarily down to the amount of cover that surrouded the coupler bar which resulted in excess breaking to locate the couplers.
| 02SL - Stations (LUL) | Cxxx-NCR-001190 | NCR | Geothermal Loops |  | Crossrail | PDP | LIS - Liverpool Street Station (Central) |  | 2014-03-31 | 2014-02-10 12:39 | -49 | 2013-10-23 15:56 | Civil - Civil Engineering General | 2500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Further to Cxxx-SVI-00001, Gecco attended site on 22nd October 2013 to flow test the potentially damaged loops. Piles P340, P144, P311 and P345 were tested, with piles P340, P144 and P345 found to be completely blocked (both loops).
| 02SL - Stations (LUL) | Cxxx-NCR-001193 | NCR | Geothermal loop damaged when trimming piles at pile cut-off level |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2014-02-28 | 2013-12-02 11:05 | -88 | 2013-10-31 13:34 | Civil - Excavation | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | One of the Geothermal Loops was damaged at the pile cut-off level, of Pile P134, during the pile break-down activity. A Method Statement and ITP briefing took place this week in which it was specifically stated to be careful around the geothermal pipes and to complete a shallow cut when close to the geothermal loops.
| 02SL - Stations (LUL) | Cxxx-NCR-001194 | NCR | Blomfield Box - Piles P128 & P129 cages exceeding level tolerance |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2013-12-31 | 2013-11-21 10:30 | -40 | 2013-10-31 15:46 | Geotechnical Engineering - Concrete - Bored Pile | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On completion of breaking down piles P128 and P129 the cages have been found to be above the allowable tolerence of +50-100. The levels are as follows, P128 = 106.225ATD and P129 = 106.275ATD which are 225mm and 275mm above the design level of 106.000ATD.
| 02SL - Stations (LUL) | Cxxx-NCR-001195 | NCR | Mini Pile Capping Beam pour 5 low strength 28 day cube results |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2014-02-28 | 2013-12-06 13:24 | -84 | 2013-11-01 12:35 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | The 28 day results for the mini pile capping beam are 47.0 N/mm2 and 48.0 N/mm2 which is below the specified strength of 50.0 N/mm2.
| 02SL - Stations (LUL) | Cxxx-NCR-001196 | NCR | Blocked geothermal loops in P103 and P107 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2014-02-28 | 2014-02-10 12:34 | -18 | 2013-11-18 09:11 | Civil - Civil Engineering General | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | One geothermal loop in each of P103 and P107 is blocked. No flow can be achieved.
| 02SL - Stations (LUL) | Cxxx-NCR-001197 | NCR | Low Concrete Strength Results |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2014-03-30 | 2014-01-13 10:21 | -76 | 2013-12-03 13:21 | Structural Engineering - Concrete Member | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Counterfeit Items | Completed |  | Please be advised that the 28 days design concrete strength (50N/mm2) was not achieved for pours 9, 8A and 7. See attached test results from __ Please be aware that pours 8A and 7 were poured together.
| 02SL - Stations (LUL) | Cxxx-NCR-001198 | NCR | Omitted Mini Prisms Capping Beam |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2014-05-31 | 2014-03-06 22:43 | -86 | 2013-12-04 08:35 | Surveying - Instrumentation and Monitoring | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Mini prisms MP500 series on drawing Cxxx-MMD-C-DDA-C101_Z-31101, were omitted in error.
| 02SL - Stations (LUL) | Cxxx-NCR-001200 | NCR | Blocked geothermal loop - pile PW342 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2014-11-30 | 2014-10-07 12:11 | -54 | 2013-12-05 11:13 | Civil - Civil Engineering General | 500 |  | Damaged | Reject | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | One of the two geothermal loops in pile PW342 is blocked. The loop has been jetted out but it still has no flow.
| 02SL - Stations (LUL) | Cxxx-NCR-001201 | NCR | Broken Instrumentation |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2014-06-30 | 2014-04-11 12:20 | -80 | 2013-12-06 14:17 | Surveying - Instrumentation and Monitoring | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following piezometers are broken due to excavator breaking cable. PZ4 at level 75.9 matd PZ1 at level 73.4 matd
| 02SL - Stations (LUL) | Cxxx-NCR-001202 | NCR | BFB - Pour 1 slab 106.740mATD waterproofing requiring repair. |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2014-03-31 | 2014-01-14 21:25 | -76 | 2013-12-09 10:11 | Civil - Civil Engineering General | 1500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The PrePruf waterproofing coming from pour 1 that is to lap onto pour 5 has been cut short of the required lapping detail. See attached photo's.
| 02SL - Stations (LUL) | Cxxx-NCR-001203 | NCR | blocked geothermal loops - pour 4/ pour 5 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2014-03-31 | 2014-02-10 12:32 | -49 | 2013-12-09 17:36 | Civil - Civil Engineering General | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The following pile numbers in pours 4 and 5 have one blocked loop each: P140, P152, PW338, PW339 and PW351. The loops have all been jetted several times and flow tested. All available methods have been used to attemp to unblock them but none have been successful.
| 02SL - Stations (LUL) | Cxxx-NCR-001205 | NCR | BFB - Pour 5 Slab 106.740mm levels exceeding tolerance |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2014-04-30 | 2014-04-29 09:40 | -1 | 2014-01-06 12:02 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | See the attached sketch showing areas in the slab that are outside of the construction tolerance for SSL of +10/-0mm. The size of the errors would suggest that the root cause is unclear.
| 02SL - Stations (LUL) | Cxxx-NCR-001206 | NCR | Blocked Geothermal Loops - Pour 4 106.74m slab |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2014-01-21 | 2014-01-16 21:40 | -5 | 2014-01-07 11:49 | Civil - Civil Engineering General | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | further to NCR 1203, one geothermal loop in each of PW336, PW335 and PW330 are blocked. The loops have been jetted and no flow can be achieved.
| 02SL - Stations (LUL) | Cxxx-NCR-001207 | NCR | BFB - Missing couplers to pile PW409 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2014-05-31 | 2014-03-12 10:50 | -80 | 2014-01-31 10:27 | Geotechnical Engineering - Concrete - Bored Pile | 3000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The couplers in PW409 appear to be missing. These were checked and confirmed as present when the cage arrived as per the pile log Cxxx-LAO-C-LRC-C101_WS103-50006. It was noticed on some piles that as the cage was lowered to depth the orientation of the cage would start to rotate and not picked up by the engineer. The pile has been broken back to the helical bar and no couplers have been found. If the couplers are found it is anticipated that they would not be orientated such that a threaded bar can be installed.
| 02SL - Stations (LUL) | Cxxx-NCR-001208 | NCR | BFB - Blocked inclinometer tubes on piles PW317, PW327 & PW335 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2014-05-31 | 2014-03-30 16:56 | -62 | 2014-02-04 13:41 | Geotechnical Engineering - Concrete - Bored Pile | 3000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Prior to installation of the I&Ms, inclinometer tubes PW317, PW327 & PW335 were dipped to check depth and have been found with blockages which is believed to be a combibation of bentonite and concrete. Levels of the blockages as below. PW317 = 101.000mATD PW327 & PW 335 = 87.000mATD
| 02SL - Stations (LUL) | Cxxx-NCR-001209 | NCR | Geothermal Loops- SB2 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2014-02-19 | 2014-02-17 23:28 | -2 | 2014-02-05 17:10 | Geotechnical Engineering - Geotechnical Engineering - General | 500 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the pouring slab pour 3 at the -1 level yesterday evening the geothermal pipe work circuit marked SB2 on the attached sketch lost pressure at the manifold connection during the placing of the concrete. Prior to pouring the concrete the circuit had held a 5bar pressure for over 5 hours. As a precaution during the pours the circuits are normally held under a 5bar pressure until the following day of the concrete pour.
| 02SL - Stations (LUL) | Cxxx-NCR-001210 | NCR | Geothermal Loop Blockage - Blomfield Box |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2014-05-31 | 2014-02-18 10:12 | -102 | 2014-02-06 12:11 | Geotechnical Engineering - Geotechnical Engineering - General | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | PW321 has two blocked loops, this is located in pour 6. Additionally to this PW316 has one blocked loop. The loops have been jetted for at least 45 minutes and no flow can be achieved.
| 02SL - Stations (LUL) | Cxxx-NCR-001211 | NCR | BFB - Damage to multiple lining wall couplers in the grout box piles |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2014-05-31 | 2014-03-18 23:21 | -74 | 2014-02-10 12:29 | Civil - Civil Engineering General | 2500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A number of the lining wall couplers were damaged when exposing them. Although in some instances steps to prevent damage were taken by installing sacrificial plastic caps into the coupler prior to installation of the pile reinforcement cage this was not completed in all instances.
| 02SL - Stations (LUL) | Cxxx-NCR-001212 | NCR | Geothermal loop bloackages Pour 6 (106.74m slab) |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2014-05-31 | 2014-03-14 15:01 | -78 | 2014-02-26 17:03 | Civil - Civil Engineering General | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In pour 6 1 loop in each of pile numbers PW304, PW368, PW367, PW359 and PW357 are completely blocked. No flow can be achieved.
| 02SL - Stations (LUL) | Cxxx-NCR-001213 | NCR | BFB - Orientation and missing couplers in piles PW401 and PW463 respectively |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2014-06-30 | 2014-04-01 13:03 | -90 | 2014-02-28 10:05 | Geotechnical Engineering - Concrete - Bored Pile | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 1. While exposing the couplers at the 101.500mATD pile PW401 couplers have been found to be out of orientation tolerance, however the coupler bars have been installed without any clashes to the couplers in adjacent pile PW477. See attached sketch EO_SK_002 2. Also when exposing the couplers, pile PW463 has 2 missing couplers as show on attached sketch EO_SK_02.
| 02SL - Stations (LUL) | Cxxx-NCR-001216 | NCR | Lining Wall Couplers GL 3/C |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2014-05-31 | 2014-04-30 09:55 | -31 | 2014-03-12 11:56 | Structural Engineering - Reinforcement | 5000 |  | Damaged | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Some of the couplers in the final lining wall pour GL 3/C are not accepting the thread of the positional attachment that forms the female part of the coupler. This is for 2 reasons, either there is slight damage to the head of the coupler or the orientation is such that it will not allow the positional part of the coupler or the threaded bar to be installed. Examples of the problems can be seen in the attached photos and described below: IMG_2538 – Here the couplers in MP125 have twisted when being installed. They are facing the adjacent pile MP126 and therefore cannot be installed. IMG_2551 – The couplers are orientated slightly differently across the pile. While the reinforcement misses the majority of the bars the congestion of the reinforcement resulted in the occasional clash being inevitable. IMG_2545, IMG_2546 and IMG_2547 – A large number of the couplers do not accept the female part of the positional coupler. While some have visible nicks taken out of them through exposing the couplers, a number (as shown in the images) have no visible damage. The thread appears very delicate and potentially slight oxidisation of the thread is preventing the positional section from screwing in.
| 02SL - Stations (LUL) | Cxxx-NCR-001217 | NCR | Piezometer PZ32 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2014-11-30 | 2014-11-27 09:28 | -3 | 2014-03-18 11:21 | Surveying - Instrumentation and Monitoring | 5000 |  | Damaged | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | Piezometer PZ32 as marked on attached sketch has stopped working on 31/01/2014. The piezometer was more than likely struck by the construction of the tunnel enlargement of RCE-E. See attached incident report. This piezometer cannot be recovered anymore.
| 02SL - Stations (LUL) | Cxxx-NCR-001218 | NCR | Errors in Material Compliance Requests |  | Crossrail | PDP | LIS - Liverpool Street Station (Central) |  | 2014-06-16 | 2014-04-18 20:24 | -59 | 2014-03-18 16:54 | Materials - Approval | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | A number of examples of incomplete or incorrect MCRs have been seen recently, indicating that the prepare, check and approval system is not workign effectively. Examples of issues include: 'CE Marking Required' field being ticked with no Declaration of Performance being attached, or a statement from the Supplier that the material is not manufactured to a harmonised standard, incomplete decal, wrong MCR template and no ISO 9001 certificate or certificate number for the supplier.
| 02SL - Stations (LUL) | Cxxx-NCR-001219 | NCR | Change control of the Contractors design management plan |  | Crossrail | PDP | LIS - Liverpool Street Station (Central) |  | 2015-03-31 | 2015-06-19 13:09 | 80 | 2014-03-19 13:24 | Mechanical - Mechanical Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Liverpool Street Station Permanent Works Design Management Plan Cxxx-LAO-Z-STP-C101_WS102-50003 rev 3 not current at time od QS502-05 surveillance. Reffer to surveillance report for details.
| 02SL - Stations (LUL) | Cxxx-NCR-001220 | NCR | Contractors design review records were not fully available |  | Crossrail | PDP | LIS - Liverpool Street Station (Central) |  | 2014-09-30 | 2014-06-13 11:58 | -109 | 2014-03-19 13:30 | Mechanical - Mechanical Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | Two Asite design review records, both for Cxxx - Liverpool Street Station Blomfield Box - Stage F MEP Drawings – Volume 5 – Public Health Drawings, issued for review by the designer on the 28th September and 8th October document the Contractors comments as “Comments made directly on DG hard copy & See attached mark up” respectively. The Contractor confirmed that the DG hard copy and attached mark up were not available
| 02SL - Stations (LUL) | Cxxx-NCR-001221 | NCR | Contractors design statements were not accepted |  | Crossrail | PDP | LIS - Liverpool Street Station (Central) |  | 2014-08-31 | 2014-06-13 13:17 | -79 | 2014-03-19 15:08 | Mechanical - Mechanical Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | Design Statements Cxxx-LAO-Z-XST-C101-50005 rev 1.0, Cxxx-LAO-Z-XST-C101-50004 rev 1.0 and Cxxx-LAO-Z-XST-C101-50006 rev 1.0 at time of surveillance were not accepted ( at DECAL code 2)
| 02SL - Stations (LUL) | Cxxx-NCR-001222 | NCR | BFB - Cover to pile PW477 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-05-30 | 2016-05-26 14:09 | -4 | 2014-03-27 13:38 | Geotechnical Engineering - Concrete - Bored Pile | 1500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Below the soffit of the 106.740 slab in the grout box a section of approximately 700mm high to pile PW477 has a cover zone out of tolerance. See attached photo. We have reviewed the installation of the piles in this area (sequence, timing, concrete etc…) and believe this issue was not caused by the construction or the sequencing of the pile (see attached sequence). We believe that the ground has given way at that location after pulling the casing out, this potentially due to the presence of the North Vault in that area (see attached sketch __-070-SK01). The mini piles were constructed in order to hold the road and avoid any potential caving in, however we believe that obstructions were encountered up to 106mATD whilst constructing the mini piles, which would suggest that the north vault was ground bearing at that level and could have therefore pushed the concrete into PW477 when we retrieved the casing. The North Vault were not in the GBR and therefore any unexpected consequences relating to these vaults are outside of our scope.
| 02SL - Stations (LUL) | Cxxx-NCR-001223 | NCR | BFB - Concrete void to the soffit of RC beam on GL 6/C-D on the 106.740m slab |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-10-31 | 2015-10-27 10:35 | -4 | 2014-04-10 08:27 | Civil - Civil Engineering General | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On exposing the soffits to the 106.740m slab during the top down excavation the RC beam on GL 6/C-D has been found to have a void in the concrete soffit, see atttached photo.
| 02SL - Stations (LUL) | Cxxx-NCR-001224 | NCR | Damage Slab Couplers- 101.340 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2014-10-31 | 2014-08-06 10:13 | -86 | 2014-04-15 09:58 | Structural Engineering - Concrete Member | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the exposing of the pile couplers for the 101.40 slab a number of them has been damaged. Attached is a sketch showing the location of each damage coupler?
| 02SL - Stations (LUL) | Cxxx-NCR-001225 | NCR | RE: BFB - Damage to concrete edges/openings on the 106.740 SSL during excavation. |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-12-31 | 2015-11-12 16:48 | -49 | 2014-04-22 08:00 | Civil - Civil Engineering General | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the excavation of the 106.740 slab down to the 101.340 slab some of the conrete has been damaged to the edges/openings of the slab.
| 02SL - Stations (LUL) | Cxxx-NCR-001227 | NCR | RE: BFB - Damaged lining wall couplers from 101.340 SSL to 106.740 SSL |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2014-07-31 | 2014-06-30 11:01 | -31 | 2014-05-02 17:34 | Civil - Civil Engineering General | 1500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | On exposing the lining wall couplers in the piles the head of 20 female couplers have been slighly damaged thus not allowing the the male coupler bar to be threaded into the female head. This currently equates to 3% although this is not the full survey due to the fact that we are unble to access the couplers at the higher position at this time. As requested in Cxxx-NCR-001216 please find attached elevations showing the exact location of the damaged couplers. This will be updated and submitted once access is available.
| 02SL - Stations (LUL) | Cxxx-NCR-001228 | NCR | BFB - Void in pile PW310 between level 95.580 SSL & 101.340 SSL |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2014-08-31 | 2014-06-30 11:05 | -62 | 2014-05-15 21:13 | Geotechnical Engineering - Concrete - Bored Pile | 1000 |  | Material | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the excavation for the 95.580 SSL pile PW310 has been found to have a void in the concrete exposing the reinforcement. See attached photo.
| 02SL - Stations (LUL) | Cxxx-NCR-001229 | NCR | BFB - Damaged Geothermal loop in pile PW310 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2014-08-31 | 2014-06-30 10:55 | -62 | 2014-05-27 11:59 | Civil - Civil Engineering General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | While breaking back the void in pile PW310 as per previously raised NCR Cxxx-NCR-001228 we have damaged the geothermal loop, see attached photo. Also see attached 'Gecco-LS1-SE2' showing the affected loop of concern.
| 02SL - Stations (LUL) | Cxxx-NCR-001230 | NCR | BFB - Grout box capping as-builts show vertical tolerance exceeded |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2014-06-11 | 2014-06-10 13:21 | -1 | 2014-05-28 12:34 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Please see attached as-builts for the grout box capping beam that shows in certain areas that the vertical tolerance of +-10mm has been exceeded although plan position has been maintained. The worst case is scenario is 20mm out of verticality
| 02SL - Stations (LUL) | Cxxx-NCR-001231 | NCR | BFB - Damaged slab couplers in the 95.580 SSL |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2014-08-31 | 2014-06-29 20:20 | -63 | 2014-05-29 14:42 | Civil - Civil Engineering General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On exposing the slab couplers for the 95.580 SSL we have damaged 3 couplers which equates to 2.5% of the 122, 2 No. 20mm couplers and 1 No. 32mm coupler.
| 02SL - Stations (LUL) | Cxxx-NCR-001232 | NCR | BFB - Plunge column bracket holes at the wrong height |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2014-09-30 | 2014-07-01 14:11 | -91 | 2014-06-03 08:17 | Geotechnical Engineering - Concrete - Bored Pile | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Some of the holes drilled on the two plunge columns (P202 & P204) in the stair core wall were drilled to the wrong level. The holes on the west side of the plunge column closest to gridline B5 (P204) are approximately 200mm too high. All of the holes at the 95 level slab on the plunge column closest to gridline B4 (P202) are approximately 200mm too high. If left at these levels they will clash with the steel reinforcement.
| 02SL - Stations (LUL) | Cxxx-NCR-001233 | NCR | Moor House Shaft – Lining wall plan shape |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-12-31 | 2016-11-16 16:28 | -45 | 2014-07-08 10:55 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the first concrete pour for the 500mm thick lining wall the rate of rise for the shutters was not adhered to. This resulted in the shutters moving during the pour. The shutters have moved in 25-40mm on two sides and out 20mm on the opposite sides forming an ellipse. Due to the nature of the shuttering system and the movement witnessed in two directions the volume of the shaft is assumed to be the same as the design. Also note that the shaft has changed from a 950mm thick wall to a 500mm thick wall at this location. Therefore the volume of air in this section will be greater than the amount designed, which would be based on the volume passing through the 950mm section. The reinforcement has moved with the shutters so the cover to the reinforcement is as per design. The lining wall is structurally sound but does not adhere to the construction tolerances shown on drawing Cxxx-MMD-C-DDJ-C101-10011 section C6.
| 02SL - Stations (LUL) | Cxxx-NCR-001234 | NCR | BFB - Damaged slab couplers to the 89.820 SSL |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2014-07-23 | 2014-07-29 09:37 | 6 | 2014-07-09 10:03 | Civil - Civil Engineering General | 3000 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On exposing the slab couplers for the 89.820 SSL we have damaged 11 of the couplers out of 132 which equates to 8.3%. Please see attached marked up sketch '89 Slab Coupler Damage.pdf' that identifies the damaged slab couplers which are the top 2 positions on the sketch. At the piling phase the waler at this level was 780mm thick, this has since been increased to 1140mm which means that the slab couplers are 180mm above the centre line of the waler beam. The increased depth also means that 2 of the lining wall couplers from the wall below will now be within the waler beam. We have also damaged 3No. of these B20 couplers also shown on the attached sketch as the bottom 2 positions.
| 02SL - Stations (LUL) | Cxxx-NCR-001236 | NCR | BFB - Damaged Geothermal loop in pile PW354 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2014-10-31 | 2014-08-27 10:31 | -65 | 2014-07-14 09:02 | Civil - Civil Engineering General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | While breaking back pile PW354 to locate the couplers we have damaged the geothermal loop, see attached photo.
| 02SL - Stations (LUL) | Cxxx-NCR-001237 | NCR | Lack of hydrophilic strip in the kicker construction joint of the Moor House Shaft lining wall |  | Crossrail | PDP | LIS - Liverpool Street Station (Central) |  | 2015-12-31 | 2015-09-20 20:41 | -102 | 2014-07-22 12:29 | Civil - Civil Engineering General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | A hydrophilic water stop has not been provided in the kicker construction joint at the base of Moor House Shaft, which is a non-conformance with the following requirements: Civil and Structural specification Cxxx-MMD-C-RSP-C101-50006 clause KF10.3212 a) requires 'hdrophilic water stops shall be incorporated at all construction joints as indicated on the Drawings'. Waterproofing Details drawing Cxxx-MMD-C-DDD-C101-10702 indicatively show a hydrophilic strip in the construction joint between the base slab and wall above. Drawing Cxxx-MMD-C-DDJ-C101-10011 items W6 and W7 requires the contractor to provide detailed proposals for waterproofing and to waterproof all construction joints as indicatively shown on drawing Cxxx-MMD-C-DDD-C101-10702.
| 02SL - Stations (LUL) | Cxxx-NCR-001238 | NCR | BFB - 95.580m slab levels out of tolerance |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2014-10-31 | 2014-09-18 09:55 | -43 | 2014-07-25 12:53 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Please see the attached marked up as-built that highlights the areas in the slab that are outside of the construction tolerance for SSL of +10/-0mm.
| 02SL - Stations (LUL) | Cxxx-NCR-001239 | NCR | Broadgate Ticket Hall pile mat works commencing without accepted ITP |  | Crossrail | PDP | LIS - Liverpool Street Station (Central) |  | 2014-10-28 | 2014-08-27 17:05 | -62 | 2014-07-30 23:19 | Civil - Fill | 500 |  | Planning | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | The ITP for the piling mat, including fill to the existing LU substation was accepted on 28th July 2014, after the works had commenced. Part 20.5 of Volume 2B requires that the contractor shall not commence relevant works until the ITP has been accepted.
| 02SL - Stations (LUL) | Cxxx-NCR-001240 | NCR | 106.740 Slab soffit out of tolerance |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2014-11-30 | 2014-09-14 21:43 | -77 | 2014-08-06 13:52 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The areas marked green in the attached soffit asbuilt survey are out of tolerance.
| 02SL - Stations (LUL) | Cxxx-NCR-001241 | NCR | 101 beams out of tolerance |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-07-31 | 2015-07-23 21:08 | -8 | 2014-08-06 13:51 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In some locations as shown in the marked up sketch attached the beams are out of tolerance. The thickness tolerance as given on the General Notes drawing (Cxxx-MMD-C-DDJ-C101-10011) is +15/-0mm. In the locations marked the thickness of the beams is slightly smaller than the design.
| 02SL - Stations (LUL) | Cxxx-NCR-001242 | NCR | BFB - Damaged lining wall couplers from 89.820 SSL to 95.580 SSL |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-05-31 | 2014-12-18 09:21 | -164 | 2014-08-12 11:58 | Civil - Civil Engineering General | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On exposing the lining wall couplers in the piles from the 89 slab to the 95 slab we have currently damaged 12 out of the 745 female couplers. Please see attached sketch for the location of the couplers. On the sketch the coupler locations that are not circled have not yet been exposed. One these have been exposed the sketch will be updated and re-submitted
| 02SL - Stations (LUL) | Cxxx-NCR-001244 | NCR | BFB - Temporary/Permanent openings out of tolerance to the 101.340 SSL |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-05-31 | 2014-12-18 09:22 | -164 | 2014-08-18 10:32 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On completion of our as-builts to the openings in the 101.340 SSL we have found in 2 areas that we have exceeded the tolerance of +/- 20mm on plan as per Cxxx-RFI-002057 and the vertical tolerance of +/- 10mm. See attached marked up as-built.
| 02SL - Stations (LUL) | Cxxx-NCR-001245 | NCR | BFB - Damaged Geothermal Loop in pile PW342 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2014-11-30 | 2014-11-11 11:24 | -19 | 2014-08-21 15:27 | Civil - Civil Engineering General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | While breaking back pile PW342 to locate the couplers we have damaged the geothermal loop, see attached photo.
| 02SL - Stations (LUL) | Cxxx-NCR-001246 | NCR | Column downstand kicker plan position out of tolerance |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-05-31 | 2015-01-29 13:32 | -122 | 2014-08-22 15:15 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | On completion of our as-builts to the downstand kickers in the 89.820 SSL we have found one column B7 that we have exceeded the tolerance of +/- 20mm on plan as per the General Notes drawing Cxxx-MMD-C-DDJ-C101-10011. The kicker and the coupler bars have been placed 50mm North of the plan position. See attached marked up as-built.
| 02SL - Stations (LUL) | Cxxx-NCR-001247 | NCR | Blocked Extensometers in Blomfield Box shaft |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-05-31 | 2015-02-20 10:46 | -100 | 2014-08-27 11:08 | Surveying - Instrumentation and Monitoring | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Please be aware that Extensometers EX1, EX2, EX3, EX4 and EX5 are at the moment blocked and no measurements can be recorded in accordance with specification Cxxx-MMD-C-RSP-C101-50005 and Cxxx answer of Cxxx-RFI-002084. Cxxx have attempted to remove the blockage the traditional and previously successful way but have not been able to remove the blockages. Different equipment is to be delivered and Cxxx to clear blockage as soon as possible. Cxxx will record and distribute measurements as soon as the blockages are cleared.
| 02SL - Stations (LUL) | Cxxx-NCR-001248 | NCR | BTH - Temporary Piles TW02 & AD01 out of positional tolerance |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2014-11-30 | 2014-09-16 08:57 | -75 | 2014-08-29 17:57 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Temporary Pile No.s TW02 & AD01 have been constructed 8.8mm and 6mm out of positional tolerance respectively.
| 02SL - Stations (LUL) | Cxxx-NCR-001249 | NCR | Damaged Geothermal Loop in piles PW313 and PW322 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2014-11-30 | 2014-11-14 10:16 | -16 | 2014-09-02 08:57 | Civil - Civil Engineering General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | While breaking back piles PW313 and PW322 to locate the couplers we have damaged the geothermal loop.
| 02SL - Stations (LUL) | Cxxx-NCR-001250 | NCR | BTH-Top of cage level high for plile F103 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2014-11-30 | 2014-09-30 10:33 | -61 | 2014-09-08 18:09 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The cage for pile ref. F103 was found to be out of level tolerance on the 05/09/14. The current cage positional tolerance as referenced in KP10-3211 and most specifically in clause B3.4.1 of the Specification for Piling and Embedded Retaining Walls Second Edition is +150mm -50mm. The cage for pile ref. F103 was installed to the correct level but was found to be 130mm higher than the allowable level tolerance, following the casing extraction.
| 02SL - Stations (LUL) | Cxxx-NCR-001251 | NCR | BFB Damaged Slab Couplers 84.060 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2014-11-30 | 2014-10-03 09:33 | -58 | 2014-09-05 14:09 | Civil - Civil Engineering General | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On exposing the slab couplers for the 84.060 SSL we have damaged 7 of the couplers out of 132 which equates to 5.3%. Please see attached marked up sketch '84 Slab Coupler Damage.pdf' that identifies the damaged slab couplers.
| 02SL - Stations (LUL) | Cxxx-NCR-001252 | NCR | Damaged Geothermal Loop |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-05-31 | 2015-01-30 16:22 | -121 | 2014-09-18 07:22 | Civil - Civil Engineering General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During pressure testing on circuits SD1 and SC2, on the 16th September it became apparent that they were not holding pressure. The reasoning for this is that during phase 2 of the dewatering installations the auger of the rig damaged geothermal loops in piles (PW303) and (PW353 or PW354). The damage occurred between level 75 - 76m ATD while drilling IDW1 and IDW8 (see attached for circuit sketches).
| 02SL - Stations (LUL) | Cxxx-NCR-001253 | NCR | Damaged Geothermal Loop PW316 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2014-11-30 | 2014-10-22 13:31 | -39 | 2014-09-19 13:06 | Civil - Civil Engineering General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the drilling works for the lining wall between 89 - 95m ATD geothermal loop 2 within pile PW316 was damaged. This loop resides within circuit SA1.
| 02SL - Stations (LUL) | Cxxx-NCR-001254 | NCR | Extension of Construction Time - pile ref. B125 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2014-11-30 | 2014-11-10 19:38 | -20 | 2014-09-20 16:57 | Civil - Geotechnical Engineering | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The time period for the construction of pile ref. B125 was 33h as the pile was excavated in the morning of the 16/09/14 and the concreting operation completed on the 17/09/14 at 17:00
| 02SL - Stations (LUL) | Cxxx-NCR-001255 | NCR | Calibration records and equipment schedule were not provided following CRL surveillance on Piling at BTH. |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2014-12-21 | 2014-12-14 22:48 | -7 | 2014-09-22 08:42 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | During Crossrail surveillance dated 4th September 2014 a request was made for cube mould and flow equipment calibration records associated with BTH piling works. A ‘monthly check’ spreadsheet was provided for test equipment, however date of delivery, implementation date etc was missing on some of the items, in particular flow test equipment. A request was made for the calibration certificates of the cube moulds and flow test equipment where it was detailed on the spreadsheet that they were first implemented on site February 2013, however no records were provided other than the supplier certificates provided following initial purchase. UKAS Publication LAB 21, Calibration and Measurement Traceability for Construction Materials Testing Equipment states a yearly level 3 check is required for both cube mould and flow test equipment. Additionally Works Information Vol 2B Part 20.8 states “The Contractor shall maintain a schedule of all inspection, measuring and test equipment used for works that includes records of the calibration of such equipment to nationally recognised standards”. This NCR was raised following the surveillance as no appropriate schedule of equipment with appropriate records to demonstrate in date calibration could be provided.
| 02SL - Stations (LUL) | Cxxx-NCR-001256 | NCR | BFB - Plunge column on GL B/6 outside of the allowable tolerance at the 84.060 SSL |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2014-10-03 | 2014-10-03 09:59 | 0 | 2014-09-24 14:15 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On completion of the excavation and blinding for the soffit of the 84.060 SSL it has been found that the plunge column is 31.35mm out of the allowable tolerance. This has been taken from the installation tolerances of 20mm for plan position and 1/400 verticality which equates to 78.65mm but excludes any fabrication tolerances of the plunge column. This now only provides 80mm cover from the west face of the plunge column to the edge of the concrete face. Currently the reinforcement has been designed to have 2x5 B40 bars on the side face of beam B23 and a single line of B40 bars for the column encasement as detailed on CADS drawing Cxxx-LAO-C-DWG-C101_WS103-50265 from design intent drawing Cxxx-MMD-C-DDL-C101_7-33701 which creates a cover issue, see attached mark up. Please note that if the column had been installed perfectly plumb as per the plan position without using any of the available tolerance then Cxxx would still have been unable to install the detailed reinforcement due to the space available and the fabrication tolerances. On plan the available space is 190mm but the current design would require 193mm. This is made up from 35mm cover 20mm for the links and 3x46mm for the side bars and the couplers for the column encasement.
| 02SL - Stations (LUL) | Cxxx-NCR-001258 | NCR | BTHPIL - Pile Verticality B165 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-01-31 | 2014-11-13 20:55 | -79 | 2014-10-20 12:50 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Refer to Pile # B165. Crossrail Piling Specification, Clauses KP10.3211 & KP10.3213 allow maximum tolerance for verticality of 1:150 which equates to 6.66mm / metre. Casing As-Built for for this pile as recorded on form QR7 in this pile records records the casing verticality as 1:100 or 10mm / metre off vertical in the West direction. Total casing length was 10.0m BGL. Constructed pile length is 31.5m
| 02SL - Stations (LUL) | Cxxx-NCR-001259 | NCR | BTHPIL - Pile Verticality B163 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-01-31 | 2014-12-05 15:43 | -57 | 2014-10-20 13:08 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Refer to Pile # B163. Crossrail Piling Specification, Clauses KP10.3211 & KP10.3213 allow maximum tolerance for verticality of 1:150 which equates to 6.66mm / metre. Casing As-Built for for this pile as recorded on form QR7 in this pile records records the casing verticality as 1:125 or 8mm / metre off vertical in the North direction. Total casing length was 10.0m BGL. Constructed pile length is 31.5m
| 02SL - Stations (LUL) | Cxxx-NCR-001260 | NCR | BTHPIL - Pile Verticality B162 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-08-01 | 2015-03-06 16:51 | -148 | 2014-10-20 13:21 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Refer to Pile # B162. Crossrail Piling Specification, Clauses KP10.3211 & KP10.3213 allow maximum tolerance for verticality of 1:150 which equates to 6.66mm / metre. Casing As-Built for for this pile as recorded on form QR7 in this pile records records the casing verticality as 1:125 or 8mm / metre off vertical in the West direction. Total casing length was 10.0m BGL. Constructed pile length is 31.5m
| 02SL - Stations (LUL) | Cxxx-NCR-001261 | NCR | BTHPIL - Pile Verticality TW11 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-01-31 | 2014-11-13 16:44 | -79 | 2014-10-20 13:46 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Refer to Pile # TW11. Crossrail Piling Specification, Clauses KP10.3211 & KP10.3213 allow maximum tolerance for verticality of 1:150 which equates to 6.66mm / metre. Casing As-Built for for this pile as recorded on form QR7 in this pile records records the casing verticality as 1:83 or 12mm / metre off vertical in the West direction. Total casing length was 10.0m BGL. Constructed pile length is 34.5m
| 02SL - Stations (LUL) | Cxxx-NCR-001262 | NCR | BTH-Top of cage level high for plile B119 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-06-30 | 2015-07-09 13:53 | 9 | 2014-10-21 14:30 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The cage for pile ref. B119 was found to be out of level tolerance on the 12/09/14. The current cage positional tolerance as referenced in KP10-3211 and most specifically in clause B3.4.1 of the Specification for Piling and Embedded Retaining Walls Second Edition is +150mm -50mm. The cage for pile ref. B119 was installed to the correct level but was found to be 50mm higher than the allowable level tolerance, following the casing extraction. The level to which the reinforcement bars extend complies with the Cxxx requirements set out on drawing ref. Cxxx-MMD-C-DDD-C101-04401 rev C05. The coupler levels in this pile could be up to 200mm higher than the level specified in drawing ref. Cxxx-MMD-C-DDD-C101-41110 and Sketch ref. Cxxx-MMD-C-DDH-C101-60056 but remain within the slab.
| 02SL - Stations (LUL) | Cxxx-NCR-001263 | NCR | BTH-Top of cage level high for plile B122 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-06-30 | 2015-07-08 16:21 | 8 | 2014-10-21 14:31 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The cage for pile ref. B122 was found to be out of level tolerance on the 15/09/14. The current cage positional tolerance as referenced in KP10-3211 and most specifically in clause B3.4.1 of the Specification for Piling and Embedded Retaining Walls Second Edition is +150mm -50mm. The cage for pile ref. B122 was installed to the correct level but was found to be 130mm higher than the allowable level tolerance, following the casing extraction. The level to which the reinforcement bars extend complies with the Cxxx requirements set out on drawing ref. Cxxx-MMD-C-DDD-C101-04401 rev C05. The coupler levels in this pile could be up to 280mm higher than the level specified in drawing ref. Cxxx-MMD-C-DDD-C101-41110 and Sketch ref. Cxxx-MMD-C-DDH-C101-60056 but remain within the slab.
| 02SL - Stations (LUL) | Cxxx-NCR-001264 | NCR | BTH-Top of cage level high for plile B123 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-06-30 | 2015-07-08 16:03 | 8 | 2014-10-21 14:56 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The cage for pile ref. B123 was found to be out of level tolerance on the 26/09/14. The current cage positional tolerance as referenced in KP10-3211 and most specifically in clause B3.4.1 of the Specification for Piling and Embedded Retaining Walls Second Edition is +150mm -50mm. The cage for pile ref. B123 was installed using hanging chains as the reinforcement supplier did not include any cage feet with this load. Cage feet allows for a more robust reinforcement positioning but dependent on pile geometry, cage feet are not desirable for lengths of over 1m. The cage was hung during concreting, chains removed and casing extracted. The action of extracting the casings caused the cage to drop in the pile by 136mm lower than the allowable level tolerance. The level to which the reinforcement bars extend complies with the Cxxx requirements set out on drawing ref. Cxxx-MMD-C-DDD-C101-04401 rev C05. The coupler levels in this pile could be up to 200mm lower than the level specified in drawing ref. Cxxx-MMD-C-DDD-C101-41110 and Sketch ref. Cxxx-MMD-C-DDH-C101-60056 but remain within the slab.
| 02SL - Stations (LUL) | Cxxx-NCR-001266 | NCR | BFB - Plunge column B6 out of tolerance to soffit of 78.120 SSL |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-01-31 | 2014-11-14 12:20 | -78 | 2014-10-24 15:01 | Structural Engineering - Structural Engineering - General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | With reference to previous NCR 1256 and RFI 2192 we have completed the excavation to the soffit of the 78.120 SSL around plunge column B6. Our as-built shows that the column is now 91.35mm out of the allowable verticality taken from the 1/400mm installation vertical tolerance and the 20mm tolerance for plan position. This now only provides 20mm cover from the west face of the plunge column to the edge of the concrete face of the beam.
| 02SL - Stations (LUL) | Cxxx-NCR-001267 | NCR | NCR - BFB - 89.820m slab levels out of tolerance |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-05-31 | 2014-11-28 10:44 | -184 | 2014-11-07 15:23 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Please see the attached marked up as-builts that highlight the areas in the slab that are outside of the construction tolerance for the SSL of +10/-0mm. Proposed Answer: We propose to do nothing as this is similar to the NCR raised for the 106.740 slab (Cxxx-NCR-001205-01) and the 95.580 slab (Cxxx-NCR-001238).
| 02SL - Stations (LUL) | Cxxx-NCR-001268 | NCR | NCR - BFB - 95.580m and 89.820m slab soffit levels out of tolerance |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2014-11-21 | 2014-11-24 14:36 | 3 | 2014-11-07 15:33 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Please see the attached marked up as-builts that highlight the areas in the slab that are outside of the construction tolerance for the soffit of +0/-10mm.
| 02SL - Stations (LUL) | Cxxx-NCR-001269 | NCR | Earth resitivity testing |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-01-31 | 2014-11-28 10:49 | -64 | 2014-11-13 08:25 | Electrical - General | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Insufficient work planning by the subcontractors | Completed |  | The Soil Resistivity Test was carried out in Blomfield box to confirm the electrical resistance of the soil. This was carried out on 4/11/2014 The Soil Resistivity Test was not included within the ITP (Cxxx-LAO-E-ITP-C101_WS103-50021)
| 02SL - Stations (LUL) | Cxxx-NCR-001270 | NCR | Broken strain gauge in concrete pour level 78.120 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-02-28 | 2014-12-02 23:46 | -88 | 2014-11-18 16:07 | Surveying - Instrumentation and Monitoring | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Please be aware that 1no strain gauge in below location is failing to respond since the concrete was poured on Saturday 15th November. After extensive investigation, the conclusion is that the strain gauge is broken during the concrete placement. It is the strain gauge location 1 (SG106e) strain gauge. See sketch for strain gauge position attached.
| 02SL - Stations (LUL) | Cxxx-NCR-001271 | NCR | BTHPIL - Mislaid Cube Set 28th August '14 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-03-31 | 2014-12-16 21:25 | -105 | 2014-11-24 18:09 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The sampling regime for BTHPIL for concrete testing is 50m3 as per SPERW B19.8.5 & KF10-04 table. The set of cubes for 28th August was taken to the collection area at Blomfield and collected by __ or mislaid before Cxxx Engineer had a chance to mark up the cubes with a construction date, pile reference and testing age etc.
| 02SL - Stations (LUL) | Cxxx-NCR-001272 | NCR | NCR - BFB - 84.060m sofft levels out of tolerance |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-05-31 | 2015-03-24 15:31 | -68 | 2014-11-26 06:43 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Please see attached marked up as-builts that highlight the areas of the slab soffit that are outside of the construction tolerance for the SSL of +0/-10mm. Proposed Answer: We propose to do nothing as this is similar to the NCR rasied for the 106.740 slab (Cxxx-NCR-001205-01), the 95.580 slab (Cxxx-NCR-001238) and the 89.820 slab (Cxxx-NCR-001267).
| 02SL - Stations (LUL) | Cxxx-NCR-001273 | NCR | NCR-BTHPIL- Unidentified Service Strike at TW40 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-08-31 | 2015-08-28 14:40 | -3 | 2014-12-09 13:03 | Civil - Geotechnical Engineering | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | External Phenomenon - Not Defined | Completed |  | Concrete loss was experienced after the casing was removed from the pile. The initial concrete level right before the casing extraction was about 1m above platform level (114.5 mATD). Once the casing was extracted the concrete level dropped approximately 6m below platform level (108.5 mATD). The predicted concrete level it was 113.000 mATD. An extra 5m3 of concrete were requested to to top up the pile but the final concrete level after the pouring only reached 110.000 mATD. Another 5m3 extra were poured next day (27/11/14) and final concrete level (113.000 mATD) was achieved. The expected volume of concrete was 9.5m3 but a total of 19.5m3 were used to complete the pile.
| 02SL - Stations (LUL) | Cxxx-NCR-001274 | NCR | NCR-BTHPIL- Cold Joint Pile B174 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-06-30 | 2015-07-22 07:16 | 22 | 2014-12-09 14:08 | Civil - Geotechnical Engineering | 10000 |  | Incomplete Works | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Pile B174 was not able to be fully concreted on the same day. First concrete load started at 12:10 the 2nd of December the level reached by the first concrete loads was approximately 94 mATD. At this point the crowd rope of the rig started to break down and it would have been unsafe to proceed. With the rig out of service casing from Pile B174 could not be extracted therefore concreting of the pile could not be completed. In first instance we were adviced by Crossrail to concrete to a level rigth before the slab couplers lap bars (112.200 mATD). This concrete discharge took place between 14:25 and 14:45. A final concrete load was discharge between 16:15 and 16:25 in order to reach the bottom of the casing (103.700 mATD) avoiding ingress of water and soil from the ground. Not further concreting happened that day. Next day it was agreed to fill up the bore with shingle up to top of steel level (107.812 mATD) and top up the pile with concrete.
| 02SL - Stations (LUL) | Cxxx-NCR-001275 | NCR | BTHPIL - B101 - Final Top Of Concrete Level lower than Cut Off Level |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-09-30 | 2015-09-30 10:41 | 0 | 2014-12-09 07:35 | Civil - Geotechnical Engineering | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | From a level of 111.500/112.000 mATD to a level of 106.000mATD we have encountered various man made obstructions which were not identified in the SI information and are more adverse than on the GBR. These obstructions were made of concrete (reinforced and unreinforced) and brickwork and we recovered what appeared to be a concrete kerbstone or similar also (see attached pictures). An overall of 1 hours was required to core / break through the obstructions on B101 and ensure verticality as per required tolerances despite the adverse conditions. this pile was fully cased to a toe level of 85.9mOD. During the extraction of this casing in sections during the concreting works, the concrete was continually topped up to ensure that the Top Of Concrete level was maintained and that when the final section of casing (10m) was extracted by the rig, the TOC level would occur within the guidewall to allow a maximum trimming level of 1.0m (113.000mATD PPL to 112.000mATD TOC level) The final section (10m long) of casing, prior to extraction, had TOCasing lvl at 115.5 mATD. TOConcrete was 115.300 mATD. When final section was removed, the concrete slumped to a TOC level of 111.400mATD As some of the made ground fell in on top of the concrete during casing extraction, and was inaccessible and could not be removed, top up with concrete on top of the contaminated section was not carried out as it was felt that this would compound tthe difficulty in executing the remedial works.
| 02SL - Stations (LUL) | Cxxx-NCR-001276 | NCR | __X - Plunge columnon GL B/6 outside of allowable toleranceat the 73.750 SSL |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-03-31 | 2014-12-22 11:05 | -99 | 2014-12-11 09:26 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | With reference to Cxxx-RFI-002271 we now confirm that the plunge column on GL B/6 is 207mm out of plan position, see attached sketch. This is a further 36mm from the position on the level 78.120. In the RFI we had predicted this to be 38.5mm. When including the installation tolerances of +- 20mm for plan position plus the 1/400 verticality tolerance(2.5mm/m) this totals to an allowable tolerance of 102.1mm at the 73.750m level, therefore the plunge column is 104.9mm outside of the allowable tolerance.
| 02SL - Stations (LUL) | Cxxx-NCR-001277 | NCR | __X - Pile P202 out of verticality tolerance |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-03-31 | 2015-01-08 13:25 | -82 | 2014-12-11 16:12 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | At the excavation level of 74m the as-built of pile P202 has been found to be 171mm outside of the allowable vertical tolerance of 190mm so a total of 361mm from plan position at the 106.740 SSL. The tolerace is made up of +-25mm for plan position and 1/200 verticality tolerance so 5mm/m that quals 190mm. This has been taken over 33m from pile platform level of 107m. The plunge column is within tolerance, however with the pile being out of tolerance the as-built position of the plunge column to the as-built position ofthe pile is 381mm center to center.
| 02SL - Stations (LUL) | Cxxx-NCR-001278 | NCR | BTH- Top of cage level high for Pile B105 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-12-31 | 2015-07-15 08:12 | -169 | 2015-01-08 09:20 | Civil - Geotechnical Engineering | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The cage for pile ref. B105 was found to be out of tolerance on the 10/12/14 The current cage positional tolerance as referenced in KP10-3213, RFI 335 & SPERW B3.4.1 is +50mm/-100mm. The cage for pile Ref. B105 was installed to the correct level adding 10mm feet and considering 40mm settlement. But was found to be 62mm higher than the allowable level tolerance after casing extraction. The final Top of Steel level was 112.062 mATD instead of 111.900 mATD. (Tolerance level: 111.800-111.950mATD). The level to which the reinforcement bars extend complies with the Cxxx requirements set out in drawing rf. Cxxx-MMD-C-DDD-C101-04401 rev C04.The coupler levels are out of tolerance similar quantity as the top of cage but remain with the slab.
| 02SL - Stations (LUL) | Cxxx-NCR-001279 | NCR | NCR - BFB - 89.820m slab levels out of tolerance (replaces NCR 1267) |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-06-30 | 2015-07-23 21:20 | 23 | 2014-12-18 15:56 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | Please see the attached marked up as-builts that highlight the areas in the slab that are outside of the construction tolerance for the SSL of +10/-0mm. Proposed Answer: We propose to do nothing as this is similar to the NCR raised for the 106.740 slab (Cxxx-NCR-001205-01) and the 95.580 slab (Cxxx-NCR-001238).
| 02SL - Stations (LUL) | Cxxx-NCR-001280 | NCR | __X - 4no. piles out of verticality tolerance |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-03-31 | 2015-01-29 13:38 | -61 | 2014-12-22 16:49 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | At the excavation level of 72.5mATD, the as built record of the below listed piles show the piles to be out of the allowable vertical tolerance of 197.5mm. The allowable tolerance is made up of +/-25mm in plan position and 1/200 verticality tolerance (over 34.5m), the sum of which equates to 197.5mm. Pile 206 - out of tolerance by 73.5mm Pile 204 - out of tolerance by 80.5mm Pile 208 - out of tolerance by 112.5mm Pile 201 - out of tolerance by 79.5mm
| 02SL - Stations (LUL) | Cxxx-NCR-001281 | NCR | Water ingress through lining wall construction joints |  | Crossrail | PDP | LIS - Liverpool Street Station (Central) |  | 2017-06-30 | 2017-01-23 10:28 | -158 | 2014-12-23 10:47 | Civil - Civil Engineering General | 50000 |  | Material | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Water is penetrating through the lining wall construction joints at a number of locations within the Blomfield Box.
| 02SL - Stations (LUL) | Cxxx-NCR-001282 | NCR | __X - Trigger Levels not achieved as per Specification KE10 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-03-31 | 2015-01-20 16:17 | -70 | 2015-01-09 11:33 | Surveying - Instrumentation and Monitoring | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | The Contractor confirms that the trigger levels for pore water pressure as stated in KE10 Excavation and Filing Specification, Table KE10-01 for the lowest level of excavation (78 to 71m ATD) were not achieved.
| 02SL - Stations (LUL) | Cxxx-NCR-001283 | NCR | __X - Missing reinforcement in waler beam WB1 for the VD2 wall at level 78.120 SSL |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-03-31 | 2015-02-13 14:52 | -46 | 2015-01-13 13:30 | Structural Engineering - Reinforcement | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | On the level 78.120m we have not installed the 8 number B25 bars on waler beam WB1 required for the inner face of the VD2 wall on the east face as per design intent drawing Cxxx-MMD-C-DDL-C101_7-33716 and fabrication drawing Cxxx LAO-C-DWG-C101_WS103-50141.
| 02SL - Stations (LUL) | Cxxx-NCR-001284 | NCR | __X - 1500 dia pile bars cut too low |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-01-28 | 2015-01-29 13:34 | 1 | 2015-01-14 10:18 | Structural Engineering - Reinforcement | 500 |  | Planning | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During the excavation to the soffit of the 73.750 slab it was necessary to cut down the pile reinforcement for our excavators to gain access through the excavation. This has resulted in the B32 bars being cut to low. See below for the amount of bars cut in each pile. P201 – 13 bars P203 – 11 bars P204 – 1 bar P207 – 5 bars P210 – 4 bars P211 – 24 bars P214 – 24 bars P215 – 24 bars P216 – 24 bars
| 02SL - Stations (LUL) | Cxxx-NCR-001285 | NCR | Earthing Detail C |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-04-30 | 2015-02-06 16:12 | -83 | 2015-01-15 16:14 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | During the installation of detail C as drawn on Drawing Cxxx-LAO-E-DWG-C101_WS103_Z-50014 was amended without an agreed FCD in place. The attached sketch indicates the derivation from the initial detail C. 1. Sand fill to void in 300mm blinding omitted. We had to use this as pressure relief for uplift on the blinding due to pore water issues. Therefore no fill was placed. 2. Due to number 1 we did not need the compressible wrap. The void is empty. 3. We used tape rather than a seal plate. 4. The compressible fill in the 50mm blinding has been omitted.
| 02SL - Stations (LUL) | Cxxx-NCR-001286 | NCR | __X - Lining wall cover to pile PW325 at the soffit of the 78 slab |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-02-04 | 2015-01-30 13:24 | -5 | 2015-01-21 09:12 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | As per the photo in the attached Examination Record we have identified that the reinforcement for the lining wall at the location of pile PW325 does not have any cover.
| 02SL - Stations (LUL) | Cxxx-NCR-001287 | NCR | __X - Excess cover to starter bar couplers on level 78.120 SSL at the VD1 and VD2 walls |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-04-30 | 2015-02-25 13:32 | -64 | 2015-01-21 11:21 | Structural Engineering - Reinforcement | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The near face starter bar couplers in the waler beams on level 78.120m for the connection to the VD1 and VD2 walls shown on CADS drawings Cxxx-LAO-C-DWG-C101_WS103-50197 as bar mark E84 and drawing Cxxx-LAO-C-DWG-C101_WS103-50198 as bar mark E54 have been installed with approximately 300mm cover.
| 02SL - Stations (LUL) | Cxxx-NCR-001288 | NCR | BTH - Pile No. B101 Reinforcement Cage Settlement |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-12-31 | 2015-07-15 08:16 | -169 | 2015-01-26 12:00 | Geotechnical Engineering - Concrete - Bored Pile | 3000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Pile No. B101 was constructed on 05.12.14. The pile cage was levelled in as per the IFC drawings however the pile cage had settled within the pile overnight. The design level of the pile cage is 113.400mAoD however the actual level of the pile cage is 113.079mAoD which is 321mm lower than design.
| 02SL - Stations (LUL) | Cxxx-NCR-001290 | NCR | __X - Geothermal loops lost in the 73.750 SSL |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-04-30 | 2015-03-12 16:05 | -49 | 2015-01-29 08:48 | Civil - Civil Engineering General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | On completion of exposing the 1500 dia piles for the 73.750 SSL we conducted the geothermal works and have discovered that a number of loops were blocked and therefore are lost from circuits PA1 and PA2. The lost loops are as follows. Pile 203 - loop 4 Pile 205 - loop 1 Pile 206 - loops 3 & 4 Pile 208 - loops 2 & 3 Piles 209 - loop 3 Pile 213 - loop 3
| 02SL - Stations (LUL) | Cxxx-NCR-001291 | NCR | re-bar connection to earthing system |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-06-30 | 2015-05-11 12:25 | -50 | 2015-01-29 11:38 | Electrical - General | 1000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | sheathed and unsheathed cable conductors was used to pack out earth claps around 40mm rebar
| 02SL - Stations (LUL) | Cxxx-NCR-001292 | NCR | __X - PW323 exceeding Vertical/positional tolerance |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-02-12 | 2015-01-30 13:30 | -13 | 2015-01-29 12:00 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Pile PW323 has been installed out of the allowable vertical and therefore the position of this pile at the top of the 73.750 SSL has exceeded the tolerance by 75mm. This is in an easterly direction which is away from the box.
| 02SL - Stations (LUL) | Cxxx-NCR-001293 | NCR | Lining Wall Pour not Achieved Full Height |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-05-31 | 2015-03-12 07:50 | -80 | 2015-02-06 15:30 | Civil - Civil Engineering General | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | When pouring the lining wall on the 78.120 to 84.060 level the top up pour on the North and West walls GL 4-5/A-C (see attached mark up) the concrete was pumped into a closed shutter and a strip at the top has been left low creating a void (see attached photos). A Schwing SP1800 was used for pouring the lining wall because this was on site for the base slab pour. Previously Cxxx had used a Putzmeister P715. Concerns were raised by the site team that the amount of concrete poured with each pump was too large to control at the end of the pour and could lead to excess concrete being poured and blowing the shutter. To avoid this a letter box was placed in the pour so any excess concrete would be released. However, when the letter box was filled the areas either side did not fill to the top. To rectify this a Putzmeister P715 will be used in future pours.
| 02SL - Stations (LUL) | Cxxx-NCR-001298 | NCR | __X - Cover to Reinforcement on the 73.750 Lining Wall |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-05-31 | 2015-03-11 13:34 | -81 | 2015-02-10 09:13 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The couplers fixed for the downstand kicker for the 73.750 were not fixed in the correct position. This has resulted in areas were the correct cover will not be achieved by following the design.
| 02SL - Stations (LUL) | Cxxx-NCR-001300 | NCR | __X - Reinforcement Around AP1 Fixed in the Wrong Location |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-05-31 | 2015-03-11 11:28 | -81 | 2015-02-10 09:49 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The line marked for the fixers around AP1 was marked incorrectly. With referance to drawing Cxxx-LAO-C-DWG-C101_WS103-50204, this has resulted in 4no U-Bars (bar mark 42) and 4no. couplers (bar mark E10) being fixed in the wrong location.
| 02SL - Stations (LUL) | Cxxx-NCR-001301 | NCR | Wall W6 @ 78.120m |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-05-31 | 2015-04-28 12:50 | -33 | 2015-02-12 10:28 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Wall W6 at 78.120m was cast with B25's horizontal bars as opposed to B32's
| 02SL - Stations (LUL) | Cxxx-NCR-001302 | NCR | Anchor bars into pile walls@ 73.750m east |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-05-31 | 2015-03-02 10:56 | -90 | 2015-02-13 09:50 | Civil - Civil Engineering General | 2000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | During an inspection of the reinforcement it was noticed that the anchor bars within the lining wall on W2 connecting into the pile wall had insufficient anchorage length into the wall.
| 02SL - Stations (LUL) | Cxxx-NCR-001303 | NCR | BTH - Northern capping beam waterproofing |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2015-12-31 | 2015-07-08 15:12 | -176 | 2015-02-18 13:46 | Civil - Civil Engineering General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | The Prepurfe waterproofing installed as part of the northern capping beam works has been damaged during the excavation works for the northern escalator decline. The detail around the existing substation wall as instructed under PMI-00562 requires a lap length of 300mm below the capping beam to connect to the lining wall waterproofing. During the excavation the waterproofing has been damaged in a number of areas resulting in only 100mm lap length available for the next stage of waterproofing. See attached photos showing the damage.
| 02SL - Stations (LUL) | Cxxx-NCR-001304 | NCR | ITP, installation of southern exhumation tenting |  | Crossrail | PDP | LIS - Liverpool Street Station (Central) |  | 2015-05-31 | 2015-04-16 12:55 | -45 | 2015-02-19 11:41 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Improper resource allocation | Completed |  | Further to Cxxx-EWN-00699, the Project Manager has immediate concerns that the Contractor has not yet issued for acceptance critical documentation required to meet the current Cxxx Programme of works detailed as follows: • Inspection test plan for installation of propping – due to commence 20/02/15 • Method Statement for the installation of the propping - due to commence 20/02/15 • Inspection test plan for installation of southern exhumation tenting – due to commence 19/02/15 The Contract allows the Project Manager up to 28 days to review the above listed documentation. The Contractor should also be aware that no works can proceed unless this documentation has been accepted by the Project Manager. This situation could potentially delay the entire programme of works
| 02SL - Stations (LUL) | Cxxx-NCR-001305 | NCR | Excavation activity without approved Required Excavation Support Sheet (RESS) |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2015-06-30 | 2015-06-04 10:36 | -26 | 2015-03-10 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | The contractor failed to submit and schedule the appropriate SRG meeting, baseline information for the I&M installed and required excavation support sheet before progress past stage 13 of the construction sequence drawings Cxxx-MMD-C-DDB-C101_Z-42925. Following the installation of the 110.700m props within the northern escalator decline the contractor should have schedule and produced the information for an SRG meeting to review and approve the RESS for further excavation. The contractor did not do this and progressed with the excavation to a depth of 2m without this in place. As stated within the contractors management plan for ground movement Cxxx-LAO-C-STP-C101-50001 this should have been carried out before the excavation progressed.
| 02SL - Stations (LUL) | Cxxx-NCR-001306 | NCR | BTHPIL - Broadgate Ticket Hall Temp Works Piles TW8, TW9, TW10, TW11 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-08-31 | 2015-06-24 13:03 | -68 | 2015-03-12 16:51 | Geotechnical Engineering - Concrete - Bored Pile | 8000 |  | Incorrect Installation | Rework | 2 (6-60k) | Complete | Management Problem - Other | Completed |  | Excavation currently under way for northern side of Broadgate Ticket Hall at Liverpool street station. During excavation and pile trimming works, It was discovered that the Top Of Steel level for Piles TW8, TW9 and TW10 are not where they were recorded at at the time of construction. TW11 top of steel level adjacent is within tolerance and has been excavated.
| 02SL - Stations (LUL) | Cxxx-NCR-001307 | NCR | BTH - North Escalator Decline Sloped Blinding Levels too High |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-06-30 | 2015-04-22 10:22 | -69 | 2015-03-18 22:49 | Structural Engineering - Concrete Member | 1500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The sloped structural blinding to the northern escalator decline was constructed up to 120mm high in places.
| 02SL - Stations (LUL) | Cxxx-NCR-001308 | NCR | BTH - Northern escalator slab 106.095 |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2015-11-21 | 2015-11-19 16:32 | -2 | 2015-03-28 12:43 | Civil - Civil Engineering General | 3000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Various issues with the design and workmanship of the northern escalator decline base slab 106.095. Design: The mini gate design drawings for the waterproofing and drainage were not fully accepted before works commenced onsite. The waterproofing was installed without a detail resulting in the contractor installing additional waterproofing in areas where it was not required. The drainage design min gate did not pick up the missing level of the drainage run and wrong drainage detail all on drawings Cxxx-LAO-P-DDA-C101_3-4-1233. This meant the wrong gully was ordered resulting in the gully having to be boxed out and an additional pour required. The mini gate was only signed off after the drainage had been installed and was waiting for concreting on the next shift. The rebar drawings failed to capture that pile B164 clashed with the starter bar alignment resulting in the wall starter and U bars having to be altered onsite, this could have been avoided with a simple step in the wall starters. Workmanship: The backblinding installed by the contractor on the eastern was installed 130mm to far east resulting in an extra 130mm of concrete cover to the eastern edge, design cover is 50mm. The temporary works holding down bolts for the access deck and propping scheme clashed with the permanent works piles and wall starters. This resulted in delay with the installation of the bolts and modification to 1no permanent pile reinforcement. Various issues with the pre pour inspection : cleanliness of pour, reinforcement not fixed in locations, insufficient lap length and stop end installation clashing with starter bar spacing. All of the above issues caused delay to installation of the slab and additional works to the programme.
| 02SL - Stations (LUL) | Cxxx-NCR-001309 | NCR | Broadgate tickethall compressive filler |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2015-10-31 | 2015-08-19 16:27 | -73 | 2015-03-31 14:17 | Civil - Base Course | 1000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | BTH - In the tickethall area the construction sequence drawing Cxxx-MMD-C-DDB-C101_Z-42926 states that 100 thk. compressive boards needs to be installed between the 107.950m slab and existing shaft foam concrete area of the old substation structure. Following conversation with the contractor on the approved material that needs to be installed the contractor proceeded to install standard 90mm polystyrene board in the area without any MCR acceptance. CRL carried out a prepour inspection and notified the contractor that the material was not approved and did not meet the performance criteria of the suggested compressive board Cellcore HX. Due to the material installed not being approved the concrete delivered to site had to be turned away and the materials/ works for the area had to be stripped out. This consisted of polystyrene boards, reinforcement mesh and formwork. The works carried out were not as per the approved ITP and the MCR process stated within the ITP had not been followed. The only reason the pour was stopped and correct material was ordered was due to CRL picking this up on the prepour inspection. See attached photos of the material installed and the removal works carried out after the pre pour inspection.
| 02SL - Stations (LUL) | Cxxx-NCR-001310 | NCR | Moorgate Ticket Hall - Commencement of Fabrication of the Temporary Staircases without an Accepted Inspection and Test Plan |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-07-31 | 2015-05-01 10:24 | -91 | 2015-04-08 10:36 | Structural Engineering - Structural Engineering - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Other management problem | Completed |  | Fabrication of Moorgate Ticket Hall Alternative Access Route Temporary Staircases 1, 2, 3, & 4 has commenced without an Accepted Inspection and Test Plan or an Accepted Welding Procedure & Qualification Records .
| 02SL - Stations (LUL) | Cxxx-NCR-001311 | NCR | Site welding of stiffner plates to king posts |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-06-30 | 2015-04-28 09:41 | -63 | 2015-04-20 09:29 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Site welding works at Broadgate Ticket Hall have commenced prior to the "__ Welding Procedure & Qualification Records and Tests, Welder Qualification" being revised to include the welder currently on site.
| 02SL - Stations (LUL) | Cxxx-NCR-001312 | NCR | BTH - Low Pile Cages at Ticket Hall Level |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-07-31 | 2015-06-25 15:27 | -36 | 2015-04-21 09:59 | Geotechnical Engineering - Concrete - Bored Pile | 6000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Upon pile breakdown, it was discovered that the piles highlighted in RED on the attached have low reinforcement cages.
| 02SL - Stations (LUL) | Cxxx-NCR-001313 | NCR | BTH - Pile No. TW13 Constructed at the Incorrect Level |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-07-31 | 2015-06-25 15:28 | -36 | 2015-04-22 23:55 | Geotechnical Engineering - Concrete - Bored Pile | 4000 |  | Documentation and Records | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | BTH Pile No. TW 13 has been constructed at the incorrect level due to a typo on the piling schedule. The pile cut off level on the piling schedule showed a level of 105.27mAoD however the correct pile cut off level sshould have been 107.25mAoD
| 02SL - Stations (LUL) | Cxxx-NCR-001314 | NCR | BTH - Pile No. B228 constructed out of positional tolerance. |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-07-31 | 2015-06-25 15:25 | -36 | 2015-04-23 00:20 | Geotechnical Engineering - Concrete - Bored Pile | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Pile No. B228 has been constructed out of positional tolerance resulting in the reinforcement cage being too close to the existing substation wall. See attached photo
| 02SL - Stations (LUL) | Cxxx-NCR-001315 | NCR | __X - ITP for Blockwork in the Blomfield Box was not submitted 4 weeks prior to the planned start of works |  | Crossrail | PDP | LIS - Liverpool Street Station (Central) |  | 2015-10-31 | 2015-07-27 10:58 | -96 | 2015-04-27 14:31 | Architectural - Brickworks/Blockworks | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | The ITP for blockwork in the Blomfield Box was not submitted 4 weeks prior to the start of planned work (27th April 2015). Following informal review the ITP was signed as Code 1 on the 24th April 2015.
| 02SL - Stations (LUL) | Cxxx-NCR-001316 | NCR | BTH - Inclinometer verticality, damaged coupler & damaged tubing (IN205 & IN203) |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-07-31 | 2015-07-08 16:16 | -23 | 2015-04-29 14:59 | Geotechnical Engineering - Geotechnical Monitoring | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The inclinometer tube (IN205) cast into Pour 2 Slab has been cast out of the permitted tolerance for verticality and the coupler joint in the tube has been dislodged during concreting which has resulted in a manual probe not being able to be used in this location. Inclinometer tube (IN203) has been damaged at approximately level 105.00mAoD during pile installation which has resulted in a manual not being able to be used in this location.
| 02SL - Stations (LUL) | Cxxx-NCR-001317 | NCR | Installation of inclinometer tube INX205 |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2015-07-31 | 2015-06-30 12:50 | -31 | 2015-05-11 10:34 | Surveying - Instrumentation and Monitoring | 3000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The addtional section installed on Inclinometer tube INX205 within pour 1 wall at GL1 has not been installed to the correct verticality. The installation of the addtional section as per attached photos shows the tube leaning south-eastwards towards the exisitng LU vent shaft struture. Due to the verticallity the next section of tube to be installed will fall outside of the wall extent if the same verticality is continued for the next wall pour to 112.8m.
| 02SL - Stations (LUL) | Cxxx-NCR-001319 | NCR | __X: Defective Concrete on the South Wall 110.500m to 112.560m |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-09-30 | 2015-09-17 16:38 | -13 | 2015-05-12 14:07 | Civil - Structural Engineering | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Ref: Photo - WP_20150507_001 (attached) When pouring the south wall from 110.500m to 112.560m excessive foam was used to plug the unused tie holes in the PERI formwork panels. In one of these holes excessive foam was used and this was present on the inside of the shutter. When concrete was placed the foam left a small void with exposed rebar.
| 02SL - Stations (LUL) | Cxxx-NCR-001320 | NCR | __X Half landing pre-pour check level +92 |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2015-06-11 | 2015-06-10 14:03 | -1 | 2015-05-14 11:07 | Civil - Civil Engineering General | 0 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | During the pre-pour inspection of the half-landing at level +92 three problems with the reinforcement were identified. At the time of the pour, if not for the intervention of the CRL Field Engineer, the half landing would have been poured without all identified issues being incorporated.
| 02SL - Stations (LUL) | Cxxx-NCR-001321 | NCR | BTH - Welding Documentation not accepted prior to the start of off-site fabrication for temporary access deck |  | Crossrail | PDP | LIS - Liverpool Street Station (Central) |  | 2015-10-31 | 2015-07-31 17:00 | -92 | 2015-05-17 21:30 | Structural Engineering - Welding | 500 |  | Planning | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | During a visit to __ on the 8th May by CRL Field Engineer, __, it became apparent that fabrication of temporary access deck for the Broadgate Ticket Hall had commenced despite the associated welding documentation not having been submitted and accepted.
| 02SL - Stations (LUL) | Cxxx-NCR-001322 | NCR | BTH - No accepted ITP in place prior to the start of off-site fabrication of temporary access deck pre-cast units |  | Crossrail | PDP | LIS - Liverpool Street Station (Central) |  | 2015-10-31 | 2015-07-31 17:03 | -92 | 2015-05-17 21:54 | Civil - Civil Engineering General | 500 |  | Planning | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | On 13th May it became apparent that the off-site pre-cast units for the Broadgate Ticket Hall temporary access deck had been manufactured without an accepted ITP being in place.
| 02SL - Stations (LUL) | Cxxx-NCR-001323 | NCR | __X upstand channel on 84m lvl |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-08-31 | 2015-09-14 09:46 | 14 | 2015-06-03 10:37 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the casting of the 84m level drainage channel the bonded membrane was not cut down to the required height of 50mm and in fact extended up past the finish concrete level. On post inspection it was evident that the in some areas the top had not bonded to the wall sufficiently.
| 02SL - Stations (LUL) | Cxxx-NCR-001324 | NCR | MTH - Wall W6 cast out of positional tolerance |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-08-31 | 2015-08-28 18:12 | -3 | 2015-06-05 12:58 | Civil - Civil Engineering General | 3000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Concluding Pour 2 on level 109.100 we have found wall W6 to be out of position by 25mm as shown on marked up plan and photo. The remainder of the wall was stepped at this location bringing it back to its design position.
| 02SL - Stations (LUL) | Cxxx-NCR-001325 | NCR | MTH - Missing starter bars to column C9 at junction of Beam B3 & wall W9 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-08-31 | 2015-08-04 12:44 | -27 | 2015-06-16 15:50 | Structural Engineering - Structural Engineering - General | 1500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | We have cast beam B3 identified on drawing Cxxx-MMD-C-DDL-C101_2-11158 without the starter bars required for column C9.
| 02SL - Stations (LUL) | Cxxx-NCR-001326 | NCR | MTH - Concrete void to Beam B3 on Pour 1 Basement slab |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-10-31 | 2015-10-01 10:44 | -30 | 2015-06-17 09:53 | Civil - Civil Engineering General | 3000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On striking the shutters to the 300mm wide beam strip next to Moor House shown on drawing Cxxx-MMD-C-DDL-C101_2-11156, where we had boxed out a section for the drainage to pass through a concrete void is present below the box out, see attached photo.
| 02SL - Stations (LUL) | Cxxx-NCR-001327 | NCR | BTH - Northern Capping Beam |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2016-12-31 | 2016-11-30 11:50 | -31 | 2015-06-17 17:15 | Civil - Structural Engineering | 5000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | The project Manager has been notified that the U bars installed within the northern decline capping upstand as part of the lower beam section pour have been installed to the incorrect level. The U bar have been set to the highest part of the upstand level instead of the designed lower section with an additional section to be formed at a later date. The U bars installed have been set to the Setting out point levels as stated on Cxxx drawings Cxxx7-MMD-C-DDB-C101_Z-41201. Due to the size of the reinforcement and the level of the lower concrete pour it will not be possible to achieve the minimum splice for the same size bar to adjust the level.
| 02SL - Stations (LUL) | Cxxx-NCR-001328 | NCR | __X- Waterproofing along the North Wall and W297 |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2015-09-24 | 2015-08-26 22:39 | -29 | 2015-06-18 16:22 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On the 3rd of June 15 __ (the waterproofing supplier) visited __ site and showed concerns with the way LAO applied the PA 800 waterproofing material against various sections of the retaining wall W297 and the North wall (pictures attached).
| 02SL - Stations (LUL) | Cxxx-NCR-001329 | NCR | BTH Concrete to Wall Pour 3 - Discharging Concrete Vertically in excess of 2m |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-09-30 | 2015-07-31 15:01 | -61 | 2015-07-07 22:30 | Structural Engineering - Concrete Member | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Concrete is being discharged into BTH - Ticket Hall Wall Pour 3 vertically through a height greater than 2m
| 02SL - Stations (LUL) | Cxxx-NCR-001330 | NCR | MTH - Column C7-1 starter bars out of position |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-09-30 | 2015-08-03 10:56 | -58 | 2015-06-23 16:47 | Structural Engineering - Reinforcement | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | When setting out kickers for the columns in Pour 1 next to Moor House we have found that the northern column of type C7-1 has been installed 1m out of position to its design position.
| 02SL - Stations (LUL) | Cxxx-NCR-001331 | NCR | MTH - Reinforcement bent to staricase from the 107.750 SSL to allow Temporary Works |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-08-31 | 2015-08-07 17:29 | -24 | 2015-06-23 18:06 | Structural Engineering - Reinforcement | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | With reference to Specification KF10 - Insitu Concrete Cxxx-MMD-C-RSP-C101-5006 clause 'KF10.3231 a) Re-bending onsite is not permitted, before or after fixing into position, unless accepted by the Project Manager.', we have had to bend the starter bars for the stairs from the 107.750 SSL to enable the installation of the slab edge shutters when casting the 109.100 SSL. See attached photo of the bent bars.
| 02SL - Stations (LUL) | Cxxx-NCR-001332 | NCR | MTH - Column C2 shutter blown 30mm at base of column |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-12-31 | 2015-11-11 09:47 | -50 | 2015-06-24 10:23 | Civil - Civil Engineering General | 1000 |  | Testing and Commissioning | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On striking the in-situ column on GL 8 to the 109.100 SSL we have found that the column box has blown by 30mm on the northwest corner, see attached photos. The southern corner has maintained its position.
| 02SL - Stations (LUL) | Cxxx-NCR-001333 | NCR | BTH - Kicker not formed for column on GL 10/A, Northern Ticket Hall basement |  | Crossrail | PDP | LIS - Liverpool Street Station (Central) |  | 2016-01-31 | 2015-10-12 13:57 | -111 | 2015-06-28 22:11 | Civil - Civil Engineering General | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The kicker for column GL 10/A in the BTH Northern Ticket Hall has not been formed in accordance with the location indicated on the drawings, as required by the structural specification KF10. The note on drawing Cxxx-MMD-C-DDJ-C101-10011 requires kickers to be 150mm unless otherwise noted.
| 02SL - Stations (LUL) | Cxxx-NCR-001334 | NCR | __X - Incorrect position of cast in couplers for 81.180mATD half landing |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-08-03 | 2015-07-31 17:08 | -3 | 2015-07-01 16:59 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The couplers on the south east connection of the half landing at 81.180mATD spaced correctly to the extends of the slab. The correct number of couplers has been installed but there is a section of 400mm with no couplers as shown on the attached sketch. We propose to drill and fix 3 number B25 bars top and bottom in this region.
| 02SL - Stations (LUL) | Cxxx-NCR-001335 | NCR | __X Lvl 73 Making good of steel dewatering well |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-10-31 | 2015-12-07 12:45 | 37 | 2015-07-06 16:44 | Structural Engineering - Concrete Member | 1000 |  | Incomplete Works | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | __X level 73 operatives are working throughout the basement making good to the concrete walls and soffit. A section of steel dewatering well pipe located adjacent to the Haki stairs under the soffit that is penetrating through the face of the wall has been made good around, but not cut back beyond the face of the wall. It is protruding approx 50mm see picture attached.
| 02SL - Stations (LUL) | Cxxx-NCR-001336 | NCR | Incorect setting out information |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-11-30 | 2015-10-21 10:20 | -40 | 2015-07-07 08:12 | Structural Engineering - Steel Member | 3000 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Setting out information used to install bolt sets was C3229-ENG-TW-01094, and it’s associated CAD drawing. Steel built to drawing DAM-GA-07. These two drawings had a discrepancy of approximately 1050mm in the plan length of raking props bolted to R2, R3 and R4.
| 02SL - Stations (LUL) | Cxxx-NCR-001337 | NCR | MTH - Rebar bent when installing formwork to wall W9 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-09-30 | 2015-08-04 12:48 | -57 | 2015-07-07 19:47 | Structural Engineering - Reinforcement | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | With reference to specification KF10 – Insitu Concrete Cxxx-MMD-C-RSP-C101-50006 clause ‘KF10.3231 a) Re-bending onsite is not permitted before or after fixing into position, unless accepted by the Project Manager.’ When installing the A-frame shutter for wall W9 the reinforcement starter bars to wall W3b has been bent at the corner, see attached photo.
| 02SL - Stations (LUL) | Cxxx-NCR-001338 | NCR | BTH Incorect concrete used in clamshell slab |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-09-30 | 2015-07-31 15:58 | -61 | 2015-07-08 12:04 | Civil - Concrete Pavement | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Concrete wagons mixed up between BTH and MTH, D4 mix used for clamshell slab rather than D5 that was planned. Also the concrete did not have curing agent applied and suffered from some surface cracking.
| 02SL - Stations (LUL) | Cxxx-NCR-001339 | NCR | MTH - Concrete pour to wall W9 aborted |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-11-30 | 2015-08-23 11:49 | -99 | 2015-08-18 10:02 | Civil - Civil Engineering General | 2000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | On placing the first concrete skip into wall W9 on 7th July 2015 it was identified that the shear links in the wall had not been installed. As a result the pour was cancelled and the shutters opened to remove the concrete so that the shear links could be installed.
| 02SL - Stations (LUL) | Cxxx-NCR-001340 | NCR | BTH - Damage to PPC access plank no. 011. |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-09-30 | 2015-07-10 15:01 | -82 | 2015-07-08 14:20 | Structural Engineering - Pre-cast | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Surface damage to PCC plank during instalation.
| 02SL - Stations (LUL) | Cxxx-NCR-001341 | NCR | BTH Southern Decline Props too long |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-10-31 | 2015-10-21 14:56 | -10 | 2015-07-10 14:56 | Structural Engineering - Steel Member | 10000 |  | Design | Rework | 2 (6-60k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Discrepancy between Temporary Works design and Permanent Works design, has resulted in some of the props for the southern decline being manufactured too long to fit. Props at 107.700m and 105.875m
| 02SL - Stations (LUL) | Cxxx-NCR-001342 | NCR | BTH - South Decline Wall North Pour 1 Concrete Temperature in Excess of 30 degrees |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-09-30 | 2015-07-31 16:07 | -61 | 2015-07-13 01:06 | Structural Engineering - Concrete Member | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | 3No. loads of concrete were tested prior to discharging into the concrete pump during the concreting of the South Decline Wall North Pour 1. (See attached concrete records) The concrete specification KF10 (KF10.3204d) states that "At the time of disposition in the Works, the concrete temperature shall not be less than 5 degrees centigrade or more than 30 degrees centigrade unless otherwise agreed".
| 02SL - Stations (LUL) | Cxxx-NCR-001343 | NCR | BTH Displaced couplers, Southern Decline, South Wall 2 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-09-30 | 2015-08-03 14:32 | -58 | 2015-07-13 12:28 | Structural Engineering - Reinforcement | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Couplers at the east end of pour 2, south wall of southern decline, are displaced. This may provide difficulty in fixing the adjacent wall (1 + 3)
| 02SL - Stations (LUL) | Cxxx-NCR-001344 | NCR | BTH Damage to UC in plunge column / king post |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-10-31 | 2015-08-19 16:31 | -73 | 2015-07-15 12:06 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Surface indentation to UC sections, as a result of over-breaking when removing concrete.
| 02SL - Stations (LUL) | Cxxx-NCR-001345 | NCR | BTH Void former on angle brackets |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-10-31 | 2015-08-03 14:24 | -89 | 2015-07-15 16:43 | Structural Engineering - Concrete Member | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | On north wall pour 1, of southern decline void formers were not used above the angle brackets. This is not best practice as requires breaking out of concrete (pic 003). Void formers used on south wall pour 2 (pic 002), and can be seen being installed on pour 3 (pic 004).
| 02SL - Stations (LUL) | Cxxx-NCR-001346 | NCR | BTH Misaligned shear studs, access deck |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-09-30 | 2015-08-18 17:48 | -43 | 2015-07-15 17:06 | Structural Engineering - Steel Member | 1000 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Shear studs along the at the east side of plank 014, and 008 did not align with the voids in the PCC planks. There is a potential that this will affect some of the planks 001-007 which are yet to be installed.
| 02SL - Stations (LUL) | Cxxx-NCR-001347 | NCR | __X - Reinforcement protruding through 112mATD slab |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-08-31 | 2015-07-31 13:37 | -31 | 2015-07-16 10:20 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | When constructing the beam B3 on drawing Cxxx-lao-c-dwg-c101_ws103-50240 bar mark B22 was installed so that the bob went up into the column because of buildability issues. One of these bars was knocked out of position so that it only has 5mm cover to the column.
| 02SL - Stations (LUL) | Cxxx-NCR-001348 | NCR | __X - Column B11 starter bars cast in the wrong place |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-08-31 | 2015-08-04 13:58 | -27 | 2015-07-16 17:47 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | When casting the slab at the 112mATD the starter bars for column C16 were cast out of position. This means that 4no. B20 bars sit outside of the column on one face and there is excessive cover on the opposite face. See attached photo.
| 02SL - Stations (LUL) | Cxxx-NCR-001349 | NCR | MTH. Missing couplers in wall (W8) for half landing 110.900m level |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-10-31 | 2015-09-18 10:40 | -43 | 2015-07-18 10:18 | Civil - Civil Engineering General | 3000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Please refer to attached NCR sketches. On post pour inspection BM E166 ref drawing Cxxx-LAO-C-DWG-C101_WS099-50012 (coupler bars within the RC wall for the half landing 110.900) have been missed out of the RC wall construction.
| 02SL - Stations (LUL) | Cxxx-NCR-001350 | NCR | MTH. Incorrect coupler height C6 for Beam 9 street level |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-10-31 | 2015-09-18 10:42 | -43 | 2015-07-18 11:13 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Please refer to attached site sketch for clarity. Couplers E57, E51 and E56 have been installed at the incorrect level (approx 350mm height) within C6 at street level slab for beam 9.
| 02SL - Stations (LUL) | Cxxx-NCR-001351 | NCR | __X - Column C12 starter bars installed in the wrong location |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-08-31 | 2015-08-26 11:22 | -5 | 2015-07-20 18:03 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | When casting the 112mATD slab the starter bars were placed in the wrong position so the bars on the East face are 100mm away from the main bar position.
| 02SL - Stations (LUL) | Cxxx-NCR-001352 | NCR | __X - Beam B23 missing couplers |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-10-31 | 2015-08-28 13:22 | -64 | 2015-07-21 09:21 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | When casting the wall and slab for the 112 slab pour 2 no couplers were placed for beam B23. Instead of 3no. B32 bars top and bottom with 3no. B16 each face for a 500mm beam we have cast 2no. B25 top and bottom to pick up a 350mm deep slab.
| 02SL - Stations (LUL) | Cxxx-NCR-001353 | NCR | __X - Column C1-2 concrete dropped from more than 4m |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-11-30 | 2015-11-27 09:13 | -3 | 2015-07-22 07:28 | Civil - Civil Engineering General | 1000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | When pouring concrete for column C1-2 from 112.860mATD to 118.360mATD the concrete was dropped from 5.7m instead of the 4m agreed under Cxxx-FCD-001239 for mix D5.
| 02SL - Stations (LUL) | Cxxx-NCR-001354 | NCR | __X - Low cover to edge of 112.860mATD slab |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-08-31 | 2015-08-04 13:59 | -27 | 2015-07-23 09:18 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | When pouring slab pour 1 for the 112.860mATD an area of 100mm by 400mm was cast with 20mm cover. When poured the spilce bars for the next pour were left sticking out and as people stepped on them this caused the concrete on the surface to crack. See attached photos.
| 02SL - Stations (LUL) | Cxxx-NCR-001355 | NCR | __X - Party wall waterproofing damage |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-02-29 | 2016-01-26 12:00 | -34 | 2015-07-27 14:55 | Civil - Civil Engineering General | 3000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | During the demolition of the party wall on the South East end of site the waterproofing below has been damaged by the falling debris.
| 02SL - Stations (LUL) | Cxxx-NCR-001356 | NCR | __X - Column C2-2 Starter bars incorrectly placed |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-10-31 | 2015-08-18 08:01 | -74 | 2015-07-27 17:12 | Civil - Civil Engineering General | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | When casting the column C2-2 from 106.740-112.860 the starter bars were not stepped at the top so the starter bars above 112.860 are in the wrong position. See attached photo.
| 02SL - Stations (LUL) | Cxxx-NCR-001357 | NCR | __X - Starter bars cast in the wrong place |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-08-31 | 2015-08-26 11:24 | -5 | 2015-07-28 14:14 | Civil - Civil Engineering General | 1500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | When casting the 112.860mATD slab pour 2 some starter bars for walls W11 and W14 were cast in the wrong place. See attached photos and sketches.
| 02SL - Stations (LUL) | Cxxx-NCR-001358 | NCR | BTH Southern decline batter GL4 - 5 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-10-31 | 2015-08-13 23:04 | -79 | 2015-07-28 17:08 | Civil - Excavation | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Batter dug between gridline 4 and 5 in the southern decline deviated moderately from the ‘dig line’ conveyed in the RESS (dated 24/07/15 relating to dig of 102.2 level GL 1-4) See attached photo; the RESS ‘dig line’ is the red profile, and the as-built line is the blue. The resulting green area is under-dug, and the orange area over-dug. The overall intent of the RESS has been adhered to, with a minor deviation in the detail.
| 02SL - Stations (LUL) | Cxxx-NCR-001360 | NCR | BTH Digging 102.2 level before RESS |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-10-31 | 2015-08-04 17:50 | -88 | 2015-07-30 12:09 | Civil - Excavation | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Dig commenced on the batter between GL4 -5 before the relevant RESS had been signed.
| 02SL - Stations (LUL) | Cxxx-NCR-001361 | NCR | __X - 78.120MATD Cover to Wall Starter Bars |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-08-15 | 2015-08-26 11:25 | 11 | 2015-08-01 09:00 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | For the wall highlighted on the attached skecth the cover to the starter bars on one face is 15mm which is less than Cmin 25mm.
| 02SL - Stations (LUL) | Cxxx-NCR-001362 | NCR | MTH - Street level pour 1 bottom reinforcement installed to incorrect level at step. |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-10-31 | 2015-08-14 12:03 | -78 | 2015-08-03 17:00 | Structural Engineering - Reinforcement | 3000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On constructing pour 2 we have found that bar mark B13 on CADS drawing Cxxx-LAO-C-DWG-C101_WS099-50025 has been installed at the wrong level where there is a step in the soffit between GL Z and A. See attached photo's and mark up
| 02SL - Stations (LUL) | Cxxx-NCR-001363 | NCR | MTH - Damaged concrete and couplers on MH3 as per Cxxx-RFI-002707 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-10-31 | 2015-08-23 11:50 | -69 | 2015-08-03 17:47 | Structural Engineering - Reinforcement | 5000 |  | Damaged | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | As per Cxxx-RFI-002707 the concrete on MH3 is damaged as well as the couplers raised in Cxxx-RFI-002567. C501 completed the works as shown in the photos to RFI 2707 but never protected them which is inevitable they would be damaged. The photo's do not show how C501 back filled this area i.e. tracking with machines and rolling material which is also likely to have caused damage to the exposed couplers.
| 02SL - Stations (LUL) | Cxxx-NCR-001364 | NCR | MTH - Couplers missing in column C3 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-10-31 | 2015-08-23 11:51 | -69 | 2015-08-06 08:24 | Structural Engineering - Reinforcement | 1000 |  | Incomplete Works | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | On constructing the walls around the OSD column which includes Column C3 on CADS drawing Cxxx-LAO-C-DWG-C101_WS099-50014 the couplers, bar mark E65, for wall W7 have not been installed. See attached mark up.
| 02SL - Stations (LUL) | Cxxx-NCR-001365 | NCR | __X- Lightning Protection |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2016-01-31 | 2016-01-19 13:11 | -12 | 2015-08-06 11:22 | Electrical - General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Lightning Protection system not installed as per approved gated design
| 02SL - Stations (LUL) | Cxxx-NCR-001366 | NCR | BTH - Damage to Southern Decline, North wall 1 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-11-30 | 2015-09-10 12:17 | -81 | 2015-08-11 10:23 | Structural Engineering - Concrete Member | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Section of lining wall in the southern decline, north wall pour 1 at aproximatly GL4, 105.075 level damaged by excavator bucket.
| 02SL - Stations (LUL) | Cxxx-NCR-001367 | NCR | __X - VD2 invert sheet membrane penetrated |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-12-11 | 2016-01-06 15:20 | 26 | 2015-08-11 14:08 | Civil - Tunnelling | 5000 |  | Damaged | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Sub contractor has drilled though and penetrated the sheet membrane waterproofing system and injected with __ Master rock 350 hydrophilic resin. The hydrophilic resin has reacted and expanded beneath the membrane causing it to heave where exposed at the Blomfield Box end. See photos 1-3 dated 11/08/15.
| 02SL - Stations (LUL) | Cxxx-NCR-001368 | NCR | __X 112 slab pouring columns from height |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-11-30 | 2015-11-27 08:45 | -3 | 2015-08-12 08:28 | Structural Engineering - Concrete Member | 5000 |  | Incorrect Installation | Use As-Is | 3 (3-6k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | Contrary to Cxxx-LAO-C-ITP-C101_WS103-50410, General Concreting Operations, Item 26, and KF10-3204(a), concrete mix D5 was discharged from 5m into 7no columns C12, C13, C1-1, C1-1, C14, C16, C19 and 1no wall (73-81) (attached). Cxxx are to confirm that C2, C4 and C17 were also not poured from greater than 2m. These columns were poured between 20-JUNE to 30-JUNE.
| 02SL - Stations (LUL) | Cxxx-NCR-001369 | NCR | BTH - Pile Bars not Achieving Anchorage in Decline Wall South Pour 5 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-09-23 | 2015-08-18 16:05 | -36 | 2015-08-12 16:03 | Civil - Civil Engineering General | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 5no. terminated anchor bars and 3no. post fixed anchor bars have been installed without the required 900mm anchorage from the first layer in the rear face.
| 02SL - Stations (LUL) | Cxxx-NCR-001370 | NCR | BTH - Coupler damage on soffit of north wall pour 1 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-11-30 | 2015-09-17 12:14 | -74 | 2015-08-12 17:35 | Structural Engineering - Reinforcement | 5000 |  | Damaged | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Approximately 19no. couplers (mostly front face) have been damaged in the excavation/soffit removal process. Located at the 105.075 level of north wall pour 1, of the southern decline.
| 02SL - Stations (LUL) | Cxxx-NCR-001371 | NCR | __X - Lift shaft stater bars within void at 112.860mATD |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-11-30 | 2015-09-17 16:47 | -74 | 2015-08-13 07:20 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | For the lift shaft at 112.860mATD 3no. starter bars each face were not capped off on the level below so they sit within a void. See attached skecth and picture.
| 02SL - Stations (LUL) | Cxxx-NCR-001372 | NCR | BTH - Pile Anchor Bars not Achieving Anchorage in Decline Wall North Pour 3b |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-08-27 | 2015-08-19 11:47 | -8 | 2015-08-13 08:49 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 6no. terminated pile anchor bars do not meet the minimum 900mm anchorage from the first layer in the rear face of decline wall north pour 3b.
| 02SL - Stations (LUL) | Cxxx-NCR-001373 | NCR | BTH - Pile 262, 263 + 264 low |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-11-30 | 2015-09-01 13:40 | -90 | 2015-08-13 16:05 | Geotechnical Engineering - Concrete - Bored Pile | 5000 |  | Design | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Piles 262, 263 and 264 were designed and instaled in line with Pilling Shedule 04002, with a cut off level of 107.345. Temporary props designed in accordance with Construction Sequence 42929, with a prop level of 110.8. Piles are too low to be propped.
| 02SL - Stations (LUL) | Cxxx-NCR-001374 | NCR | MTH - Cold joint to stairs on the 107.750m slab up to the 109.100m slab on GL 7/W |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-11-30 | 2015-10-06 14:00 | -55 | 2015-08-14 13:45 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On striking the stairs from the 107.750m slab to the 109.100m there appears to be cold joints in the concrete as shown on the attached photo.
| 02SL - Stations (LUL) | Cxxx-NCR-001375 | NCR | MTH - Missing angle fillet to beam soffit on 110.900m SSL landing |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-11-30 | 2015-10-28 10:45 | -33 | 2015-08-14 17:06 | Civil - Civil Engineering General | 3000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On completion of erecting the formwork/falsework for the half landing at 110.9m SSL it is evident that we have not installed the angle fillet to the beam soffit as shown on the attached.
| 02SL - Stations (LUL) | Cxxx-NCR-001376 | NCR | Issue of IRFs - __ lightning Protection |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2015-12-31 | 2015-11-24 23:30 | -37 | 2015-08-17 15:57 | Electrical - General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Lightning Protection installation activities required as witness points within approved ITP. IRFs for these have not been issued to allow witnessing of activities in line with works information.
| 02SL - Stations (LUL) | Cxxx-NCR-001377 | NCR | __X - VD1 waterproofing injection |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-12-31 | 2015-10-28 17:10 | -64 | 2015-08-18 17:48 | Tunnelling - Tunnelling General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Insufficient surveillance of subcontractors | Completed |  | Subcontractor __ (__) have drilled through and penetrated the Masterseal waterproofing system and injected with __ Masterrock 350 hydrophilic resin, similar to Cxxx-NCR-001367. The location is in the invert at the construction joint left by Cxxx in VD1, chainage 34.0, as part of Cxxx-PMI-00853.
| 02SL - Stations (LUL) | Cxxx-NCR-001378 | NCR | BTH - Pile Anchor Bars not Achieving Anchorage in Decline Wall West Pour 1 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-09-30 | 2015-09-13 12:44 | -17 | 2015-08-19 07:59 | Civil - Civil Engineering General | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 8no. B32 coupled pile bars did not achieve adequate anchorage as per Cxxx-RFI-002671.
| 02SL - Stations (LUL) | Cxxx-NCR-001380 | NCR | __X - Precast Stairs Damage on installation |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-02-20 | 2016-01-20 12:30 | -31 | 2015-08-20 16:39 | Structural Engineering - Pre-cast | 1500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | During the installation of the pre-cast stairs through openings A1 & B1 some of the precast stair units have suffered damage to the corners. See photos attached.
| 02SL - Stations (LUL) | Cxxx-NCR-001381 | NCR | __X - Column damage GL B/8 112-118 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-09-25 | 2015-09-23 12:32 | -2 | 2015-08-20 17:36 | Civil - Civil Engineering General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | When constructing the 118.860mATD slab the top of the column on GL B/8 has been damaged. See attached photo.
| 02SL - Stations (LUL) | Cxxx-NCR-001382 | NCR | BTH - Pile Anchor Bars not Achieving Anchorage in Decline Wall NorthPour 3a |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-10-30 | 2015-09-10 14:52 | -50 | 2015-08-21 15:32 | Civil - Civil Engineering General | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 14no. of the pile anchor bars in the southern decline north wall pour 3a do not meet the requirements of Cxxx-RFI-002671.
| 02SL - Stations (LUL) | Cxxx-NCR-001383 | NCR | __X - Lightning Protection Connection Damaged |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-11-30 | 2015-12-16 15:23 | 16 | 2015-08-24 11:30 | Civil - Civil Engineering General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The during the construction of the 118mATD slab pour 1 the connection shown on the attached sketch was damaged and the cable was removed after the connection was tested.
| 02SL - Stations (LUL) | Cxxx-NCR-001384 | NCR | BTH - South Wall pour 4, pile coupler embedment |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-11-30 | 2015-09-10 12:59 | -81 | 2015-08-28 11:28 | Structural Engineering - Reinforcement | 4500 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | One pile coupler (between GL4 -5 on the southern wall pour 4) did not have the required embedment depth, due to location and angle of Cxxx pile.
| 02SL - Stations (LUL) | Cxxx-NCR-001385 | NCR | BTH - Making Good Around Rear Face Coupler Bar Insufficient in Decline Wall North Pour 1 Soffit |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-10-13 | 2015-09-10 14:00 | -33 | 2015-09-01 11:09 | Civil - Civil Engineering General | 500 |  | Incomplete Works | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | 1no. rear face 3 reinforcing bar has had insufficient making good around the coupler between decline wall north pour 1 and 2. This would result in a void being left in the concrete if the void was not filled see attached photograph.
| 02SL - Stations (LUL) | Cxxx-NCR-001386 | NCR | MTH - Street Level Pour 2 reinforcement installed incorrectly where splicing into 112.500m slab |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-11-30 | 2015-09-18 10:43 | -73 | 2015-09-03 13:17 | Structural Engineering - Reinforcement | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On Street level pour 2 there are 6 B32 bars installed (BM 03) shown on CADS drawing Cxxx-LAO-C-DWG-C101_WS099-50027. The furthest bar north, so closest to the tower crane does not have any cover, see attached photo.
| 02SL - Stations (LUL) | Cxxx-NCR-001387 | NCR | MTH - PRM lift opening overbreaking |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-12-31 | 2015-12-15 16:59 | -16 | 2015-09-07 10:10 | Civil - Demolition/Site Clearance | 750 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The street level slab at Moorgate Ticket Hall between GL 11 and Gl 12 is being broken out for the PRM lift opening. Along GL 12 two areas of the exisitng slab have been over broken.
| 02SL - Stations (LUL) | Cxxx-NCR-001388 | NCR | Demolition Shield Installation |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-12-31 | 2015-11-19 15:55 | -42 | 2015-09-07 16:05 | Structural Engineering - Steel Member | 3000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | During the installation of the demolition shield there were clashes between the southern brickwork wall of 2/734 and CMS trunking.
| 02SL - Stations (LUL) | Cxxx-NCR-001390 | NCR | Dowel Bar Drilling and Platform Corbel Installation in CP9 |  | Contr | HAG | LIS - Liverpool Street Station (Central) |  | 2015-09-29 | 2015-09-23 13:41 | -6 | 2015-09-15 14:20 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other management problem | Completed |  | During the installation of dowel bars for CP9 platform corbels the drilled holes were not sufficiently cleaned by brushing and blowing prior to injecting with resin and inserting dowels.
| 02SL - Stations (LUL) | Cxxx-NCR-001391 | NCR | MTH - Concrete pour to wall W3a & W3b incomplete due to crane breakdown. |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-12-31 | 2015-10-01 10:46 | -91 | 2015-09-16 14:54 | Civil - Civil Engineering General | 500 |  | Equipment Breakdown | Use As-Is | 4 (0.5-3k) | Complete | External Phenomenon - Power failure or transient | Completed |  | During the concrete pour of the Street Level wall W3a & W3b on GL W our tower crane broke down restricting us from completing the pour to its intended construction joint.
| 02SL - Stations (LUL) | Cxxx-NCR-001392 | NCR | MTH - Grout infill failure on top of Culvert drain |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-03-31 | 2016-03-10 11:50 | -21 | 2015-09-16 15:39 | Civil - Civil Engineering General | 15000 |  | Material | Repair | 2 (6-60k) | Complete | Material/Preservation Problems - Other | Completed |  | To make up the difference in level on top of the culvert drain (approx 40mm) to the structural slab level of 107.750m we applied approved material Flexcrete Fastfill. We have now found an area where the grout has failed for a reason that is unknown. See attached photo where a hole has blown open and the grout appears to have expanded and cracked the area.
| 02SL - Stations (LUL) | Cxxx-NCR-001394 | NCR | __X: Low cover to mould face of precast north wall units |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-12-31 | 2015-11-06 14:33 | -55 | 2015-10-01 20:21 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | With refernce to the attached NCR and cover surveys, there is low cover on the mould face [trackside face] of the unit Local Deficiency [Worst case] 006 - 45mm 103 - 44mm 014 - 39mm 013 - 38mm 008 - 47mm 012 - 48mm
| 02SL - Stations (LUL) | Cxxx-NCR-001395 | NCR | BTH - Thermometer in concrete curing tank below minimum temperature |  | Crossrail | PDP | LIS - Liverpool Street Station (Central) |  | 2015-12-28 | 2015-12-20 21:18 | -8 | 2015-09-29 22:57 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | On Thursday 24th September the thermometer within the concrete curing tank in the BTH site was checked and this showed a current temperature of less than 18 degrees, below the required range of 20 +/- 2 degrees, see attached photo. This was advised to Eddie McCready.
| 02SL - Stations (LUL) | Cxxx-NCR-001396 | NCR | PLT - CP9 Corbel Design Deviations |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2015-12-31 | 2015-11-10 09:05 | -51 | 2015-09-30 12:08 | Structural Engineering - Concrete Member | 1500 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the construction of the corbels in CP9 defects were identified which required corrective action. They were; A. Excessive cover to the inside face shutter which measured in the region of 75mm in locations. The design requirement is Cnom = 40mm. B. Insufficient lap length between the face forming dowel bars fixed into the lining. Cxxx design states a minimum lap length of 200mm. In some locations this was measured to be around 60mm with an estimated average of around 125mm being achieved. This issue is believed to have occurred due to no allowances being made for the variation in tunnel lining profile leading to the lower dowels being drilled too high in locations. Both issues were discussed with Cxxx prior to pouring and rectification action agreed. This NCR has been raised to record the agreed alternative installation. Corrective action: A. Where cover excess cover outside allowed deviation (+10mm), addition links with front lacers were installed to reduce the cover to approx. 40mm. B. Contractor to ensure dowel bars have minimum anchorage length of 400mm inside corbel concrete where lap lengths have not been achieved.
| 02SL - Stations (LUL) | Cxxx-NCR-001397 | NCR | __X - North Wall Precast Drawings |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-12-31 | 2015-12-24 07:35 | -7 | 2015-09-30 14:07 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | The Contractor has commenced manufacture and installation of the North Wall Precast Units for Blomfield Box with drawings at CODE2 status requiring comments. Whilst the drawings have been revised and re-submitted they are not CODE 1 yet. Therefore the Contractor is at risk.
| 02SL - Stations (LUL) | Cxxx-NCR-001398 | NCR | __X - Column B7 Level 73.75 out of tolerence |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-01-31 | 2015-11-25 08:49 | -67 | 2015-10-01 14:57 | Structural Engineering - Steel Member | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On inspection of as-built drawings for Column B6 on Level +73.75m and +78.12 ATD of __X, deviation at top and middle of column were outside plan tolerance of +/-20mm as specified.
| 02SL - Stations (LUL) | Cxxx-NCR-001400 | NCR | __X - Columns out of tolerance 118-122 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-12-31 | 2016-01-19 16:17 | 19 | 2015-10-02 12:55 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Three of the vertical elements at the 118mATD to 122 mATD level are out of tolerance. The column GL B9 falls outside of the tolerance of +15/-0mm for cross sections and thicknesses of members. The column GL D6 falls outside of the tolerance of +/-20mm for column/wall position in plan. The wall GL D/7-8 falls outside of the tolerance of +/-10mm verticality for walls/columns. The as-built survey has been attached with the errors highlighted.
| 02SL - Stations (LUL) | Cxxx-NCR-001401 | NCR | BTH -Pile Anchor Bar not Enough Anchorage Decline Wall South Pour 6 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-11-13 | 2015-10-30 09:50 | -14 | 2015-10-05 12:32 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | 1no. pile anchor bar did not have sufficient anchorage in decline wall south pour 6 due to it being installed at an angle of approximately 45 degrees. It was installed at an angle of 45 degrees as every other attempt to install the bar resulted in the pile cage being hit.
| 02SL - Stations (LUL) | Cxxx-NCR-001403 | NCR | MTH - Crack in Street Level slab from ring bolt installation |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-12-31 | 2015-11-23 13:47 | -38 | 2015-10-08 10:04 | Structural Engineering - Structural Engineering - General | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | On installing a scaffold ring bolt in the face of the construction joint in pour 2 next to Moorhouse the soffit of the slab and the face of the construction joint has cracked, see attached photo and mark up for location.
| 02SL - Stations (LUL) | Cxxx-NCR-001404 | NCR | BTH - Decline Wall West Pour 2 Poor Surface Finish Post Striking of Formwork |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-12-31 | 2015-11-13 13:58 | -48 | 2015-10-08 09:41 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The surface finish of the decline wall west pour 2 was not to an acceptable F2 standard (see photographs attached). Minor finishing works would not classify an NCR but the extent of the finishing works required to bring this wall up to standard was deemed a nonconformity by the Crossrail Field Engineer, __ Section Engineer and the __ Quality Control Inspector.
| 02SL - Stations (LUL) | Cxxx-NCR-001405 | NCR | __X Precast north west corner |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-12-31 | 2015-11-10 10:52 | -51 | 2015-10-08 13:35 | Structural Engineering - Reinforcement | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | Incorporation of a temporary prop into the permanent works. This also resulted in >50% steel being omitted. Cxxx-FCD-001283 was raised detailing a change in the reinforcement in this area to accommodate the temporary prop. The Project Manager was informed of issue 4 hours prior to planned pour. Goodwill with the designer was required to work up a solution.
| 02SL - Stations (LUL) | Cxxx-NCR-001406 | NCR | __X North wall precast column-column stitch |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-12-31 | 2015-11-16 13:48 | -45 | 2015-10-08 13:42 | Civil - Structural Engineering | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Inspection of column-column stitches. 4no B16s installed instead of 4no B20s, on presentation of reinforcement for inspection. Issue was raised on 07/10/2015, prior to inspection.
| 02SL - Stations (LUL) | Cxxx-NCR-001407 | NCR | __X Lightning protection system installation |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2015-12-31 | 2015-11-24 12:12 | -37 | 2015-10-09 10:37 | Electrical - General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | No contractor attendance for installation and continuity testing of down conductors for Lightning protection system in line with the approved ITP. IRF issued without times of activities and no notice of works being undertaken
| 02SL - Stations (LUL) | Cxxx-NCR-001408 | NCR | __X: Blockwork Commence at 112 SSL witn incomplete design |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-01-31 | 2016-01-08 15:56 | -23 | 2015-10-15 09:10 | Architectural - Brickworks/Blockworks | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | To enable work continuity, Cxxx have instructed the trade contractor __ Ltd to commence work on 112 SSL using design information not yet submitted to Crossrail for acceptance . __ Ltd will build to limited scope as per the attached marked-up plan drawings . Due to pending final Builders works agreement due 16th October , work will only proceed with the first lift of blockwork (1575mm high) to safeguard builders work above . For walls between gridlines 8-9/ B-D, revisions to layout and stair support walls require final drawings to be issued by 16th October.Therefore, walls between gridlines 8-9/ B-D will not be built until drawings are submitted though Gate Impact Process
| 02SL - Stations (LUL) | Cxxx-NCR-001410 | NCR | MTH - Holes in Street Level Sump base slab |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-12-31 | 2015-12-11 15:11 | -20 | 2015-10-16 10:12 | Civil - Civil Engineering General | 1500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | When casting the 112.500m slab and sump in the High Walk Access Stair the tie through bolts for holding down the shuttered box in the sump did not have water barrier connectors resulting in holes penetrating through the base.
| 02SL - Stations (LUL) | Cxxx-NCR-001411 | NCR | __X: Precast North Wall Unit 102 Architectural Finish |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-11-30 | 2015-11-11 09:03 | -19 | 2015-10-20 15:14 | Architectural - Walls | 500 |  | Planning | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper handling of material | Completed |  | Ref: Cxxx-LAO-S-DWG-C101_WS103-50002 Unit 102 was delivered with its architectural finish dirty and stained. This was due to insufficient time between casting the unit and carrying out finishing works. While green, porous and more susceptible to staining, the concrete was finished in the blasting area and __ Manufacturing yard (a dirty environment).
| 02SL - Stations (LUL) | Cxxx-NCR-001412 | NCR | __X: Precast North Wall Unit 102 Missed cast in lighthing protection |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-01-31 | 2016-01-28 15:15 | -3 | 2015-10-20 15:47 | Civil - Civil Engineering General | 1500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | Unit 102 is 1 of 5 precast north wall units to have lightning protection cast within (see attached detail). Due to a drawing issue error, this detail was missed in the casting of this unit.
| 02SL - Stations (LUL) | Cxxx-NCR-001415 | NCR | BTH - Inclinometer blocked (IN207) |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-12-31 | 2015-12-21 11:01 | -10 | 2015-10-21 09:46 | Geotechnical Engineering - Geotechnical Monitoring | 3000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The inclinometer tube (IN207) due to be cast into Slab pour 6 has been found to be blocked at approximately 7.5m below the slab level. The blockage has been investigated with a camera and attempts have been made to unblock the tube, but it is suspected that concrete has entered the tube during pilling.
| 02SL - Stations (LUL) | Cxxx-NCR-001417 | NCR | BTH - Pile Cages low - Piles 247, 248, 251, 253, 260, 261 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-11-05 | 2015-11-05 10:59 | 0 | 2015-10-22 09:18 | Civil - Civil Engineering General | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The construction of the Southern Ticket Hall slab requires the line of piles spanning diagonally between gridline C10 and B11 to anchor into the slab with starter bars. The rebar cages in piles 247, 248, 251, 253, 260 and 261 all appear to have been cast in lower than the design level. This has resulted in their rebar falling short of the minimum 350mm projection from the concrete cut-off.
| 02SL - Stations (LUL) | Cxxx-NCR-001418 | NCR | BTH - Southern Ticket Hall Slab 6 Top Mat Clash with Precast Column Reinforcement |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-01-31 | 2015-11-30 15:47 | -62 | 2015-11-09 11:48 | Civil - Civil Engineering General | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Southern ticket hall slab 6 top mat reinforcement clashed with pre-cast column interlocking couplers. The column in question is located on GL B/10 and the level of the clash was approximately 107.950m ATD.
| 02SL - Stations (LUL) | Cxxx-NCR-001419 | NCR | Installation of CMS in __ staircase |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2016-01-31 | 2016-02-08 08:46 | 8 | 2015-10-23 15:16 | Electrical - Cable Management | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Insufficient information made available to the worker. | Completed |  | CMS installation not installed as per Current agreed construction drawings. FCD process not being followed.
| 02SL - Stations (LUL) | Cxxx-NCR-001421 | NCR | __X - Damage to concrete during tunnel breakthroughs |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-07-31 | 2016-07-28 10:47 | -3 | 2015-10-28 08:47 | Civil - Civil Engineering General | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Interfacing problems | Completed |  | During the breakthroughs for VD1, VD2 and AP1 several in-situ concrete elements have been damaged on levels 73mATD and 78mATD.
| 02SL - Stations (LUL) | Cxxx-NCR-001422 | NCR | __X - Party wall waterproofing damage GL 1 to 5 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-04-30 | 2016-03-07 14:07 | -54 | 2015-10-28 09:09 | Civil - Civil Engineering General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During construction works the party wall waterproofing has been damaged. This has occurred between GL 1 to 5, along GL A.
| 02SL - Stations (LUL) | Cxxx-NCR-001423 | NCR | BTH - South Decline North Wall 6 & 7 - Insufficient Pile Anchorage |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-11-13 | 2015-11-13 13:29 | 0 | 2015-10-30 10:58 | Civil - Civil Engineering General | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 27no. Pile anchor bars did not have enough anchorage into the southern decline lining wall pours 6 & 7.
| 02SL - Stations (LUL) | Cxxx-NCR-001424 | NCR | Continuing works with documents that have not been Coded |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-11-04 | 2015-11-13 15:16 | 9 | 2015-10-30 15:18 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Works for the installation of metal decking in the Blomfield Box, within CP9, started without the ITP (Cxxx-LAO-O4-ITP-C101-50062) and the MS (Cxxx-LAO-O4-GMS-C101-50082) being coded by Crossrail.
| 02SL - Stations (LUL) | Cxxx-NCR-001425 | NCR | __X: Plenum slab 114.860 SSL to be increased form 200mm dp to 300mm dp |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-02-28 | 2016-01-27 15:58 | -32 | 2015-11-25 12:54 | Civil - Civil Engineering General | 1000 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Due to the u-bars, protruding for the precast north wall units, being out of position the plenum slab (114.860m) we need to cut and resin fix new bars. We are unable to change the depth of the slab due to spaceproofing issues.
| 02SL - Stations (LUL) | Cxxx-NCR-001426 | NCR | MTH - Incomplete site records of concrete cube results for the OSD column pour 4 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-12-31 | 2015-11-04 11:16 | -57 | 2015-10-30 16:03 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Not Defined | Completed |  | We currently don’t have a site record for our 56 day cube results to the OSD column pour 4 that was sampled on 09/06/15. This is due to __ mistakenly disposing of our spare cube without testing it. The result is required as our 28 day cube result is 86 N/mm² and therefore it does not meet the requirement of 95 N/mm². We have contacted our supplier __ who internally made and tested their own set of cubes from the same concrete batch and have provided us with their cube results as attached. As shown in their results table the date, concrete ticket number and volume matches that of the delivery ticket signed for on site for the concrete that was placed in the OSD column, see attached. Their results show that the required strength has been reached at both 28 and 56 days, 124.3 N/mm² and 138 N/mm² respectively.
| 02SL - Stations (LUL) | Cxxx-NCR-001427 | NCR | MTH - Investigation required for possible cold joint to Street Level Wall on GL 7 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-01-31 | 2015-12-01 14:10 | -61 | 2015-11-03 09:24 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | With reference to the attached photo we have identified the possibility of a cold joint in the Street Level wall on GL 7.
| 02SL - Stations (LUL) | Cxxx-NCR-001428 | NCR | MTH - Crack in Highwalk Escalator slab |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-01-31 | 2015-12-01 14:09 | -61 | 2015-11-03 15:48 | Civil - Civil Engineering General | 7000 |  | Material | Repair | 2 (6-60k) | Complete | External Phenomenon - Other | Completed |  | Since striking the falsework to the Highwalk Escalator slab we have found water appearing in the soffit on wet days running from one side to the other (GL6 to GL7). It is now evident that there is a potential crack in the slab as per the attached photo's. The slab was cast with self compacting mix D5 and there was no delay between loads that would warrant a cold joint. The concrete cubes were tested to be 35 N/mm2 allowing for the permit to strike being signed off.
| 02SL - Stations (LUL) | Cxxx-NCR-001429 | NCR | __X CMS Installation staircase |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2016-02-28 | 2015-12-01 21:15 | -89 | 2015-11-05 16:50 | Electrical - Cable Management | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | CMS within __ staircase platform level and platform level +1 commenced without approved construction drawings
| 02SL - Stations (LUL) | Cxxx-NCR-001430 | NCR | __X: Mortar Cubes Not Made in Accordance with Approved Procedure |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-01-31 | 2016-02-04 13:26 | 4 | 2015-11-10 17:45 | Architectural - Brickworks/Blockworks | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | During the site visit (5/11/2015), the __ Supervisor showed the location where the last set of manufactured 100mm mortar cubes were being stored. it was noticed that both the 4N and 40N cubes were stored uncovered in a corner of the site at Level 89 free to the elements. Furthermore, it was noticed that the sampling information on the cubes were showed that they had been manufactured on 31st October 2015, six days before the surveillance visit.
| 02SL - Stations (LUL) | Cxxx-NCR-001431 | NCR | __X: Precast North Wall Unit 120 Damaged During Demould |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-02-28 | 2016-01-08 11:41 | -51 | 2015-11-10 08:45 | Civil - Structural Engineering | 750 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper handling of material | Completed |  | Unit has been damaged during demoulding, causing a large crack around part of the finger pocket. The unit will be repaired in line with Section 7 our the approved repair methodology (attached)
| 02SL - Stations (LUL) | Cxxx-NCR-001432 | NCR | __X: Protruding u-bars out of position in north wall precast units |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-12-09 | 2015-12-07 09:45 | -2 | 2015-11-25 12:57 | Civil - Structural Engineering | 1000 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | Due to confusion when reading the drawings, u-bars have been installed incorrectly in the precast units. They are 15mm lower than design which reduces the cover to the soffit to a measure that is insufficient.
| 02SL - Stations (LUL) | Cxxx-NCR-001433 | NCR | __X Starter bars for C3 from 106-112 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-12-31 | 2015-11-30 11:59 | -31 | 2015-11-11 11:22 | Structural Engineering - Concrete Member | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | Insufficient number of starter bars installed for Column C3.
| 02SL - Stations (LUL) | Cxxx-NCR-001434 | NCR | MTH - Incomplete concrete pour to Highwalk Access Stair level 113.705 to 115.488 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-01-31 | 2015-11-27 09:54 | -65 | 2015-11-13 08:33 | Civil - Civil Engineering General | 500 |  | Incomplete Works | Repair | 4 (0.5-3k) | Complete | Personnel Error - Other human error | Completed |  | When casting the Highwalk Access Stair up to level 115.488 we were short by 1.5m of concrete to complete the pour thus creating a construction joint, see attached photo. We contacted our supplier who was unable to supply any further concrete due to the plant being closed.
| 02SL - Stations (LUL) | Cxxx-NCR-001435 | NCR | BTH - Damage to underside of 107.950m Slab during basement excavation |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-02-28 | 2016-02-22 12:17 | -6 | 2015-11-16 08:14 | Civil - Civil Engineering General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | During the top-down excavation of the ticket hall basement, the excavators have caused minor damage to sections of the soffit of the ticket hall slab.
| 02SL - Stations (LUL) | Cxxx-NCR-001436 | NCR | Commencing Fabrication of Riser Frames without accepted documentation |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-02-28 | 2015-11-30 18:21 | -90 | 2015-11-18 07:34 | Materials - General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | The fabrication of the ME&P module frames commenced without all appropriate documentation being accepted by the Project Manager.
| 02SL - Stations (LUL) | Cxxx-NCR-001437 | NCR | BTH - Void in pile B171 southern ticket hall |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-02-28 | 2015-12-15 14:16 | -75 | 2015-11-17 17:01 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Approximately a 3m section of pile B171 located in the basement of the southern ticket hall has not been correctly concreted, resulting in a void in the pile.
| 02SL - Stations (LUL) | Cxxx-NCR-001438 | NCR | __X - Missing Couplers in 112 slab stitch pour 3 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-02-28 | 2015-11-30 17:33 | -90 | 2015-11-18 17:39 | Civil - Civil Engineering General | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | B25 couplers have been missed in two locations shown on the attached sketches.
| 02SL - Stations (LUL) | Cxxx-NCR-001439 | NCR | __X - Cracks in 133 slab |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-04-30 | 2016-04-21 07:54 | -9 | 2015-11-19 15:49 | Civil - Civil Engineering General | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | __ Engineer in the presence of CRL Representative has conducted further visual investigation of the cracking in the 133.860 SSL slab on 21/01/16. Findings are as follows: - Cracking appears to be isolated to areas around internal upstand plinth and columns GL C/9 & C/8. - Cracks vary in width from very narrow/ hairline to approximately 1mm (on the surface), and length from 100-500mm. - Tap tests were performed along the cracks and no obvious defects were observed in the underlying material. - Cracks in two locations (one near external column and one near the internal upstand plinth) were chased out to investigate their approximate depth. In both locations the cracks appeared to be discontinuous or <<0.3mm only 1-2 millimetres from the surface. - The soffit of the 133.860 SLL slab and beams was inspected and no defects/ structural cracking was found. Investigation has confirmed the original root cause of plastic shrinkage cracking due to insufficient protection of the freshly placed concrete during curing to be the most likely cause of the damage. Due to the limited extent and severity of the damage, and the fact that this floor is internal, __ propose no corrective action at this stage.
| 02SL - Stations (LUL) | Cxxx-NCR-001440 | NCR | __X 112 slab - poor workmanship |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-01-31 | 2015-11-27 09:02 | -65 | 2015-11-19 16:13 | Structural Engineering - Reinforcement | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | During inspection of the 112 slab, it was found that: steel had not been tied sufficiently, around box outs there was excessive to no cover provided and an untied bar was found to be protruding through the slab. Photos attached. These were closed out prior to pour by two fixers.
| 02SL - Stations (LUL) | Cxxx-NCR-001441 | NCR | __X - Fire ceiling at 109 missing couplers |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-02-28 | 2015-11-30 12:19 | -90 | 2015-11-20 18:19 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | The couplers shown on the attached sketch have been missed.
| 02SL - Stations (LUL) | Cxxx-NCR-001442 | NCR | __X: U-bars missing from the western side of Unit 024 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-02-28 | 2016-01-21 11:08 | -38 | 2015-11-25 12:26 | Structural Engineering - Pre-cast | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Ref: Attached NCR from __ Manufacturing and Agreed Detail to resolve U-bars shown in the design intent for the Precast North Wall were not detailed on __ Manufacture's Design Drawing. Therefore they were not cast in the precast. These u-bars were for the westernmost vertical stitch between the precast and the adjacent insitu concrete.
| 02SL - Stations (LUL) | Cxxx-NCR-001443 | NCR | __X: Precast North Wall, Damage Inflicted On Unit 121 During Demould |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-02-28 | 2016-01-08 11:42 | -51 | 2015-11-25 12:45 | Structural Engineering - Pre-cast | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During demould, Unit 121 suffered damage to an internal edge (see attached photos). A significant portion of the concrete came away with the mould.
| 02SL - Stations (LUL) | Cxxx-NCR-001444 | NCR | BTH - Water Ingress Through Construction Joints in the Southern Escalator Decline Wall |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-12-31 | 2016-11-10 14:28 | -51 | 2015-12-10 13:43 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Water ingress has been noted from the construction joints in the southern escalator decline in the following locations: 1) Decline wall north pour 3b and decline wall north pour 5. This is located between GL 1 - 2 at level 92.400m ATD. 2) Decline wall south pour 6 between GL 4 - 5 at level 99 - 98m ATD.
| 02SL - Stations (LUL) | Cxxx-NCR-001445 | NCR | __X - Rebar exposed on the soffit of Beam E on the 129 level |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-02-28 | 2016-01-15 11:31 | -44 | 2015-11-26 19:16 | Civil - Civil Engineering General | 1500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Reinforcement can be seen protruding through the soffit of the beam. This appears to be a loose piece of reinforcement which was left in the base of the pour. See attached photo.
| 02SL - Stations (LUL) | Cxxx-NCR-001446 | NCR | BTH - Basement Slab Pile Anchor Bars |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-03-30 | 2016-01-25 12:38 | -65 | 2015-11-30 09:35 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Several piles around the ticket hall contain couplers to tie into the basement slab which do not meet the design intent. Piles B213, B214, B218, B224, B227 and B244 contain couplers which are not set perpendicular to the pile line and subsequently direct the anchor bars off at a variety of angles. Pile F103 appears to be missing the couplers detailed in the design intent.
| 02SL - Stations (LUL) | Cxxx-NCR-001447 | NCR | Incorrect holes to __ Staircase CMS |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-02-28 | 2015-12-16 10:50 | -74 | 2015-12-02 09:10 | Electrical - Cable Management | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Incorrect holes drilled in CMS not aligning with bracketry. Gaps left so CMS is not compliant to IP4X.
| 02SL - Stations (LUL) | Cxxx-NCR-001448 | NCR | __X: Structural Damage to Unit 106 of the Precast North Wall |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-02-28 | 2016-02-04 16:40 | -24 | 2015-12-02 17:44 | Structural Engineering - Pre-cast | 1500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The temporary works design for casting the vertical stitches between the precast panels utilizes the lifting points cast into these panels. It is believed, upon cast the stitches either side of unit 106, the concrete pressure, for reasons not understood, was not evenly distributed between the lifting sockets of unit 106 and the adjacent panels. Therefore, the lifter shown, cast into unit 106, seems to have been overloaded and has therefore failed. The unit has suffered structural damage to a depth not yet known. The damage has been identified, by means of tapping the concrete surface with a steel rod, as a void behind the concrete surface. Cxxx intend to break the concrete back to the extents of the damage and then re-cast with in situ concrete. The images also show and area of concrete, between four cast-in sockets, where the concrete has fallen away. The cause of this damage has yet to be identified. The time this damage occurred has also yet to be identified. It is known, however, that the unit was not delivered having suffered this damage. This will be repaired with a dry mortar patch, in accordance with Concrete Making Good and Repair ITP Cxxx-LAO-O4-ITP-C101-50021.
| 02SL - Stations (LUL) | Cxxx-NCR-001449 | NCR | __X - 137 Slab Box out cover |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-02-28 | 2016-01-08 15:56 | -51 | 2015-12-03 15:37 | Structural Engineering - Reinforcement | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Pre pour was carried with Cxxx designer and signed off. Outstanding items were raised with Cxxx. During pouring box outs were inspected by CRL FE and found to have minimal cover due to proximity of bars. Foreman was instructed and supervised to move bars to cmin, at least and cnom, where practicable. See attached email regarding 133 and 112 slabs.
| 02SL - Stations (LUL) | Cxxx-NCR-001451 | NCR | PC Column Base Grout GL11 W and GL11 Y |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-01-28 | 2016-01-08 15:39 | -20 | 2015-12-04 15:41 | Civil - Civil Engineering General | 2000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Insufficient information made available to the worker. | Completed |  | The grout around the edges of the PC column bases on GL11 Y and GL11 W have cracked.
| 02SL - Stations (LUL) | Cxxx-NCR-001452 | NCR | __X - 3no. couplers installed at incorrect centres for 118 Slab Pour 2 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2015-12-18 | 2015-12-14 23:05 | -4 | 2015-12-04 16:05 | Civil - Civil Engineering General | 500 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | Supervision - Supervisor does not have access to all pertinent information | Completed |  | With reference to drawing Cxxx-LAO-C-DWG-C101_WS103-50300 bar mark E67 should have been installed at 125mm centers but were installed at 150mm centers. This occurred because the code 2 comments were not passed to the site operatives.
| 02SL - Stations (LUL) | Cxxx-NCR-001454 | NCR | __X: Concrete broken away from nib at base of North Wall Unit 023 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-05-29 | 2016-04-12 15:21 | -47 | 2015-12-04 17:06 | Structural Engineering - Pre-cast | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Upon installation of the precast unit, the fragile nib at the base of the unit has been undergone enough stress to cause a portion of the nib to fracture and fall away
| 02SL - Stations (LUL) | Cxxx-NCR-001455 | NCR | __X: Damage to base of precast unit 124 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-05-01 | 2016-02-23 14:40 | -68 | 2015-12-04 17:19 | Structural Engineering - Pre-cast | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper handling of material | Completed |  | Upon installation of the precast unit, the fragile nib at the base of the unit has been undergone enough stress to cause a corner of the nib to fracture and fall away
| 02SL - Stations (LUL) | Cxxx-NCR-001456 | NCR | __X: Unit 120 cast misshapen (not square) meaning one corner is proud of the architectural face of the wall |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-03-30 | 2016-03-23 09:23 | -7 | 2015-12-10 13:06 | Structural Engineering - Pre-cast | 500 |  | Manufacturing Defect | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Unit 121 has been cast misshapen and is not square. Therefore, while three corners of precast unit 121 are in their designed position, one is not. It is proud of the architectural face of the wall. See attached photo mark up and location plan.
| 02SL - Stations (LUL) | Cxxx-NCR-001457 | NCR | __X Omission of 92.4 slab after blockwork |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-04-30 | 2016-01-27 15:56 | -94 | 2015-12-05 11:37 | Structural Engineering - Concrete Member | 5000 |  | Planning | Repair | 3 (3-6k) | Complete | Personnel Error - Other human error | Completed |  | Cxxx raised on 04/DEC, that 92.4 slab had been omitted. Blockwork has been completed on this level, enclosing the area where the slab would be built. This may require the demolition of blockwork in order to facilitate the construction of the slab.
| 02SL - Stations (LUL) | Cxxx-NCR-001459 | NCR | BTH - Waterproofing to Eastern Edge of Basement Slab |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-02-11 | 2016-02-05 15:53 | -6 | 2015-12-17 13:44 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The basement slab has been poured and the waterproofing has not been installed as per Cxxx-LAO-C-DDD-C101-41407 Detail 31. __ was not installed underneath the slab resulting in the water path being reduced by 2m.
| 02SL - Stations (LUL) | Cxxx-NCR-001460 | NCR | __X: Blockwork suffered water damage, at level 106.740m, from concrete sawing above |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-08-01 | 2016-04-19 12:28 | -104 | 2015-12-15 08:28 | Architectural - Brickworks/Blockworks | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | Whilst saw cutting, inadequate protection was established to the finished architectural blockwork at 106.740m (beneath). Slurry / water has covered the face of the blockwork, damaging it.
| 02SL - Stations (LUL) | Cxxx-NCR-001461 | NCR | __X: Precast North Wall Dummy Joint Out of Vertical Alignment with Upper Panel |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-04-30 | 2016-04-05 15:36 | -25 | 2016-02-04 12:27 | Structural Engineering - Pre-cast | 500 |  | Manufacturing Defect | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | After installation it was found that one of the dummy joints on precast panel 122 did not match the joint below. See attached sketch. Due to the location of the panel being back of house on the West face we intend to leave as is.
| 02SL - Stations (LUL) | Cxxx-NCR-001462 | NCR | __X: Mortar Cubes made by __ for Blockwork failed at 28days |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-05-01 | 2016-04-19 14:08 | -12 | 2015-12-09 15:47 | Architectural - Brickworks/Blockworks | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | Ref: 28 day cube results (failure); 56 day cube results (pass).pdf (ATTACHED) Specimens made for compressive strength testing, of Wi Mortar (40N/mm2) have failed at age of 28days. These were made on 26/06/15 and represent Wi mortar used in the structural columns and beams in blockwork at Platform Level +3.
| 02SL - Stations (LUL) | Cxxx-NCR-001463 | NCR | BTH - Construction Joint Void Between Decline Wall North Pour 1 & 2 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-12-31 | 2016-11-10 14:30 | -51 | 2015-12-10 12:22 | Civil - Civil Engineering General | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On inspection a void was found between decline wall north pours 1 & 2. The void runs from the water bar (__ 500S) and the near face of the wall. The void is approximately 10mm wide. Photographs have been attached for clarity.
| 02SL - Stations (LUL) | Cxxx-NCR-001464 | NCR | __X - VD1 Wraparound shrinkage cracks |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-05-31 | 2016-06-06 10:34 | 6 | 2015-12-11 18:56 | Civil - Civil Engineering General | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Shrinkage cracks have been identified on VD1 wraparound. The crack width at each respective location is shown on drawing “Cxxx-MMD-C4-DDD-C101_Z-00621 C03 – NCR Crack location” which references the relevant crack photos. A photo of the wraparound (positioned within VD1 facing __X) and the sketch produced by Dan Reader on a site visit 10/12/15 have also been attached. The concrete pour was carried out on Friday 27th November and was cured by keeping the formwork in place for 2.5 days before striking on Monday 30th November. This method of curing is aided by the consistent temperature and high air humidity provided by the tunnel environment. The MCR for the concrete is attached which includes the mix design. REVISION 1: Shrinkage cracks have been identified on the upper half of VD1 wraparound also. The crack width at each respective location is shown on drawing “Cxxx-MMD-C4-DDD-C101_Z-00621 C03 – NCR Crack location REV1” which references the relevant crack photos. The concrete pour was carried out on Thursday 10th December and was cured by keeping the formwork in place for 3.5 days before striking on Monday 14th December. Curing agent was applied to the exposed face upon striking.
| 02SL - Stations (LUL) | Cxxx-NCR-001465 | NCR | BTH - Additional Construction Joint in Decline Wall South Pour 10 & 11 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-03-30 | 2016-02-05 16:02 | -54 | 2015-12-15 16:34 | Civil - Civil Engineering General | 3000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A leak occurred while decline wall south 10 & 11 was being poured which resulted in the pour being abandoned. This resulted in the pour height being incomplete.
| 02SL - Stations (LUL) | Cxxx-NCR-001466 | NCR | __X: Cable protruding from 118.860m slab |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-03-30 | 2016-01-26 12:01 | -64 | 2015-12-15 09:53 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In casting the 118.860m slab stitch, a cable, believe to be earthing, was left protruding from the slab.
| 02SL - Stations (LUL) | Cxxx-NCR-001467 | NCR | __X - Damage to Column D4 at 112.860 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-02-13 | 2016-02-01 13:51 | -12 | 2015-12-15 10:29 | Civil - Civil Engineering General | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | During the installation of the North Wall Precast Units damage was caused to column D4 on the 112 level. (See the attached Pictures)
| 02SL - Stations (LUL) | Cxxx-NCR-001468 | NCR | __X: Damage inflicted on column to facilitate temporary works bracket for Precast North Wall |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-03-30 | 2016-02-05 16:13 | -54 | 2015-12-15 10:34 | Civil - Civil Engineering General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Due to poor coordination between the temporary and permanent works design, a concrete column had to be broken away to make space for a temporary works item (bracket).
| 02SL - Stations (LUL) | Cxxx-NCR-001469 | NCR | __X - Concrete cubes not stored correctly |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-03-30 | 2016-01-25 07:58 | -65 | 2015-12-18 08:20 | Civil - Civil Engineering General | 0 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | For the pour carried out on the 04/12/2015 for column B2 from 106-112 the concrete cubes were left out in the open over night. This will be reviewed when the compressive strength results are obtained.
| 02SL - Stations (LUL) | Cxxx-NCR-001470 | NCR | __X - Defects in soffit on 78.120mATD slab |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-07-31 | 2016-07-28 10:53 | -3 | 2015-12-18 08:41 | Civil - Civil Engineering General | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | When cleaning out the soffit formwork for the 78.120mATD slab all of the loose material was blown into areas of the deep beams and was not removed prior to pouring concrete. This material is a mixture of wood dust and tie wire. The defective areas will be broken out and repaired in line with our Method Statement for making good.
| 02SL - Stations (LUL) | Cxxx-NCR-001471 | NCR | MTH. Blockwork installed to MHS RC beam soffit on street level prior to instructed RC remedial works completed |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-03-31 | 2015-12-20 21:22 | -102 | 2015-12-18 09:27 | Civil - Civil Engineering General | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Management Problem - Other management problem | Completed |  | The MHS blockwork was mistakenly installed to the soffit of the existing MTH soffit beam at street level which still requires additional works (refer to EWN946, PMI 808, EWN1039). At the time of blockwork installation the additional concrete repair method was still to be agreed. __ removed the top two layers of blockwork to allow for the additional works to the soffit to be completed. Please note that the additional works to the MHS RC beam soffit in this area is not a NCR and is instructed works by CRL. The blockwork will be completed once the additional remedial works method has been agreed and implemented on site.
| 02SL - Stations (LUL) | Cxxx-NCR-001472 | NCR | __X - Drill & Fix List |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-06-30 | 2017-07-24 16:10 | 24 | 2015-12-18 16:21 | Structural Engineering - Reinforcement | 10000 |  | Documentation and Records | Repair | 2 (6-60k) | Complete | Management Problem - Inadequate administrative control | Completed |  | FCD-001334 (See attached) FCD-001331 (See attached) Drawing Cxxx-LAO-C-DWG-C101_WS103-5029 (See attached) 129 Wall 4 (-50331) 133 Wall 4 (-50333) 118 riser infill (above riser 786) Half Landing @ 127 Plenum Slab 116.760 (poured 10/02/16) Plenum Slab 114.360 (poured 29/01/16) Plenum Slab 114.360-118.860 (poured 03/02/16) Plenum Slab 114.860 (poured 22/01/16) Wall 112-118 GLB pour #3 (poured 05/02/16) Grout Box 112-118 GL B1-3 wall pour #2 (poured 04/02/16) Wall 112-118 GLB West grid pour #1 (poured 02/02/16)
| 02SL - Stations (LUL) | Cxxx-NCR-001473 | NCR | MTH - staining to precast columns |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-03-31 | 2017-07-27 12:49 | -247 | 2016-01-05 16:37 | Structural Engineering - Pre-cast | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | 2 no. precast concrete columns on GL 10/ Y-Z have sustained staining from the timber beam formwork. Column on GL 10/Y has minor mechanical damage
| 02SL - Stations (LUL) | Cxxx-NCR-001474 | NCR | BTH - South Basement Lining Wall 1 Missing Couplers |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-02-03 | 2016-01-14 12:57 | -20 | 2016-01-06 08:00 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 5no B25 couplers are missing from the downstand kicker cast as part of the North Ticket Hall slab in front of pile B171. 3no. B32 couplers are missing from the pile clutch between piles B172 and B173.
| 02SL - Stations (LUL) | Cxxx-NCR-001475 | NCR | __X - Missing Chamfers on External Edges |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-10-31 | 2016-12-14 13:29 | 44 | 2016-01-06 16:03 | Civil - Civil Engineering General | 2500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Several external edges at Blomfield Box have been cast without chamfers. An as-built of all the areas will be produced and a remedial action will be proposed.
| 02SL - Stations (LUL) | Cxxx-NCR-001476 | NCR | Removal of Moorhouse Blockwork underside of Waterproofing |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-04-04 | 2016-04-01 10:32 | -3 | 2016-01-06 16:50 | Architectural - Brickworks/Blockworks | 1000 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | In 5No. locations blockwork has incorrectly been installed to the underside of non compliant waterproofing. The blocks should have been left out so that we could scabble off the waterproofing.
| 02SL - Stations (LUL) | Cxxx-NCR-001477 | NCR | __X - South Wall 112-118 Void at top of wall between GL 4-5 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-03-07 | 2016-01-25 07:59 | -42 | 2016-01-07 08:55 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following striking of the south wall between the 112-118 slab GL4-5 a void was found at the interface between the 118 slab and top of the wall ( See pictures)
| 02SL - Stations (LUL) | Cxxx-NCR-001478 | NCR | BTH - Decline Wall South Pour 10/11 & Decline Wall North Pour 8/9 Minor Surface Void |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-12-31 | 2016-11-10 14:29 | -51 | 2016-01-11 10:23 | Civil - Base Course | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the post pour inspection of decline wall south pours 10 & 11 (top up) and decline wall north pours 8 & 9 it was found that in places up to a 10 mm void can be found where the two pours do not meet. When probed the void extended into the wall up to 100 mm in places.
| 02SL - Stations (LUL) | Cxxx-NCR-001479 | NCR | __X - Couplers at incorrect spacing on 118 slab |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-03-04 | 2016-01-18 10:18 | -46 | 2016-01-08 11:31 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | See attached sketch showing the area were couplers have been installed at 200mm centers instead of 150mm centers. The reinforcement in the slab has been fixed at 150mm centers as per design.
| 02SL - Stations (LUL) | Cxxx-NCR-001480 | NCR | __X - North Wall Precast Missing Box Out |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-03-08 | 2016-03-03 09:24 | -5 | 2016-01-12 12:38 | Civil - Civil Engineering General | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Drawing Cxxx-MMD-C-DDA-C101_A-31013 shows a box out that should be provide in the North precast wall near the intersection of gridlines D and 4. This box out was not included in the precast design and no box out was installed on the panel when it arrived on site. We have broken out the area on the precast unit so that the OSD column plinth can be installed. We will then agree a repair methodology using the same materials as the original unit and repair the damaged area.
| 02SL - Stations (LUL) | Cxxx-NCR-001481 | NCR | __X Non-production of PPIRs as per ITP |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-03-31 | 2016-01-25 14:00 | -66 | 2016-01-13 08:33 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Non-production of PPIRs as per ITP (-50410), item 22, for works conducted on 8th/9th Jan.
| 02SL - Stations (LUL) | Cxxx-NCR-001485 | NCR | MTH - Only 1 No. 28 day cube result available per Street Level Wall on GL 6 and GL 7 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-02-16 | 2016-02-12 15:15 | -4 | 2016-01-19 14:38 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Other human error | Completed |  | We currently only have one 28 day cube result which is not in accordance with BS EN 12350-1:2009 and BS 1881-125:1986 for the Street Level wall on GL 6 and also one 28 day result for the Street Level pour on GL 7 which were cast on 21/09/15 and 28/09/15 respectively. The 28 day cube result we do have has reached the required strength as shown on the attached Test Data sent through by __.
| 02SL - Stations (LUL) | Cxxx-NCR-001486 | NCR | BTH - Hy-Rib used to Form the Ticket Hall Basement Sump |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-02-17 | 2016-02-05 15:50 | -12 | 2016-01-20 09:31 | Civil - Civil Engineering General | 1500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Hy-Rib, which is a proprietary permanent metal stop-end made from expanded metal, has been used to form the sump in the ticket hall basement. Photos have been attached showing this.
| 02SL - Stations (LUL) | Cxxx-NCR-001487 | NCR | __X - Half landing at 127.620 cast at the wrong level |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-03-16 | 2016-03-15 11:42 | -1 | 2016-01-20 08:40 | Civil - Civil Engineering General | 5000 |  | Design | Repair | 3 (3-6k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | The half landing at the 127.620 has been cast at a level of 127.810. This is due to an error in the __ drawing. The precast stairs therefore do not fit. We intend to break out the half landing and recast in the correct position.
| 02SL - Stations (LUL) | Cxxx-NCR-001488 | NCR | BTH - Decline Precast Special Planks |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-02-17 | 2016-02-08 16:17 | -9 | 2016-01-20 15:43 | Architectural - Roofing & Exterior Treatment | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The BTH decline precast roof transition units have not been constructed as per the ICD.
| 02SL - Stations (LUL) | Cxxx-NCR-001490 | NCR | NCR-MTH-Incorrect hole locations on Moorhouse precast frame |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-04-30 | 2016-04-21 11:37 | -9 | 2016-01-21 17:18 | Structural Engineering - Structural Engineering - General | 1000 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Personnel Error - Other human error | Completed |  | Ref Cxxx-LAO-C-DDD-C101_Z-11137 The two steel columns, C1 and C2, were fabricated with the 14mm connection bolt holes in with wrong location. 4No. m14 holes were incorrect on the web and 2No. m14 holes were drilled on the wrong flange.
| 02SL - Stations (LUL) | Cxxx-NCR-001491 | NCR | BTH - Basement Level - upstand and downstand kicker misalignment |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-02-22 | 2016-02-22 17:40 | 0 | 2016-01-25 16:14 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The upstand kickers poured as part of the basement slab are misaligned with the ticket hall downstand kickers in several locations. In three locations, this has resulted in a step in the concrete where the lining wall has been cast. The attached scan of the pour layout with surveyed data at the downstand and upstand kickers identifies the location of these discrepancies. The key areas are: Point 1, where the downstand kicker sits 79mm into the cavity; Point 3, where the upstand kicker sits 40mm into the lining wall; Point 7, where the upstand is stepped back into the lining wall by 20mm; Point 8, where the downstand is stepped back into the lining wall by 74mm; Point 20, where the upstand kicker sits 31mm into the cavity. In all cases, cover to reinforcement has been maintained within specifications and lining walls have been poured to meet the general arrangement drawings. As-built of lining walls will be provided to CRL to identify any issues.
| 02SL - Stations (LUL) | Cxxx-NCR-001492 | NCR | __X - Missing Box Out on the 84.060mATD Slab |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-03-29 | 2016-03-03 13:06 | -26 | 2016-02-02 10:20 | Civil - Civil Engineering General | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | The box out shown on the attached drawing was not included during construction. This is required for Systemwide cable routes and cannot be taken along a different route. We propose to core drill a 200mm diameter hole in this location. Please confirm this is acceptable.
| 02SL - Stations (LUL) | Cxxx-NCR-001493 | NCR | Blomfield Box Riser 784 Frame Construction Errors |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-02-24 | 2016-02-08 14:46 | -16 | 2016-01-27 14:10 | Electrical - General | 500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Riser 784 bottom module manufactured and delivered without holes and threaded bushes for temporary wing plates to allow keying off at 118 slab level as per planned installation sequence. Latest drawing not followed. This lead to abortive shift for Lifting Team and Crane Driver. MEP operatives were deployed elsewhere on CMS works.
| 02SL - Stations (LUL) | Cxxx-NCR-001494 | NCR | __X - Column C1 GL B2 starter reinforcement |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-03-28 | 2016-03-16 17:30 | -12 | 2016-02-01 13:23 | Civil - Civil Engineering General | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | The starter reinforcement for column C1 from 106-112 has been installed as 8no. B25 instead of 16no. B25. The reinforcement was fixed based on a code 1 CADs drawing which was incorrect.
| 02SL - Stations (LUL) | Cxxx-NCR-001495 | NCR | BTH - Cube Tank Temperature outside specification |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-03-02 | 2016-03-03 11:21 | 1 | 2016-02-03 09:07 | Civil - Civil Engineering General | 0 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | On a recent inspection of the Cube shed it was observed that the temperature of the cube tank was 17C rising. This is outside of specification.
| 02SL - Stations (LUL) | Cxxx-NCR-001496 | NCR | BTH - Reinforcement left in mud /standing water |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-03-02 | 2016-02-25 14:39 | -6 | 2016-02-03 14:15 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Contamination | Completed |  | Reinforcement for basement internal walls sat in muddy standing water on the basement slab level. Residue from the muddy water was left on some of the bars as they dried. This is incorrect storage practice.
| 02SL - Stations (LUL) | Cxxx-NCR-001498 | NCR | builders work holes within block work walls __ platform +1,+2,+3 |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2016-05-31 | 2016-06-13 07:54 | 13 | 2016-02-04 15:37 | Architectural - Brickworks/Blockworks | 10000 |  | Supervision/Management | Repair | 2 (6-60k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | Block work wall penetrations for MEP services had been coordinated inline with Cxxx gated design and not the stage F drawings produced by Cxxx. this has created major re works to the CMS installation and also to the block work walls where new penetrations are now required.
| 02SL - Stations (LUL) | Cxxx-NCR-001499 | NCR | __X - 28 day cube failure for fire ceilings at 109mATD and 116mATD |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-05-27 | 2016-04-01 11:32 | -56 | 2016-02-05 08:13 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The 28 day cube results taken on the 22/12/2016 have failed to meet the requirements of the specification. See attached cube results and pour history. The concrete was tested on site and was within the specified limits for an F5 concrete mix and the density of the cubes tested was good. Therefore we can only assume that this is an anomalous result. We will wait for the 56 day result to close out this NCR. See attached 56 day result which meets the strength requirement.
| 02SL - Stations (LUL) | Cxxx-NCR-001500 | NCR | __X - North Wall Precast Panel 124 Surface Crack |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-05-27 | 2016-04-01 10:30 | -56 | 2016-02-05 08:24 | Civil - Civil Engineering General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Upon inspection of damage to another precast panel in the vicinity, a crack has been discovered on the exterior face of unit 124. The crack has been measured with a crack width ruler and found to be under 0.3mm. Photos and mark-up of the extent of the damage attached. No evidence of damage has been found on the inside face of the panel. The exact cause of the damage in unknown, however it may have been a result of overstressing the bottom of panel whilst positioning it with the temporary works items.
| 02SL - Stations (LUL) | Cxxx-NCR-001501 | NCR | MEP RISER MODULE 784 FOR BLOMFIELD BOX |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2018-01-31 | 2017-12-21 19:56 | -41 | 2016-02-05 11:30 | Electrical - Cable Management | 10000 |  | Manufacturing Defect | Repair | 2 (6-60k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Module 784 has now been delivered to site and installed, on inspection it is clear that in its current state the Module is not fit for purpose, this is due to the ladder not being fit for the purpose it is designed and un usable as a ladder, the gaps around cms penetrations are to large, access to install cable cleats on the cable trays is not possible to to the lack of access to the back of the cable trays, this is an outstanding issue raised during design review that had not been addressed and will now require additional work on site to rectify
| 02SL - Stations (LUL) | Cxxx-NCR-001502 | NCR | BTH - Decline Slab Pour 12 Reinforcement |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-03-07 | 2016-03-01 17:30 | -6 | 2016-02-08 17:13 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Due to reinforcement congestion when fixing the decline lining wall either side of base slab pour 12 it was not always possible to cast the couplers picking up the top mat in the correct position. As a result 12no. T1 screw bars have been fixed into T3 on the south side and 14no. T1 screw bars have been cast into T3.
| 02SL - Stations (LUL) | Cxxx-NCR-001503 | NCR | MTH - Missing couplers in Wall W1 pour W2 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-04-30 | 2016-02-26 09:34 | -64 | 2016-02-08 14:09 | Structural Engineering - Reinforcement | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | When casting the top up of Wall 1 pour W2 shown on CADS drawing Cxxx-LAO-C-DWG-C101_WS099-50052 and Motts drawing Cxxx-MMD-C-DDA-C101_2-12001 which is approximately from level 112.320 to 112.845, 6 B32 couplers BM E89 have not been installed. Also see attached markup for clarity.
| 02SL - Stations (LUL) | Cxxx-NCR-001504 | NCR | Blomfield box riser Module 786 |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2016-11-30 | 2016-10-19 14:13 | -42 | 2016-02-10 13:40 | Electrical - Cable Management | 5000 |  | Supervision/Management | Rework | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | we have been advised today that riser module 786 is to be delivered to site and installed tonight 10/02/2016, there has been no notification of final inspection of MEP modules which is a witness point within Cxxx ITP Cxxx-lao-o4-itp-c101-ws103_50051 section 4.1, and in addition we have not seen any assurance evidence listed in the ITP SECTION 3 module assembly. In addition there is still an outstanding design comment raised on all modules relating to access to the cable trays to install cable cleats, this has not been rectified on the first riser module installed 784 and we have not been advised if this has been rectified on this riser module 786.
| 02SL - Stations (LUL) | Cxxx-NCR-001505 | NCR | __X CMS installation Platform +1 inadequate support |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2016-05-31 | 2016-04-26 11:55 | -35 | 2016-02-10 15:31 | Electrical - Cable Management | 3000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Supervision - Other | Completed |  | CMS installation within Blomfield box has been subject to repeated alteration with regards to the height and configuration of the CMS layout. This has changed once again and as a result the top tier of Containment has been installed and fixed onto inadequate support brackets, this will need reworking to make it fit for purpose. 2 no. Cable trays installed along the southern wall of the vent shaft in __X, these are over hanging the uni struts installed and not fully supported
| 02SL - Stations (LUL) | Cxxx-NCR-001506 | NCR | MHS. Trimming of kicker in VD4 shaft |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-07-31 | 2016-07-01 11:32 | -30 | 2016-02-11 11:26 | Civil - Civil Engineering General | 1500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Personnel Error - Other human error | Completed |  | The kicker cast by __ at the invert of VD4 doesn’t align with the tunnel opening of VD4. The following discrepancies have been identified a) the end of the kicker is radial and not perpendicular to the centre line b) opening is off set form the centre line c) is smaller than the required opening. The proposal is for the kicker to be broken back to the required alignment, apply a reinforcement protection coating (Flexcrete E492 - MCR Cxxx-LAO-O4-XDS-C101-50170) and to be made good. The affected zones are: area 1) 550x900x150mm, area 2) 300x900x150mm containing B12 reinforcement
| 02SL - Stations (LUL) | Cxxx-NCR-001507 | NCR | BTH - Basement wall 9, 10, 11, 12 finish |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-04-07 | 2016-04-04 13:41 | -3 | 2016-02-11 17:25 | Structural Engineering - Concrete Member | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Basement walls 9, 10, 11, 12 have surface defects in the form of blow-holes, and some chamfers have been missed of exposed wall corners.
| 02SL - Stations (LUL) | Cxxx-NCR-001508 | NCR | MTH Future PRM Lift Precast Slabs Level |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-03-15 | 2016-03-17 08:49 | 2 | 2016-02-16 09:03 | Civil - Structural Engineering | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | The level of the precast slabs in the future PRM area are set at a level of 113.980m, 70mm below the proposed 114.050m SSL. The PC slabs were to be sat on 120*120*10 angle irons, the steel angles installed on site were 200*200*18 angle irons. This is the reason for the change 70mm change in level.
| 02SL - Stations (LUL) | Cxxx-NCR-001509 | NCR | BTH- Basement sump missing reinforcement |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-03-21 | 2016-03-03 11:40 | -18 | 2016-02-22 12:13 | Structural Engineering - Concrete Member | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Reference is Broadgate Ticket Hall 104.150 SSL basement sump. Drawing ref. Cxxx-LAO-C-DWG-101_WS102-50225, Cxxx-LAO-C-TSC-C101_WS102-50119 Missing links (bar mark 9). Only 23 out of the 26 required were installed. Refer attached "basement sump-1". Incorrect splicing of L-bars in locations as detailed in sketch attached "basement sump-1 & 2". Incorrect anchoring of links due to existing reinforcement congestion. Refer "basement sump-2".
| 02SL - Stations (LUL) | Cxxx-NCR-001510 | NCR | __X - OSD Couplers Not Installed |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-06-30 | 2016-06-23 13:44 | -7 | 2016-02-23 09:32 | Civil - Civil Engineering General | 1000 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The B25 couplers for the future OSD shown on the attached sketch taken from the design intent where not installed. These couplers where not added to the reinforcement detail drawings and this was not picked up on any comment sheet until after the beams where poured. We will carry out a scan of the reinforcement to assess whether we can drill through and resin fix coupler bars.
| 02SL - Stations (LUL) | Cxxx-NCR-001511 | NCR | BTH - Basement Services Opening Incorrectly Constructed |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-07-31 | 2016-07-27 08:08 | -4 | 2016-02-29 13:58 | Civil - Civil Engineering General | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The vertical services opening connecting the southern decline to the basement at the location of the disability lift has been constructed incorrectly. The opening has been constructed such that it is some 1.0m short as part of the partition wall was overpoured.
| 02SL - Stations (LUL) | Cxxx-NCR-001512 | NCR | MTH - PRM Lift GL 11 - 12 Box out position |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-05-31 | 2016-05-19 10:00 | -12 | 2016-03-02 13:21 | Civil - Civil Engineering General | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | When constructing the builders work box out (810x393mm wide) for the lift control panels, the setting out was undertaken incorrectly from the drawing attached (Layout for Builder L1 – __). The box out in the wall was created when viewed from outside of the lift shaft rather than the inside. This created the wrong orientation of the control panels and is not acceptable to the lift manufacturer ‘__’.
| 02SL - Stations (LUL) | Cxxx-NCR-001513 | NCR | __X - Gulley cast in the wrong location |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-06-23 | 2016-04-11 17:53 | -73 | 2016-03-03 13:29 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The gulley on the 137.060mATD slab shown on the attached drawing has been installed in the wrong location. When discussing with the MEP team the gulley does not work in this location. We need to core drill through the slab and reinstall this gulley in the correct location. We intend to core drill a 250mm diameter core and install the gulley and grout in place using a non shrink grout. For the gulley that is installed we will cut flush with the concrete and fill with grout. Please confirm that this is acceptable.
| 02SL - Stations (LUL) | Cxxx-NCR-001515 | NCR | __X - AP1 Wraparound downstand width |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-07-31 | 2016-04-06 09:15 | -116 | 2016-03-08 10:31 | Civil - Civil Engineering General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Down stand as detailed on drawing Cxxx-MMD-C4-DDD-C101_Z-00620 and clarified in email by __ (Cxxx) in email dated Mon 07/03/2016 as minimum of 250mm could not be achieved. This is due to the need to balance the requirement s of Cxxx-FCD-001349 and permanent and temporary works. A minimum od 140mm has been achieved.
| 02SL - Stations (LUL) | Cxxx-NCR-001516 | NCR | TUN - AP1 Blockwork Discrepancy |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-07-31 | 2016-04-06 09:17 | -116 | 2016-03-08 15:23 | Architectural - Brickworks/Blockworks | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Various penetrations in the blockwork constructed at the Western end of tunnel AP1 have been installed as per the latest __ information and not as per the latest MEP (Crown House Technologies) builderswork information. Of these, two of the penetration's height is approximately 90mm less than design. Refer to attached overlay of MEP and __ penetrations for penetration and discrepancy locations.
| 02SL - Stations (LUL) | Cxxx-NCR-001517 | NCR | BTH - As-built position of AP8 walls 6, 7 and 8 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-06-03 | 2016-06-03 16:34 | 0 | 2016-03-08 15:28 | Structural Engineering - Concrete Member | 5000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the pouring of the wall it was noted that the top of the shutter had moved away from the re-bar, attempts were made to extent the push-pull props to correct the movement. This partially corrected the error, but started to lift the shutter so no more adjustments were made to the props. Survey of the wall after striking reviled the maximum deflection of the wall from design position as 61mm south.
| 02SL - Stations (LUL) | Cxxx-NCR-001518 | NCR | TUN - Damage to UTX ducts in PTW |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-07-31 | 2016-04-21 09:34 | -101 | 2016-03-08 17:59 | Electrical - Cable Management | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | One pair of UTX ducts installed in Platform Tunnel West have been damaged by passing MEWPs operated by __ personnel. Please see attachments.
| 02SL - Stations (LUL) | Cxxx-NCR-001520 | NCR | MTH. Concrete Cubes Crushed at incorrect durations |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-06-30 | 2016-03-15 16:18 | -107 | 2016-03-09 17:26 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Other human error | Completed |  | A set of 4no concrete cube have been taken for MTH concrete samples MTH 99 to MTH 104 (attached) however a mistake has occurred on site when completing the __ paperwork requesting that the cubes are crushed after A: 7 days B: 14 days C: 28 days and D: Spare. The spare cubes where disposed off once conformation of the 28 day cube result reached required strength. This means that there is only one 28 day test result for samples MTH 99 to MTH 104.
| 02SL - Stations (LUL) | Cxxx-NCR-001521 | NCR | MTH - Cut to top flange of GL Z existing steel beam |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-06-30 | 2016-03-24 08:10 | -98 | 2016-03-10 16:15 | Structural Engineering - Steel Member | 3500 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Insufficient information made available to the worker. | Completed |  | A cut has been made incorrectly through the top flange of the existing steel beams on GL Z in Moorgate ticket hall adjacent to GL 9.
| 02SL - Stations (LUL) | Cxxx-NCR-001522 | NCR | MTH - Staining to PC columns on delivery |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-07-31 | 2016-05-19 10:03 | -73 | 2016-03-10 16:37 | Structural Engineering - Pre-cast | 3000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper storage of material | Completed |  | 3 no. white architectural columns were delivered to site on 9th March with staining/ dirty marks.
| 02SL - Stations (LUL) | Cxxx-NCR-001523 | NCR | BTH Decline Screwjacks |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-06-01 | 2016-05-31 16:00 | -1 | 2016-05-04 14:01 | Structural Engineering - Pre-cast | 6000 |  | Documentation and Records | Rework | 3 (3-6k) | Complete | Subcontractor Problems - Insufficient work planning by the subcontractors | Completed |  | 26No. Screw jack supports required for the southern decline precast planks sloping section have been fabricated with the angle of the threaded sockets facing the same direction as opposed to being handed.
| 02SL - Stations (LUL) | Cxxx-NCR-001524 | NCR | Late Delivery of Riser Modules |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-07-31 | 2016-04-26 11:49 | -96 | 2016-04-05 08:48 | Materials - General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Modules due for delivery on 10/03/2016 were not delivered.
| 02SL - Stations (LUL) | Cxxx-NCR-001525 | NCR | Damage to Blockwork During Riser Module Installation |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-07-31 | 2016-06-06 15:26 | -55 | 2016-04-05 08:59 | Architectural - Brickworks/Blockworks | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Scrapes to surface of blockwork
| 02SL - Stations (LUL) | Cxxx-NCR-001526 | NCR | Riser Module 790 Installed Without The Hydrant Pipework Being Installed |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-06-30 | 2016-06-22 14:09 | -8 | 2016-04-05 09:00 | Mechanical - Piping | 5000 |  | Material | Rework | 3 (3-6k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | The Riser Module 790 was assembled and installed without the required galvanized hydrant pipework being included within the fabrication. Pipework was not available for delivery in time to install into the prefab module prior to the last remaining required delivery and installation date.
| 02SL - Stations (LUL) | Cxxx-NCR-001527 | NCR | Galvanising Damaged on Pipework Stored at Westferry |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-08-31 | 2016-05-26 14:07 | -97 | 2016-04-05 09:04 | Mechanical - Piping | 10000 |  | Material | Repair | 2 (6-60k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Galvanising debonded from substrate
| 02SL - Stations (LUL) | Cxxx-NCR-001529 | NCR | TUN - Pressure relief drainage damaged by precast trolley |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-04-11 | 2016-04-06 09:12 | -5 | 2016-03-14 17:36 | Civil - Drainage | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | An area of installed pressure relief drainage in the Westbound Tunnel has been damaged by the tug and precast trolley. The 25mm layer of concrete above the drainage was cracked and the eggcrate sheet caved in under the weight of the trolley loaded with a precast L-wall. See attachments.
| 02SL - Stations (LUL) | Cxxx-NCR-001530 | NCR | BTH - Waterproof install to top of ticket hall wall 15 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-05-12 | 2016-05-11 14:27 | -1 | 2016-03-17 18:16 | Structural Engineering - Concrete Member | 3000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Pile clutches were not prepared prior to waterproofing. For the pile faces the standard detail was used, but it was not possible to achieve this in the clutches. In these locations the __ was lifted up and LM applied to the clutch and to the back side of the __. Where there were gaps in-between piles these were dry packed with mortar before installing LM. This system provides the same water path and length of LM seal, so will be equivalent to the original design.
| 02SL - Stations (LUL) | Cxxx-NCR-001531 | NCR | BTH - Slab 6 Infill U-bars incorrect length |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-04-16 | 2016-04-05 13:51 | -11 | 2016-03-19 10:43 | Civil - Civil Engineering General | 500 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Error by manufacturer in shipping or marking | Completed |  | The U-bars detailed as Barmarks E/232 & E/233 for the Slab 6 infill were incorrectly fabricated. The U-bars have one leg shorter than the other by an average of 90mm. This results in the U-bar as unable to fix into the P13 couplers at B1 and T1.
| 02SL - Stations (LUL) | Cxxx-NCR-001532 | NCR | BTH - AP8 Backblinding Misalignment |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-04-19 | 2016-04-08 11:44 | -11 | 2016-03-22 14:07 | Civil - Civil Engineering General | 6000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The backblinding for the north AP8 lining wall encroaches on the cover of the steel work for the AP8 roof.
| 02SL - Stations (LUL) | Cxxx-NCR-001533 | NCR | BTH - Slab 6 Infill Site formed L-Bars stress cracking |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-07-31 | 2016-04-08 11:50 | -114 | 2016-03-23 11:37 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Several L bars were missing from the reinforcement delivery. The steel fixing foreman opted to bend site stock bar to replace the missing bars. During bending, the bars cracked under stress.
| 02SL - Stations (LUL) | Cxxx-NCR-001534 | NCR | FFO - Fixing Failure - Acoustic Wall Linning |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-07-31 | 2016-04-29 10:11 | -93 | 2016-03-24 15:18 | Architectural - Walls | 3000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | LOCATION: Level 95 North, East and South concrete walls (refer attached plan) Level 101 North wall (refer attached plan) DETAIL; *Specified anchor fixing (F2 on Cxxx-LAO-A-DWG-C101_Z-50001) as per above locations, do not embed in concrete walls as required due to congested rebar *Locations where fixing cannot be installed properly appear to be 1500mm from slab level (as per attached photos) *Number of 8mm diameter holes have been drilled with max depth of 30-40mm that would require remedial works to concrete (as per attached)
| 02SL - Stations (LUL) | Cxxx-NCR-001535 | NCR | __X - 112 Plenumn slab incorrectly placed & missing box outs |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-05-23 | 2016-05-23 15:25 | 0 | 2016-03-24 16:00 | Civil - Civil Engineering General | 2000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | Following the issue of __ drawing Cxxx-LAO-P_DDA_C101_31234 for comment CHT responded in relation to an incorrect detail for box outs for CHT service pipes.CHT then issued drawing Cxxx-LAO-P-DWG-C101_WS103_1-50001 amending this detail. This detail was not correctly communicated to Cxxx resulting in the box outs being installed incorrectly
| 02SL - Stations (LUL) | Cxxx-NCR-001536 | NCR | FFO - __ - Acoustic Wall Linings Bracket Fixing Commence without MCR approval |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-07-31 | 2016-05-27 11:06 | -65 | 2016-04-06 11:18 | Architectural - Walls | 500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | Acoustic Wall linings Bracket installation works commenced as per below drawings prior to final MCR approval of fixings and Accessories; Cxxx-LAO-O4-XDS-C101-50345 - Material Compliance Record for JK13.1205 LIN-803 and JK13.1206 LIN-804 System fixings & Accessories (4250) Cxxx-LAO-A-DWG-C101_Z-50001 through to Cxxx-LAO-A-DWG-C101_Z-50009
| 02SL - Stations (LUL) | Cxxx-NCR-001537 | NCR | BTH - Factory Visit to EIP on 17 Feb 2016 |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2016-07-31 | 2016-05-24 17:49 | -68 | 2016-03-29 14:49 | Civil - Structural Engineering | 1000 |  | Incomplete Works | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Insufficient work planning by the subcontractors | Completed |  | CRL and __ attended __ factory on 17 Feb 2016 to verify the PPIR for the BTH southern decline precast soffit planks (type 1 and type 2). CRL and __ were unable to verify the PPIR as the works were incomplete; CRL and __ were only informed the works were incomplete for the pre-pour inspection when they arrived to the work face in the factory.
| 02SL - Stations (LUL) | Cxxx-NCR-001538 | NCR | MTH - W/9 basement column to beam 451 connection |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-07-31 | 2016-04-20 11:57 | -102 | 2016-03-30 12:27 | Structural Engineering - Pre-cast | 500 |  | Manufacturing Defect | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The connection between the top of the basement precast column on GL 9/w and the steel stub above is detailed at 8 no. bolts. However, during installation only 6 no. could be fully threaded into the column.
| 02SL - Stations (LUL) | Cxxx-NCR-001539 | NCR | __X - 112.860 Slab rebate detail |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-06-23 | 2016-05-18 10:01 | -36 | 2016-03-31 15:29 | Civil - Civil Engineering General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Section 2-2 on drawing Cxxx-LAO-C-DWG-C101_WS103-50226 shows a U-bar which has been installed. Cxxx raised a query about this in the comments on the drawing. This was not picked up during installation on site.
| 02SL - Stations (LUL) | Cxxx-NCR-001540 | NCR | __X - Shear link for column C6 112-118 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-06-23 | 2016-04-11 09:27 | -73 | 2016-03-31 16:30 | Civil - Civil Engineering General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Drawing Cxxx-MMD-C-DDL-C101_1-33052 states that column C6 should have 4 legs in the Y direction. As this is clearly a mistake drawing Cxxx-LAO-C-DWG-C101_WS103-50254 shows 4 legs in the X direction. The reinforcement has been installed as per drawing Cxxx-LAO-C-DWG-C101_WS103-50254.
| 02SL - Stations (LUL) | Cxxx-NCR-001541 | NCR | MTH - Damage to GL 9/Y column |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-06-30 | 2016-06-22 15:35 | -8 | 2016-04-01 08:28 | Structural Engineering - Pre-cast | 500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper handling of material | Completed |  | During pitching of the white precast column, damage has been sustained to the lower southern side.
| 02SL - Stations (LUL) | Cxxx-NCR-001542 | NCR | MTH - Staining to GL 9 precast columns |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-03-31 | 2017-02-14 09:24 | -410 | 2016-04-01 16:05 | Structural Engineering - Pre-cast | 1000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Contamination | Completed |  | After installation on site and heavy rain, brown water stains have appeared on the GL 9/ Y-Z columns.
| 02SL - Stations (LUL) | Cxxx-NCR-001543 | NCR | Moorhouse Shaft Waterproofing |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-09-30 | 2016-09-06 10:58 | -24 | 2016-04-01 16:45 | Civil - Civil Engineering General | 4000 |  | System Defect | Repair | 3 (3-6k) | Complete | Material/Preservation Problems - Other | Completed |  | Waterproofing at the top of the Moorhouse shaft (Lower Basement Level 2) which was previously installed by __ as per __’s design (MHDR Waterproofing strategy Mini-gate submission - Cxxx-CRL signed - Cxxx-LAO-S-LRC-C101-50005 Rev 1.0) . On our inspection it appears that the sealant is still like putty which does not seem correct.
| 02SL - Stations (LUL) | Cxxx-NCR-001544 | NCR | BTH - AP8 Roof Slab L Bars Fabrication Error |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-07-31 | 2016-04-25 09:12 | -97 | 2016-04-03 11:05 | Civil - Civil Engineering General | 2500 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Error by manufacturer in shipping or marking | Completed |  | The AP8 lining walls have two L-bars that transfer load from the roof slab into the walls. These L-bars have been fabricated such that their vertical leg is 150mm short of the required length. As such, the horizontal legs do not sit in T1 and T3 of the roof slab as designed.
| 02SL - Stations (LUL) | Cxxx-NCR-001545 | NCR | Use of Non-Approved Sealant on Riser Ductwork |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-07-31 | 2016-07-22 07:10 | -9 | 2016-04-04 12:21 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | Arboseal product used on Riser 790 ductwork modules prior to formal approval via the MCR process.
| 02SL - Stations (LUL) | Cxxx-NCR-001546 | NCR | BTH - Southern Ticket Hall Slab 6 Out of Position |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-06-30 | 2016-06-29 15:17 | -1 | 2016-04-12 14:11 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The ticket hall slab 6 has been poured out of position, with the worst case scenario being 314mm West of its design position. This then has a knock on effect on the infill section of lining wall between the ticket hall and the southern decline as the East face of this wall needs to be poured inline with the slab. See asbuilt attached.
| 02SL - Stations (LUL) | Cxxx-NCR-001547 | NCR | MTH - OSD Starter & Couplers in the wrong position |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-07-31 | 2016-05-19 12:57 | -73 | 2016-04-06 16:55 | Structural Engineering - Reinforcement | 2000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | When we casted the 107.750mATD slab and OSD column , some starter bars and couplers for OSD wall w14-2 were placed in by setting out using West grid instead of East grid. See attached photos and drawings.
| 02SL - Stations (LUL) | Cxxx-NCR-001548 | NCR | MTH - Damage to top of PC column - basement GL w/9 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-07-31 | 2016-05-19 12:59 | -73 | 2016-04-07 15:23 | Structural Engineering - Pre-cast | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The top of the precast column on GL W/9 in the basement of Moorgate ticket hall has sustained damage during installation
| 02SL - Stations (LUL) | Cxxx-NCR-001549 | NCR | MTH - missing grout cubes for column bases |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-07-31 | 2016-07-12 14:01 | -19 | 2016-04-07 15:37 | Structural Engineering - Pre-cast | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | The grout cubes taken when the street level column bases were grouted have been mislaid on site.
| 02SL - Stations (LUL) | Cxxx-NCR-001550 | NCR | MTH - incorrect installation of TW halfen channel to side of roof beams |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-07-31 | 2016-05-11 15:38 | -81 | 2016-04-07 15:41 | Structural Engineering - Inserts | 2000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Information not detailed | Completed |  | the halfen channel for temporary works to the side of the insitu roof beams was installed incorrectly and is therefore not usable.
| 02SL - Stations (LUL) | Cxxx-NCR-001551 | NCR | __X - 112 lvl Blockwork grout spillage |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-06-07 | 2016-05-23 12:26 | -15 | 2016-04-08 18:06 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Please see the attached for information on grout spillages on the 112 level blockwork. This was as a result of grout seepage when the fire ceiling was poured. This was not clean off in time leaving the attached stains
| 02SL - Stations (LUL) | Cxxx-NCR-001553 | NCR | MTH GL11 Beamlet Finish |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-10-29 | 2016-10-10 08:50 | -19 | 2016-04-12 16:42 | Architectural - Finishes | 1000 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | There is a grout void in north east corner of the beamlet. The beamlet is connected to the east side of GL11Y column. See attached photo.
| 02SL - Stations (LUL) | Cxxx-NCR-001554 | NCR | __X Acoustic Lining |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-08-31 | 2016-07-19 15:48 | -43 | 2016-04-12 17:01 | Architectural - Walls | 4000 |  | Material | Rework | 3 (3-6k) | Complete | Material/Preservation Problems - Other | Completed |  | A number of acoustic cladding panels have been manufactured using a fabric wrap that failed to produce compliant sound absorbency results.
| 02SL - Stations (LUL) | Cxxx-NCR-001555 | NCR | BTH - Southern decline PCC planks 1 - 10 various finishing defects |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-09-30 | 2016-08-02 10:43 | -59 | 2016-04-19 08:42 | Architectural - Finishes | 3000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | PCC roof planks in the southern decline of BTH (planks 1 - 10), have been inspected as they were delivered. These inspections have flagged up several finishing issues. These include; inconsistency's with the intensity of blasting, areas of slight damage, slight marks and a poor colour match on some repairs.
| 02SL - Stations (LUL) | Cxxx-NCR-001556 | NCR | __X - Lift shaft vertical tolerance |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-05-17 | 2016-04-27 13:30 | -20 | 2016-04-19 09:37 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Following the construction of the lift shaft a full as built survey was carried out on it. It was found that the lift shaft is out of vertical tolerance by 6mm is some areas.
| 02SL - Stations (LUL) | Cxxx-NCR-001557 | NCR | MTH Beamlet Temporary Works Fixings. |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-07-31 | 2016-06-07 14:50 | -54 | 2016-04-20 08:42 | Structural Engineering - Structural Engineering - General | 2000 |  | Manufacturing Defect | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Cast in anchors (M10 bolt sockets) on the top surface of the beamlet were not installed by EIP. This is limited to the 7no beamlets on GL11 only. These top anchors were to connect the external temporary works hanger to the beamlet. The external hangers have been drilled and fixed to the beamlet using M10 threaded bar, fixed with E410 with 150mm embedment and with 60mm edge distance.
| 02SL - Stations (LUL) | Cxxx-NCR-001558 | NCR | MTH GL9 Z+1 Concrete Cracking and Cover to Reinforcement. |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-07-31 | 2016-07-08 07:42 | -23 | 2016-04-20 10:43 | Structural Engineering - Reinforcement | 1500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | 1) There is an area of reinforcement which will not achieve the minimum cover. The rebar in question is from 112.900m up to approx. 113.550m and at the GLZ+1 area. See Photo 01 which shows area affected. 2) There are three vertical couplers located on GLZ+1 at 112.845m. The concrete around these couplers has cracked and will need to be repaired. See Photo 02 this shows the area of cracking and the extent of the repair.
| 02SL - Stations (LUL) | Cxxx-NCR-001559 | NCR | TUN – PTE – East UPE crossover cracks and voiding |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-07-31 | 2016-07-22 14:39 | -9 | 2016-04-21 08:58 | Structural Engineering - Concrete Member | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | Inadequate finish to concreting works has been achieved in two areas of the UPE crossover at the east end of Platform Tunnel East. Please see attached location markup and photos. In one area voiding occurred, the largest pocket is 50 x 20mm area and 15mm deep. In a second area cracking has occurred with some loosening of material.
| 02SL - Stations (LUL) | Cxxx-NCR-001560 | NCR | Moorhouse - Only one 28day cube results for Basement B1 Level 107.750m Slab Pours |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-07-31 | 2016-05-13 09:23 | -79 | 2016-04-21 12:38 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | We currently have one 28 day cube results for the following Moorhouse Basement (B1) 107.750m level pours: Pour reference: MTH 081 (Date of Pour 20/10/2015) & Pour reference: MTH103 (Date of Pour 29/01/2016). a) One 28 day result is not in accordance with BS EN 12350-1:2009 and BS 1881-125:1986 b) Cube results for pour reference MTH103 has been crushed one day early, this is due to lab entering the pour date as 28/01/16. The one 28day cube results we have for both pours confirms that the required strength is reached, this can be found on the __ report(attached).
| 02SL - Stations (LUL) | Cxxx-NCR-001561 | NCR | BTH - SED Delta cast in plate deliverables |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-08-31 | 2016-10-03 14:03 | 33 | 2016-04-22 16:11 | Structural Engineering - Bolted Connections | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | The design check certificate for the temporary bearing of the BTH pre-cast soffit plank screw jacks on the Delta cast in plates had not been submitted and accepted, as required by Part 22.7.1 of Volume 2B. An informal copy was received on the 16th March 2016, however as of 16th April, this had not been formally submitted for acceptance via eB. No MCR was submitted for the screw jacks, as required by item 2.4 of the BTH Roof Construction ITP, Cxxx-LAO-O4-ITP-C101_WS102-50017.
| 02SL - Stations (LUL) | Cxxx-NCR-001562 | NCR | Ventilation Ductwork commenced prior to full MCR approval |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-07-31 | 2016-07-12 10:37 | -19 | 2016-04-25 16:10 | Mechanical - Heating Ventilation & Air Conditioning | 5000 |  | Material | Rework | 3 (3-6k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | Standard Non-fire rated ductwork installation commenced prior to Code 1 acceptance on Seal Tape MCR.
| 02SL - Stations (LUL) | Cxxx-NCR-001563 | NCR | BTH - Cast in Stainless Steel Pipework and Gullies to be replaced with Cast Iron Time Saver |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-09-16 | 2016-09-14 11:49 | -2 | 2016-04-25 17:30 | Mechanical - Public Health Engineering | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Time Saver Cast Iron pipe have been cast into concrete as opposed to stainless steel pipes which were specified.
| 02SL - Stations (LUL) | Cxxx-NCR-001565 | NCR | MTH. Breaking out concrete on OSD external wall for tie in with roof beam on GL8 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-07-31 | 2016-05-19 13:01 | -73 | 2016-04-29 09:11 | Civil - Civil Engineering General | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | No box out was formed in the West face of the OSD external wall for the tie in with the roof beam on GL8 (see attached site sketch). The extent of the beam has been scabbled and there is no evidence of coupler bars being install in this location.
| 02SL - Stations (LUL) | Cxxx-NCR-001566 | NCR | Design Management Plan |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-07-31 | 2016-07-22 14:35 | -9 | 2016-04-29 14:39 | Architectural - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | • The breakdown of authorities is unclear as the Design Team Organisation Chart is missing from Appendix 1. (No. 5.7) • There is not a description of a process for systematic review and verification, verification plans, verification recordings and who is responsible for the verification process. (No. 5.2) • No reference is made to the Contractors responsibility for ensuring that Subcontractors provide necessary manufacturing and fabrication certification. (No. 12) • The Mini Gates Procedure and Gate Risk Assessments are not mentioned. (No. 13)
| 02SL - Stations (LUL) | Cxxx-NCR-001567 | NCR | MTH GL11 Beamlet Grouting Location Z+1 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-08-11 | 2016-06-10 15:40 | -62 | 2016-05-03 08:27 | Structural Engineering - Grouting | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | When grouting operations were carried out, the grout did not fill the void fully. Please see attached photo.
| 02SL - Stations (LUL) | Cxxx-NCR-001568 | NCR | MTH GL11 Beamlet Damage and Chipping |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-03-31 | 2016-11-10 15:13 | -141 | 2016-05-03 12:57 | Architectural - Finishes | 1500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | The GL11 beamlets were installed, shuttered and the grouting operation was carried out. The shutters were stripped. During the stripping process there were a number of the top edges of the beamlets were chipped. Also during the stripping activities there were three no. roof planks chipped. See attached mark ups and photos.
| 02SL - Stations (LUL) | Cxxx-NCR-001569 | NCR | BTH - Water ingress to South Ticket Hall basement wall 1 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-06-28 | 2016-06-07 08:38 | -21 | 2016-05-03 16:28 | Structural Engineering - Concrete Member | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Water ingress south ticket hall basement wall 1, at the joint between this wall and slab 15. Water bar (used in pour) may block leak, but due to Blockwork program, resin injection to be used.
| 02SL - Stations (LUL) | Cxxx-NCR-001571 | NCR | BTH - AP8 Girder 9, water ingress from LU station |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-07-01 | 2016-06-29 15:48 | -2 | 2016-05-05 16:24 | Structural Engineering - Concrete Member | 3000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Water tracking along girder 9 out of station and into AP8 lintel, then passing through crack under girder 9 shoe and dripping into AP8.
| 02SL - Stations (LUL) | Cxxx-NCR-001572 | NCR | BTH - AP8/LU station, water ingress from LU station |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-09-30 | 2016-06-27 07:19 | -95 | 2016-05-05 16:32 | Structural Engineering - Concrete Member | 3000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Water tracking out of LU station structure and into joint between station and AP8 lintel. Water is evident at the northern and southern end of the lintel.
| 02SL - Stations (LUL) | Cxxx-NCR-001574 | NCR | TUN - PTE - Damage to Three Precast Slabs in Eastbound Tunnel |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-08-31 | 2016-07-25 09:34 | -37 | 2016-05-09 09:23 | Structural Engineering - Structural Engineering - General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | __ have chipped the bottom corner of three precast concrete slabs during installation which now require repair (see attached images of damage). The three slabs are located in the Eastbound Tunnel (see attached mark-up of Cxxx-LAO-S-DWG-C101-50035 for exact locations).
| 02SL - Stations (LUL) | Cxxx-NCR-001575 | NCR | BTH - Various Water Ingress Through the Southern Escalator Decline Wall |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-08-31 | 2017-08-30 16:12 | -1 | 2016-05-10 10:02 | Structural Engineering - Concrete Member | 15000 |  | Workmanship | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Water ingress has been noted in the southern escalator decline in the following locations: 3no. on the South wall, 3no. on the West wall and 5no. on the North wall. The attached sketch shows their position, and related photos. Note that the two leaks identified on Cxxx-NCR-001444 have been shown on this sketch for clarity.
| 02SL - Stations (LUL) | Cxxx-NCR-001577 | NCR | BTH - Incorectly bent bars for ticket hall roof pour 1a |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-07-05 | 2016-05-16 08:22 | -50 | 2016-05-10 14:41 | Structural Engineering - Reinforcement | 500 |  | Workmanship | Reject | 4 (0.5-3k) | Complete | Discipline/Workmanship - Error by manufacturer in shipping or marking | Completed |  | Bob-bars supplied by __ were cut and bent aprox 200mm short as the maximum radius of their bending machine is 300mm. This relates to __-50127, bar marks E/4, E/5, E/7, E/8, E/10, E/11, E/15, E/20, E/22, E/24, and E/59.
| 02SL - Stations (LUL) | Cxxx-NCR-001578 | NCR | BTH - Incorectly bent bars for ticket hall roof Ring Beam |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-07-05 | 2016-06-07 13:08 | -28 | 2016-05-10 14:53 | Structural Engineering - Reinforcement | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Bob-bars supplied by __ were cut and bent aprox 200mm short ('A' dimension) and between 0-200mm short ('B' dimension) This relates to __-50124, bar marks E/43.
| 02SL - Stations (LUL) | Cxxx-NCR-001579 | NCR | Damage to termination detail in AP1 - North Side |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-11-30 | 2016-11-29 14:27 | -1 | 2016-05-11 14:33 | Civil - Civil Engineering General | 6000 |  | Damaged | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | The termination detail as shown on Cxxx-MMD-C4-DDD-C101_Z-00055 has been damaged during the installation of the B12 Drilled in Bars as required on Cxxx-MMD-C4-DDD-C101_Z-00630. This has resulted in 3No. Holes being drill through the __dur 31 CF.
| 02SL - Stations (LUL) | Cxxx-NCR-001580 | NCR | Protection of Cut Trunking With Zinc Rich Paint |  | Crossrail | PDP | LIS - Liverpool Street Station (Central) |  | 2016-06-14 | 2016-06-01 14:51 | -13 | 2016-05-17 10:12 | Electrical - Cable Management | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | An installer was asked for the number of coats of __spray he applied to cut ends of cable trunking that he was fitting on the half landing on the stairway descending to the 101 level in the Blomfield Box. The response was that only 1 coat was applied, The workmanship specification and the __spray manufacturer's instructions require 2 coats to be applied.
| 02SL - Stations (LUL) | Cxxx-NCR-001581 | NCR | Lack of Pull Test Acceptance Criteria on ITP |  | Crossrail | PDP | LIS - Liverpool Street Station (Central) |  | 2016-08-31 | 2016-08-16 08:35 | -15 | 2016-05-17 10:07 | Electrical - Cable Management | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | There are definitive values included or referenced in the ITP as acceptance criteria for pull tests, only references to documents to enable the values to be calculated.
| 02SL - Stations (LUL) | Cxxx-NCR-001582 | NCR | Lack of Formally Issued Calculations of Loads for Pull Tests of Containment |  | Crossrail | PDP | LIS - Liverpool Street Station (Central) |  | 2016-08-31 | 2016-08-26 11:20 | -5 | 2016-05-17 10:39 | Electrical - Cable Management | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | The calculations of loads for pull testing fixing bolts for cable containment have no evidence of checking or approval, They have no official status as they were not registered in the __ and/or CRL document management systems
| 02SL - Stations (LUL) | Cxxx-NCR-001583 | NCR | TUN- Additional Construction Joint on PTE trackbed pour 2 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-06-15 | 2016-06-09 12:46 | -6 | 2016-05-18 14:19 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | A non-standard construction joint has been created in the track bed in the eastbound tunnel (PTE), this is due to a shortage on the volume of concrete for the pour on 11th May 2016. The original pour left a remaining pour area of approx. 17.5m long, 3.6m wide and between 40mm and 250mm in height (see attached sketch and photos). This left some areas of the pour with partially exposed reinforcement and a concrete level above the base of T2 steel. The exposed area which was unable to be poured was immediately coated with retarder spray at approx 22:30 on 11th May and was jet-washed in order to create a scabbled finish at 10:30 on 12th May. Following consultation with Cxxx designers it was agreed that the following steps should be taken in order to prepare the additional joint for the remaining area of concrete to be poured: • Scabble the placed concrete to a minimum of 35mm (one bar diameter) below the top reinforcement where necessary. • Prepare all of the surface to ‘rough’ finish (pressure wash green or retarded concrete to expose aggregate or scabble). • Cast track bed to design levels using C7A concrete mix. These required measures were carried out on 13thMay, with the concrete broken down to 35mm below the T2 rebar level using a breaker and the whole area was cleaned and blown using an air hose (see attached photos). The work was subsequently inspected and approved by Daniel Chasen from Crossrail at 14:30. The remaining area of concrete was poured on 16th May 2016 using the C7A concrete mix.
| 02SL - Stations (LUL) | Cxxx-NCR-001584 | NCR | BTH - Decline Precast Plank Damage |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-02-28 | 2018-11-22 09:51 | 267 | 2016-05-18 | Civil - Civil Engineering General | 1500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the installation of the AP2 Mole hole formwork, damage was incurred to the eastern most rib of precast plank 1.
| 02SL - Stations (LUL) | Cxxx-NCR-001585 | NCR | BTH - Southern Decline In-situ Roof Pour 1a Incomplete |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-06-15 | 2016-06-07 09:04 | -8 | 2016-05-18 14:36 | Structural Engineering - Concrete Member | 3000 |  | Incomplete Works | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Insufficient quantity of material to do the job | Completed |  | The concrete pour to the Southern Decline In-situ Roof Pour 1a was not completed due to concrete supplier not supplying the make up load of 4m3.
| 02SL - Stations (LUL) | Cxxx-NCR-001586 | NCR | BTH - Reinforcement to southern decline Pour 1a (BM E/4) not installed as per approved detail |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-06-15 | 2016-06-03 09:00 | -12 | 2016-05-18 14:12 | Structural Engineering - Reinforcement | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Insufficient information made available to the worker. | Completed |  | BTH RC drawing Cxxx-LAO-C-DWG-C101_WS102-50249 C03 specifies that BM E/4 should be installed at 166mm centres on the north and south side of the southern decline in-situ roof. These bars can not be installed at 166mm centres across the gallows bracket locations and an alternative detail was agreed with Crossrail. This detail was not adhered to on site which resulted in BM E4 being installed at centres in excess of 166mm across the gallows bracket locations.
| 02SL - Stations (LUL) | Cxxx-NCR-001587 | NCR | MTH Roof Plank Unit 004 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-10-16 | 2016-10-10 08:51 | -6 | 2016-05-19 13:02 | Architectural - Finishes | 1000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | PC Roof Unit 004 was struck with some A193 mesh that was being lifted. There was a scratch left in the centre of the southern vertical face of the plank.
| 02SL - Stations (LUL) | Cxxx-NCR-001588 | NCR | MTH GL10 Beamlet Fabrication Width |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-07-31 | 2016-06-10 07:53 | -51 | 2016-05-19 14:56 | Structural Engineering - Pre-cast | 1500 |  | Workmanship | Reject | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A Type A beamlet was delivered to site was out of fabrication tolerance. See Cxxx-LAO-A-DWG-C101_WS099-50290. The beamlet was rejected on site and sent back to EIP.
| 02SL - Stations (LUL) | Cxxx-NCR-001589 | NCR | MTH GL10 Beamlet Exposed Face Crack |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-06-16 | 2016-06-09 10:31 | -7 | 2016-05-19 15:15 | Structural Engineering - Pre-cast | 2000 |  | Workmanship | Reject | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | There was a 250mm crack discovered on the south face of the Type B beamlet. The beamlet was rejected. The crack emanated from the area where the external TW hangers were fitted to the beamlet.
| 02SL - Stations (LUL) | Cxxx-NCR-001590 | NCR | MTH GL10 Beamlet Fabrication Lenght |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-07-31 | 2016-06-10 08:24 | -51 | 2016-05-19 15:26 | Structural Engineering - Pre-cast | 1500 |  | Workmanship | Reject | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | There was a Type B beamlet delivered to site that was fabricated out of tolerance in relation to its length. One beamlet side was 8mm longer than the other. This beamlet was rejected and sent off site.
| 02SL - Stations (LUL) | Cxxx-NCR-001591 | NCR | BTH - Southern Decline Slabs - Pours 10, 11 & 12 Finished Levels out of Tolerance |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-08-31 | 2016-08-31 09:51 | 0 | 2016-05-20 11:07 | Structural Engineering - Bracing | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | As-built surveys carried out on the Southern Escalator Decline slabs (Pours 10, 11 & 12) have identified areas that are not in compliance with the required level tolerance.
| 02SL - Stations (LUL) | Cxxx-NCR-001592 | NCR | Isolation Valves missing on underplatform Hydrant pipework |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-08-31 | 2016-08-29 10:34 | -2 | 2016-05-23 16:32 | Fire - Suppression | 3000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | Isolation Valves missed from __ drawings when detailed on the gated design and subsequently not installed within the underplatform prefabricated modules
| 02SL - Stations (LUL) | Cxxx-NCR-001593 | NCR | BTH - Southern decline PCC planks 11 - 20 various finishing defects |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-08-17 | 2016-08-15 09:39 | -2 | 2016-05-25 07:50 | Architectural - Finishes | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Error by manufacturer in shipping or marking | Completed |  | PCC roof planks in the southern decline of BTH (planks 11 - 20), have been inspected as they were delivered. These inspections have flagged up several finishing issues. These include; areas of slight damage, slight marks and a poor colour match on some repairs.
| 02SL - Stations (LUL) | Cxxx-NCR-001595 | NCR | __ PES Truss - Bolted Connections |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-09-30 | 2016-08-10 14:38 | -51 | 2016-05-25 15:05 | Structural Engineering - Bolted Connections | 10000 |  | Damaged | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Error by manufacturer in shipping or marking | Completed |  | The PES trusses have brackets and plates installed to facilitate plenum struts and other finishing elements to be bolted to the truss. Upon inspection ahead of installation five out of the six trusses delivered to site on the 18th May 2016 and loaded out on the platform had brackets and plates that do not allow the plenum struts or finishing elements to be installed as designed. There is no tolerance within the design of the bolted connections to allow for the brackets and plates to be out of position.
| 02SL - Stations (LUL) | Cxxx-NCR-001597 | NCR | MTH Roof Plank Unit 013 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-12-13 | 2016-10-10 08:53 | -64 | 2016-05-27 09:43 | Structural Engineering - Pre-cast | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | During the installation of Roof plank unit 013, the north east corner of the plank was chipped. The chip is approx. 25mm * 25mm.
| 02SL - Stations (LUL) | Cxxx-NCR-001598 | NCR | Additional CMS installed in __ Superstructure |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-09-30 | 2016-08-17 14:31 | -44 | 2016-06-06 12:32 | Electrical - Cable Management | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | Additional Primary CMS installed within Blomfield Box Superstructure prior to FCD being raised and agreed.
| 02SL - Stations (LUL) | Cxxx-NCR-001599 | NCR | BTH - Column B10 finish |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-07-28 | 2016-06-07 08:14 | -51 | 2016-06-02 14:36 | Architectural - Finishes | 10000 |  | Workmanship | Reject | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Finish of column B10 had repaired blow holes, and large repair visible from significant distance.
| 02SL - Stations (LUL) | Cxxx-NCR-001600 | NCR | BTH - Southern decline plank |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-07-28 | 2016-07-13 10:16 | -15 | 2016-06-02 14:56 | Architectural - Finishes | 500 |  | Manufacturing Defect | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | As-built of the architectural pre-cast finish position outside agreed tolerance. As-built passed to __ to design to.
| 02SL - Stations (LUL) | Cxxx-NCR-001601 | NCR | TUN – PTW – Additional construction joint in trackbed pour 4 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-07-01 | 2016-06-17 13:59 | -14 | 2016-06-03 10:05 | Structural Engineering - Concrete Member | 500 |  | Incomplete Works | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Other human error | Completed |  | The surface of the mass fill component of PTW trackbed pour 4 was left below agreed design level at one end. This pour was the first section of trackbed to be constructed to the new design. Pour 4 was a total of 58.5m in length of which a length of 21.5m was left low. The area left low varied in depth between 80mm and 275mm. Please see “Location markup” and “Incomplete PTW trackbed pour – 31.05.16”.
| 02SL - Stations (LUL) | Cxxx-NCR-001602 | NCR | TUN – PTW – Stopend out of position in trackbed pour 4 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-08-31 | 2016-06-22 08:58 | -70 | 2016-06-03 12:00 | Structural Engineering - Concrete Member | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | The eastern stopend of PTW trackbed pour 4 was installed 155mm west of its design location. The location of this stopend is significant because they have been coordinated to avoid the track sleepers which will be installed by Cxxx.
| 02SL - Stations (LUL) | Cxxx-NCR-001603 | NCR | BTH - 1no. Bar Mark E/884 Omitted Decline Roof 1b |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-07-13 | 2016-06-23 07:48 | -20 | 2016-06-15 09:16 | Civil - Civil Engineering General | 500 |  | Manufacturing Defect | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 1no. bar mark E/884 was omitted from the southern decline roof pour 1b. This was because the coupler that the bar was supposed to screw into had a positional dolly in it. This is used during the manufacturing process to align the form work with the reinforcement.
| 02SL - Stations (LUL) | Cxxx-NCR-001604 | NCR | MTH Roof Plank 004/005 Rebar Removed |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-12-31 | 2016-11-24 12:57 | -37 | 2016-06-14 07:55 | Structural Engineering - Reinforcement | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | There was some rebar cut from roof planks 004 and 005 during the installation of the roof planks and the roof reinforcement.
| 02SL - Stations (LUL) | Cxxx-NCR-001605 | NCR | BTH - Top layer pour on Southern Escalator Decline stage 120 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-08-13 | 2016-07-20 10:33 | -24 | 2016-06-14 17:02 | Structural Engineering - Concrete Member | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | Pour 1A was poured on 14/05 using E3 concrete Pour 1B was poured on 06/06 using D7 concrete Pour 2A was poured on 09/06 using D5 concrete (1A had cured for 23 days, 1B for 3 days) Pour 2B was poured on 11/06 using D7 concrete (1B had cured for 5 days, 2A had cured for 2 days) Site cubes were crushed on D7 pours, results being 37.5kN at 3 days, and 47kN at 7 days. Cubes were crushed on D5 concrete (pour 2A), results being at 53kN at 7 days (no results available for 2 day strength) Based on these results the stage 118 concrete would have cured more than 80% of the required strength before the stage 120 concrete was poured.
| 02SL - Stations (LUL) | Cxxx-NCR-001606 | NCR | Platform Mechanical Pipe Services commenced prior to Code 1 drawing acceptance |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-08-31 | 2016-07-26 09:17 | -36 | 2016-06-15 11:35 | Systems - Drainage/Pumping Systems | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | Mech pipe service installation commenced prior to full drawing acceptance to Code 1 Construction Issue. P01 drawings being used.
| 02SL - Stations (LUL) | Cxxx-NCR-001607 | NCR | MHS- Beam Clad Installation |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-08-31 | 2016-07-01 11:33 | -61 | 2016-06-15 17:33 | Fire - Compartmentation | 0 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Incorrect fixings used to complete the repairs of __ __ Fire Protection within the Moorhouse Street Level steel beams. It was noted during Crossrail Fire engineer inspection on site, revealed that 4” nails were used instead of pigtail screw fixings.
| 02SL - Stations (LUL) | Cxxx-NCR-001608 | NCR | TUN – __ grout cubes not stored in accordance with EN 12390-2:2009 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-08-31 | 2016-07-21 08:14 | -41 | 2016-06-16 08:39 | Structural Engineering - Grouting | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper storage of material | Completed |  | The test cubes made between 25/05/16 and 02/06/16 for grouting of PES alignment beams (under control of __) have been stored incorrectly on site for a period of over two weeks, thereby not adhering to clauses 5.5.1 and 5.5.2 of EN 12390-2:2009.
| 02SL - Stations (LUL) | Cxxx-NCR-001609 | NCR | TUN - LCE Service bed crack |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-08-26 | 2016-07-19 06:52 | -38 | 2016-06-17 11:49 | Civil - Civil Engineering General | 1000 |  | Material | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | A shrinkage crack have been identified on LCE Service bed pour 1. The crack location is shown on drawing "Cxxx-MMD-C-DDA-C101_Z-20240 NCR Crack location". The crack width ranges from 1.5mm to 2mm. (Please see attached photos) 27/06/2016 An uncontrolled repair has been done in the area. The crack opening has been filled in superficially using Parex thixotropic or __ HF grout See attached photos Cxxx-NCR-001609-IM010 to Cxxx-NCR-001609-IM014
| 02SL - Stations (LUL) | Cxxx-NCR-001610 | NCR | MTH North of GL9 Y Roof Plank Chipped. |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-01-06 | 2016-07-26 08:05 | -164 | 2016-06-20 09:58 | Structural Engineering - Pre-cast | 750 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper handling of material | Completed |  | The plank was chipped when delivered to site. The plank was covered for the last number of weeks and when the area was uncovered the NCR was raised. See attached photo.
| 02SL - Stations (LUL) | Cxxx-NCR-001611 | NCR | PES - Grout Cubes |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-09-30 | 2016-08-10 14:26 | -51 | 2016-06-20 15:45 | Structural Engineering - Grouting | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Grout cubes taken for grout installation to the PES head alignment beams in bay W10 on 3rd June 2016 and bay E2 on 27th May 2016 have been mislaid and are not available for crushing to determine the strength prior to installing the trusses.
| 02SL - Stations (LUL) | Cxxx-NCR-001613 | NCR | BTH - Decline Roof Pour 1b not 450mm Thick |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-09-30 | 2016-08-10 10:31 | -51 | 2016-06-22 07:40 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Insufficient quantity of material to do the job | Completed |  | Pour 1b was not poured consistently at 450mm across the wedge plank it ranges from 450mm at north side to 200mm at south side (see photos).
| 02SL - Stations (LUL) | Cxxx-NCR-001614 | NCR | __X - Debris within drainage runs within 73m level slab |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-09-30 | 2016-09-30 15:42 | 0 | 2016-06-22 07:47 | Civil - Civil Engineering General | 3000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | During the breakout of the piles at the wraparounds, debris has becoming lodged within the through slab drainage runs. We proposed to use a Hydro jetting machine to clear the debris. This jetting will have no impact on drainage pipes themselves. We will jet and CCTV survey all runs within the 73 slab.
| 02SL - Stations (LUL) | Cxxx-NCR-001615 | NCR | BTH - Coupler Bar E/115 Missed from Decline Roof Pour 2b |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-12-31 | 2016-12-21 14:26 | -10 | 2016-06-22 08:01 | Civil - Civil Engineering General | 1000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | The coupler was missed off of the displaced lap bar in layer T2 as per Cxxx-FCD-001511.
| 02SL - Stations (LUL) | Cxxx-NCR-001616 | NCR | Grout spillage on level 106 blockwork wall |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-11-30 | 2016-10-31 10:11 | -30 | 2016-07-11 13:20 | Architectural - Brickworks/Blockworks | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Supervision - Other | Completed |  | Please see the attached for information on grout spillages on level 106. This was as a result of grout seepage when the 610mm screed was poured on the level above. This was not clean off in time leaving the attached stains. It couldn't be cleaned as there was no access on the level below to reach the spillages.
| 02SL - Stations (LUL) | Cxxx-NCR-001617 | NCR | TUN – LCE – Area of trackbed mass fill concrete poured high |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-09-30 | 2016-07-25 09:30 | -67 | 2016-06-28 17:07 | Structural Engineering - Concrete Member | 1500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Personnel Error - Other human error | Completed |  | An area of the mass fill concrete for the trackbed constructed in Launch Chamber East has been poured 110mm higher than design level. An as-built survey of the surface of the pour gives an average level of ~46.460m, the target level was 46.350m. The worst case area shows a level of 46.487m. See attached drawings “Cxxx-MMD-C-DDA-C101_Z-20240 - non conformance layout” and “Cxxx-MMD-C-DDB-C101_Z-20010 - non conformance section”.
| 02SL - Stations (LUL) | Cxxx-NCR-001618 | NCR | MTH GL8 Beamlet between GL8 and OSD |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-03-30 | 2017-07-27 13:05 | -246 | 2016-06-29 16:18 | Architectural - Finishes | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Contamination | Completed |  | The beamlet has two minor chips on the southern face. Both faces of the beamlet has staining.
| 02SL - Stations (LUL) | Cxxx-NCR-001619 | NCR | HV Switchroom Ductwork Installation |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-09-30 | 2016-09-28 08:10 | -2 | 2016-06-30 12:07 | Mechanical - Heating Ventilation & Air Conditioning | 2000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | Some ductwork has been installed within __ Street Level HV Switchroom without adequate coordination with the model and Cxxx.
| 02SL - Stations (LUL) | Cxxx-NCR-001622 | NCR | __X - Grout Box slab walls (Wall 4-1) at GL 3/A |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-09-30 | 2016-08-05 17:09 | -56 | 2016-07-04 09:44 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Supervision - Other | Completed |  | 3No. B40 couplers were not installed into the Stair wall at GL 3/ A-B.
| 02SL - Stations (LUL) | Cxxx-NCR-001623 | NCR | BTH - Southern Ticket Hall Roof Shear Reinforcement |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-08-31 | 2016-08-22 13:07 | -9 | 2016-07-04 11:40 | Civil - Civil Engineering General | 2000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 13 of the standard planks in the southern ticket hall (i.e. planks 021 - 033) have been cast with the shear links misplaced, they are too far away from the end of the plank. This is true for both ends of the plank.
| 02SL - Stations (LUL) | Cxxx-NCR-001624 | NCR | MTH GL8 Beamlet Dimensions |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-08-02 | 2016-07-06 09:31 | -27 | 2016-07-05 07:48 | Structural Engineering - Pre-cast | 500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Insufficient quantity of material to do the job | Completed |  | GL8 Beamlets were delivered to site. Unit 012 and Unit 002 were inspected before installation and were found to be out of tolerance. See attached.
| 02SL - Stations (LUL) | Cxxx-NCR-001626 | NCR | MTH Basement Wall W4 Verticallity |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-08-24 | 2016-07-26 08:21 | -29 | 2016-07-05 08:46 | Structural Engineering - Concrete Member | 3000 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Wall W4 was poured 1/7/16. The wall was checked pre pour for verticality and was within tolerance. During the placement of concrete the formwork moved, causing the wall to move out of verticality.
| 02SL - Stations (LUL) | Cxxx-NCR-001627 | NCR | __X - Missing 28day cube test results for Blockwork |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-07-20 | 2018-06-22 14:09 | -28 | 2018-06-22 10:03 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | NB - NCR no longer relevant - 28 day results now available in __ quality packs for all areas of all worksites
| 02SL - Stations (LUL) | Cxxx-NCR-001628 | NCR | BTH - Damage to Precast Column Header B10 During Installation |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-03-30 | 2017-11-29 17:03 | -121 | 2016-07-06 12:21 | Civil - Civil Engineering General | 3000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the installation of column header B10 the soffit of the unit was damaged. See attached photos.
| 02SL - Stations (LUL) | Cxxx-NCR-001629 | NCR | MTH. Beamlet reinforcement on GL 7 between GL W and Y Street level |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-08-04 | 2016-07-13 15:38 | -22 | 2016-07-07 11:47 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | The starter bars in the precast beamlet on GL7 between GL W and Y have been installed and cast incorrectly. Please see attached site sketches and photos.
| 02SL - Stations (LUL) | Cxxx-NCR-001630 | NCR | MTH GL9W Column Rebar. |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-09-30 | 2016-08-11 09:51 | -50 | 2016-07-07 11:48 | Structural Engineering - Reinforcement | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | There is positional coupler not connected in the rebar connecting the GL9W column to the GL9 beam. See attached photo.
| 02SL - Stations (LUL) | Cxxx-NCR-001631 | NCR | BTH - Shrinkage Cracking on Decline Roof Pour 2a |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-09-30 | 2016-08-10 10:33 | -51 | 2016-07-07 13:17 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Following the post pour inspection of the decline roof pour 2a it became clear that there were some shrinkage cracks running north south across the surface of the slab.
| 02SL - Stations (LUL) | Cxxx-NCR-001632 | NCR | Westbound invert containment |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-09-30 | 2016-09-30 15:25 | 0 | 2016-07-11 08:43 | Electrical - Cable Management | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The drawings issued are indicative to give the installing team an idea of how to install the containment. The installation of the bracket configuration is slightly different to that shown on the drawing.
| 02SL - Stations (LUL) | Cxxx-NCR-001634 | NCR | MTH GL8 2 no. Beamlets between GLZ and GLY |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-01-27 | 2016-11-11 09:45 | -77 | 2016-07-11 15:36 | Architectural - Finishes | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | The surface finish on two beamlets between GLZ and GLY on GL8 do not meet the requirements set out in JE50.
| 02SL - Stations (LUL) | Cxxx-NCR-001635 | NCR | MTH GL 7 Beamlet Soffit Damage |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-10-31 | 2016-11-11 09:46 | 11 | 2016-07-18 09:33 | Structural Engineering - Pre-cast | 1500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Contamination | Completed |  | Scratches and marks on the soffit of the GL 7
| 02SL - Stations (LUL) | Cxxx-NCR-001636 | NCR | TUN - Additional LCE Service bed cracks |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-08-25 | 2016-08-02 08:06 | -23 | 2016-07-18 16:00 | Civil - Structural Engineering | 500 |  | Material | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Additional shrinkage service bed cracks have been identified on LCE Service bed in he following chainages 8168.865, 8158.943, 8149.065. Crack widths range from 0.5mm to 1.5 mm.
| 02SL - Stations (LUL) | Cxxx-NCR-001637 | NCR | BTH - Ticket Hall Wall 1 Vent Shaft Opening Reinforcement Incorrect |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-09-29 | 2016-09-14 09:54 | -15 | 2016-07-21 12:02 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Wall 1 was constructed during May/June of 2015. The reinforcement fixed within the wall was fixed according to Cxxx-LAO-C-DWG-C101_WS102-50084 Rev C04. This drawing was at Code 2 status. Since the construction of the wall Rev C06 has been approved Code 1 but differs from what was built
| 02SL - Stations (LUL) | Cxxx-NCR-001638 | NCR | TUN - Damaged concrete in corbel at LCWb |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-11-30 | 2016-08-24 14:18 | -98 | 2016-07-25 13:02 | Civil - Structural Engineering | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | Damaged concrete (honeycombing) at the bottom section of the LCWb corbel - column located at Ch. 8221.292. Please see attached photos and drawing (Cxxx-MMD-C-DDA-C101_Z-20240 Comments) for location
| 02SL - Stations (LUL) | Cxxx-NCR-001640 | NCR | __X - VD2 - Leaks to VD2 Crown |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-06-30 | 2017-06-28 08:12 | -2 | 2016-07-26 13:24 | Civil - Civil Engineering General | 10000 |  | Workmanship | Use As-Is | 2 (6-60k) | Complete | External Phenomenon - Other | Completed |  | Following the handover of VD2 from Cxxx to Cxxx a number of issues with the Masterseal and sheet membrane were highlighted by Cxxx and included in the handover package (REF). These included small leaks in the crown, sides and invert. The leaks in the crown were also noted to be coming from\around some of the existing resin injection packers installed, injected and subsequently cut off by Cxxx. A small area of damage in the invert liner was also recorded. Due to the extended timeframe between Cxxx’s handover to Cxxx, the subsequent return of the area to Cxxx and casting of the VD2 wraparound, the issues with the Masterseal applied by Cxxx has been magnified. The extended programme of handovers between the three contractors has increased the time frame that is likely to have resulted in a build up of water pressure behind the membrane. Specification KW20 (Rev 12) section KW20.3401 states “The spray applied waterproofing membrane shall not be without a secondary concrete lining for a period of time that results in a build up of water pressure behind the membrane.” Cxxx have installed numerous bleeder pipes and resin injected where required, in order to control the water ingress in the crown, sides and invert. However due to the proximity of the leaks to the existing SCL, it has not been possible to achieve the 200mm minimum lap required for repairs on the Masterseal.
| 02SL - Stations (LUL) | Cxxx-NCR-001641 | NCR | __X - AP1 - Setting out error to crown |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-09-15 | 2016-08-22 11:02 | -24 | 2016-07-28 15:24 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | AP1 Crown has been set out incorrectly - see attached sketches Cxxx-NCR-001641 SKETCH 1,2 &3.
| 02SL - Stations (LUL) | Cxxx-NCR-001642 | NCR | BTH - Finishing issues with 'Megaplank' 132 - 13B |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-06-30 | 2017-06-07 10:54 | -23 | 2016-07-27 16:19 | Architectural - Finishes | 2500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Plank has various defects that need to be put right to bring up to acceptable standard, these include strap marks from transport, poorly colour matched repairs and 6no. sockets cast in error on the visible 'underside' of the plank.
| 02SL - Stations (LUL) | Cxxx-NCR-001643 | NCR | BTH - Southern Ticket Hall Architectural Soffit Plank 25 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-11-30 | 2016-11-28 16:04 | -2 | 2016-07-28 07:21 | Civil - Civil Engineering General | 2000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper handling of material | Completed |  | During transportation from __ Manufacturing to site plank 25 suffered some damage, see attached photos.
| 02SL - Stations (LUL) | Cxxx-NCR-001645 | NCR | __X- Fire dampers street level 2 and 3 slab openings |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-12-12 | 2016-12-14 14:12 | 2 | 2016-07-28 12:25 | Civil - Structural Engineering | 1000 |  | Design | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Interfacing problems | Completed |  | The structural slab openings for damper units on street level 2 and 3 do not leave enough room the required fire stopping application. The slab opening is 410 x 410mm for a damper size of 400mm x 400mm.
| 02SL - Stations (LUL) | Cxxx-NCR-001646 | NCR | __X Structural Change at Platform Riser 786 for Electrical Equipment |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-10-31 | 2016-10-25 09:55 | -6 | 2016-07-28 12:50 | Civil - Structural Engineering | 2000 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The design position of the module and electrical route was changed on the model and now conflicts with the structural opening of the slab.
| 02SL - Stations (LUL) | Cxxx-NCR-001647 | NCR | TUN - Temporary cables cast within concrete |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-11-30 | 2016-08-22 08:41 | -100 | 2016-07-28 14:15 | Structural Engineering - Concrete Member | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | 110V temporary cables have been inadvertently cast within insitu concrete pours. This has occurred in 3 areas; LCE suspended slab, westbound upstands and RCE suspended slab. See the attached mark-up showing approximate locations.
| 02SL - Stations (LUL) | Cxxx-NCR-001648 | NCR | Precast Plank GL 10-11 Soffit Damage |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-03-31 | 2017-03-10 09:00 | -21 | 2016-08-01 08:06 | Architectural - Ceilings & Soffits | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | The soffit of the precast plank 10-13 on drawing no. Cxxx-MMD-C-DDA-C101_A-11301, has been damaged. Please find attached photographs.
| 02SL - Stations (LUL) | Cxxx-NCR-001649 | NCR | Stage 2 RC Works QA Pack Missing Cube Results |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-11-30 | 2016-09-12 12:53 | -79 | 2016-08-01 10:52 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Only 2 no. 28 days cubes were produced in some of the 50m3+ pours included in the MTH Stage 2 RC works quality pack: PPIR092 - 09/01/2016 PPIR093 - 09/01/2016 PPIR117 - 08/04/2016 PPIR122 - 14/04/2016 PPIR095 - 23/01/2016 PPIR118 - 08/04/2016
| 02SL - Stations (LUL) | Cxxx-NCR-001650 | NCR | Use of __ Copper Pipe fittings without MCR approval |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-08-29 | 2016-08-11 14:03 | -18 | 2016-08-01 13:57 | Mechanical - Hot & Cold Water Supplies | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | __ Copper Pipe fittings used without an approved MCR.
| 02SL - Stations (LUL) | Cxxx-NCR-001651 | NCR | Storage of Ductwork and dampers without adequate protection |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-08-29 | 2016-08-11 14:00 | -18 | 2016-08-01 15:53 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper storage of material | Completed |  | Storage of Ductwork and ancillary items on being stored without adequate protection measures.
| 02SL - Stations (LUL) | Cxxx-NCR-001652 | NCR | Basement Reconstructed Slab Clash with Existing MHS2 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-08-31 | 2017-08-21 09:26 | -10 | 2016-08-02 09:23 | Civil - Civil Engineering General | 5000 |  | Design | Repair | 3 (3-6k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | Slab built to existing level, top of manhole MHS2 happens to be 25mm higher, creating a step around the edge of the manhole. See photos and sketch attached
| 02SL - Stations (LUL) | Cxxx-NCR-001653 | NCR | Roller Door Structural Opening __X |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-11-30 | 2016-10-07 17:20 | -54 | 2016-08-05 14:05 | Civil - Structural Engineering | 1500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | The structural opening for the roller shutter door on the eastern elevation of Blomfield Box, Street level, has an as-built dimension of 3.5m. The shop drawings have shown a dimension of 3.75m. The door has now been manufactured to the shop drawings and ready for install, meaning the opening is 250mm too narrow.
| 02SL - Stations (LUL) | Cxxx-NCR-001654 | NCR | TUN - GEN - Required Grout Strength for Precast |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-09-06 | 2016-08-11 09:20 | -26 | 2016-08-09 09:00 | Structural Engineering - Grouting | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | RFI previously raised and confirmed with __, the precast designer. This NCR is to inform CRL and allow capture on red-line drawings. __ __ HF and Parex Thixotropic Joint Filler were used for installation of the precast elements for construction of the platforms in the tunnels. Some of the 28 day cube results for __ __ HF were marginally below the design strength of the grout. __ were asked to confirm the required grout strength for the __ __ HF and Parex Thixotropic Joint Filler. Attached are the worst case cube results, a location markup of the grout in question (which was also sent to __), __ email confirmation and __ response to RFI 2565. This NCR is a duplicate of Cxxx-RFI-003480 at the request of CRL.
| 02SL - Stations (LUL) | Cxxx-NCR-001655 | NCR | TUN - LCE - PFA residue contamination to concrete pour |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-11-30 | 2016-09-06 08:15 | -85 | 2016-08-10 08:40 | Structural Engineering - Concrete Member | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | The mass fill concrete poured for the trackbed on 08/08/2016 showed PFA residue on the surface of the pour despite the fact PFA is not present in the W4 mix design. The location of the pour is shown in the attached location markup. After consulting with __ they identified that this must have been residue of CEM II concrete that was supplied to other customers. The concrete truck supplying the CEM II concrete must not have been thoroughly washed out before it was used to supply concrete to Liverpool Street Station. As CEM II is a blend of CEM I and PFA you would expect the residue to be dark colour shown. The __ Materials Technology Centre concurred that the residue looks like it contains PFA. It is significant that although the substance was dark in colour and fairly opaque it formed only a thin film on the surface of the pour. The concrete technician testing the workability of the supplied concrete demonstrated that all concrete supplied on this date was within specification on the flow table. He identified laces of a darker substance in the hopper of the pump when one of the concrete trucks was being pumped.
| 02SL - Stations (LUL) | Cxxx-NCR-001656 | NCR | Delivery Inspection checks on PES steelwork had not been recorded as complete on check sheet QCL10 for sampled Bays E6-15. |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2016-11-30 | 2016-09-27 12:07 | -64 | 2016-08-10 11:41 | Architectural - General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | A planned Crossrail Quality surveillance was undertaken on 9th August 2016 which looked at Platform Edge Screen (PES) installation. During the visit, ITP records were sampled for Eastbound Bays 6-15. The records sampled covered alignment beam installation, grouting, and truss installation. QCL10 check sheets were presented as referenced in the ITPs as the ‘verifying document’ for installation activities. On checking, the ‘Delivery Inspection’ section of the records for Bays 6-15 had not been completed and remained blank. The ‘Delivery Inspection’ activity of all fabricated items forms a Hold Point for __ under Inspection Number 3.1 of ITPs Cxxx-LAO-O4-ITP-C101- *50080 (Installation of Alignment Beams and Grouting) and *50084 (Trusses, Plenum Struts and Posts). As the QCL10 check sheets remained blank, there was no verifiable evidence to confirm that the checks/inspections (against drawings etc) had taken place prior to installation in the works. At the time of the surveillance, for the sampled areas, the beams and trusses had been installed in the works. ISO 9001 requires that organisations establish and implement the inspection, or other activities, necessary for ensuring that purchased products meet the specified purchase requirements, whilst ensuring records are established providing evidence of conformance to requirements.
| 02SL - Stations (LUL) | Cxxx-NCR-001657 | NCR | TUN - PTE - Additional construction joint in trackbed bay 5 pour 1 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-11-30 | 2016-09-06 08:21 | -85 | 2016-08-10 12:26 | Structural Engineering - Concrete Member | 500 |  | Incomplete Works | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Other human error | Completed |  | Insufficient concrete was ordered to complete the mass fill pour carried out for trackbed bay 5 pour 1 on 10/07/2016. This meant the pour was left low at the western end of the pour. Following approval from Cxxx the surface of the area left low was retarded, jetwashed and then topped up with addition concrete on 12/08/2016. Details are shown in the attached documents.
| 02SL - Stations (LUL) | Cxxx-NCR-001658 | NCR | PES - Damage to Angle Cleats Welded to the Truss |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-11-30 | 2016-11-25 16:28 | -5 | 2016-08-11 15:58 | Structural Engineering - Steel Member | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper handling of material | Completed |  | Angle cleats on a 6m truss and a 3m that are required to fix the steel blanking panel to have been knocked out of alignment during transit.
| 02SL - Stations (LUL) | Cxxx-NCR-001659 | NCR | MSH - Track slab upstands ch 8201 to 8216 |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2017-11-30 | 2016-08-30 10:48 | -457 | 2016-08-11 14:17 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Contractor start concreting of the track slab up-stands on Westbound between chainage 8201 to 8216 without construction joint prepared as per their ITP Cxxx-LAO-O4-ITP-C101_WS099-50022 R5 pint 4.3 . Please see attached photos. At the time of inspection 2/3 of the area was already concreted. No PPIR was prepared for this section of the works.
| 02SL - Stations (LUL) | Cxxx-NCR-001660 | NCR | MTH GL11 Beamlets GLW to Y |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-04-18 | 2016-11-11 09:47 | -158 | 2016-08-11 15:39 | Architectural - Finishes | 2000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | A raised access platform came into contact with two number beamlets on GL11 between GLW and GLY. Black plactic caps on the podium rubbed off the beamlets and left scuff marks.
| 02SL - Stations (LUL) | Cxxx-NCR-001661 | NCR | __X North Wall Grout Joints |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-12-11 | 2016-10-31 15:04 | -41 | 2016-08-13 12:14 | Architectural - Masonary | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | The vertical grout joints of the northern wall have had discoloration and/or staining of the grout, which does not match the signed off benchmark as attached. There does not seem to be any structural problem rather aesthetics.
| 02SL - Stations (LUL) | Cxxx-NCR-001662 | NCR | incorrect use of a proprietary fixing to CMS support bracket |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2016-11-30 | 2016-11-07 16:37 | -23 | 2016-08-15 14:40 | Electrical - Cable Management | 1000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | square plate washer used in non standard method to support suspended unistrut bracket eastern end of east bound platform.
| 02SL - Stations (LUL) | Cxxx-NCR-001663 | NCR | MTH Beamlets GL9 between GL Y and GLW |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-04-23 | 2016-11-11 09:47 | -163 | 2016-08-16 16:48 | Architectural - Finishes | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | Three number beamlets have a number of blowholes and a some overblasting.
| 02SL - Stations (LUL) | Cxxx-NCR-001664 | NCR | TUN - GEN - __ channels in platform nosing out of tolerance |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-01-31 | 2017-01-06 08:11 | -25 | 2016-08-17 15:45 | Structural Engineering - Concrete Member | 3000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Two rows of parallel __ channels have been installed along the top surface of the nosing of the platforms. These __ channels are present in both the front of house areas where precast planks were used for construction, and the back of house areas which were cast in-situ. They have been installed for both the Westbound and Eastbound tunnels. An as-built survey has been carried out of the __ channels highlighting that in a few areas the channel has been installed out of tolerance. The 'worst case' permissible tolerance available in the Cxxx baseplate is +/-20mm on position of the channels as an offset of from the CL of the track and +/-10mm on spacing between the parallel channels. See attached email from __ (Cxxx) entitled "RE Platform and Tunnels - Platform Edge __ Channel NCR.htm". For the Eastbound tunnel, the worst case misalignment is 17mm from design location of the offset from the CL of the track (this falls within the +/-20mm revised tolerance on position). The worst case misalignment on spacing is 12mm smaller than design (an 2mm exceedance of tolerance). The survey results for the Eastbound tunnel are attached - see "PTE - __ as-built survey - Results.pdf" For the Westbound tunnel, the worst case misalignment is 25mm from design location of the offset from the CL of the track (a 5mm exceedance of revised tolerance). The spacing is also 16mm larger than design (a 6mm exceedance of tolerance). The survey results and indication of the problem areas for the westbound tunnel are attached - see "PTW - __ as-built survey - Final Results.pdf" and "PTW - __ as-built survey - problem locations.pdf ". Having identified the problem locations in the Westbound tunnel Cxxx collaborated with Cxxx who provided the fabrication drawings for their baseplate connection. Cxxx fabricated two prototype plates which were used to test whether the plates could still be installed to Cxxxs requirements in spite of the tolerance exceedances.
| 02SL - Stations (LUL) | Cxxx-NCR-001665 | NCR | MSH Wall W9a Section cast below required thickness |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-10-08 | 2016-09-28 14:59 | -10 | 2016-08-19 11:20 | Structural Engineering - Concrete Member | 1000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Wall W9a is a 250mm thick wall. During the erection of the Wall W9a shutters there was a 225mm timber spacer placed on top of the shutters, for a 400mm long section. The tie rods were tightened and the wall was cast, for this top section only at 225mm.
| 02SL - Stations (LUL) | Cxxx-NCR-001666 | NCR | TUN - PTW - Slab penetrations for construction of UPE crossover wingwall at CP2 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-09-20 | 2016-09-06 12:57 | -14 | 2016-08-23 13:44 | Structural Engineering - Concrete Member | 500 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | The UPE crossover wingwall at CP1 could not be constructed until after the precast planks had been installed above. Construction of the wingwall is now problematic for the following reasons: - Concrete cannot be poured from above because access is restricted by the precast plank - It would be difficult to vibrate the concrete from above because access is restricted by the precast plank - The geometry, location and size of the concrete element does not lend itself well to using proprietary formwork, a face shutter guillotine and an external vibrator or self compacting concrete
| 02SL - Stations (LUL) | Cxxx-NCR-001667 | NCR | TUN - PTW - Incorrect cover to reinforcement for area of suspended slab |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-09-20 | 2016-09-06 08:44 | -14 | 2016-08-23 16:09 | Structural Engineering - Concrete Member | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | In LCWb suspended slab, reinforcement was installed and poured in the steel free zone with the incorrect cover. For the area shown in the attached markup cover to the underside of the slab was 25mm and cover to the topside of the slab varied from 70 - 85mm. These values are in excess of the permissible tolerance.
| 02SL - Stations (LUL) | Cxxx-NCR-001668 | NCR | TUN - GEN - Trackbed FSC surface profile tolerance exceeded |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-09-21 | 2016-09-06 12:48 | -15 | 2016-08-24 08:58 | Structural Engineering - Concrete Member | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Minor exceedances of tolerance on the surface profile of the First Stage Concrete (FSC) for the trackbed are present. These areas are shown in the attached as-builts and are highlighted in red. Worst case values are stated below: - Trackbed elevation: -15mm low / +13mm high - Upstand elevation: -17mm low / +19mm high - Channel positional misalignment: 13mm
| 02SL - Stations (LUL) | Cxxx-NCR-001670 | NCR | TUN - LCE - Column chamfers omitted |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-09-21 | 2016-09-01 13:45 | -20 | 2016-08-24 15:30 | Structural Engineering - Concrete Member | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | The chamfers were omitted on the column supporting the suspended slab in Launch Chamber East. See location markup and photo. A 20mm chamfer was required by the General Notes drawing - Cxxx-MMD-C-DDJ-C101-10011.
| 02SL - Stations (LUL) | Cxxx-NCR-001671 | NCR | BTH - Southern Ticket Hall Precast Soffit Plank 021 - 028 Surface Defects |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-12-08 | 2016-12-08 13:21 | 0 | 2016-08-25 08:24 | Civil - Civil Engineering General | 10000 |  | Manufacturing Defect | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Post inspection of the precast soffit planks 021 – 028 various surface defects were identified. Please refer to Steve Tucker’s plan drawing showing location of snags. These defects will be made good by our expert concrete finisher and then offered to the Architect for acceptance.
| 02SL - Stations (LUL) | Cxxx-NCR-001672 | NCR | BTH - STH Precast Soffit Planks 029 - 036 Various Surface Defects |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-12-08 | 2016-12-08 13:23 | 0 | 2016-08-25 08:38 | Civil - Base Course | 10000 |  | Manufacturing Defect | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Post inspection of the precast soffit planks 029 – 036 various surface defects were identified. Please refer to Steve Tucker’s plan drawing showing location of snags. These defects will be made good by our expert concrete finisher and then offered to the Architect for acceptance. Particular attention needs to be brought to the water staining between planks 036 and 143 as well as the cracking through the middle of the planks.
| 02SL - Stations (LUL) | Cxxx-NCR-001673 | NCR | BTH - STH Precast Soffit GLB Beams Finish Defects |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-09-30 | 2017-10-06 15:12 | 6 | 2016-08-25 08:44 | Civil - Civil Engineering General | 15000 |  | Manufacturing Defect | Repair | 2 (6-60k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Post inspection of the precast GL B beams 111 - 115 various surface defects were identified. Please refer to Steve Tucker’s plan drawing showing location of snags. These defects will be made good by our expert concrete finisher and then offered to the Architect for acceptance. Special attention needs to be placed on the mould marks on the north side of beam 115.
| 02SL - Stations (LUL) | Cxxx-NCR-001675 | NCR | BTH - STH Precast Soffit 143 and 144 |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2017-06-30 | 2017-06-07 10:48 | -23 | 2016-08-25 10:19 | Civil - Civil Engineering General | 1500 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Post inspection of the precast planks 143 - 144 various surface defects were identified. Please refer to Steve Tucker’s plan drawing showing location of snags. These defects will be made good by our expert concrete finisher and then offered to the Architect for acceptance. Special attention needs to be paid to the pit marks which are a result of the making good of blow holes.
| 02SL - Stations (LUL) | Cxxx-NCR-001676 | NCR | __X- Missing Lightening Protection Connections Streel Level +1 (118 OSD Roof) |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-08-31 | 2018-10-19 09:01 | 414 | 2017-02-01 18:40 | Electrical - General | 10000 |  | Workmanship | Repair | 2 (6-60k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | __ Street Level +1 OSD roof Lightening connection points marked in red on attached markup have not been left exposed (buried beneath Hotmelt waterproofing, protection screed and perimeter copping)
| 02SL - Stations (LUL) | Cxxx-NCR-001677 | NCR | BTH - LU Vent Shaft Portal Opening North Wall - Insufficient Cover |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-12-31 | 2016-10-10 09:39 | -82 | 2016-08-30 09:42 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Due to reinforcement clashes with the cast-in reinforcement from Ticket Hall Wall 1 and the Northern wall of the vent shaft portal, the reinforcement within the northern portal wall had insufficient cover
| 02SL - Stations (LUL) | Cxxx-NCR-001678 | NCR | MTH - GL 9 Beamlets Grouting Cube Results Missing |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-09-27 | 2016-09-12 13:57 | -15 | 2016-08-30 13:06 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | No grout cubes were produced during the grouting of the GL9 precast beamlets in the Moorgate Ticket Hall
| 02SL - Stations (LUL) | Cxxx-NCR-001679 | NCR | BTH - Ticket Hall wall 15 water ingress |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-01-31 | 2017-01-17 17:34 | -14 | 2016-09-07 12:21 | Structural Engineering - Concrete Member | 2000 |  | System Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | After pouring the roof of the south thicket hall, and a period of rain, some water ingress have been noticed. See attached photo's.
| 02SL - Stations (LUL) | Cxxx-NCR-001680 | NCR | BTH - Post cut blockwork opening in North-East corner of basement |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-11-06 | 2016-11-02 11:27 | -4 | 2016-09-07 12:34 | Architectural - Brickworks/Blockworks | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Service opening cut after install of blocks, cut is to a poor standard and not acceptable.
| 02SL - Stations (LUL) | Cxxx-NCR-001681 | NCR | MTH. Internal grouting line on the beamlets GL9 W to Y |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-11-30 | 2016-10-04 08:41 | -57 | 2016-09-08 10:35 | Civil - Civil Engineering General | 3000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The internal shutter for the beamlet grouting on GL9 between W and Y has bowed out approx. 15mm in a 1.5m section during the grouting operation. The line of the grout in this area will need to be scabbled back to within the construction tolerances and made good to allow for the M&E to be installed in this location. Please note that this the internal face therefore will not be seen once completed.
| 02SL - Stations (LUL) | Cxxx-NCR-001682 | NCR | Excessive concrete cover |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-10-31 | 2016-09-13 15:49 | -48 | 2016-09-08 11:31 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Wall 10 as referenced on drawing Cxxx-LAO-C-DWG-C101-50149 from level 74.200 - 78.100 has 60mm concrete cover over a 300mm high section extending the length of the wall. This section begins at the change point from 250mm thick wall wall to 140mm thick wall
| 02SL - Stations (LUL) | Cxxx-NCR-001684 | NCR | MSH- Missing Reinforcment as per drawing |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-11-30 | 2016-11-03 10:27 | -27 | 2016-09-09 10:48 | Civil - Civil Engineering General | 3000 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | Landing slab 78.1 was constructed as per drawing Cxxx-LAO-C-DWG-C101-50071 & 50072. After investigation it was found that main bars from the beam was missing from both drawings and so were not put into the slab pour.
| 02SL - Stations (LUL) | Cxxx-NCR-001685 | NCR | No UKAS accrediation for the FP Mcann facilty & Technicians at __ for the Sampling of fresh concrete |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-11-30 | 2016-11-30 16:20 | 0 | 2016-09-09 14:48 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | The __’s precast manufacturing facility at __ and the Technicians who conduct the concrete testing /sampling (carry out the concrete slump tests and produce to the concrete cubes for testing) at the same facility, currently do no not have UKAS (United Kingdom Accreditation Service) certification for the sampling of fresh concrete on site. Although the precast units were manufactured at the facility at __ , __s there have been following the same quality processes and procedures ( received via internal training) as those being carried out at one of their other facilities __ , Burton-on Trent which is UKAS accredited ( please see attached UKAS schedule), and the slump flow test have been carried out in accordance with the requirements of BS EN 12350-8:2010. Furthermore the cubes produced have been crushed and tested by __ who are UKAS accredited. As discussed the proposal to satisfactorily close out the above is that __ will undertake the training of the __ Operatives at __ and furthermore also validate the internal training already received and the processes and procedures already adopted, by providing a certificate to this effect to state that the competency of the operatives meets the required standard.
| 02SL - Stations (LUL) | Cxxx-NCR-001686 | NCR | BTH - South Ticket Hall Roof Slab Insufficient Cover |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-05-31 | 2017-05-04 16:48 | -27 | 2016-10-26 09:17 | Civil - Civil Engineering General | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The north eastern corner of the south ticket hall roof slab has been poured with insufficient cover to the top mat at the northern coupler face. A cover survey revealed cover at face of construction joint to be an average of 20mm. The survey revealed that cover increased to 50mm within about 0.5m.
| 02SL - Stations (LUL) | Cxxx-NCR-001687 | NCR | Incorrect Fire Damper Installation |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-12-23 | 2016-11-17 11:43 | -36 | 2016-09-16 08:36 | Mechanical - Heating Ventilation & Air Conditioning | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | In 3 instances within Blomfield Box, fire dampers have been installed through walls too close to an adjacent fire damper.
| 02SL - Stations (LUL) | Cxxx-NCR-001688 | NCR | Training records not provided for PES grout testing being undertaken by __ and __ personnel |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2016-12-23 | 2017-01-18 10:14 | 26 | 2016-09-16 12:42 | Architectural - General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other management problem | Completed |  | A planned Crossrail Quality surveillance was undertaken on 9th August 2016 which looked at Platform Edge Screen (PES) installation. During the surveillance exit meeting, training records were requested for __ operatives undertaking grout cube manufacture and __ operatives carrying out compressive strength testing (cube crushing) within the onsite laboratory. The request was made for records to demonstrate compliance with PMC Cxxx-PMC-02632 which states the following as a relaxation of the Works Information requirements. “1. Concrete and grout test cubes can be tested in a non-UKAS accredited laboratory for purposes of striking shutters and issuing permits to load, where personnel are UKAS trained or similar” The initial request for the training records was documented in the surveillance exit note dated 9th August 16. Following further meetings and post surveillance requests no training records from the supplier was provided with respect to __ operatives undertaking grout cube manufacture. In addition to the above, post surveillance following multiple requests, training records were provided for the __ operative (dated 13/09/16), however on review of the information, the training only covered physical concrete sampling and consistency testing. There was no reference to training associated with undertaking compressive strength testing in accordance with BS EN 12390-3. On follow up, no information was further provided as evidence of UKAS training associated with this testing. In this instance, the requirements of Works Information Part 20.8 and the subsequent PMC have not been complied with.
| 02SL - Stations (LUL) | Cxxx-NCR-001689 | NCR | MTH - Reinforcement out of place |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-12-31 | 2016-10-04 07:46 | -88 | 2016-09-17 07:56 | Structural Engineering - Reinforcement | 1500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | At 114.050 G Z+3.100m there is a slab edge. Currently reinforcing bar is protruding from that slab edge along its length by a distance of 8-80mm.
| 02SL - Stations (LUL) | Cxxx-NCR-001690 | NCR | TUN - PTW - Trackbed FSC drainage channel invert survey |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-10-17 | 2016-10-11 13:36 | -6 | 2016-09-19 08:58 | Structural Engineering - Concrete Member | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | An as-built survey of the invert of the drainage channel in Platform Tunnel West has been carried out and in certain areas the level of the surface of the concrete exceeds the +/-10mm tolerance. See attached survey and refer to the Westbound tunnel. The results of the survey have been reviewed and accepted by Cxxx. Please refer to attached email for their confirmation of acceptance. Note that this NCR covers the Westbound tunnel only and that the Eastbound tunnel is covered by a separate NCR.
| 02SL - Stations (LUL) | Cxxx-NCR-001691 | NCR | TUN - PTE - Trackbed FSC drainage channel invert survey |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-10-17 | 2016-10-11 13:39 | -6 | 2016-09-19 08:57 | Structural Engineering - Concrete Member | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | An as-built survey of the invert of the drainage channel in Platform Tunnel East has been carried out and in certain areas the level of the surface of the concrete exceeds the +/-10mm tolerance. See attached survey and refer to the Eastbound tunnel. The results of the survey have been reviewed and accepted by Cxxx. Please refer to attached email for their confirmation of acceptance. Note that this NCR covers the Eastbound tunnel only and that the Westbound tunnel is covered by a separate NCR.
| 02SL - Stations (LUL) | Cxxx-NCR-001692 | NCR | MSH - Missing couplers in exsisting structure. 74-78 level wall D |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-11-30 | 2016-11-01 13:31 | -29 | 2016-09-19 13:04 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Female couplers were not cast into the existing structures as shown on drawing Cxxx-LAO-C-DWG-C101-50063. 46no. B25 (Bar mark E50 & E49). There were couplers cast into the lining wall, however these were in the wrong position. See picture.
| 02SL - Stations (LUL) | Cxxx-NCR-001694 | NCR | MSH - Couplers missing from existing structure 78 North slab |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-11-30 | 2016-11-01 13:28 | -29 | 2016-09-19 13:40 | Civil - Civil Engineering General | 2000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Female couplers are missing from the existing structure for the connection into the 78 north slab, As per drawing Cxxx-LAO-C-DWG-C101-50067 & 50068. 67no. Bar mark E53 B20 male couplers were to be fixed in to the missing female couplers.
| 02SL - Stations (LUL) | Cxxx-NCR-001695 | NCR | Distribution Board IP Rating |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-12-23 | 2016-10-24 12:22 | -60 | 2016-09-22 11:33 | Electrical - Power Distribution | 1000 |  | Material | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Distribution Boards being installed have labels stating IP3X and 2X, however the specification asks for IP31.
| 02SL - Stations (LUL) | Cxxx-NCR-001696 | NCR | BTH – Ticket Hall Roof Pour 2 re-bar |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-11-18 | 2016-10-10 09:44 | -39 | 2016-09-23 11:59 | Structural Engineering - Concrete Member | 2000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During a site inspection with __ (Cxxx), 6no issues were raised and have been captured in the correspondence attached.
| 02SL - Stations (LUL) | Cxxx-NCR-001697 | NCR | Homogeneity of Fibre Distribution testing has not been completed for concrete elements cast with polypropylene fibre concrete. |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2016-12-23 | 2016-11-01 08:48 | -52 | 2016-09-23 12:07 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Other human error | Completed |  | A planned Crossrail Quality Surveillance was undertaken on 21st September 2016 which looked at reinforced concrete works in Moorgate Shaft. During the site visit it was noted that a number of elements had been constructed using concrete containing polypropylene fibres for fire protection. Cxxx Specification KF10 requires ‘homogeneity of fibre distribution’ (wash out) testing at a sampling rate of 1 test/ pour. It was stated post surveillance that no testing had been completed for the elements where polypropylene concrete had been used. As a result, the 80% minimum weight requirement (specification) against the 2kg/m3 dosage has yet to be validated as required by the sampling frequency.
| 02SL - Stations (LUL) | Cxxx-NCR-001698 | NCR | BTH – Ticket Hall Roof Slab Pour 2 Bar Mark E/46 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-11-18 | 2016-11-01 13:35 | -17 | 2016-09-23 12:13 | Structural Engineering - Concrete Member | 500 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Error by manufacturer in shipping or marking | Completed |  | Bar mark E/46 was bent incorrectly by __’s reinforcement supplier as a result the bar if installed will protrude out of the SSL by 100mm.
| 02SL - Stations (LUL) | Cxxx-NCR-001700 | NCR | MTH - L1 Lifting Point Locations |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-12-23 | 2016-11-14 09:24 | -39 | 2016-09-26 16:14 | Structural Engineering - Pre-cast | 2000 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | Variation between __ and __ drawings and as-built locations has resulted in lifting points in incorrect locations.
| 02SL - Stations (LUL) | Cxxx-NCR-001701 | NCR | MSH - 78.100 SSL GL 2&4 - Landing upstand beam for stairs |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-12-23 | 2016-11-10 15:09 | -43 | 2016-09-27 10:21 | Civil - Civil Engineering General | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | The beam on GL D (-) 2.5 between GL 2 & 3. Pockets were not installed in the beam. These pockets are required to connect the precast stairs to the beam at level 78.100.
| 02SL - Stations (LUL) | Cxxx-NCR-001702 | NCR | Ingress construction water causing discoloration and zinc carbonate frosting to CMS trunking in riser 784 __X |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-11-21 | 2017-10-05 14:56 | -47 | 2016-09-27 08:31 | Electrical - Electrical Engineering General | 10000 |  | Damaged | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Contamination | Completed |  | Riser 784 CMS trunking has discoloration and zinc carbonate frosting due to ingress construction water from the riser not being sealed. A report on whether this effects the containment other than discoloration has been requested from the CMS manufacturer.
| 02SL - Stations (LUL) | Cxxx-NCR-001703 | NCR | TUN - LCW - UTX duct blocked with concrete |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-10-25 | 2016-10-11 13:45 | -14 | 2016-09-27 14:35 | Electrical - Power Distribution | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | UTX duct intended for Cxxx Power has been blocked by a concrete leak. The concrete blockage is located in LCWb, is 4.55m from the edge of Moorgate shaft and is 1.1m in length with likely a small amount of feathering outside of this area. A camera has been used to investigate the duct and dip checks from either side established the approximate size of the blockage. See attached markups specifying the UTX, it’s location and identifying where the blockage is.
| 02SL - Stations (LUL) | Cxxx-NCR-001705 | NCR | Ingress construction water causing discoloration and zinc carbonate frosting to CMS lidding stored in the bottom of riser 784 __X |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-10-28 | 2016-10-19 14:16 | -9 | 2016-09-30 07:49 | Electrical - General | 2000 |  | Damaged | Reject | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper storage of material | Completed |  | As per the previous situation described under Cxxx-NCR-001702 with the ingress construction water causing discoloration and zinc carbonate frosting to the CMS. there were CMS lids stored at the bottom of riser 784 which have also been affected and damaged.
| 02SL - Stations (LUL) | Cxxx-NCR-001706 | NCR | Openings for Fire Hydrant Cabinet Platform __X |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-12-13 | 2016-12-15 10:24 | 2 | 2016-09-30 10:11 | Civil - Structural Engineering | 3000 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The structural opening for the fire outlet cabinet at platform level does not meet the required dimensions under BS 5041 Part 4: "Clearance above hand wheel not less than 200mm" and BS 9990:2006 "lowest point about 750mm above floor level". It is required to increase the size of opening by 150mm along the top and 50mm along the side edge of the opening as per attached photograph. Note the solution has been internally RFI'd and is attached.
| 02SL - Stations (LUL) | Cxxx-NCR-001708 | NCR | MSH- Vertical discharge of concrete greater than 5m |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-12-02 | 2016-11-30 11:28 | -2 | 2016-10-03 12:35 | Civil - Civil Engineering General | 2000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | When pouring wall A, B, C, D and E from level 78.1 to 83.455 concrete was skipped into the walls meaning that the concrete was vertically discharged greater than 5m.
| 02SL - Stations (LUL) | Cxxx-NCR-001709 | NCR | MTH - beam over escalator decline damaged face |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-12-31 | 2016-11-29 15:51 | -32 | 2016-10-04 09:41 | Structural Engineering - Concrete Member | 2000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | After pouring Slab over escalator decline (pour ref 154) on 28/9, the vertical links for the rear upstand have been leant back into position. This has caused spalling in multiple locations.
| 02SL - Stations (LUL) | Cxxx-NCR-001710 | NCR | CMS installaion |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2016-12-31 | 2018-01-29 13:21 | 394 | 2016-10-04 10:10 | Electrical - Cable Management | 10000 |  | Supervision/Management | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | Multi compartment trunking reducers installed within __ do not comply with LU standard 1-069 as the internal compartments do not have gusseted bends as required by 1-069 3.9.6.
| 02SL - Stations (LUL) | Cxxx-NCR-001711 | NCR | MTH-Reinforcement Discrepancy |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-11-04 | 2016-10-24 08:05 | -11 | 2016-10-07 15:01 | Structural Engineering - Reinforcement | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Information not detailed | Completed |  | Couplers for wall W1 from Cxxx-LAO-C-DWG-C101_WS099-50052 were ordered on C04 drawing. C05 drawing specifies 1.450m leg length or E248 as opposed to 1m long on E244. Bars used in wall-slab connection are of BM E244, and not E246 or E248 as specified.
| 02SL - Stations (LUL) | Cxxx-NCR-001712 | NCR | TUN - LCE - Incorrect tread width on service bed steps |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-12-23 | 2016-11-21 10:16 | -32 | 2016-10-10 09:46 | Structural Engineering - Concrete Member | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | A level change is present in the service bed in Launch Chamber East, two steps are present to allow easy access between levels. The tread width specified by design and Cxxx-RFI-003435 is 300mm for each step. The steps were mistakenly cast with 150mm tread widths, the two steps occupying the space of a single step.
| 02SL - Stations (LUL) | Cxxx-NCR-001713 | NCR | Roller Shutter Door East Elevation Blomfield Box |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-01-31 | 2017-07-18 16:25 | 168 | 2016-10-10 11:45 | Architectural - Doors | 1000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Installation works have commenced on the roller shutter door without the appropriate documentation having been accepted by CRL, Charter Global Method Statement Cxxx-LAO-O1-GMS-C101_WS103-50144.
| 02SL - Stations (LUL) | Cxxx-NCR-001714 | NCR | MSH- Missing couplers for beam 1 in slab 83 level |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-11-30 | 2016-11-01 13:26 | -29 | 2016-10-10 12:29 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 14no. B25 couplers missing from lining wall.
| 02SL - Stations (LUL) | Cxxx-NCR-001715 | NCR | MSH- Couplers installed incorrectly into lining wall |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-11-09 | 2016-11-01 13:29 | -8 | 2016-10-12 13:45 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Couplers have been cast into the lining wall of the shaft for connection into wall F level 83-88. The couplers have been cast into the lining wall at an incorrect angle and are not inline with the wall.
| 02SL - Stations (LUL) | Cxxx-NCR-001717 | NCR | Blomfield Basement Drainage- Integrity of lining of Timesaver Pipework |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-01-31 | 2016-12-14 14:45 | -48 | 2016-10-14 14:13 | Civil - Drainage | 0 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During the process of jetting debri within drainage runs within level 73 slabs, it was identified via CCTV footage that there may have been some scratching of the epoxy lining of the timesaver pipes (CRL-MCR-000273). The CCTV report shows a spiral shape dark color pattern consistent with scratching of the ochre colored epoxy lining. "Pipe 1 street -6" shows a typical example of the issue.
| 02SL - Stations (LUL) | Cxxx-NCR-001718 | NCR | BTH - Ticket Hall Roof Slab North Wall Cover |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-05-26 | 2017-04-05 16:07 | -51 | 2016-10-26 08:34 | Civil - Civil Engineering General | 6000 |  | Incorrect Installation | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | Cover to the U-bars protruding from the Northern lining walls is less than required.
| 02SL - Stations (LUL) | Cxxx-NCR-001719 | NCR | BTH - Interface between Ticket hall roof slab pours at south western corner |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-02-28 | 2016-12-09 14:23 | -81 | 2016-10-26 08:14 | Civil - Civil Engineering General | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The reinforcement fixed into the southern ticket hall roof slab does not comply with the agreed Code 1 drawing signed off by CRL/Cxxx. Barmarks E/50 & E/238 located in T3 were designed to be B 32 bars with couplers. B 25 bars without couplers were incorrectly installed instead of these. Barmark E/198 located in T1 were to be 16no B32's with couplers. B 25 bars with couplers were incorrectly installed in their place.
| 02SL - Stations (LUL) | Cxxx-NCR-001720 | NCR | Moorhouse Basement Beam Soffit Repair at Grid Line 1 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-06-30 | 2017-02-21 10:41 | -129 | 2016-10-20 17:06 | Civil - Civil Engineering General | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Contamination | Completed |  | We found some crack line in October 2016, when we hammer tested the beam soffit, we found some area has been de-bonded (hollow sound). Moorhouse Beam soffit low cover was rectified as advised by the __ methodology, these repairs approved as per Cxxx-RFI-003039. These repairs were completed in May 2016.
| 02SL - Stations (LUL) | Cxxx-NCR-001721 | NCR | BTH - North ticket hall PCC roof defects |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-03-30 | 2018-03-07 09:28 | -23 | 2016-10-21 16:51 | Architectural - Ceilings & Soffits | 2000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | See attached sketch of defects, more may become apparent once temporary works is removed.
| 02SL - Stations (LUL) | Cxxx-NCR-001722 | NCR | Installation of cms not to accepted design |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2017-02-28 | 2017-02-22 09:49 | -6 | 2016-10-25 15:09 | Electrical - General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Other management problem | Completed |  | CMS within HV switch room B - has not been installed as per Current agreed construction drawings. FCD process not being followed.
| 02SL - Stations (LUL) | Cxxx-NCR-001723 | NCR | Damage to installed equipment |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2017-02-28 | 2017-03-02 14:24 | 2 | 2016-10-25 15:17 | Electrical - General | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Luminaire installed with __ platform level +4 have sustained damage and require replacement.
| 02SL - Stations (LUL) | Cxxx-NCR-001724 | NCR | Commencement of wiring prior to inspection and sign off of CMS Zones. |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2017-01-31 | 2016-11-18 10:26 | -74 | 2016-10-25 15:23 | Electrical - General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Commencement of wiring prior to inspection and sign off of installed CMS within __.
| 02SL - Stations (LUL) | Cxxx-NCR-001725 | NCR | Installation of CMS not in line with M&W specification. |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2017-01-31 | 2016-11-17 14:42 | -75 | 2016-10-25 15:32 | Electrical - Cable Management | 1000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Supervision - Other | Completed |  | Trunking installed within __ staircases ( street level to street level-1) installed inverted unnecessarily.
| 02SL - Stations (LUL) | Cxxx-NCR-001726 | NCR | BTH - Precast Column's B9 & B10 Staining |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-03-31 | 2018-03-07 09:26 | -24 | 2016-10-26 07:03 | Civil - Civil Engineering General | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | The precast architectural columns located at gridlines B9 & B10 have sustained some reinforcement staining during the period in which the column headers were uncovered to enable fixing. This was only observed when the protection box was removed to check no grout leaks were occurring due
| 02SL - Stations (LUL) | Cxxx-NCR-001727 | NCR | Galvanized grooved end unpainted. |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-02-28 | 2016-12-02 11:26 | -88 | 2016-10-28 09:59 | Mechanical - Public Health Engineering | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Galvanized grooved end unpainted, found upon spot checks by FE.
| 02SL - Stations (LUL) | Cxxx-NCR-001728 | NCR | MTH- Future PRM Stairs |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-11-28 | 2016-11-03 08:29 | -25 | 2016-10-31 17:58 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Insufficient information made available to the worker. | Completed |  | We note that the temporary 150mm thick precast covering the future PRM stairs have been supported on concrete plinth, not installed as shown on Cxxx-MMD-C-DDD-C101_Z-11241 C02 (detail 2).
| 02SL - Stations (LUL) | Cxxx-NCR-001729 | NCR | __ ITP Cxxx-LAO-04-ITP-C101_WS103-50060 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-11-30 | 2016-11-17 15:28 | -13 | 2016-11-02 17:44 | Electrical - Power Distribution | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | __ had commenced LV Sub Main Cable installation works in advance of their ITP being approved by Crossrail Field Engineer . This is not in line with __ QA policy and works information
| 02SL - Stations (LUL) | Cxxx-NCR-001731 | NCR | MSH - Pipe work not cast into 83 level slab |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-08-31 | 2017-06-28 10:22 | -64 | 2016-12-01 14:48 | Civil - Civil Engineering General | 2500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | 2 no. pipes missed out of the slab pour at 83 level. 1 x 100mm foul drainage 1 x seepage channel
| 02SL - Stations (LUL) | Cxxx-NCR-001732 | NCR | Galvanised pipework installed does not have an MCR |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-12-05 | 2016-11-28 09:53 | -7 | 2016-11-07 11:48 | Mechanical - Public Health Engineering | 5000 |  | Documentation and Records | Use As-Is | 3 (3-6k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | Galvanized pipework installed does not have an MCR approved.
| 02SL - Stations (LUL) | Cxxx-NCR-001734 | NCR | scratched door on one of the rooms at the east end of the eastbound platform |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-12-23 | 2018-01-23 09:17 | 31 | 2016-11-11 15:57 | Architectural - Doors | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Error by manufacturer in shipping or marking | Completed |  | During site visit two doors on the east end of the eastbound platform had some scratches on the surface , further investigation showed that the scratches were actually under the PPC finish , please see atatched photos
| 02SL - Stations (LUL) | Cxxx-NCR-001735 | NCR | MSH- Missing Reinforcment |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-04-30 | 2017-02-03 12:42 | -86 | 2016-11-10 16:39 | Civil - Civil Engineering General | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | There are approximately 38 B12 sheer links missing from Beam 5 in the 92 level slab.
| 02SL - Stations (LUL) | Cxxx-NCR-001736 | NCR | Water ingress to risers and stairwells |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-08-15 | 2017-08-14 12:35 | -1 | 2016-11-11 12:36 | Electrical - General | 5000 |  | Damaged | Rework | 3 (3-6k) | Complete | External Phenomenon - Other | Completed |  | On Monday night ( 07/11/2016) there was significant rain . It was noticed on Tuesday (08/11/2016) morning that All risers and stairwells had been significantly flooded from street level and down to Platform -1. All CMS was full of water and electrical equipment in these areas was affected.
| 02SL - Stations (LUL) | Cxxx-NCR-001737 | NCR | Potential water damage to Cxxx panels when i transport |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-12-09 | 2016-11-29 11:46 | -10 | 2016-11-11 14:42 | Communications and Control Systems - General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Whilst transporting Cxxx Comms panels from Van to __ , there was an unexpected down pour of rain. There was some rain that fell on the plastic wrapped panels..
| 02SL - Stations (LUL) | Cxxx-NCR-001738 | NCR | GFRC setting out drawings at a Preliminary (P02) status and not Issued for Construction (IFC). |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2017-02-28 | 2016-12-21 14:07 | -69 | 2016-11-15 11:22 | Architectural - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | A planned Crossrail surveillance was undertaken on 11th November 2016 to look at GFRC installation being installed by __. During the site visit, drawings being used on site to set out the steelwork (base plates, frames etc.) for Bays 31 (WB) and 99 (EB) were checked. On review it was identified that the setting out drawings (Cxxx-LAO-A-DWG-C101-50263 and Cxxx-LAO-A-DWG-C101-50278 respectively) were at a P02 status and not Issued for Construction (C0X). In addition, the setting out drawings had not been submitted on eB, with the eB reference numbers for revision C01 remaining ‘Draft’ with no drawing attached. Inspection and Test Plan, Cxxx-LAO-O4-ITP-C101-50145 inspection number 3.1 states the drawings will be Code 1 and ‘Approved C Status Design Drawings’ prior to starting installation. This is a Hold Point for __ and __.
| 02SL - Stations (LUL) | Cxxx-NCR-001739 | NCR | GFRC baseplate fixings installed with non compliant embedment depths and/or base plate protrusions |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2017-02-28 | 2016-12-19 13:36 | -71 | 2016-11-15 11:32 | Architectural - General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | A planned Crossrail surveillance was undertaken on 11th November 2016 to look at GFRC installation being installed by __. During the site visit, the base plate fixings were looked at, in particular embedment depths. During the review it was identified that a significant number of fixings had varying embedment depths based on the visible thread above the base plate. In some instances, the fixing thread visible above the platform slab was recorded as >110mm (see photo). Based on a fixing length of 215mm, the embedment depth achieved would be 115mm. Drawing Cxxx-LAO-A-DWG-C101-50013 (C01) requires an embedment depth of 130mm. In instances this has not been achieved. In addition, the detailing on the drawing refers to an anchor protrusion above the baseplate as being 30mm. In a number of instances this protrusion varied greater than the 30mm defined. Moreover, it was also highlighted that fixings had been embedded to deep; resulting in nuts once tightened showing no visible thread pitch above the nut (see photo). Industry standards state a minimum of two threads should be exposed above the nut to ensure the nut engages correctly. In order to close this NCR a review should be undertaken on all installed base plate fixings to ensure compliance with the design details and industry standards.
| 02SL - Stations (LUL) | Cxxx-NCR-001740 | NCR | TUN - BWK - Cxxx Resin damage to wall of OHLE room |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-12-14 | 2016-12-06 11:52 | -8 | 2016-11-16 16:59 | Architectural - Brickworks/Blockworks | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | The OHLE blockwork wall in Reception Chamber West in the tunnels has been damaged by resin injection works to the tunnel secondary lining. The resin injection was carried out by Cxxx and has resulted in significant staining to the blocks themselves and damage to the mastic joint where the blockwork ties into the SCL.
| 02SL - Stations (LUL) | Cxxx-NCR-001741 | NCR | TUN - BWK - Split lintol block above door frame in RCW |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-02-28 | 2017-01-05 10:56 | -54 | 2016-11-16 17:20 | Architectural - Brickworks/Blockworks | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | The central lintol block above one of the blockwork doorframes has split when __ Doors applied their fixings into the blockwork. The door is at the entrance to the OHLE room in Reception Chamber West in the tunnels.
| 02SL - Stations (LUL) | Cxxx-NCR-001742 | NCR | __X - BWK - Blockwork damaged on door opening E-02-237-D01 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2016-12-14 | 2016-12-09 16:28 | -5 | 2016-11-16 17:43 | Architectural - Brickworks/Blockworks | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Supervision - Other | Completed |  | The low level blockwork by door opening E-02-237-D01 has been damaged. Damage most likely caused by MEWP usage for MEP install. Door opening had been fully protected - damage only discovered when the protection was removed.
| 02SL - Stations (LUL) | Cxxx-NCR-001743 | NCR | __X - FFO - Superstructure BAL-208 Handrail Install |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-02-28 | 2017-06-07 10:25 | 99 | 2016-11-30 17:41 | Architectural - Handrail | 10000 |  | Workmanship | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Other | Completed |  | CRL/__ Site walk REF: CRL-OBS-12335 2. Generally the "super structure" BoH stair handrails and balustrades exhibit poor workmanship and do not conform to the design drawings and standards: a) Typical stanchion base connection to concrete base: The grout infill has overflowed and the grout has spread and adhered to the concrete stair surface as well as the stanchion itself (see Photo 2) b) Throughout, the installation position, alignment and fit are generally poor, generally not conforming to BS standards. Refer to photo 3: vertical elements are not plumb (or near plumb), corresponding top and mid rails are not the same length of alignment. c) Surface mounted baseplate connections for balustrade stanchions were not included as a general detail in PAD's drawings (there were some notable exceptions which were commented on). Throughout the current installation there are numerous examples of baseplates connection that deviate from the accepted "pocket" detail. There are numerous examples of the baseplates and associated bolts forming unacceptable trip hazards within the clear width of the staircase (see photos 4 & 5). d) The balustrade height at landings should be 1100mm to conform to BS standards. This has not been achieved: refer to Photo 6 e) To provide a smoother handrail for the user, the bolt connections on the handrails should consistently face inwards. The location of bolt connections along the installed works is inconsistent. f) A benchmark was required to be agreed upon with the Project Manager before full works were to proceed. No benchmark has been submitted or agreed to.
| 02SL - Stations (LUL) | Cxxx-NCR-001745 | NCR | Installation of serrated washers on tray joints |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-02-28 | 2018-05-18 11:29 | 444 | 2016-11-24 16:01 | Electrical - Cable Management | 25000 |  | Incorrect Installation | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | It has been noticed that the serrated washers used for fixing the cable tray joints are not in line with good engineering practice . The serrated washers are being pulled through the manufactured joining holes in the tray joints. These are not fit for purpose
| 02SL - Stations (LUL) | Cxxx-NCR-001746 | NCR | beding radius of cables too tight |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-03-28 | 2017-04-04 15:29 | 7 | 2016-11-24 16:26 | Electrical - General | 500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | It appears the bending radius of a cable is too tight and the insulation has crinkled.
| 02SL - Stations (LUL) | Cxxx-NCR-001747 | NCR | damaged 50mm x 50 mm trunking at low level in cross passage 09 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-02-28 | 2017-03-07 09:37 | 7 | 2016-11-24 16:31 | Electrical - Cable Management | 1000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | A trunking installed at low level in cross passage 09 has been stood on and damaged
| 02SL - Stations (LUL) | Cxxx-NCR-001748 | NCR | Incorrect dampers installed at Broadgate ticket hall |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-02-28 | 2017-02-21 14:31 | -7 | 2016-11-29 11:21 | Mechanical - Heating Ventilation & Air Conditioning | 1500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Insufficient work planning by the subcontractors | Completed |  | The incorrect room transfer dampers have been installed in Broadgate ticket hall basement, BSK6 dampers should have been installed but BSK4 is shown on the drawing.
| 02SL - Stations (LUL) | Cxxx-NCR-001749 | NCR | MSH - Missing chamfer around openings in 97 Level slab |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-06-30 | 2017-04-19 08:03 | -72 | 2016-11-30 08:58 | Civil - Civil Engineering General | 1000 |  | Material | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Chamfer missing around box outs in 97 level south slab. See drawings
| 02SL - Stations (LUL) | Cxxx-NCR-001750 | NCR | MSH - Incorrect position for starter bars |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-04-28 | 2017-01-07 14:13 | -111 | 2016-11-30 16:14 | Civil - Civil Engineering General | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Starter bars for insitu stairs from 91 level slab to 92 level slab GL B are cast into the slab out of position by 500mm
| 02SL - Stations (LUL) | Cxxx-NCR-001751 | NCR | MEP - Lack of approved ITP for offsite manufacture of DfMA Riser Modules for Moorgate Shaft |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-02-28 | 2017-02-26 22:12 | -2 | 2016-12-01 14:41 | Mechanical - Mechanical Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | BTH - No accepted ITP in place prior to the start of off-site fabrication of DfMA Riser Modules. Work has commenced at CHT Factory in Oldbury without an approved ITP in place. This was confirmed on the 25/11/2016 during a factory visit by __ Quality Inspectors - __ and __. The current ITP Cxxx-LAO-O4-ITP-C101-50171 Rev 1.0 was submitted to
| 02SL - Stations (LUL) | Cxxx-NCR-001752 | NCR | Inadequate installation of luminaire plug arrangement |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-02-28 | 2017-11-15 15:15 | 260 | 2016-12-02 15:57 | Electrical - Lighting | 9000 |  | Incorrect Installation | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Other | Completed |  | Following on from a random inspection of the Design Plan luminaire, where the plug and flexible conduit arrangement has been installed by the supplier. The attached photographs demonstrate incorrectly stripped cable ends. The inner sheath is still visible and therefore incorrectly connected within the plug arrangement.
| 02SL - Stations (LUL) | Cxxx-NCR-001753 | NCR | Works proceeded without an accepted ITP |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-02-28 | 2017-01-18 10:37 | -41 | 2016-12-06 10:22 | Mechanical - Piping | 500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Moorgate tickethall street level -1, mechanical pipework has been installed without an accepted Inspection Test Plan (ITP).
| 02SL - Stations (LUL) | Cxxx-NCR-001754 | NCR | Moorgate Tickethall CMS water damage |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-07-31 | 2017-07-28 15:13 | -3 | 2016-12-06 16:32 | Electrical - Electrical Engineering General | 2500 |  | Damaged | Reject | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | After a site inspection there was found to be water damage along the Grid line W CMS in Moorgate ticket hall.
| 02SL - Stations (LUL) | Cxxx-NCR-001755 | NCR | MSH - Incomplete concrete pour |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-03-31 | 2017-01-05 10:58 | -85 | 2016-12-07 09:01 | Civil - Civil Engineering General | 1000 |  | Incomplete Works | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | 97 Level North slab concrete pour was not completed in one pour as planned. See picture.
| 02SL - Stations (LUL) | Cxxx-NCR-001756 | NCR | earth gapping requirements |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-08-28 | 2017-07-28 13:27 | -31 | 2016-12-07 10:05 | Electrical - General | 8000 |  | Incorrect Installation | Rework | 2 (6-60k) | Complete | Design Problem - Other | Completed |  | The design and site installation of the earth gapping has not been implemented. Design specification attached
| 02SL - Stations (LUL) | Cxxx-NCR-001757 | NCR | Cabling commencing in staircase prior to ITP hold being signed for CMS |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-01-31 | 2016-12-16 08:55 | -46 | 2016-12-07 10:11 | Electrical - General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Wiring has commenced in staircases prior to Hold point being signed of on ITP for CMS
| 02SL - Stations (LUL) | Cxxx-NCR-001758 | NCR | __X wiring has commenced on street level -1 half landing prior to CMS being signed off |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-02-28 | 2016-12-16 08:57 | -74 | 2016-12-07 10:25 | Electrical - Cable Management | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Wiring has commenced in the __ street level -1 prior to the hold point being respected on the CMS ITP
| 02SL - Stations (LUL) | Cxxx-NCR-001759 | NCR | trunking in street level +4 for |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-02-28 | 2017-03-01 10:54 | 1 | 2016-12-07 11:27 | Electrical - Cable Management | 1000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Supervision - Other | Completed |  | A trunking has been fixed directly to the soffit without using brackets
| 02SL - Stations (LUL) | Cxxx-NCR-001760 | NCR | access to back of trays for cleating |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-02-28 | 2017-05-17 14:44 | 78 | 2016-12-07 11:55 | Electrical - Cable Management | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | There are areas where CMS tray has been installed on a 41 x 41 unistrut against slabs. This does not give enough access to cleat cables onto the trays
| 02SL - Stations (LUL) | Cxxx-NCR-001761 | NCR | cable tray installed which could be a potentail hazard |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-02-28 | 2017-03-27 08:53 | 27 | 2016-12-07 13:34 | Electrical - Cable Management | 2000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | There is containment installed on street level +4 which will create a hazard when entering the room
| 02SL - Stations (LUL) | Cxxx-NCR-001762 | NCR | ammount of trace heating boxes against original design |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-03-31 | 2017-03-28 16:41 | -3 | 2016-12-13 17:21 | Electrical - General | 0 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | Excel Portum have installed the trace heating boxes against the gated design. 5 additional trace heating boxes have been installed which in turn requires 5 x additional power supplies. This could also increase the requirements in DBs and reduce the 25% spare capacity. See RFI on asite RFI 003563 AND RFI 3449
| 02SL - Stations (LUL) | Cxxx-NCR-001763 | NCR | Chiller Attenuation/Ductwork Installation Issue |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-04-30 | 2017-04-13 05:34 | -17 | 2016-12-21 15:49 | Mechanical - Heating Ventilation & Air Conditioning | 5000 |  | Design | Repair | 3 (3-6k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | Chillers are installed on street level +3, the ductwork will not fit through the builderswork hole through the slab to exhaust on to street +4 louver panel.
| 02SL - Stations (LUL) | Cxxx-NCR-001764 | NCR | Wrong cladding panels installed on manafactured chillers |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-04-30 | 2017-04-10 11:20 | -20 | 2016-12-22 12:57 | Mechanical - Heating Ventilation & Air Conditioning | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | The Chillers which are installed on street +3 were supplied with non compliant insulation.
| 02SL - Stations (LUL) | Cxxx-NCR-001765 | NCR | MSH - AP6 - Radial Pour missing waterbar (left) |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-07-10 | 2017-02-13 14:33 | -147 | 2016-12-22 16:48 | Civil - Civil Engineering General | 2000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | AP6 - Due to the incomplete information received (Cxxx_PMI_01082) regarding the requirement for the water bar to be installed at every single horizontal construction joint, at second radial pour no waterbar was installed, please see attached photo.
| 02SL - Stations (LUL) | Cxxx-NCR-001766 | NCR | MSH - AP6 - Grout tubes in radial pour (left) |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-07-10 | 2017-02-13 14:36 | -147 | 2016-12-22 16:59 | Civil - Civil Engineering General | 2000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Cxxx Grout tubes have been part casted into the radial pour (left)
| 02SL - Stations (LUL) | Cxxx-NCR-001767 | NCR | MTH - Not following approved drawing for setting out of Granazzo Flooring |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-05-01 | 2017-02-22 11:44 | -68 | 2017-01-04 10:54 | Architectural - Flooring | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Information not detailed | Completed |  | __ have laid the floor tiling in Moorgate Ticket Hall area between gridlines 10 to 9 without following the setting out details on drawing Cxxx-LAO-A-DWG-C101_WS099-50356 where there should have been a cut tile adjacent to the darker strip that follows the beamlet on griddline 10
| 02SL - Stations (LUL) | Cxxx-NCR-001768 | NCR | MSH - Couplers cast incorrectly 105 stair landing |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-06-30 | 2017-06-28 09:50 | -2 | 2017-01-04 13:19 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | For the connection between the beams in the 105 landing and the 750 core wall. B25 couplers are cast into the 750 wall. In the south 750 core wall from level 102-107 the B25 couplers for the west landing beam have been cast into the wall in the wrong position and can not be used.
| 02SL - Stations (LUL) | Cxxx-NCR-001769 | NCR | MSH - Excessive honey combing |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-07-31 | 2017-04-19 08:04 | -103 | 2017-01-05 17:20 | Civil - Civil Engineering General | 800 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Inadequate/insufficient tooling. | Completed |  | On the South side of the south 750mm core wall from 92-97 level there is an area of concrete that has excessive (not acceptable for F2 finish) surface honey combing.
| 02SL - Stations (LUL) | Cxxx-NCR-001770 | NCR | MSH- Missing chamfer on soffit of 97 level beams |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-07-31 | 2017-06-28 09:58 | -33 | 2017-01-05 17:33 | Civil - Civil Engineering General | 500 |  | Material | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Insufficient quantity of material to do the job | Completed |  | There is no chamfer on the soffit of beams B4, B5 and B2 on the 97 level slab.
| 02SL - Stations (LUL) | Cxxx-NCR-001771 | NCR | Broadgate drainage drawing is incorrect and has been approved. |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-04-30 | 2017-04-13 10:49 | -17 | 2017-01-16 16:47 | Mechanical - Public Health Engineering | 1500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | Broadgate tickethall public health drawing has incorrect invert levels on gravity drainage pipework. The gravity drainage connection to the macerator is higher then the waste connection to a WC.
| 02SL - Stations (LUL) | Cxxx-NCR-001772 | NCR | __X - Street Level -1 Missing Structural Nib at Door Opening (GL A/3.5) |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-04-30 | 2017-02-24 16:37 | -65 | 2017-01-13 09:33 | Architectural - Doors | 3000 |  | Incomplete Works | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Along the lining wall located on Gridline A, between gridlines 3 and 4 a structural concrete nib is shown on the drawings. This nib is to form the southern side of the opening for the door frame for door E-02-631-D06. This nib has not been constructed and as such, the opening is too large for the door frame by approximately 150mm.
| 02SL - Stations (LUL) | Cxxx-NCR-001773 | NCR | Ductwork MFD's are not installed correctly. |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-06-30 | 2017-05-02 09:50 | -59 | 2017-01-16 17:07 | Mechanical - Heating Ventilation & Air Conditioning | 20000 |  | Workmanship | Rework | 2 (6-60k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | MFD's installed by __ have been installed incorrectly, they have been installed with less then the minimum space of 25mm all the way around the perimeter of the damper for firestopping.
| 02SL - Stations (LUL) | Cxxx-NCR-001774 | NCR | Air handling unit heater battery is installed before bag filter |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-07-31 | 2017-06-21 11:32 | -40 | 2017-01-16 15:40 | Mechanical - Heating Ventilation & Air Conditioning | 2000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Air handling units 251 & 252 have been manufactured with the bag filters installed in a position that the fresh air intake will pass through the heater before passing through the filters. This will mean any particles of dust will be heated meaning there is the possibility of smoke in the ventilation system.
| 02SL - Stations (LUL) | Cxxx-NCR-001775 | NCR | Insulation on Fire rated ductwork |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-10-04 | 2019-01-07 09:08 | 95 | 2017-07-11 11:07 | Mechanical - Heating Ventilation & Air Conditioning | 800000 |  | Incorrect Installation | Rework | 1 (>60k) | Complete | Design Problem - Other | Completed |  | The incorrect Insulation has been used on some fire rated ductwork sections, this may require a different insulation than what has been installed.
| 02SL - Stations (LUL) | Cxxx-NCR-001776 | NCR | installation of LV cabling on cable trays prior to ITP hold being released |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-05-31 | 2017-05-22 08:58 | -9 | 2017-03-14 07:54 | Electrical - General | 1000 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Cleating of cables
| 02SL - Stations (LUL) | Cxxx-NCR-001777 | NCR | installation of LV cabling prior to CMS ITP check sheet sign off |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-04-30 | 2017-02-21 09:00 | -68 | 2017-01-17 16:22 | Consents - General | 500 |  | Incomplete Works | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | LV cabling was installed on Cable trays up the B route in Superstructure prior to sign off from Client of CMS
| 02SL - Stations (LUL) | Cxxx-NCR-001778 | NCR | Damage to Grannazzo Floor tiling and bedding due to water ingress |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-08-31 | 2017-02-06 16:32 | -206 | 2017-01-20 11:22 | Architectural - Flooring | 18000 |  | Damaged | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Contamination | Completed |  | The flooring in Moorgate ticket hall and basement levels have been damaged due to water ingress from the __ demolition site next door
| 02SL - Stations (LUL) | Cxxx-NCR-001779 | NCR | TUN - Incomplete works at IRF inspection |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2017-04-30 | 2017-04-18 08:00 | -12 | 2017-01-20 14:54 | Electrical - Cable Management | 1000 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Supervision - Other | Completed |  | During the IRF inspection of 39no. CMS/Modules installed and offered as inspected and complete on the west bound platform, numerous snags were identified highlighting examples of unfinished/incomplete work. This included loose fixings, no fixings, swarf in drilled compartments and of insufficient quality to be offered as completed works.
| 02SL - Stations (LUL) | Cxxx-NCR-001780 | NCR | Blockwork at Moorgate tickethall basement accommodation not installed to drawing. |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-06-30 | 2017-06-28 10:41 | -2 | 2017-01-23 18:10 | Architectural - Brickworks/Blockworks | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Blockwork in rooms 2/318 SLR-F and 2/319 SLR-M are not built to the live BIM model, this has caused the ductwork dampers MFD-1259 and 1262 to not be located in correct position. This has also caused both rooms to be smaller then shown on MEP drawing.
| 02SL - Stations (LUL) | Cxxx-NCR-001781 | NCR | SCL saw cut joints not made good/sealed |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-07-31 | 2017-07-27 13:07 | -4 | 2017-01-24 17:21 | Civil - Structural Engineering | 3000 |  | Incomplete Works | Repair | 4 (0.5-3k) | Complete | Previous Construction - Interfacing issues | Completed |  | The air/pressure test carried out by __ to the PES smoke extract plenum on the western half of platform tunnel east has failed. Subsequent smoke/vapour tests to investigate the cause indicated leakage via the saw cut joints in the SCL which have not been made good/sealed. We await Crossrail’s response with regards to the course of action
| 02SL - Stations (LUL) | Cxxx-NCR-001782 | NCR | POM's Non-structural reinforced wall starter bars missing |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-09-30 | 2017-07-12 10:14 | -80 | 2017-01-25 17:24 | Civil - Civil Engineering General | 1500 |  | Planning | Repair | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | Missing starter bars for the non-structural Lift 1 Extension (POM's) walls, As horizontal starter bars indicated on Cxxx-LAO-C-DDD-C101_Z-11182 are not installed during the construction of lift walls.
| 02SL - Stations (LUL) | Cxxx-NCR-001783 | NCR | Non Conforming Basket Tray |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2017-05-31 | 2017-04-12 15:53 | -49 | 2017-01-26 15:07 | Electrical - Cable Management | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | During a quality surveillance at Cxxx Liverpool Street Station a number of issues were found regarding the basket tray that had been installed in CER 1 on street level -1 of Blomfield box. 1) Post Surveillance it was discovered that the MCR for the __ Basket Tray had not been approved by CEG. CRL-MCR-003675 is currently in the initiate stage on eB and still awaiting submission by __. The M&W Spec JY63, MEP Support Components, states under section 1401 part a; “Materials shall have been found acceptable by the materials compliance process and included in the materials compliance record.” 2) The installation of the basket tray does not form part of the Inspection and Test Plan for Blomfield Box – Installation of CMS - Cxxx-LAO-O4-ITP-C101¬_WS103-50037 REV 5 or the Method Statement Cxxx-LAO-O1-GMA-C101_WS103-50105.
| 02SL - Stations (LUL) | Cxxx-NCR-001784 | NCR | Conduit box installed incorrectly |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2017-05-31 | 2017-03-27 12:48 | -65 | 2017-01-26 15:00 | Electrical - Cable Management | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | During a quality surveillance at Cxxx Liverpool Street Station it was noted that circular conduit boxes had been installed with one central fixing throughout Blomfield box. See attached photos However M&W Spec JY60, Conduit and Cable trunking, states under point 3211 part c; “Use a minimum of two screw fixings for standard circular conduit boxes and four screws for large conduit boxes and adaptable boxes up to 150mm x 100mm.”
| 02SL - Stations (LUL) | Cxxx-NCR-001785 | NCR | Flat washers not installed to compartment trunking |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2017-05-31 | 2017-04-05 14:30 | -56 | 2017-01-26 15:06 | Electrical - Cable Management | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During a quality surveillance at Cxxx Liverpool Street Station it was noted that compartment trunking had been installed on the maintenance staircase between Street Level -1 and Platform Level 0 without flat washers. This is the only area of the station where flat washers have not been installed. See photos attached. M&W Spec JY90, Fixing to Building Fabric, states under point 3210; “Fix equipment, brackets and supports by drilling holes and fixing using set screws or bolts complete with washers, shake proof washers and loose nuts.”
| 02SL - Stations (LUL) | Cxxx-NCR-001786 | NCR | Clearance between CMS and Comms Cabinet |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2017-05-31 | 2017-04-24 09:54 | -37 | 2017-01-26 15:13 | Electrical - Cable Management | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Supervision - Other | Completed |  | During a Crossrail quality surveillance it was recorded that the gap between the bottom of high level multi-compartment trunking and the top of the communications cabinets within CER 1 Street Level -1 is less than 300mm. Two measurements were taken and the gap ranged from 165mm to 170mm. See photo attached. M&W Spec JY60, Conduit and Cable Trunking, states under point 3203 part b); “Minimum general spacing’s between conduits, trunking, and: i) Equipment - 300 mm.” The installation has not met this requirement.
| 02SL - Stations (LUL) | Cxxx-NCR-001787 | NCR | North Core Wall 97.040m Localised Cover to Reinforcement |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-11-06 | 2017-09-20 09:49 | -47 | 2017-01-30 11:34 | Structural Engineering - Reinforcement | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | There is a section of reinforced concrete wall where the reinforcement is suspected to not meet the specifications. The wall in question is the North Core Wall (97.040m to 102.395m). The area in question is the south face of the core wall is 4900mm West of GL D. The level of the area in question is approximately 97.300m.
| 02SL - Stations (LUL) | Cxxx-NCR-001789 | NCR | MSH Beam B15 (-11162) Height on the 103m level. |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-08-27 | 2017-02-22 14:43 | -186 | 2017-02-08 16:23 | Structural Engineering - Concrete Member | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | Referring to Cxxx-MMD-C-DDL-C101_3-11162, beam B15 has been cast with a top of concrete level 103.060m. This is 40mm lower than the design 103.100m. The beam is cast to the required 1455mm depth.
| 02SL - Stations (LUL) | Cxxx-NCR-001790 | NCR | Commencement of wiring prior to CMS inspection/sign off |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2017-04-30 | 2017-03-08 11:01 | -53 | 2017-02-09 09:58 | Electrical - Cable Management | 1000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | Lighting and small power wiring has commenced in __ superstructure and also Platforms and tunnel B.O.H east bound/east end prior to the installed CMS being inspected and signed off in line with ITP.
| 02SL - Stations (LUL) | Cxxx-NCR-001791 | NCR | MSH - 107-113 South Lift shaft concrete. |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-08-31 | 2017-03-27 12:42 | -157 | 2017-02-09 12:53 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The concrete placed in the lift shaft walls from the 107.550m level to the underside of the Street level slab (PPIR, Pour history sheet and concrete ticket attached) was placed outside the 2 hour window as stated in specification KF10 – Insitu Concrete (KF10.3202). Each concrete wagon (Ticket no 21300522 and 21300528) was flow tested at the time of dispatch and was found to be within the specified tolerances stated in BS8500 part 1.
| 02SL - Stations (LUL) | Cxxx-NCR-001792 | NCR | MSH - Missing wall starter bars on level 113 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-08-31 | 2017-03-02 12:24 | -182 | 2017-02-14 10:02 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | 113 level slab was poured without starter bars for wall 12.
| 02SL - Stations (LUL) | Cxxx-NCR-001793 | NCR | BTH - Reduced cover on __ upstand wall 21 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-06-30 | 2017-04-12 13:01 | -79 | 2017-02-17 13:30 | Structural Engineering - Concrete Member | 3000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Due to detailing of shear links in the north canopy wall and installation of the vertical bars in previous pour, the required cover of 45mm was not achieved. See attached pictures.
| 02SL - Stations (LUL) | Cxxx-NCR-001794 | NCR | MOORHOUSE - Incorrect position for 2no gullys at basement level |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-10-31 | 2017-04-20 15:39 | -194 | 2017-02-16 15:03 | Civil - Civil Engineering General | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | As shown in attached sketches 1no. gully in room 2/417 and 1no. gully in room 2/416 in Moorhouse has been cast into the basement slab at incorrect positions.
| 02SL - Stations (LUL) | Cxxx-NCR-001795 | NCR | Damage to completed insulation |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-05-31 | 2017-05-02 09:58 | -29 | 2017-02-23 11:32 | Mechanical - Heating Ventilation & Air Conditioning | 15000 |  | Damaged | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Other | Completed |  | It has been noted that during site walks/inspections with __ that ductwork and pipework insulation has been subject to damage by other trades. These works have already been inspected and signed off by CRL they have been damaged prior the these inspections.
| 02SL - Stations (LUL) | Cxxx-NCR-001796 | NCR | MSH Missing steel detail 113 level slab |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-10-31 | 2017-03-10 09:55 | -235 | 2017-02-20 13:44 | Civil - Civil Engineering General | 700 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | There are a number of starter bars missing in beam 7 (Cxxx-LAO-C-DWG-C101_WS099-50032) on the 113 level slab as shown in attached picture.
| 02SL - Stations (LUL) | Cxxx-NCR-001797 | NCR | GFRC Stainless Steel Support Frame Onsite Remedials |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-05-31 | 2017-03-21 08:55 | -71 | 2017-02-21 09:39 | Architectural - General | 5000 |  | Manufacturing Defect | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The GFRC stainless steel support frames installed in PTW and PTE have a number of different issues that need rectifying before the panels are installed. Refer to the attached for details.
| 02SL - Stations (LUL) | Cxxx-NCR-001798 | NCR | BTH - Positional tolerance of PCC roof |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-04-22 | 2017-04-18 16:15 | -4 | 2017-02-21 11:58 | Architectural - Ceilings & Soffits | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | PCC casting tolerance, plus in-situ tolerance for the walls/columns and installation tolerance of the PCC planks combined to make adherence to 3mm unachievable on site.
| 02SL - Stations (LUL) | Cxxx-NCR-001799 | NCR | MSH - AP6 Wraparound - Wall Pour Right - Honeycombing |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-03-21 | 2017-03-17 08:56 | -4 | 2017-02-21 18:47 | Civil - Civil Engineering General | 700 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | There is honeycombing on AP6 Wraparound right hand side wall pour.
| 02SL - Stations (LUL) | Cxxx-NCR-001800 | NCR | TUN - Commencement of wiring prior to CMS inspection/sign off |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2017-06-30 | 2017-06-14 14:35 | -16 | 2017-02-22 09:33 | Electrical - Cable Management | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Lighting and small power wiring has commenced in Platforms and tunnel B.O.H east bound/west end prior to the installed CMS being inspected and signed off in line with ITP.
| 02SL - Stations (LUL) | Cxxx-NCR-001801 | NCR | Uneven firestopping around dampers |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-10-01 | 2018-09-20 09:40 | -11 | 2017-02-28 10:23 | Fire - Compartmentation | 5000 |  | Workmanship | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Insufficient information made available to the worker. | Completed |  | The issue has been raised by __ following their attempts to install back plates around installed dampers after completion of fire stopping materials. In most cases it was found that due to the uneven nature of the fire stopping around the damper it was impossible to fit the back plates evenly and correctly, therefore the material will need to be removed and redone ensuring that the finish is even and flush to the blockwork.
| 02SL - Stations (LUL) | Cxxx-NCR-001802 | NCR | MSH. Missing void in the MSH lift / riser wall between GL C to D, GL 5 to 4 at approx 90.400m |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-06-30 | 2017-04-12 14:52 | -79 | 2017-03-06 11:17 | Civil - Civil Engineering General | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The box out within the West wall of the MSH lift shaft /riser at 90.400m shown on drawing Cxxx-MMD-C-DDB-C101_Z-11062 has been missed.
| 02SL - Stations (LUL) | Cxxx-NCR-001803 | NCR | MSH. Relocation of __ ducting within the street level slab over the ES5 decline precast |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-12-31 | 2017-06-29 08:37 | -185 | 2017-03-06 13:56 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | A bank of 3no cast in Ductile Iron sleeves for the __ M&E shown on drawing Cxxx-LAO-E-DDH-C101_2-00001 and on the attached site sketch where missed when concreting the adjacent street level slab.
| 02SL - Stations (LUL) | Cxxx-NCR-001804 | NCR | MSH. Floating Hydrophilic strip around __ service trench at Street Level |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-12-31 | 2017-03-16 15:32 | -290 | 2017-03-06 16:07 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Insufficient information made available to the worker. | Completed |  | A section of hydrophilic strip on the Street Level around the __ service trench came loose when concreting the kicker. Please refer to the attached site sketches and photos for location and details.
| 02SL - Stations (LUL) | Cxxx-NCR-001805 | NCR | Broadgate Ticket Hall Dampers |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-07-05 | 2017-06-28 11:47 | -7 | 2017-03-07 08:54 | Mechanical - Heating Ventilation & Air Conditioning | 15000 |  | Design | Rework | 2 (6-60k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | The Broadgate Ticket Hall motorised fire dampers (BSK 4 series) have __ plates that do not fit within the wall opening without clashing with other services and or structure. As the manufacturer has confirmed we have to install these __ plates for the BSK 4 dampers, we are proposing to remove the current BSK 4 dampers that are causing the issue and replace them with the BSK C6 series which will fit and therefore rectify the current issue. All drawings and details of both dampers are attached for information
| 02SL - Stations (LUL) | Cxxx-NCR-001808 | NCR | MSH VD5 tunnel wrap around lack of cover to North Face |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-12-31 | 2017-05-08 13:37 | -237 | 2017-03-09 18:14 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Please refer to the attached site sketch and photos. The north section of the VD5 tunnel wrap around has been cast and it is apparent that the reinforcement cover (on the internal face) is less than the 70mm specified on rebar drawing Cxxx-MMD-C4-DDD-101_Z-00637.
| 02SL - Stations (LUL) | Cxxx-NCR-001809 | NCR | MSH - Acoustic Lining LIN-803 - Non MCRed Fixings Installed |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-12-31 | 2017-04-21 13:27 | -254 | 2017-03-10 18:50 | Architectural - Finishes | 4000 |  | Material | Repair | 3 (3-6k) | Complete | Management Problem - Inadequate administrative control | Completed |  | __ Acoustic Linings installed in Moorgate Shaft Level 88.305 and 83.655 with non-MCRed fixings. Fixings F1 and F3 discovered to be not the correct brand as per MCR Cxxx-LAO-O4-XDS-C101-50345 - Material Compliance Record for JK13.1205 LIN-803 and JK13.1206 LIN-804 System fixings & Accessories (4250)
| 02SL - Stations (LUL) | Cxxx-NCR-001810 | NCR | MSH - FFO - Acoustic Linings LIN-803 Panels - Water Ingress |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-12-31 | 2017-07-28 14:29 | -156 | 2017-03-10 19:03 | Architectural - Finishes | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | LIN-803 Acoustic Panels installed in Moorgate Shaft Level 88.305 subject to 10/20mm of water on slab.
| 02SL - Stations (LUL) | Cxxx-NCR-001811 | NCR | MSH. Missing 20mm gap at top of the MSH lift wall (below the Street Level slab) |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-12-31 | 2017-05-08 12:32 | -237 | 2017-03-13 17:24 | Civil - Civil Engineering General | 2500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Please refer to the attached site sketch for clarity. The soft joint on the top of the lift wall / underside of Street Level slab as detailed on drawing Cxxx-LAO-C-DWG-C101_WS099-50138 has been missed.
| 02SL - Stations (LUL) | Cxxx-NCR-001812 | NCR | Pull testing not carried out for Ductwork Installation |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2017-06-30 | 2017-05-02 09:37 | -59 | 2017-03-14 09:08 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | A planned Crossrail surveillance of the Ductwork Installation was undertaken at Liverpool Street Station on the 07.03.17. As part of the surveillance Moorgate Shaft ITP document number Cxxx-LAO-O4-ITP-C101-50070 was viewed after the site visit raised the issue of Ductwork being installed before the support brackets had been pull tested. This was confirmed by a site operative on site. Moorgate Shaft ITP document number Cxxx-LAO-O4-ITP-C101-50070 - Section 3.5 States: “Set out & install fixings. Conduct random pull out testing on installed fixings”. This is a hold point and no installation of Ductwork should have been installed before pull tests had taken place. Works Information Volume 2B - Part 13 – Assurance, Records and Certification - 13.2 Assurance states: “The Contractor shall provide progressive assurance that the Contractor’s design (where appropriate) and the constructed works comply with the requirements set out in the contract. The Contractor’s progressive assurance will also be used by the Project Manager and Employer to demonstrate that the legal comm__ents and obligations placed on the contract by the Crossrail Act 2008 have been discharged. __ assurance means that there will be continual confirmation of compliance by the generation of contemporaneous records.” Works Information Volume 2B - Part 20 – Quality Management - Part 20.8 Inspection and Testing States: “The Contractor and his subcontractors and suppliers of any tier engaged in supplying, manufacturing, construction, installation, commissioning and testing or any other service connected with the works, shall maintain ITPs appropriate for the services they provide that are accepted by the Supervisor. These accepted ITPs shall stipulate the necessary level and frequency of tests and inspections for each aspect of the works.”
| 02SL - Stations (LUL) | Cxxx-NCR-001813 | NCR | BTH - South decline - Central __ wall section cast up to 100mm high |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-07-27 | 2017-07-24 08:35 | -3 | 2017-05-30 16:32 | Structural Engineering - Concrete Member | 7000 |  | Workmanship | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Other | Completed |  | A setting out error has resulted in the central wall being cast with the top of the wall steeper than design. Three pours had taken place before the error was spotted. The attached sketch shows the (Central wall remidials.pdf) shows the proposed remediation of the wall. Solution has been put to __, and accepted, see __-__-RFI-00815
| 02SL - Stations (LUL) | Cxxx-NCR-001814 | NCR | MSH. Leaks on Moorgate Escalator decline |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-08-31 | 2017-07-11 08:47 | -51 | 2017-03-22 13:26 | Civil - Civil Engineering General | 2500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | External Phenomenon - Not Defined | Completed |  | Please refer to attached site sketch for clarity and location of leaks. Further to CCN-02262 "MSH Waterproofing around the ES5 turrets @102.395m AOD level" it is apparent that the ground water is still leaking around the turret and escalator slab on the North face after the RC works is completed.
| 02SL - Stations (LUL) | Cxxx-NCR-001815 | NCR | TUN - Commencement of wiring prior to CMS inspection/sign off |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2017-06-30 | 2017-04-18 08:04 | -73 | 2017-03-22 12:56 | Electrical - Cable Management | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Supervision - Other | Completed |  | Lighting and small power wiring has commenced in Platforms and tunnel B.O.H West bound/west end prior to the installed CMS being inspected and signed off in line with ITP.
| 02SL - Stations (LUL) | Cxxx-NCR-001819 | NCR | MSH-118 Slab West face |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-09-29 | 2017-04-19 12:12 | -163 | 2017-03-28 12:56 | Civil - Civil Engineering General | 850 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the concrete pour of the 118 level slab the shutter on the west face moved 30mm west. This has caused the slab to be poured 30mm bigger then as per design. the Reinforcement did not move there is just currently excess cover.
| 02SL - Stations (LUL) | Cxxx-NCR-001821 | NCR | MSH - Cast in sockets for Cxxx - 2nos M20 sockets were not cast into the wall |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-12-06 | 2017-10-03 12:46 | -64 | 2017-03-31 13:36 | Civil - Civil Engineering General | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | The two lower of the C1 position M20 sockets shown on the drawing KC-13001-D-01 Rev.A were not cast into the wall. Cxxx is instructed to install these sockets under the Cxxx-PMI-01284.
| 02SL - Stations (LUL) | Cxxx-NCR-001822 | NCR | __X - PL + 4 Riser Doors installed in incorrect opening |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-06-30 | 2017-05-08 09:47 | -53 | 2017-03-31 12:51 | Civil - Civil Engineering General | 3000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Doors E03-784-D01 & E03-785-D01 have been installed in each others opening.
| 02SL - Stations (LUL) | Cxxx-NCR-001823 | NCR | The wall adjacent to 8-87 Moorfields is built 100mm too far east |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-12-09 | 2017-06-14 08:28 | -178 | 2017-04-03 11:29 | Civil - Civil Engineering General | 3000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The wall adjacent to 8-87 Moorfields (Wall-F on drawing Cxxx-LAO-C-DWG-Cxxx-50193) is built 100mm too far east from level +122.510 up to +126.300.
| 02SL - Stations (LUL) | Cxxx-NCR-001824 | NCR | MSH. Missing void in wall between GL B to C, GL 1 to 2 at +91.670m level |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-05-31 | 2017-05-09 08:21 | -22 | 2017-04-05 07:50 | Civil - Civil Engineering General | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The box out in the wall shown in section C of the drawing Cxxx-MMD-C-DDA-C101_6-11040 Rev.C05 has been missed. The box out was introduced at the request Cxxx-FCD-1562.
| 02SL - Stations (LUL) | Cxxx-NCR-001825 | NCR | __X - VD2 - Blocked Reinjectable Hoses |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-07-31 | 2017-08-14 12:01 | 14 | 2017-04-10 14:20 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Following injection and flushing of VD2 reinjectable hoses it has been noted that there are some hoses which are blocked. See attached Schematics for reference. (Cxxx-NCR-001825 Sketch 1 (REV AB).pdf)
| 02SL - Stations (LUL) | Cxxx-NCR-001826 | NCR | __X - VD1 - Blocked Reinjectable Hoses |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-07-31 | 2017-08-14 11:52 | 14 | 2017-04-10 14:20 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Following flushing of VD1 reinjectable hoses it has been noted that there are some hoses which are blocked. See attached Schematics for reference. (Cxxx-NCR-001826 - Sketch 1 (REV AB2).pdf)
| 02SL - Stations (LUL) | Cxxx-NCR-001827 | NCR | __X - AP1 - Blocked Reinjectable Hoses |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-09-30 | 2017-09-29 16:29 | -1 | 2017-04-10 14:21 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Following flushing of AP1 reinjectable hoses it has been noted that there are some hoses which are blocked. See attached Schematics for reference. Cxxx-NCR-001827 Sketch 1 (Rev AB1).pdf - Overview Cxxx-NCR-001827 Sketch 2 (Rev AB1).pdf - Invert Cxxx-NCR-001827 Sketch 3 (Rev AB1).pdf - Sides Cxxx-NCR-001827 Sketch 4 (Rev AB1).pdf - Crown
| 02SL - Stations (LUL) | Cxxx-NCR-001828 | NCR | TUN - CH5 - Blockwork wall built in incorrect location |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-07-31 | 2017-07-18 08:17 | -13 | 2017-04-12 10:35 | Architectural - Brickworks/Blockworks | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | 12/4/17 - update: Uploaded marked up drawings - Blockwork key plan and blockwork setting out (Wi and __). The blockwork of Second Lift of North side in CH5 has been built when it is not required.
| 02SL - Stations (LUL) | Cxxx-NCR-001829 | NCR | E and S fabrication drawings are not being uploaded to Eb. |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-09-29 | 2017-10-03 09:11 | 4 | 2017-04-13 10:08 | Mechanical - Heating Ventilation & Air Conditioning | 20000 |  | Documentation and Records | Use As-Is | 2 (6-60k) | Complete | Design Problem - Other | Completed |  | After numerous requests E and S are still failing to upload C01 drawings onto Asite which consequently results in the drawings being unable to be uploaded to Eb. This in turn means the installation on site of ductwork is not installed to the approved gated design due to E and S changed to the drawings. An example of this is in VD7 where the ductwork installed is different to the approved drawing on Eb.
| 02SL - Stations (LUL) | Cxxx-NCR-001830 | NCR | MEP services have obscured access to Cxxx grout boxes in CP9 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-07-31 | 2017-10-03 09:21 | 64 | 2017-04-13 13:08 | Mechanical - Public Health Engineering | 3000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | We have been notified by Cxxx that there are a number of grout boxes in CP9 that are obscured by Cxxx services. On a site visit with Luke Mason, CRL FE, 12/04/2017, it was established that a number of grout boxes will be able to be accessed. Grout boxes that will require the removal of some services to allow the grout boxes to be relocated immediately adjacent to the original location.
| 02SL - Stations (LUL) | Cxxx-NCR-001831 | NCR | MTH. Incorrect collar for soffit precast panels |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-05-17 | 2017-05-08 13:12 | -9 | 2017-04-19 14:54 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Please refer to explore drawing Cxxx-LA0-A-DWG-C101_WS099-50517 and attached photos and sketches for clarity. The collars for the MTH precast soffit panels type 005, 006, 009, 010, 015, 016 (to fit around the precast columns) have been cast with a fa__ed collar not a smooth elliptical collar 20mm larger than the precast column neck. __ have checked the dimensions of the fa__ed collar and can confirm that the dimension from the face of the precast column neck to the face of fa__ed collar is a maximum of 20mm and a minimum of 14mm. The joint will be hidden in the permanent position behind a stainless steel trim (30mm off the column face) ref to drawing Cxxx-LAO-A-DDD-C101_1-22613
| 02SL - Stations (LUL) | Cxxx-NCR-001832 | NCR | MTH drainage and gullies |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-11-30 | 2017-10-11 15:08 | -50 | 2017-04-19 16:10 | Civil - Civil Engineering General | 1500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | A number of toilet outlets and floor gullies in Moorgate Ticket Hall were full of debris (some even being filled with solid concrete). Some examples of this can be seen in rooms 2/417 and 2/421. Please see attached photos showing examples.
| 02SL - Stations (LUL) | Cxxx-NCR-001833 | NCR | MSH - Recess line for OSD plate G on North 750mm wall, built 75mm too far west |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-08-31 | 2017-08-21 09:32 | -10 | 2017-04-20 16:36 | Civil - Civil Engineering General | 5000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | MSH - The Eastside recess line for OSD plate G on North 750mm wall, built 75mm too far west from level+ 117.100 until level +117.780. The wall is currently built up to level +117.780 on this area and from GLE up to Easting:4020.180. OSD plate G is not installed yet (box out was provided during pouring of the wall) and it will be installed in the correct position as per Dwg: Cxxx-MMD-C-DDA-C101_Z-11601.
| 02SL - Stations (LUL) | Cxxx-NCR-001834 | NCR | Fire Stopping |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-06-30 | 2018-11-28 10:05 | 151 | 2017-04-20 16:58 | Fire - Compartmentation | 500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Management Problem - Other management problem | Completed |  | __ Compound ITP; • Works not being progressively signed off on checksheet (__/__/CRL) • ITP to be updated to include reference all __ Standard Dwgs, • include details of reinforcement __ __ ITP-50098; • Update ITP to include compound __ works as per MCR-50523 __ Compound Dwg-50537 not on eB
| 02SL - Stations (LUL) | Cxxx-NCR-001835 | NCR | MSH - 122 OSD Steel plates out of position |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-05-19 | 2017-05-12 11:12 | -7 | 2017-04-21 10:25 | Structural Engineering - Steel Member | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | As discussed with A. Douglas on 21/04. Centre of steel plates A1, A2 and A3 on Cxxx-MMD-C-DDA-C101_Z-11601 are detailed as being 2.450m from GL1. Drawing number Cxxx-MMD-C-DDA-C101_B-11031 details centre of plinths at GL1 + 2175mm+ 650mm/2 = 2500mm. Plates have been set to GL1 + 2500mm (ie +50mm).
| 02SL - Stations (LUL) | Cxxx-NCR-001836 | NCR | BTH - Basement floor screed cracks |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-08-28 | 2017-08-25 12:01 | -3 | 2017-05-30 17:03 | Architectural - Flooring | 1000 |  | Material | Repair | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | Cracks have developed in the screed, predominantly in the corridors within BTH.
| 02SL - Stations (LUL) | Cxxx-NCR-001837 | NCR | Insufficient training provided by __ for installing HUS fixings |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-01-25 | 2018-12-18 10:41 | -38 | 2018-12-06 09:50 | Mechanical - Heating Ventilation & Air Conditioning | 1000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | This NCR is to cover the lack of training for the use of the __ pull tester / fixings by the __ operatives during the first few months of installation. They have since then all been trained by the hiliti representative and provided with certificates. We have conducted random pull out tests with CRL in attendance on the fixings that were installed prior to the training. All pull out tests have passed.
| 02SL - Stations (LUL) | Cxxx-NCR-001838 | NCR | MSH - Lining wall D2 leaks |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-07-31 | 2017-07-11 08:23 | -20 | 2017-04-24 16:55 | Civil - Civil Engineering General | 3000 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | We (__) had constructed Lining wall D2 in August 2016 and it has started to leak in April 2017.
| 02SL - Stations (LUL) | Cxxx-NCR-001839 | NCR | MSH - 8 Moorfields Mass fill |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-08-31 | 2017-08-29 10:54 | -2 | 2017-04-26 10:33 | Civil - Fill | 2500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Section of mass fill at 8 Moorfields from 113.700 to 117.200 (approx 3.5m) has encroached onto the 8 Moorfields site.
| 02SL - Stations (LUL) | Cxxx-NCR-001840 | NCR | __X - BWK - Mastic debonding on level 112 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-09-30 | 2017-07-19 16:33 | -73 | 2017-04-26 17:15 | Architectural - Brickworks/Blockworks | 3000 |  | Material | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In some areas where the blockwork has been constructed on street level (112) debonding of the mastic has occurred. Debonding has taken place from different substrates including blockwork and concrete. The gaps in the mastic left due to the mastic debonding tend to be 0-3mm wide and 25-150mm in length. Review and closure of this level will form the prototype for resolving this issue site wide.
| 02SL - Stations (LUL) | Cxxx-NCR-001842 | NCR | MTH. Incorrect brackets for the Moorgate Ticket Hall precast soffit panels |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-06-30 | 2017-06-27 10:35 | -3 | 2017-05-03 16:54 | Civil - Civil Engineering General | 5000 |  | Planning | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Electrical or instrument noise | Completed |  | Please refer to the site sketches for clarity. 1. An surveying error was taken and recorded on the as-built of the existing Moorgate Ticket Hall soffit which has meant that 10no of the S/S brackets detailed on drawing Cxxx-LAO-A-DWG-C101_WS099-50517 and document Cxxx-LAO-A-XCL-C101_WS099-50011 have been designed and manufactured between 75mm and 100mm too long and cannot be used. 2. The position of one bracket on unit no 10 clashes with the existing beam on GL8 and cannot be used as currently designed.
| 02SL - Stations (LUL) | Cxxx-NCR-001843 | NCR | Damage to Kerb Fixing Angle on AP6 Base Brackets |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-08-31 | 2017-08-31 13:49 | 0 | 2017-05-04 08:39 | Architectural - General | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | The kerb fixing angle on the AP6 base brackets in some instances has been damaged during transit to site and/or during movement on site from the bottom of Finsbury Shaft upto AP6, refer to the attached photos indicating typical damage.
| 02SL - Stations (LUL) | Cxxx-NCR-001844 | NCR | Broadgate Ticket Hall |  | Crossrail | PDP | LIS - Liverpool Street Station (Central) |  | 2017-08-31 | 2017-09-02 11:12 | 2 | 2017-05-04 08:10 | Mechanical - Heating Ventilation & Air Conditioning | 5000 |  | Planning | Rework | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The main extract fan located in the plant room street -1 has been installed with the access hatch for maintenance on the top with no provision for access due to the distance between the top of the fan and the soffitt, also the side access doors have been installed facing the east wall, also leaving no room for access. We cannot accept dropping the fan down as an access and maintenance plan for this particular fan.
| 02SL - Stations (LUL) | Cxxx-NCR-001845 | NCR | Map Damper Installation Main Ticket Hall level-BTH |  | Crossrail | PDP | LIS - Liverpool Street Station (Central) |  | 2017-08-31 | 2017-08-02 11:10 | -29 | 2017-05-04 08:37 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | HVAC ductwork has been installed through BTH rooms 2/411-2/406-2/331-2/663 & 2/401 it has been noted the the MAP dampers have not been installed as per the __ gated drawing ( Cxxx-LAO-H-DDA-C101_2-41341 ) and therefore making future maintenance difficult.
| 02SL - Stations (LUL) | Cxxx-NCR-001846 | NCR | MTH Main AHU 201 -BW Holes |  | Crossrail | PDP | LIS - Liverpool Street Station (Central) |  | 2017-08-31 | 2017-06-21 11:47 | -71 | 2017-05-04 09:02 | Mechanical - Heating Ventilation & Air Conditioning | 5000 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | CRL have noted that the newly erected main AHU 201 located on street -1 level has 2 connections on the east side of the unit, the connections do not line up with the large BW holes that have been preformed as part of the civils construction. This will result in either moving the AHU or making ductwork sections to allow a connection between the AHU and the BW holes.
| 02SL - Stations (LUL) | Cxxx-NCR-001847 | NCR | __X CER |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2017-08-31 | 2017-08-09 12:22 | -22 | 2017-05-04 11:24 | Mechanical - Heating Ventilation & Air Conditioning | 20000 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Design Problem - Other | Completed |  | Mechanical smoke dampers, extract grilles and cleaning doors all requiring maintenance access installed above electrical CMS & equipment such that no access is available contrary to CDM 2015 reg. 9
| 02SL - Stations (LUL) | Cxxx-NCR-001848 | NCR | Smoke Damper Installation SOR area MTH |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2018-12-24 | 2019-10-07 06:59 | 287 | 2017-05-04 11:51 | Mechanical - Heating Ventilation & Air Conditioning | 5999 |  | Incorrect Installation | Use As-Is | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | MAP smoke dampers requiring routine maintenance are installed at high level approx. 1.5m above ceilings within the SOR and adjacent areas, contrary to Cxxx A&M document s. 11.8 which considers all ductwork will be installed within 500mm of ceiling face such dampers, cleaning doors etc will be accessible. Safe maintenance access does not appear to be provided which will be exacerbated should electrical CMS be installed in accord with the current drawings.
| 02SL - Stations (LUL) | Cxxx-NCR-001849 | NCR | 3400 GFRC Cladding - BigHead GFRC Pull-out failure |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-07-31 | 2017-07-27 14:10 | -4 | 2017-05-05 12:05 | Architectural - General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the installation of the GFRC cladding at Tottenham Court Road w/c 30th January 2017 the Contractor and his installer __ Ltd became aware of an issue with some of the BigHead sockets cast into the GFRC panel and the supporting GFRC ‘tusk’. Whilst the issue has not been experienced here at Liverpool Street Station this NCR has been raised because __ are manufacturing and supplying the GFRC cladding here. The BigHead sockets are cast into the GFRC to form connection points to attach stainless steel rails and brackets etc. It was observed that the GFRC material appeared to fail as a result of the BigHead socket being pulled out.
| 02SL - Stations (LUL) | Cxxx-NCR-001850 | NCR | __X - Fire Systems ITP not followed by A__ |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-07-31 | 2017-07-21 14:39 | -10 | 2017-05-12 14:06 | Fire - Detection | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Installation of fire System not following intervention points on Cxxx-LAO-O4-ITP-C101_WS103-50059. __ assurance has not been maintained for works completed thus far.
| 02SL - Stations (LUL) | Cxxx-NCR-001851 | NCR | Damaged lagging in mega riser |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-08-31 | 2017-09-25 08:27 | 25 | 2017-05-15 14:35 | Mechanical - Heating Ventilation & Air Conditioning | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | There are 2 locations of damaged lagging ion the HVAC system n the mega riser (MGSH), the ductwork system was lagged at __ Manufacturing.
| 02SL - Stations (LUL) | Cxxx-NCR-001852 | NCR | Backstrap joint in the MGSH mega riser has been installed to the wrong flange joint |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-07-31 | 2017-06-21 11:56 | -40 | 2017-05-20 12:10 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate resources | Completed |  | __ have installed the backstrap to the wrong flange joint in the Moorgate shaft mega riser.
| 02SL - Stations (LUL) | Cxxx-NCR-001853 | NCR | TUN - BWK - Out of Tolerance Setting Out AP1 / AP5 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-03-30 | 2018-04-06 10:25 | 7 | 2017-05-22 06:43 | Architectural - Brickworks/Blockworks | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | As per attached markups, blockwork walls built out of tolerance on position.
| 02SL - Stations (LUL) | Cxxx-NCR-001854 | NCR | MTH. Unusable cast in lifting eye for MSH Lift no 3 and incorrect cast in sockets for MTH Lift 4 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-07-31 | 2017-06-28 10:13 | -33 | 2017-05-25 11:37 | Civil - Civil Engineering General | 4500 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Lift no 3 Moorgate Shaft Please refer to attached photo and sketch. One of the smaller M20 lifting eye sockets has been displaced during the concreting operation therefore we are unable to adequately screw the lifting eye into it. Lift no 4 - Moorgate Ticket Hall One of the lifting eyes has been cast 100mm from the theoretical position and the socket for the SWL 5te lifting eye is incorrect.
| 02SL - Stations (LUL) | Cxxx-NCR-001855 | NCR | MSH – ES5 Slab nibs at Platform Level +3 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-07-31 | 2017-06-15 08:21 | -46 | 2017-05-26 07:35 | Civil - Civil Engineering General | 2000 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | Slab nibs adjacent to doors at the bottom of ES5 are encroaching into the minimum space proofing requirements for the escalator.
| 02SL - Stations (LUL) | Cxxx-NCR-001856 | NCR | MTH Street |  | Crossrail | PDP | LIS - Liverpool Street Station (Central) |  | 2017-08-30 | 2017-07-17 10:57 | -44 | 2017-05-31 08:12 | Mechanical - Heating Ventilation & Air Conditioning | 5000 |  | Damaged | Reject | 3 (3-6k) | Complete | Material/Preservation Problems - Improper handling of material | Completed |  | CRL were handed inspection packs for supply & extract ductwork MTH street -1 as shown on drawing Cxxx-LAO-H-DDA-C101_2-12041, aswell as other snags we have noted that the ductwork has several areas where it has been damaged. The relevant ITP states that the ductwork should be free of damage, CRL can not accept a installation that does not meet the standards set out in the ITP
| 02SL - Stations (LUL) | Cxxx-NCR-001857 | NCR | BTH MFD Storage Generally |  | Crossrail | PDP | LIS - Liverpool Street Station (Central) |  | 2017-06-28 | 2017-06-22 08:15 | -6 | 2017-05-31 11:44 | Mechanical - Heating Ventilation & Air Conditioning | 5000 |  | Damaged | Reject | 3 (3-6k) | Complete | Material/Preservation Problems - Improper storage of material | Completed |  | We have noted that MFDs are being stored uncovered with the ends open and are being filled with general rubbish and ductwork stores materials-this is not acceptable.
| 02SL - Stations (LUL) | Cxxx-NCR-001858 | NCR | MGSH Ductwork Storage |  | Crossrail | PDP | LIS - Liverpool Street Station (Central) |  | 2017-06-28 | 2017-06-21 11:52 | -7 | 2017-05-31 12:06 | Mechanical - Heating Ventilation & Air Conditioning | 1000 |  | Planning | Reject | 4 (0.5-3k) | Complete | Subcontractor Problems - Insufficient surveillance of subcontractors | Completed |  | We have noted that a large delivery of ductwork and plant has been stored on level +1 MGSH-Chiller room area- at the time of the site walk ( 31.5.2017 AM ) the ductwork& plant was uncovered and not stored on any timber, it was also noted that __ civils where complete scabbling works around the stored ductwork
| 02SL - Stations (LUL) | Cxxx-NCR-001859 | NCR | Tunnel ends Comms CMS link into Cxxx interface |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-09-30 | 2017-12-08 12:16 | 69 | 2017-06-01 15:34 | Electrical - Cable Management | 10000 |  | Design | Rework | 2 (6-60k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | This NCR highlights in the non compliance for Comms tray requirements up to the tunnel mouth.
| 02SL - Stations (LUL) | Cxxx-NCR-001860 | NCR | BTH - North escalator plinth setting out |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-08-01 | 2017-06-23 13:59 | -39 | 2017-06-02 16:19 | Structural Engineering - Concrete Member | 4000 |  | Design | Repair | 3 (3-6k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Drawing showing plinth locations had an incorrect dimension (1350 rather than 1400) to one of the escalator plinths in the north decline. Other plinths dimensioned off this, subsequently 5 out of 6 were 50mm out of position.
| 02SL - Stations (LUL) | Cxxx-NCR-001861 | NCR | MSH. Waterproofing under screed in Old Keats place |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-07-04 | 2017-06-07 15:12 | -27 | 2017-06-06 07:44 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Supervision - Supervisor does not have access to all pertinent information | Completed |  | We have accidently installed the concrete screed in a section of the Street Level slab to the standard __ screed details but without installing the waterproofing as detailed on drawing Cxxx-LAO-C-DDA-C101_Z-50901 (marked up drawing attached).
| 02SL - Stations (LUL) | Cxxx-NCR-001862 | NCR | Ventilation Ductwork |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2017-08-31 | 2017-07-14 07:35 | -48 | 2017-06-06 07:54 | Mechanical - Heating Ventilation & Air Conditioning | 2500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Contamination | Completed |  | Specification JY30.1423 requires ventilation ductwork to meet the internal cleanliness level PDI level 2 as provided within HVCA publication TR/19, under s. 2.14.2 (b) of this standard is the requirement to manually wipe out the internal surfaces of ducts immediately prior to installation. This requirement is also contained within the various ventilation system installation method statements ie Cxxx-LAO-01-GMS-C101-50086 (s 5.2.8 at page 13). From random checks and the level of dirt & dust found it would appear internal surfaces are not being wiped prior to installation moreover, there is no evidence of the requisite rags at any work face or installation area and no wiping out has been observed.
| 02SL - Stations (LUL) | Cxxx-NCR-001863 | NCR | BTH - ticket hall level Cast in conduit installation. |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2017-09-11 | 2017-08-17 08:37 | -25 | 2017-06-06 08:49 | Electrical - Cable Management | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Management Problem - Other | Completed |  | A large amount of Cast in Conduits installed off site within the pre cast soffit for BTH level (approx 35no.) have been installed without threaded ends and couplings. Conduits installed have only cut ends, preventing them from being connected to follow on CMS that will be installed at high level within BTH.
| 02SL - Stations (LUL) | Cxxx-NCR-001864 | NCR | BTH, Blocked cast in conduit. |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2017-10-31 | 2017-10-09 13:13 | -22 | 2017-06-07 10:51 | Electrical - Cable Management | 1500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | 25mm conduit installed in at high level in Broadgate ticket hall was found to be blocked. conduit had been installed and subsequently cast in above ticket hall gate line.
| 02SL - Stations (LUL) | Cxxx-NCR-001865 | NCR | MTH. Precast soffit panels MTH basement |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-08-31 | 2017-07-07 15:05 | -55 | 2017-06-08 09:54 | Civil - Civil Engineering General | 2000 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | We have had to drill and fix the FAZII bolts for the type B brackets shown on drawing Cxxx-LAO-A-DWG-C101_WS099-50517 20mm further West due to clashes within the existing LUL ticket hall RC structure. This has meant that the post drilled bolts have been installed outside the fixing tolerances for the brackets, so in order to make them fit we have had to mag drill the bracket B baseplates to suit the new position of the post fix bolts. Please refer to the attached drawing for clarity.
| 02SL - Stations (LUL) | Cxxx-NCR-001866 | NCR | MTH - OSD Lift Pit Slab Level |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-09-29 | 2017-10-02 07:11 | 3 | 2017-06-13 16:46 | Structural Engineering - Concrete Member | 2500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Cxxx-MMD-C-DDA-C101_1-11034 specifies Structural Slab level of 112.450 for OSD lift pits. This is reinforced by Cxxx-LAO-C-DWG-C101_WS099-50155 from CADS. However, PMI 01023 issued 9th June 2016 indicates SSL of 112.250. Discrepancy in works information has led to slab being poured 200mm high.
| 02SL - Stations (LUL) | Cxxx-NCR-001867 | NCR | MSH - OSD Lift Pit Spine Walls |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-09-05 | 2017-08-29 10:44 | -7 | 2017-06-13 16:57 | Structural Engineering - Reinforcement | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | Drawing no Cxxx-LAO-C-DWG-C101_WS099-50155 details 550mm thick base slab to 112.450 with CEDS layer above. Detail A and Section 2-2 show reinforcement not tying into base slab or side walls. Cxxx have tied steel into walls and slab.
| 02SL - Stations (LUL) | Cxxx-NCR-001868 | NCR | Identified snags being closed out prior to rectifications completed. |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2017-09-30 | 2017-09-21 08:14 | -9 | 2017-06-14 13:14 | Electrical - General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Contractors punch list for installation works at __X/MTH/BHT/P+T identifies numerous outstanding snags as signed off/completed. Upon receiving punch list (11/06/17) it was noted that multiple snags and issued raised during IRF inspections with CRL were closed by comments from construction team without rectifications being undertaken or evidence/information requested to confirm installation as satisfactory. Examples of snags and comments as below: • water damaged CMS identified - closing comment advises install signed off, instruction required • Missing Washers - closing comment advises Installed as per Project leaders direction. • Access to CMS to install cleat cables - closing comment advises; as per gated design • Earth Gapping not installed - closing comment advises, await design info & PMI
| 02SL - Stations (LUL) | Cxxx-NCR-001869 | NCR | MSH - 107 Bwk to Rc wall out of position |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-07-13 | 2017-06-27 08:06 | -16 | 2017-06-15 11:07 | Architectural - Brickworks/Blockworks | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | 2 no. walls of Cxxx-LAO-A-DDD-C101_2-22812 were converted from Blockwork to RC as part of Cxxx-__-130-CI-0105. The wall running NS between GLC-D and GL4-5 has been poured in concrete 140mm too far to the east. This makes room SRI-A smaller by 140mm and the escalator void 140mm larger.
| 02SL - Stations (LUL) | Cxxx-NCR-001870 | NCR | __X Additional MFSD's |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2017-07-17 | 2017-07-14 08:09 | -3 | 2017-06-19 08:12 | Mechanical - Heating Ventilation & Air Conditioning | 4000 |  | Design | Use As-Is | 3 (3-6k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | CRL has been advised of additional MSFD's are to be installed to the Western wall of __ Battery room 2/761 to the plant room vent supply & extract and also the dedicated battery room extract. These dampers are not shown upon the __ design layout Cxxx-LAO-H-DDA-C101_2-31342 rev P05, or __ drawing Cxxx-LAO-H-DWG-C101_WS103_2-5001 rev C03 or the __ installation drawing 994/15/Street-1/001. It should be noted that although the __ drawing carries a note stating issued under FCD ref Cxxx-FCD-001453 this particular drawing wasn't included to that FCD. The __ drawing although installed to has not been issued under FCD. Can you please advise why additional dampers are required as these do not appear to be necessary, if they are pleaswe issue the relevant drawing under FCD accordingly.
| 02SL - Stations (LUL) | Cxxx-NCR-001871 | NCR | __X Battery Room MFSD Access |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2017-08-16 | 2017-07-20 09:02 | -27 | 2017-06-19 12:19 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The actuator fitted to pressure release damper ref. MFD-264 within __ battery room currently has to be accessed through a gap approx. 200mm deep between 2No 400 wide ventilation ducts. This is inadequate access for wiring, actuator removal or routine maintenance checks. It is also noted that the location of the proposed MEWP / Tower to reach this actuator would appear to clash with the emergency lighting battery rack. Should this clash be the case then the proposed access to MSFD's 257 & 258 in the same location using the same machine will also be unattainable.
| 02SL - Stations (LUL) | Cxxx-NCR-001872 | NCR | MTH - Basement Precast Socket / Bracket locations |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-08-09 | 2017-07-06 09:03 | -34 | 2017-06-20 16:19 | Structural Engineering - Bolted Connections | 500 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Error by manufacturer in shipping or marking | Completed |  | Precast Plank 001 on Cxxx-LAO-A-DWG-C101_WS099-50517 has had the sockets for bolted connections cast at 350mm from plank edge, rather than 475mm as required on site.
| 02SL - Stations (LUL) | Cxxx-NCR-001873 | NCR | __X, TUN, Fire separation of installed distribution Boards |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2018-09-28 | 2020-01-21 16:06 | 480 | 2017-06-21 13:23 | Electrical - LV Equipment | 10000 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Management Problem - Other | Completed |  | Distribution boards have not been installed in line with the requirements of the M&W specs. The requirements for distribution boards to be installed with; • A and B distribution boards to be separated by a 1 hour fire barrier. • Emergency lighting boards to be separated from A+B boards This information formed part of the gated design but has not been included within the F2 design drawings In addition a requirement of the MCR for db’s details distribution boards Approved for use in sub-surface locations in rooms where the room volume does not exceed 200m3 and it has a minimum one hour compartmentation compliant with LU standard. Areas that exceed the above require suitable enclosure/compartmentation . There are numerous locations within __ and the platforms/tunnels where the above requirements have not been met. Switch room 8/669 on east bound east end has A, B and E boards installed without the required separation and no space provision to install enclosures allowed for. Riser locations and corridors exceed the 200m3 volume.
| 02SL - Stations (LUL) | Cxxx-NCR-001874 | NCR | Damage to Paint - SOR Mullions |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-09-30 | 2017-07-06 15:40 | -86 | 2017-06-26 07:29 | Architectural - General | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Scratches to paint noted on 2no mullions ( see attachments), unable to determine whether damage happened in transit or during offload.
| 02SL - Stations (LUL) | Cxxx-NCR-001875 | NCR | BTH - continued installation of non conforming multi compartment trunking reducers |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2017-12-31 | 2017-08-31 07:29 | -122 | 2017-06-26 11:54 | Electrical - Cable Management | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | It was noted during an IRF inspection of CMS within BTH that unsuitable multi compartmented trunking previously identified and highlighted to the contactor under Cxxx-NCR-001710 and subsequently Cxxx-PMI-01310 are still being installed after the communications listed. As previously detailed, the internal configuration of these reducers impede capacity and potentially risk damage to the cables to be installed.
| 02SL - Stations (LUL) | Cxxx-NCR-001876 | NCR | MGS - CMS installation, cable tray parallel uni strut support brackets. |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2017-08-10 | 2017-08-10 07:18 | 0 | 2017-06-26 12:41 | Electrical - Cable Management | 1000 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Supervision - Other | Completed |  | During inspection of CMS installed in MGS for IRF inspection, it was noted that unistrut supports at Platform +2 upper(7/236) and also Platform +2 (S/236) are installed parallel to the cable tray and are impeding the available space to tie/cleat cables therefore reducing the overall capacity.
| 02SL - Stations (LUL) | Cxxx-NCR-001877 | NCR | MSH. Crack in ES5 Precast unit no 1 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-07-26 | 2017-07-04 07:53 | -22 | 2017-06-28 10:06 | Civil - Civil Engineering General | 500 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | A crack has formed in the unit at a temporary works support location following de-mould.
| 02SL - Stations (LUL) | Cxxx-NCR-001878 | NCR | Benchmark not followed |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2017-09-30 | 2017-08-03 14:01 | -58 | 2017-06-28 12:02 | Fire - Fire Systems & General | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Surveillance on __ Fire Alarm Systems/Design was carried out at Liverpool Street station. We visited Blomfield Box Street Level and came across the Fire Alarm Control Panel which had been installed at the bottom of staircase adjacent to at the Back Exit of the station. Upon investigation it was found that the installation didn't follow the agreed benchmark (fire Alarm Control Panel in CER). Although the Fire Alarm installation hadn't been offered for inspection there were clear differences between installed panels (both Fire Alarm and Damper) to agreed benchmark.
| 02SL - Stations (LUL) | Cxxx-NCR-001879 | NCR | BTH - FFO - Circular MAP Damper BSKC6 - Fire compound Incorrect Install (SHARPFI__) |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-09-22 15:17 | 2018-01-16 09:03 | 116 | 2017-06-29 10:21 | Architectural - General | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | 3 x Circular MAP Dampers have not been installed in accordance with the MAP Damper details (Attached) Dampers located BTH Street Level -1 , CER and SCR rooms.
| 02SL - Stations (LUL) | Cxxx-NCR-001880 | NCR | GFRC Acoustic Panels - PTW & PTE |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-09-12 | 2017-09-12 09:11 | 0 | 2017-06-29 13:15 | Architectural - General | 5000 |  | Manufacturing Defect | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Error by manufacturer in shipping or marking | Completed |  | PTW and PTE Acoustic panels have not been manufactured in accordance with the ITP, there are quality issues with the installation of the acoustic insulation on the back of the panels.
| 02SL - Stations (LUL) | Cxxx-NCR-001881 | NCR | MSH. Damage to ES5 escalator precast unit 01 during transportation to site |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-09-30 | 2017-07-28 09:05 | -64 | 2017-06-30 12:44 | Civil - Civil Engineering General | 2500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Precast unit no 1 (Cxxx-LAO-C-DWG-C101_WS099-50169) was damaged during transportation to site (when the lorry driver did an emergency stop to prevent and accident on the motorway). The unit slid forward from the packing timbers which broke off sections of concrete on the North and South side of the unit. A small section of the underside of the precast unit was also damaged. The precast unit was inspected upon site delivery and the attached photos taken. There is no evidence of any cracking or structural damage to the precast unit.
| 02SL - Stations (LUL) | Cxxx-NCR-001882 | NCR | PLT - Shrinkage Cracking to CH2 slab |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-08-02 | 2017-07-26 12:39 | -7 | 2017-07-05 11:35 | Civil - Civil Engineering General | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Shrinkage cracking has been noted on the CH2 slab which was poured on 29/06/17. While the concrete used for the pour (Cxxx-LAO-O4-XDS-C101-50086 D5a ) meets strength and durability requirements, its higher cement content has resulted in higher shrinkage.
| 02SL - Stations (LUL) | Cxxx-NCR-001883 | NCR | Non- Compliant Material |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-09-22 | 2017-08-23 10:25 | -30 | 2017-07-05 11:09 | Architectural - General | 1000 |  | Incorrect Installation | Reject | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | Non-compliant materials installed on the external of the SOR room. __ breather membrane status code 3 as attached.
| 02SL - Stations (LUL) | Cxxx-NCR-001884 | NCR | Fixing pads not installed correctly on invert for CMS brackets |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-09-02 | 2017-07-28 15:15 | -36 | 2017-07-05 16:05 | Civil - Structural Engineering | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Some fixing pads as part of lakemere cladding in the decline of broadgate ticket hall have not been installed correctly to fix the CMS brackets
| 02SL - Stations (LUL) | Cxxx-NCR-001885 | NCR | damaged cable in bottom of lift shaft 7. |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-09-30 | 2017-10-10 12:33 | 10 | 2017-07-05 16:15 | Electrical - Power Distribution | 1500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | An installed cable has been damaged when removal of scaffold was being executed
| 02SL - Stations (LUL) | Cxxx-NCR-001886 | NCR | lightning protedtion points on __ street level roof were filled in and damaged |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-08-02 | 2017-07-26 15:40 | -7 | 2017-07-05 16:25 | Electrical - Earthing & Bonding | 10000 |  | Damaged | Rework | 2 (6-60k) | Complete | Management Problem - Inadequate supervision | Completed |  | There was 3 lightning protection points non coming. 2 points were filled in and covered by OSD landing pads. 1 point was cut by accident
| 02SL - Stations (LUL) | Cxxx-NCR-001887 | NCR | MAP MFD Storage |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-08-31 | 2017-08-09 06:54 | -22 | 2017-07-07 13:30 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper handling of material | Completed |  | Unacceptable method of storing MAP dampers and calcium blocks stored inside the damper.
| 02SL - Stations (LUL) | Cxxx-NCR-001888 | NCR | TUNS & PLAT - Cracks in vertical joints within UPE |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-05-31 | 2018-05-17 13:28 | -14 | 2017-07-07 12:35 | Civil - Structural Engineering | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Crack appearing along vertical grouted element between Precast unit within UPE at periodical interval throughout the length of the platforms
| 02SL - Stations (LUL) | Cxxx-NCR-001889 | NCR | Bonding Conductors |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-12-28 | 2018-11-20 09:44 | 327 | 2017-07-11 11:07 | Electrical - Earthing & Bonding | 80000 |  | Incorrect Installation | Reject | 1 (>60k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | The main bonding conductors in Blomfield Box are installed using __ 649-1B. The cable that should be used is Railsure.
| 02SL - Stations (LUL) | Cxxx-NCR-001890 | NCR | BGTH- DW144 Installed instead of flameshield |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-08-10 | 2017-08-10 14:10 | 0 | 2017-07-13 10:11 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | __ have manufactured and installed a section of DW144 ductwork at BGTH Street level -1 which should be Firerated (__) ductwork as indicated on the schematic Cxxx-LAO-H-DDE-C101-Z-41006. This was not picked up when the drawing was issued for approval to __ it was only at a later date when reviewing schematics that the incorrect install was incorrect.
| 02SL - Stations (LUL) | Cxxx-NCR-001891 | NCR | MGS Acoustic treatment to ducts |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2019-03-31 | 2019-05-24 10:33 | 54 | 2017-07-18 13:21 | Mechanical - Heating Ventilation & Air Conditioning | 6000 |  | Design | Repair | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Ductwork within the acoustic envelope of tunnel vent fans requires acoustic treatment to prevent fan noise from entering the ducted ventilation systems. The requirements and materials to achieve the necessary noise reduction to the ductwork are stipulated within the acoustic review document Cxxx-LAO-A-RGN-C101-50012. The design layout and the manner in which the ductwork has been installed precludes the installation of the materials provided for within the acoustic report to the main pressure relief duct at Platform +2 MGS. The situation is also exacerbated by installation of electrical CMS close to the ductwork in certain places. Either alternative methods & materials need to be specified to achieve the acoustic attenuation or the ductwork requires alteration.
| 02SL - Stations (LUL) | Cxxx-NCR-001892 | NCR | GFRC Stainless Steel Support Frame Onsite Remedials - AP6 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-08-15 | 2017-08-16 07:24 | 1 | 2017-07-18 13:49 | Architectural - General | 1500 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The stainless steel leveling braces for the single ribs in AP6 are not able to be bolted to the adjacent standard rib because of a clash with an infill strut U bracket welded to the standard rib.
| 02SL - Stations (LUL) | Cxxx-NCR-001893 | NCR | GFRC Stainless Steel Support Frame Onsite Remedials - AP6 Single Rib Base Bracket |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-11-30 | 2017-11-17 11:29 | -13 | 2017-07-18 15:18 | Architectural - General | 2000 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | The AP6 single rib base brackets (10#) have been manufactured with a passenger panel strut L tab missing on one side.
| 02SL - Stations (LUL) | Cxxx-NCR-001894 | NCR | MTH Granazzo Terrazzo Flooring - Production stage testing, measuring and calibration of tools and materials. |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-03-31 | 2020-03-24 12:23 | 724 | 2020-03-20 16:10 | Architectural - Flooring | 500 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | It has been identified that no evidence of calibration is in place for the following as part of __’s production process for the manufacture of Granazzo Terrazzo Flooring on all of Crossrail’s projects: • Volumetric measuring of constituent materials for batching • Dimensional measuring tools • SRV testing equipment
| 02SL - Stations (LUL) | Cxxx-NCR-001895 | NCR | Platform & Tunnels-Westend of Westbound-BOH area |  | Crossrail | PDP | LIS - Liverpool Street Station (Central) |  | 2017-12-01 | 2017-11-22 13:57 | -9 | 2017-07-19 07:29 | Mechanical - Heating Ventilation & Air Conditioning | 12000 |  | Design | Repair | 2 (6-60k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Further Information 23.8.2017 below. Cxxx have installed ductworks at the west end of the westbound platform as drawing Cxxx-LAO-H-DDA-C101_8-12353, CRL have previously noted concerns with the configuration of the ductwork which is installed within the escape walkway to the platform. The walkway area being shown upon drawing Cxxx-LAO-A-DDD-C101_Z-27020. The works information baseline standards (version 12) included a number of Technical Specifications for railway Interoperability including Safety in Railway Tunnels EU 162/2008. This was revised as 1303/2014 and subsequently instructed for incorporation under PMI ref Cxxx-PMI-01074. Both the original and revised standard provide for escape walkways to be afforded a minimum headroom of 2250mm AFFL. From measurements taken on site the following ducts appear non compliant with this requirement, Extract air from the __/R (8/712), this exits the room to lineside at approx. 1600mm AFFL before rising to approx. 2150mm AFFL and then running for approx. 10 metres before turning away from lineside to enter the back of house passage. Support brackets are below the above levels. The pressure relief duct from the __/R (8/712), this exits the room to lineside at approx. 2000mm with the underside of it’s support brackets at 1920mm AFFL. This level is maintained for approx. 2500mm before the duct rises to above. It should be noted that, the above levels were taken from the current SSL with a 100mm allowance to final FFL. As previously advised it should be noted that the minimum width of the Crossrail escape walkways is 1100mm as detailed within Cxxx / Cxxx information. This requirement is also noted within the Cxxx / Cxxx / Cxxx ICD document Cxxx-__-K1-RSP-C101-50001 agreed by Cxxx signature 14 December 2015.
| 02SL - Stations (LUL) | Cxxx-NCR-001896 | NCR | MTH - Basement Water Ingress Staining Precast |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-07-19 | 2018-04-10 14:02 | -100 | 2017-07-19 08:10 | Geotechnical Engineering - Dewatering | 2000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Inadequate/insufficient tooling. | Completed |  | After last night's rainfall, there has been further water ingress into the Moorgate Ticket Hall basement. This has resulted in the staining of precast columns and newly installed precast soffit panels. This has been due to the OSD contractor being unable to suitably repair water ingress on the street level of the Moorgate Ticket Hall slab.
| 02SL - Stations (LUL) | Cxxx-NCR-001897 | NCR | PLT - ES2 - Lower Pit Walls cast out of Tolerance |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-08-17 | 2017-08-11 07:07 | -6 | 2017-07-20 13:36 | Civil - Civil Engineering General | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Supervision - Insufficient supervision | Completed |  | Following survey of ES2 lower pit for the Escalator Truss have been found to be out of tolerance. Walls A1, B, C, D as marked on attached sketch Cxxx-NCR-001897 Sketch 1, encroach into the pit by 50-70mm.
| 02SL - Stations (LUL) | Cxxx-NCR-001898 | NCR | Dampers in __ BAT and FCR rooms |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-10-08 | 2017-10-06 13:38 | -2 | 2017-07-20 09:31 | Mechanical - Heating Ventilation & Air Conditioning | 2750 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | In Blomfield Box, the current design shows one supply duct work passing through the BAT room and then serving the FCR. In the event of a Fire in the BAT room the MFD will close and therefore prevent cooling to the FCR.
| 02SL - Stations (LUL) | Cxxx-NCR-001899 | NCR | __X street+1 level - inadequate access to rear of installed cable tray |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2017-09-04 | 2017-10-03 10:58 | 29 | 2017-07-21 08:45 | Electrical - Cable Management | 2500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Supervision - Other | Completed |  | Installed cable tray in __ riser street +1 level does not have adequate access to rear to facilitate the cleating of cables.
| 02SL - Stations (LUL) | Cxxx-NCR-001900 | NCR | MEP RISER MODULE 786 FOR BLOMFIED BOX |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-01-31 | 2017-12-06 16:18 | -56 | 2017-07-24 15:55 | Electrical - Cable Management | 10000 |  | Manufacturing Defect | Repair | 2 (6-60k) | Complete | Design Problem - Other | Completed |  | Module 786 has now been delivered to site and installed, on inspection it is clear that in its current state the Module is not fit for purpose, this is due to the ladder not being fit for the purpose it is designed and un usable as a ladder, the gaps around cms penetrations are to large, this is an outstanding issue raised during design review that had not been addressed and will now require additional work on site to rectify. Find attached riser '786 takeoff' and 'typical proposed repairs'
| 02SL - Stations (LUL) | Cxxx-NCR-001901 | NCR | MEP RISER MODULE 790 FOR BLOMFIED BOX |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-01-31 | 2017-12-21 19:58 | -41 | 2017-07-24 15:59 | Electrical - Cable Management | 4500 |  | Manufacturing Defect | Repair | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | Module 790 has now been delivered to site and installed, on inspection it is clear that in its current state the Module is not fit for purpose, this is due to the ladder not being fit for the purpose it is designed and un usable as a ladder, the gaps around cms penetrations are to large, this is an outstanding issue raised during design review that had not been addressed and will now require additional work on site to rectify. Find attached riser '790 takeoff' and 'typical proposed repairs'
| 02SL - Stations (LUL) | Cxxx-NCR-001902 | NCR | MTH - Moorhouse Draft Relief Shaft Platfrom +4.5 - Metalwork |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-07-15 | 2019-06-18 15:53 | -27 | 2019-06-17 07:41 | Architectural - Balustrade | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | Single step down from metalwork walkway from moorhoure shaft Cat ladder platform walkway onto concrete landing.
| 02SL - Stations (LUL) | Cxxx-NCR-001903 | NCR | TUN – Lift 7 halfen channels out of tolerance / not installed |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-11-30 | 2018-05-08 12:31 | 159 | 2017-07-25 17:03 | Structural Engineering - Concrete Member | 2000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | A survey of Lift Shaft 7 shows that some of the halfen channels are either out of tolerance or not installed. Two horizontal channels around the lower level opening have been cast approximately 90mm lower than design and six channels (two around the upper level opening and four on the side walls) were missed in construction. Refer to the attached mark-up showing as-built locations.
| 02SL - Stations (LUL) | Cxxx-NCR-001904 | NCR | No FCD for the relocation of FAP at bottom of back staircase |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2017-09-30 | 2017-08-04 14:06 | -57 | 2017-07-27 07:20 | Fire - Fire Systems & General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Surveillance on A__ Fire Alarm Systems/Design was carried out at Liverpool Street station. We visited Blomfield Box Street Level 0 and found a Fire Alarm Control Panel (FAP) had been installed at the bottom of the staircase. Upon checking Fire Detection Layout Drawing Cxxx-LAO-E-DDA-C101_1-31171 C02 it was found that the FAP had been relocated from the top to the bottom of the stairs. The Contractor was asked for the Field Change Document (FCD) which captured this change. No FCD had been produced. The Contractor was asked for the Field change Document that had captured this change. No FCD had been produced. Post surveillance the Contractor has raised a new FCD Cxxx-FCD-001947 which is under review.
| 02SL - Stations (LUL) | Cxxx-NCR-001905 | NCR | MSH - OSD Column Concrete Strength not achieved |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-09-21 | 2017-08-31 07:21 | -21 | 2017-07-27 16:13 | Structural Engineering - Concrete Member | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | A per attached, concrete for OSD column East has not reached full strength after 56 days.
| 02SL - Stations (LUL) | Cxxx-NCR-001906 | NCR | PES - Plenum Access Hatches |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-12-11 | 2018-03-02 10:01 | 81 | 2017-08-02 15:17 | Architectural - General | 10000 |  | Design | Repair | 2 (6-60k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The PES upper grille frames are obstructing the plenum access hatches and preventing them being opened.
| 02SL - Stations (LUL) | Cxxx-NCR-001907 | NCR | BTH - NTH screed bay lifting |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-01-19 | 2017-12-08 17:30 | -42 | 2017-08-22 10:46 | Structural Engineering - Structural Engineering - General | 6000 |  | Material | Repair | 3 (3-6k) | Complete | Material/Preservation Problems - Other | Completed |  | The south east corner of the screed bay highlighted on the attached drawing has lifted aprox 10mm from the structural slab below. Bay was poured on 27/07/17
| 02SL - Stations (LUL) | Cxxx-NCR-001908 | NCR | PLT - Screeding - Secondary concrete slab curling\lifting |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-04-27 | 2018-03-05 10:40 | -53 | 2017-08-23 07:56 | Structural Engineering - Structural Engineering - General | 30000 |  | Material | Repair | 2 (6-60k) | Complete | Design Problem - Other | Completed |  | The secondary concrete slab within platforms and tunnels has lifted in some locations between 1-4mm in some locations as per attached marked up drawings. Pour dates are marked on attached drawings Locations are AP2, CP9 and AP6 (Northern Line Link)
| 02SL - Stations (LUL) | Cxxx-NCR-001909 | NCR | MTH - Mastic debonding |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-10-03 | 2018-10-30 10:44 | 27 | 2017-08-29 10:59 | Architectural - Brickworks/Blockworks | 5000 |  | Material | Repair | 3 (3-6k) | Complete | Material/Preservation Problems - Other | Completed |  | As discussed with __ (CRL), and __ and __ (__), mastic debonding has been occurring site-wide in areas where blockwork has been completed. This NCR has been raised to capture the quantity and scope of the works required in clearing the debonding present in the Moorgate structures. Remedial measures are highlighted in Cxxx-NCR-001840.
| 02SL - Stations (LUL) | Cxxx-NCR-001910 | NCR | BTH - Mastic Debonding |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-10-03 | 2018-10-31 10:37 | 28 | 2017-08-29 11:01 | Architectural - Brickworks/Blockworks | 3500 |  | Material | Repair | 3 (3-6k) | Complete | Material/Preservation Problems - Other | Completed |  | As discussed with __ (CRL), and __ and __ (__), mastic debonding has been occurring site-wide in areas where blockwork has been completed. This NCR has been raised to capture the quantity and scope of the works required in clearing the debonding present in the Broadgate structures. Remedial measures are highlighted in Cxxx-NCR-001840.
| 02SL - Stations (LUL) | Cxxx-NCR-001911 | NCR | __X - Mastic Debonding |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-10-03 | 2018-06-24 20:40 | -101 | 2017-08-29 11:03 | Architectural - Brickworks/Blockworks | 20000 |  | Material | Repair | 2 (6-60k) | Complete | Material/Preservation Problems - Other | Completed |  | As discussed with __ (CRL), and __ and __ (__), mastic debonding has been occurring site-wide in areas where blockwork has been completed. This NCR has been raised to capture the quantity and scope of the works required in clearing the debonding present in the Moorgate structures. Remedial measures are highlighted in Cxxx-NCR-001840.
| 02SL - Stations (LUL) | Cxxx-NCR-001912 | NCR | TUN - Mastic Debonding |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-10-03 | 2018-10-31 10:42 | 28 | 2017-08-29 11:05 | Architectural - Brickworks/Blockworks | 3500 |  | Material | Repair | 3 (3-6k) | Complete | Material/Preservation Problems - Other | Completed |  | As discussed with __ (CRL), and __ and __ (__), mastic debonding has been occurring site-wide in areas where blockwork has been completed. This NCR has been raised to capture the quantity and scope of the works required in clearing the debonding present in the Moorgate structures. Remedial measures are highlighted in Cxxx-NCR-001840.
| 02SL - Stations (LUL) | Cxxx-NCR-001913 | NCR | PES - Light Box Inconsistent Lit Appearance |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-03-05 | 2018-03-14 12:45 | 9 | 2017-08-30 13:44 | Architectural - General | 25000 |  | Manufacturing Defect | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Error by manufacturer in shipping or marking | Completed |  | The __ supplied PES light boxes at Tottenham Court Road when energised had an inconsistent lit appearance, a ‘checkerboard’ effect on the front panel and there is the potential for the light boxes at LIS to be the same.
| 02SL - Stations (LUL) | Cxxx-NCR-001914 | NCR | MTH. Lack of cover to reinforcement bars and debonded grout/concrete topping GLW GL6 to 8+5m Street Level |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-12-09 | 2017-09-11 14:16 | -89 | 2017-08-31 07:16 | Civil - Civil Engineering General | 5000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Management Problem - Inadequate supervision | Completed |  | Upon removal of the areofill movement joint between the existing LUL structure and new CRL Moorgate Ticket Hall Street level slab to undertake a temporary waterproofing solution at the joint location it has become apparent that some inadequate remedial works has been installed on the newly constructed CRL reinforced concrete slab at street level between GL 6 to 8 West of GLW (the location is within the OSD site boundary). It is apparent that the reinforcement within this area has less than the required 35mm cover and appears that a concrete grout has been post applied over the reinforcement bars which has now de bonded. Please refer to the attached site photos and sketches for clarity and location.
| 02SL - Stations (LUL) | Cxxx-NCR-001915 | NCR | MTH - 2 x 28 day Cube results not available |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-12-01 | 2017-09-14 12:41 | -78 | 2017-09-06 16:19 | Structural Engineering - Testing | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | As per the attachment, for 4 sets of concrete cubes, there are not the required 2 sets of cube crush results at 28 days as required for the submission of the quality pack. This NCR is to capture this fact. The cubes affect a total of 12 concrete elements. Please note, that every set of cubes has at least two results which have achieved the specified strength at or before the age of 28 days.
| 02SL - Stations (LUL) | Cxxx-NCR-001916 | NCR | __X - Street Level -1 - Doors (E-02-777-D02 & E-02-OSD-D02)- Incorrect dimensions. |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-12-04 | 2018-07-05 12:23 | 213 | 2017-09-13 14:11 | Architectural - Doors | 6000 |  | Manufacturing Defect | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | __ supplied two doors for __ (E-02-777-D02 & E-02-OSD-D02) to incorrect dimensions.
| 02SL - Stations (LUL) | Cxxx-NCR-001917 | NCR | MSH - NLL - AP10 Stairs out of tolerance |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-01-16 | 2017-11-07 13:16 | -70 | 2017-09-18 14:05 | Structural Engineering - Concrete Member | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | Please see asbuilt plan drawing and spreadsheet showing height and plan discrepancies. Stars in AP10 vary from 5mm proud to 30mm too small, and 4mm high to 20mm low as compared to Cxxx-LAO-C-DDB-C101_Z-41800.
| 02SL - Stations (LUL) | Cxxx-NCR-001918 | NCR | confirmation required on cable gland selection for 4 core 16 mm |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-11-07 | 2017-11-23 11:06 | 16 | 2017-09-18 14:09 | Electrical - Power Distribution | 2500 |  | Material | Rework | 4 (0.5-3k) | Complete | Supervision - Other | Completed |  | Confirmation that cables glands are correct on 16 mm 4 core cable.
| 02SL - Stations (LUL) | Cxxx-NCR-001921 | NCR | BTH - BWK - Toilet Door Nibs Omitted |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-10-01 | 2018-04-08 21:23 | -176 | 2017-09-22 08:47 | Architectural - Brickworks/Blockworks | 3000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | __ have not built the required nibs for doors E-03-416-D01 and E-03-417-D01 as specified on drawing Cxxx-LAO-A-DWG-C101_WS102_3-50001. This has led to an interface issue between tiling and the doors, as the doors have been installed to fit the openings.
| 02SL - Stations (LUL) | Cxxx-NCR-001922 | NCR | Doors made to incorrect dimensions |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-01-23 | 2018-09-05 12:29 | 225 | 2017-09-25 13:09 | Architectural - Doors | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Two doors (E-03-416-DO1 & E-03-417-D01) in Broadgate Ticket Hall / Plant room level where delivered to site and fitted by teckentrup into the toilet location and could not be fully opened as rendering and ceramic tiling on the walls inhibited this operation and door ironmongry clashed with wall tiles.
| 02SL - Stations (LUL) | Cxxx-NCR-001923 | NCR | BTH - Canopy Rear elevation Glazing Bracket Holes |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-01-31 | 2018-03-05 13:27 | 33 | 2017-10-05 10:58 | Architectural - Glazing | 10000 |  | Manufacturing Defect | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Holes drilled in glazing bracket - too close to bracket edge.
| 02SL - Stations (LUL) | Cxxx-NCR-001924 | NCR | Incorrect Door Size |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-01-23 | 2018-04-12 10:20 | 79 | 2017-09-25 13:12 | Architectural - Doors | 3000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Moorgate St level door W-02-501-D01 made to incorrect dimensions.
| 02SL - Stations (LUL) | Cxxx-NCR-001925 | NCR | Guide Rails Roller Shutter Door |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-12-22 | 2017-10-13 10:03 | -70 | 2017-09-25 12:34 | Architectural - General | 2000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Throating of guide rails was recognized as damage by CRL/ LUL.
| 02SL - Stations (LUL) | Cxxx-NCR-001926 | NCR | VD7 Ductwork inaccessible due to HV containment installed across access doors |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-10-01 | 2018-01-10 13:53 | -264 | 2017-09-25 16:33 | Electrical - General | 1000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | VD7 Spiral ductwork is inaccessible and access doors will not be able to be accessed for maintenance due to containment installed in the area.
| 02SL - Stations (LUL) | Cxxx-NCR-001927 | NCR | PES Post Base Plate Positions |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-12-31 | 2017-11-28 09:49 | -33 | 2017-09-27 08:07 | Architectural - General | 1500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | __ have installed the PES post base plates onto the holding down bolts cast into the pre-cast platform slab and the position of some of these in respect to chainage position are out of tolerance. The position of the base plates from the centerline of the track however are all within tolerance.
| 02SL - Stations (LUL) | Cxxx-NCR-001928 | NCR | BTH - Change to Silicone/Glass joint detail. |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-12-22 | 2018-01-04 09:20 | 13 | 2017-09-29 14:52 | Architectural - Glazing | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Site installation of structural silicon joint between vertical glass panels does not match approved drawing detail.
| 02SL - Stations (LUL) | Cxxx-NCR-001929 | NCR | BTH - Floor paint in EER room |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-11-26 | 2017-11-29 10:15 | 3 | 2017-09-27 16:57 | Architectural - Flooring | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | Room 3/153 EER, has had the floor sealed with Pristine Elitie Pro-Seal. __ have then installed the controllers for ES6, fixed to floor and wired in before (3M) floor paint installed. Issue has been noted before ES1 controllers have been installed.
| 02SL - Stations (LUL) | Cxxx-NCR-001930 | NCR | Incorrect cable gland on A1028 PSD |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-10-26 | 2017-10-10 07:53 | -16 | 2017-09-28 12:56 | Electrical - Power Distribution | 1000 |  | Incorrect Installation | Reject | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | This NCR covers the selection of correct glands on the PSD panel for a 4 core 35 mm FP600s cable. The incorrect gland was selected as a 50 mm was selected and installed instead of a 40 mm.
| 02SL - Stations (LUL) | Cxxx-NCR-001931 | NCR | BTH - Canopy - Additional cover plate added to C channel support. |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-12-22 | 2017-11-13 17:15 | -39 | 2017-09-29 15:30 | Architectural - Glazing | 3000 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | An additional stainless steel cover plate was added to the rear of the channel support between vertical fins. This change was not approved or captured by a design change.
| 02SL - Stations (LUL) | Cxxx-NCR-001932 | NCR | __X ST+4 TECKENTRUP DOOR CLASH WITH INSTALLED SERVICES |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-01-31 | 2018-03-20 15:12 | 48 | 2017-10-02 09:10 | Electrical - General | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | There is a clash between the plenum access hatch and the installed services in __ Street level +4 see attached photo.
| 02SL - Stations (LUL) | Cxxx-NCR-001933 | NCR | MSH. Leak in D Wall causing water penetration within the MCC room at platform +3 level |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-01-12 | 2017-10-19 10:01 | -85 | 2017-10-04 13:37 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Inadequate/insufficient tooling. | Completed |  | There is water penetrating into the MMC room at Platform +3 level from behind the blockwork. Either the water ingress points need to be sealed (if possible) or the water needs to be successfully channeled into the gully channel behind the blockwork wall to prevent any further leaks into the room.
| 02SL - Stations (LUL) | Cxxx-NCR-001935 | NCR | MSH - Cxxx OHLE Room door clear opening |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-02-28 | 2017-11-08 10:51 | -112 | 2017-10-19 08:45 | Architectural - Doors | 5000 |  | Design | Repair | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | During a site visit by Cxxx the structural opening into the OHLE switchroom ref. 9/669 SSR 1 was measured and the door clear opening checked (door reference W-09-669-D02). It was found that the door clear opening was insufficient when the raised floor screed in the room was taken into consideration. Door clear opening at this stage was 2183H x 1826W - refer Moorgate door schedule Cxxx-LAO-A-TSC-C101_WS099-50001 The size of the OHLE switch that must pass through the door is 2118H x 1230W refer Cxxx-Cxxx D-ICD Cxxx-LAO-E-AAG-C101-50002. The floor screed thickness is 100mm resulting in an effective clear opening of 2083mm.
| 02SL - Stations (LUL) | Cxxx-NCR-001936 | NCR | __X Ventilation Shafts Floor Grillage/Mesh Infill |  | Crossrail | PDP | LIS - Liverpool Street Station (Central) |  | 2018-06-30 | 2018-07-17 08:30 | 17 | 2017-10-14 07:22 | Mechanical - Heating Ventilation & Air Conditioning | 25000 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Drawing Cxxx-LAO-A-DDD-C101_Z-37006 ( __ BOH Metalwork SOW-Upper levels ) indicates the requirement for AM-315 floor grillage/mesh in the 3 ventilation shafts. We believe these were a requirement from SDR2. The ventilation shafts have been constructed without the grillage/mesh being installed. We have discussed the grillage/mesh requirements with the LUL engineer and they are required.
| 02SL - Stations (LUL) | Cxxx-NCR-001937 | NCR | Moorgate Shaft Stairs Risers and Landings |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-01-31 | 2018-04-18 12:36 | 77 | 2017-10-12 11:31 | Civil - Civil Engineering General | 3000 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Within Moorgate shaft some of the stair riser heights are landing are inconsistent. Survey has been attached. Remedial action stated as below.
| 02SL - Stations (LUL) | Cxxx-NCR-001938 | NCR | __ clash with steel mullions and OSD wall |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-12-22 | 2017-10-17 15:39 | -66 | 2017-10-13 07:23 | Structural Engineering - Reinforcement | 1000 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | __ are completing installing their steel mullions on the south side of the escalator decline however where there is an interface with the OSD column the design does not accommodate that that the OSD column (including outer wall) and the ES5 escalator decline are designed and installed on 2 different grid systems therefore the steelwork in this area currently does not fit. Please could you confirm that is it is acceptable to locally break back the OSD surrounding wall 160mm thick from 0mm to 50mm as per the attached drawing so that the __ steelwork can be installed. We will also coat the area with Flexcrete 851 once broken back. Cxxx to confirm the wall can be broken back.
| 02SL - Stations (LUL) | Cxxx-NCR-001939 | NCR | FDP-353 Positioned Under an Access Hatch |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-03-07 | 2018-03-12 16:45 | 5 | 2017-10-13 09:32 | Fire - Detection | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | Fire damper panel in __ PL+4 has been relocated without agreement. This now clashes with the permanent access hatch for access and maintenance
| 02SL - Stations (LUL) | Cxxx-NCR-001940 | NCR | PLT - ES2 - Scaffold Plinth Clash with Escalator support |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-12-12 | 2017-12-19 09:55 | 7 | 2017-10-13 16:24 | Civil - Base Course | 2000 |  | Design | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | 3no. Scaffold plinths clash with the upper support beam of ES2 bank of escalators. Following discussion with __ (CRL) and __ (__) it was determined that it would be best to remove plinths and replace with post fixed galvanised plinths in revised location to mitigate clash.
| 02SL - Stations (LUL) | Cxxx-NCR-001942 | NCR | MGS 2/663 supply damper access |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2017-12-01 | 2017-12-08 12:15 | 7 | 2017-10-18 12:43 | Electrical - Cable Management | 1500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | CMS has been installed directly below and adjacent to MSFD 1218 installed to the supply air duct at it's entry to room 2/663. The CMS precludes suitable access for MFSD maintenance and, as such the installations do not comply with specification JA section JA.6402 and specification JY30 sections JY30.1411 and JY30.1415.
| 02SL - Stations (LUL) | Cxxx-NCR-001943 | NCR | PLT - AP11 - SCL repair |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-11-15 | 2017-11-10 11:36 | -5 | 2017-10-18 09:30 | Civil - Base Course | 1200 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | While breaking out come excess concrete an operative has broken out a 350x350x110mm area of SCL below the AXIS level in AP12.
| 02SL - Stations (LUL) | Cxxx-NCR-001944 | NCR | MGS 2/663 Extract damper access |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2018-10-01 | 2017-12-08 12:17 | -297 | 2017-10-18 13:09 | Electrical - Cable Management | 2500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | CMS has been installed directly below and adjacent to the MSFD installed to the extract air duct at it's exit from room 2/663. The CMS precludes suitable access for MFSD maintenance and, as such the installations do not comply with specification JA section JA.6402 and specification JY30 sections JY30.1411 and JY30.1415.
| 02SL - Stations (LUL) | Cxxx-NCR-001945 | NCR | MGS 4/761 MSFD access |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2018-10-01 | 2018-09-10 12:27 | -21 | 2017-10-18 14:08 | Electrical - Cable Management | 5999 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | CMS has been installed directly below and adjacent to MSFD 1408 installed to the extract air duct at it's exit from room 4/761. The CMS precludes suitable access for MFSD maintenance and, as such the installations do not comply with specification JA section JA.6402 and specification JY30 sections JY30.1411 and JY30.1415. Also CMS support brackets require cutting back to allow access to the supply damper.
| 02SL - Stations (LUL) | Cxxx-NCR-001946 | NCR | Co-ordination of services within CCTV room Moorgate shaft accommodation |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-10-01 | 2018-11-29 12:41 | 59 | 2017-10-19 07:52 | Mechanical - Heating Ventilation & Air Conditioning | 3500 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | CCTV room MEP services within the ceiling void have been installed with poor co-ordination. The ventilation ductwork is preventing lumineers to be installed in the ceiling grid.
| 02SL - Stations (LUL) | Cxxx-NCR-001947 | NCR | Firecompound installed prior to Ductwork signoff |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-04-30 | 2018-05-17 10:27 | 17 | 2017-10-24 16:44 | Fire - Compartmentation | 3999 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | __ have intiated fire-stopping in some instances in Moorgate shaft before IRF has been issued to Crossrail team for inspection of ductwork system . It is apparent that local interim inspection is required in some instances prior to completed system offerred to inspect in-wall / fire stop detailing is correct, eg fire-rated ductwork . This is due to build sequence locally for fire-stopping works access, requiring ductwork left out / removed so full duct system cannot be reviewed __ to provide list/plan of detailed locations
| 02SL - Stations (LUL) | Cxxx-NCR-001948 | NCR | MSH - Street -1 DC2 Cabinet Re-location |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2017-11-23 | 2017-12-11 09:14 | 18 | 2017-10-26 09:37 | Communications and Control Systems - General | 1500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | Further to Cxxx-FCD-001956, DC2 was relocated into FAN 1A (Moorgate Shaft Street -1). The new DC2 plinth provided by Cxxx was located adjacent to block wall between 2/776 and CIR-PL 2/236. The location of the plinth adjacent to the block wall meant the DC2 cabinet door can no be opened fully 90 degrees and clashes with the blockwall. Cxxx have since installed a new plinth within 2/776 (N.B. available since early September 2017) however to date DC2 remains on the original non compliant plinth location, it is also not sufficiently protected with other trades/materials risking damage to the Cxxx asset until relocated and protected. The associated containment/cabling (including comms & power) will also require moving to the new DC2 permanent location.
| 02SL - Stations (LUL) | Cxxx-NCR-001949 | NCR | AP9 and AP6 - Portal Cracks |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2017-11-24 | 2017-11-07 09:56 | -17 | 2017-10-27 07:53 | Civil - Civil Engineering General | 1000 |  | Material | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Soffit cracks occurred on AP9 in 3 places. A - 0.3mm B - 0.4mm C - 0.4mm AP6 crack 0.4mm
| 02SL - Stations (LUL) | Cxxx-NCR-001950 | NCR | __X - BWK - Unstable Wall Street Level |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-03-30 | 2017-12-11 09:23 | -109 | 2017-10-31 10:36 | Architectural - Brickworks/Blockworks | 2500 |  | System Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Insufficient information made available to the worker. | Completed |  | The wall above door number E-01-664-D01 as shown on blockwork setting out drawing 32803 is unstable due to the additional builderworks added to it. These buildersworks were not instructed to the subcontractor and so there is no record of the origin of these works taking place. The cause however is obvious as it is providing routing for CMS from the switch room into the corridor on this level.
| 02SL - Stations (LUL) | Cxxx-NCR-001951 | NCR | __X - Level +4 - Doors - Lack of Design Coordination |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-03-02 | 2018-07-13 08:02 | 133 | 2017-11-02 16:42 | Architectural - Doors | 1000 |  | Design | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | The housing installed for the valve of the water main at __ platform +4 in room plant room is blocking access to the room due to the door opening this way (as per approved design).
| 02SL - Stations (LUL) | Cxxx-NCR-001952 | NCR | Door Frames made to incorrect type |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-02-28 | 2018-06-29 08:45 | 121 | 2017-11-02 17:05 | Architectural - Doors | 3000 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Doors (4 x No) supplied, manufactured and delivered to site by __ (W-07-788-D01, W-07-786-D01, W-07-794-D01, W-07-794-D02) had the incorrect type of door frame fitted.
| 02SL - Stations (LUL) | Cxxx-NCR-001954 | NCR | MSFD Access 7/233 |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2018-10-01 | 2018-05-10 09:31 | -144 | 2017-11-06 10:24 | Electrical - Cable Management | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | SER 7/613 extract system exits the room to 7/233, a MSFD is fitted to the party wall requiring access within 7/233. Electrical trunking has been installed beneath the damper preventing access.
| 02SL - Stations (LUL) | Cxxx-NCR-001955 | NCR | MTH. Stainless steel plates OSD interface South East corner street level |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-01-05 | 2017-11-15 13:34 | -51 | 2017-11-06 16:33 | Civil - Civil Engineering General | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | The steel plates for the OSD contractor on the Street level have been manufactured and installed to as-built dimensions. The as-built failed to pick up a kick in the East concrete slab profile at street level therefore has pushed the plate locations out to the east by approx. 20-25mm. Sketch Cxxx-MMD-C-DDH-C101-60519 rev 2 on document Cxxx-MMD-C-QAP-C101-50004 states that there is to be a max 5mm gap between panels. Because there are only 2 components to cover the steel protection we will end up with a larger gap of 5mm in this location.
| 02SL - Stations (LUL) | Cxxx-NCR-001956 | NCR | MSH - BWK - Grout staining of wall & dirtying of drainage channel. |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-01-26 | 2017-11-09 08:38 | -78 | 2017-11-07 08:46 | Architectural - Brickworks/Blockworks | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Interfacing problems | Completed |  | Attached wall was halfway through construction at time of issuing of Cxxx_PMI_1472. Wall construction started on 26th June. 1st lift complete on 3rd July. PMI confirmed to be issued on 4th July and was received on 11th July. On release of grout tubes by Cxxx, the drainage channel below was filled with grout, and the wall was stained. __ have cleaned out the drainage channel however the wall is still stained with grout.
| 02SL - Stations (LUL) | Cxxx-NCR-001958 | NCR | Tun - East bound West end CMS install not to accepted design |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2018-06-30 | 2018-06-09 11:46 | -21 | 2017-11-08 09:27 | Electrical - Cable Management | 10000 |  | Supervision/Management | Rework | 2 (6-60k) | Complete | Management Problem - Inadequate supervision | Completed |  | CMS past the platform end of the east bound ( west end) to the tunnel end wall - has not been installed as per Current accepted design. FCD process not being followed. T1 T2 and T3 containment has been installed at low level, accepted design has this at high level current position means that this will clash with the C6XX walkway to be installed
| 02SL - Stations (LUL) | Cxxx-NCR-001959 | NCR | Access to insulate the ductwork after CMS installation in Moorgate Shaft |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-10-04 | 2018-09-20 14:00 | -14 | 2017-11-08 11:57 | Mechanical - Heating Ventilation & Air Conditioning | 30000 |  | Design | Use As-Is | 2 (6-60k) | Complete | Management Problem - Other management problem | Completed |  | We are raising this NCR to cover the programme clash where the installation of services required for completion of KD12 deliverables. There is a requirement to install the CMS under the Fire Rated Ductwork in Moorgate Shaft to achieve the KD12 date before __s have completed their Fire Risk assessments for the necessity for Fire Rated Ductwork Insulation. The areas that are affected by this NCR are: • Platform +3 outside the MCC & FCR rooms. • Platform +4 Outside TVF Damper Room. • Platform +2Upper plant area. Subject to __ completing ad agreeing the Fire Risk Assessments there may be a requirement to remove some short sections of CMS to install thermal lagging however until advised by __ on whether any insulation is required and the extent & type we are unable to stop the works required to maintain programme.
| 02SL - Stations (LUL) | Cxxx-NCR-001960 | NCR | PES Post Base Plate Grouting |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-01-31 | 2018-01-30 15:24 | -1 | 2017-11-10 09:08 | Structural Engineering - Structural Engineering - General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | The grouting to a PES post base plate on PTW between cross passages CP3 and CP3a at chainage 8317.443 has visible voids between the base plate and the grout.
| 02SL - Stations (LUL) | Cxxx-NCR-001961 | NCR | Installation of Asset Labels to Smoke Detectors |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-03-31 | 2018-06-28 14:29 | 89 | 2017-11-10 10:53 | Fire - Detection | 3000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Asset labels attached adjacent to Smoke Detectors in Blomfield Box and at Platform Ends either identify an incorrect design alternative ID (due to a recent revision of these IDs) or do not have any Design Alternative ID.
| 02SL - Stations (LUL) | Cxxx-NCR-001963 | NCR | Blanking Panel SL+2 Blomfield Box |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-02-28 | 2018-01-17 13:46 | -42 | 2017-11-16 12:22 | Architectural - General | 3000 |  | Incomplete Works | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Area at grid C Street level +2 East elevation has an area missing a blanking panel.
| 02SL - Stations (LUL) | Cxxx-NCR-001964 | NCR | TUN – structural opening for CH1 totem missed in construction |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-05-16 | 2018-01-18 10:03 | -118 | 2017-11-21 15:20 | Structural Engineering - Concrete Member | 1500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | The structural opening for one of the totems in the CH1 central concourse was not formed during construction of the platform slab. The steel around two of these totems was also not spaced out correctly to avoid bolt locations. A survey was carried out showing which bolt locations will clash with steel reinforcement. Refer to the attached mark-up of Cxxx-LAO-A-DDD-C101_8-26163 Rev P04 showing locations. __ propose the following redial action: - core drilling 370mm x 100mm penetration through structural slab (using a 100mm drill bit), making good to metal decking and applying reinforcement protector to provide cover to exposed steel - coring out reinforcement in bolt holes (using circa 18mm drill bit) to allow installation of M16 bolts Cxxx to confirm structural acceptability of core-drilling.
| 02SL - Stations (LUL) | Cxxx-NCR-001965 | NCR | Ductwork Mezzflange in a Wall Line Moorgate PL+3 |  | Crossrail | PDP | LIS - Liverpool Street Station (Central) |  | 2018-08-09 | 2019-02-18 15:33 | 193 | 2018-01-10 11:16 | Mechanical - Heating Ventilation & Air Conditioning | 1500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | CRL have continually noted to Cxxx that a mezz flange on a section of 1400x800 extract ductwork will be situated in a wall line, this has not previously been accepted at Liverpool St. The contractor has not actioned the concerns and it has been noted today that a wall has now been started.
| 02SL - Stations (LUL) | Cxxx-NCR-001968 | NCR | Site wide - Escalator Guards Missing |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-09-29 | 2018-09-17 09:41 | -12 | 2017-11-24 09:42 | Mechanical - Escalators | 5000 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | At a meeting between __, LU and CEG, it was identified that __ are not compliant with the Pan TfL specification for guarding between adjacent escalators in a bank where they are close together. __ has omitted guarding between machines from their design, creating a safety risk when maintaining one escalator, with the other being within reach, and still live/moving.
| 02SL - Stations (LUL) | Cxxx-NCR-001969 | NCR | Dameged Chillers __ & MGSH |  | Crossrail | PDP | LIS - Liverpool Street Station (Central) |  | 2018-10-31 | 2018-01-10 10:41 | -294 | 2017-11-27 14:22 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Further to OBS 16071 raised 10.5.2017 we have noted today (27.11.2017) that further damage has been inflicted on the chiller coils at __ superstructure, the plant room is under the WAD system and this should have helped the control of damage to plant. All plant needs to be protected as per JA 6502.
| 02SL - Stations (LUL) | Cxxx-NCR-001970 | NCR | Holding down bolts for PES post baseplate missing in the precast slab on PTE |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-04-30 | 2018-05-17 09:45 | 17 | 2017-11-28 11:34 | Civil - Civil Engineering General | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | With regards to the holding down bolts cast into the precast platform slabs to receive the baseplates for the PES posts, it appears that at one location on PTE ( Platform Tunnel East) the cluster of 4 bolts have not been cast into the precast slab. Please see attached markup Cxxx-__-PNP-SK149-A Rev 1 showing the location ( opposite crosspassage CP6). Remedial proposal to be confirmed.
| 02SL - Stations (LUL) | Cxxx-NCR-001974 | NCR | __X - All levels - General lighting |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-04-20 | 2018-06-05 16:02 | 46 | 2017-11-29 12:19 | Electrical - Lighting | 10000 |  | Incorrect Installation | Rework | 2 (6-60k) | Complete | Supervision - Other | Completed |  | Inconsistent lengths of Copex on some DesignPlan light fittings.
| 02SL - Stations (LUL) | Cxxx-NCR-001976 | NCR | TUN – concrete voiding in AP11 RC wall |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-01-01 | 2017-12-19 09:57 | -13 | 2017-12-04 15:15 | Structural Engineering - Concrete Member | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | On striking the shutters to the 140mm wide RC walls at the back of AP11 (behind Lift Shaft 7), concrete voiding was revealed between two box outs, see attached photo. The width of this section is 150mm and the depth of void approximately 50mm. __ propose breaking out this section of wall down to the base of the box outs, leaving the reinforcement intact and undamaged. This section of the wall will then be recast when the wall is poured to full height (to SCL soffit).
| 02SL - Stations (LUL) | Cxxx-NCR-001977 | NCR | CER Drawings used on site do not match current revisions on eB |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2018-03-31 | 2018-02-13 07:02 | -46 | 2017-12-05 09:58 | Communications and Control Systems - General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | A planned Crossrail surveillance was undertaken to look at the Installation of Comms cable in two CER rooms, CER 1 and CER 3. __ provided the following Cabinet Layout Drawings for each room: - CER 1: Cxxx-SMN-R3-DDA-C101_2-00005 Revision P03 (effective 4/11/2016) - CER 3: Cxxx-SMN-R3-DDA-C101_3-00002 Revision P04 (effective 30/1/17) On checking eB it was identified that the current revisions for *00005 and *00002 were C02 dated 12/9/17. Both drawings are included on RIR 27 which was instructed under Cxxx-PMI-01572. Based on this there has been a failure in the control of drawings. Furthermore, there are installation changes to cabinet types between the revisions for respective drawings. As part of closure to the NCR the Contractor should investigate to ensure the correct cabinets have been installed per the changes from P03/P04 to C02/C02.
| 02SL - Stations (LUL) | Cxxx-NCR-001978 | NCR | MCR not approved prior to installation of E-COR Stainless Steel Box |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2018-02-28 | 2018-02-13 13:00 | -15 | 2017-12-05 10:05 | Electrical - General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other management problem | Completed |  | A planned Crossrail surveillance was undertaken to look at the Installation of Comms cable. Post Surveillance it was discovered that the MCR for the E-COR Stainless Steel Box installed in the PA/VA Riser Termination had not been approved prior to delivery and installation on site. At the time of the surveillance, __ were installing the box; however the MCR had not been approved by CRL until 20/11/17. This contravenes section 2.1 of ITP Cxxx-LAO-O4-ITP-C101-50156. MCR Decal sheet should be code 1 prior to installation. This is a hold point for both __ and __. Although the MCR is now code 1 this installation shows a breakdown in the material acceptance process.
| 02SL - Stations (LUL) | Cxxx-NCR-001979 | NCR | Contradiction of Protective Device Type between Distribution Board Schedule and Site Installation |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2018-05-31 | 2018-06-27 13:38 | 27 | 2017-12-05 10:15 | Electrical - General | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | A planned Crossrail surveillance was undertaken to look at the Installation of Comms cable in two CER rooms, CER 1 and CER 3. __ provided the following Cabinet Schedule: - C 502-LAO-E-TSC-C101_WS102-50003 Revision 5.0 The Distribution Board schedule for board ‘3-731/DBU/P02’ lists two 16 amp type B protective devices are to be used in the 1-L1 and 1-L2 slots of the board. During the site visit it was identified that two 16 amp type C protective devices have been installed. (See photos) Cxxx was asked to provide evidence to justify deviating from the Distribution Board Schedule; as no justification has been provided this NCR has been raised. Furthermore, as closure to this NCR the contractor should investigate the remarks to install the cabinet in CER 02 as on the schedule as the cabinet has been installed in CER 3.
| 02SL - Stations (LUL) | Cxxx-NCR-001980 | NCR | Reinforcement to firestopping |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2018-06-30 | 2018-08-13 06:41 | 44 | 2017-12-06 14:22 | Fire - Compartmentation | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Insufficient information made available to the worker. | Completed |  | 2No services penetrations to the front wall of the MGS HV switchroom 2/664 exceed the dimensional limitations for un-reinforced compound fire stopping in accord with the manufacturers (__) requirements as appended to ITP. Penetrations were fire stopped without requisite reinforcement which had to then knocked out for retrospective installation of reinforcement ahead of re-stopping.
| 02SL - Stations (LUL) | Cxxx-NCR-001981 | NCR | 2 no ATS installed in BTH basement with no FCD issued and F2 MCR status |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-10-03 | 2018-06-09 11:47 | -116 | 2017-12-08 13:54 | Electrical - Power Distribution | 10000 |  | Design | Rework | 2 (6-60k) | Complete | Design Problem - Inadequate or defective design | Completed |  | 2 no Lift 8 and Lift 9 ATS have been installed in BTH basement due to lack of space within the LEER room as designed with no FCD issued and F2 MCR status
| 02SL - Stations (LUL) | Cxxx-NCR-001982 | NCR | Door clash with installed CMS in riser |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-10-03 | 2018-08-30 20:51 | -34 | 2017-12-08 13:58 | Electrical - Cable Management | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | In Blomfield box Platform +2 riser 789 the entrance door does not open 90 degree and is clashing with the installed CMS
| 02SL - Stations (LUL) | Cxxx-NCR-001984 | NCR | Fire Damper Panel Power Cabling |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-04-27 | 2018-09-12 07:40 | 138 | 2017-12-08 13:50 | Fire - Detection | 15000 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | Cabling for the fire dampers that are required to have operational functionality as part of life safety systems cause and effect strategy during a fire scenario are installed in singles in trunking not just conduit. The FTL-Sifer Cable is only certified for installation in conduit when used for operation of services forming part of life safety systems required to retain functionality. The Dampers affected are as followed: OPE Blomfield dampers MFD D51, MFD 955, MFD 956. Staircase pressurisation Blomfield- MFD 165,MFD 266, MFD 264, MFD 268, MFD 272, MFD 357, MFD 359, MFD 1052 MFD 262 Moorgate OPE MFD 864, ISD 1308,1309,1404,1405 MFD 1909 Staircase Pressurisation MFD 1905, MFD 1508, MFD 1409, MFD 1311, MFD 1289, MFD 1290, MFD 1A11, MFD 1815, MFD 1814
| 02SL - Stations (LUL) | Cxxx-NCR-001985 | NCR | MGSH St -1- Installed domestic pipework damaged prior to install |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-10-01 | 2018-01-19 11:39 | -255 | 2017-12-08 14:25 | Mechanical - Public Health Engineering | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Personnel Error - Not Defined | Completed |  | There is a number of instances where pipework which has been installed has been damaged after install.
| 02SL - Stations (LUL) | Cxxx-NCR-001986 | NCR | MGSH- Electrical services installed impeding firestoppers access before install. |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-10-01 | 2018-01-18 14:25 | -256 | 2017-12-08 14:50 | Electrical - General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | In Moorgate shaft street level -1 ductwork was temporarily removed to allow access for __ to firestop the builderswork the ductwork penetrated. But before __ completed there works __ Electrical have installed services meaning neither the duckwork can be re-instated or the firestopping complete.
| 02SL - Stations (LUL) | Cxxx-NCR-001988 | NCR | PES / PSD __s Missing on PTW |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-04-30 | 2018-06-07 12:32 | 38 | 2017-12-08 15:35 | Civil - Structural Engineering | 1500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | With regards to the halfen channels cast into the precast platform slabs to receive the Cxxx baseplates / bracketry for the platform edge screens / screen doors, it appears that at one location on PTW ( Platform Tunnel West) , the halfen channels have not been cast into the precast slab as per the attached __ Manufacturing drawing Cxxx-LAO-S-DWG-C101-50042 rev C02 ( ie not cast far enough) and hence Cxxx are not able install their bracketry . Please see attached markup Cxxx-__-PNP-SK150-A Rev 1 and photo “ Photo- PES __ -__-08-12-2017-1A” showing the location ( immediately to the East of crosspassage CP7).
| 02SL - Stations (LUL) | Cxxx-NCR-001989 | NCR | __X-Flood Barrier |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-03-07 | 2018-08-07 10:23 | 153 | 2017-12-13 15:44 | Architectural - General | 2500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Flood Barrier in __ main entrance; Unable to complete installation as cross beam section was made to long to fit the structural opening size.
| 02SL - Stations (LUL) | Cxxx-NCR-001990 | NCR | BTH - Stainless steel liner fixing isolation |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-03-31 | 2018-03-02 09:08 | -29 | 2017-12-19 09:54 | Structural Engineering - Inserts | 1500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The stainless steel cavity liner in the escalator declines ES1 and ES6 in Broadgate Ticket Hall is made from stainless steel, the bolts that have been used to fix the system to the wall have a sheradised finish. Full isolation should normally be provided where there is the potential for contact between dissimilar metals, the installation has used plain nylon washers which do not isolate the shank of the fixing from the fixture.
| 02SL - Stations (LUL) | Cxxx-NCR-001991 | NCR | VCDs to Fire rated ductwork |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2018-03-05 | 2018-09-20 13:06 | 199 | 2017-12-20 12:07 | Mechanical - Heating Ventilation & Air Conditioning | 2999 |  | Material | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Insufficient surveillance of subcontractors | Completed |  | Fire rated ductwork systems including all components are required to satisfy BS476-24. Volume control dampers manufactured by BSB engineering type SC submitted under MCR-003007 have been incorporated to fire rated ductwork without the necessary BS476-testing and accreditation thereby negating the fire rating of the duct systems in to which they are installed.
| 02SL - Stations (LUL) | Cxxx-NCR-001992 | NCR | GFRC - Tusk Fixings |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-06-30 | 2018-11-21 14:51 | 144 | 2017-12-21 09:10 | Architectural - Finishes | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | When fixing GFRC panels to the Platform-CP5 junction tusk elements the tusks are exhibiting cracks around the Big Head inserts.
| 02SL - Stations (LUL) | Cxxx-NCR-001994 | NCR | TUN – Breaking out required for services installation in AP2 RC corbels due to __ design not being in place before construction |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-05-20 | 2018-03-19 11:16 | -62 | 2017-12-21 10:49 | Civil - Civil Engineering General | 1500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The concrete works in AP2 were carried out prior to CMS design being finalised. CHT now require concrete to be broken out to facilitate installation. The services to be installed include (refer to attached mark-up for locations): - 5no. 30mm diameter copper pipes (__) and fire protection sleeves through corbel and slab - 6no. 32mm diameter conduits through corbel and slab __ propose locally breaking out the AP2 corbel and slab, keeping the reinforcement intact. Once pipework has been installed, the areas will be re-cast in accordance with the general concreting method statement. These remedial works have already been discussed and agreed with Adrian Douglas of Cxxx.
| 02SL - Stations (LUL) | Cxxx-NCR-001995 | NCR | Air Handling Units lighting |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2018-08-02 | 2019-08-07 06:21 | 370 | 2017-12-22 10:37 | Mechanical - Mechanical Engineering General | 2000 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Specification JY40.1406 (d) requires air handling units to be provided with factory fitted internal lighting with door operated switches. The contractors MCR's 000249 and 004979 confirm these lights as "3.The lamp type used is bulk head LED type which are predominantly metal, 20 gram plastic. No incandensent lamps shall be used. LED mainly metal". The air handling units have been supplied without factory fitted lights or the door switches to operate.
| 02SL - Stations (LUL) | Cxxx-NCR-001996 | NCR | GEN - MEP Containment drop rod design and check |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-08-24 | 2019-02-06 08:42 | 166 | 2018-01-05 13:41 | Electrical - Cable Management | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Containment drop rods have been designed and installed through calculation of applied loading followed by assessment of diameter, number or rods required and spacing between rods from manufacturer's load tables. There are a number of other Crossrail specification requirements such as factors of safety or fire performance that need consideration beyond the manufacturer's information. A full structural design and check of the arrangements used had not been carried out ahead of construction commencing.
| 02SL - Stations (LUL) | Cxxx-NCR-001997 | NCR | __ drawings not on eB - __ not commenting / approving drawings in the allowed time frame |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-09-17 | 2018-02-19 14:53 | -210 | 2018-01-15 11:47 | Mechanical - Heating Ventilation & Air Conditioning | 50000 |  | Design | Repair | 2 (6-60k) | Complete | Design Problem - Other | Completed |  | There are __ drawings which we have installed to but have not been uploaded to eB and approved by CRL. Various EWN have been raised against __ to comment on the drawings, these are in turn holding up the uploading and approval process of the drawings
| 02SL - Stations (LUL) | Cxxx-NCR-001998 | NCR | 110v socket outlets integral protection |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-10-24 | 2018-07-18 15:04 | -98 | 2018-01-18 16:26 | Electrical - General | 1500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | The 110V Socket Outlet design submitted by __ and accepted by CRL as part of the Gate 3 design does not comply with the CRL requirements as described in the recent PTR Cxxx-RFI-004181
| 02SL - Stations (LUL) | Cxxx-NCR-001999 | NCR | Installed surge suppression to Distribution boards |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-09-24 | 2018-10-23 15:05 | 29 | 2018-01-18 16:47 | Electrical - Power Distribution | 40000 |  | Incorrect Installation | Rework | 2 (6-60k) | Complete | Design Problem - Inadequate man -machine interface | Completed |  | Surge suppression has been installed to general distribution boards over and above the general requirements of the CRL specification JY71, Section JY71.1201 sub-section H)
| 02SL - Stations (LUL) | Cxxx-NCR-002000 | NCR | __X St Level +3 – Copper “C” crimp fixed directly to galvanised tray work (dissimilar metals) |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-09-12 | 2018-03-21 09:42 | -175 | 2018-01-25 17:20 | Electrical - Electrical Engineering General | 1000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Supervision - Other | Completed |  | On Blomfield Box street level +3, the copper C crimps are fixed directly to the galvanised tray work. This is causing two dissimilar metals to react with one another.
| 02SL - Stations (LUL) | Cxxx-NCR-002004 | NCR | __X St Level +4 or Platform +4 – 25% spare capacity not provided on CMS tray installed under DB’s |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-09-13 | 2019-09-30 09:07 | 382 | 2018-01-25 17:27 | Electrical - Electrical Engineering General | 1500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | On Blomfield Box the 25% spare capacity in the CMS under the DB's are not being provided.
| 02SL - Stations (LUL) | Cxxx-NCR-002005 | NCR | __X St Level +3 – Fan Room C/900 – Clash between ductwork and plenum access hatch door |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-08-02 | 2018-06-26 14:12 | -37 | 2018-02-13 15:35 | Electrical - Electrical Engineering General | 1500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Blomfield Box Street Level +3, there is a clash between the ductwork and the plenum access door. Please see attached photograph.
| 02SL - Stations (LUL) | Cxxx-NCR-002006 | NCR | __X St Level +0 – Transformer Room Lobby 1/042 – CMS lid covered by ductwork lagging preventing removal of trunking lid |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-08-31 | 2018-06-28 10:56 | -64 | 2018-02-13 15:43 | Electrical - Electrical Engineering General | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Supervision - Other | Completed |  | In Blomfield Box Street level, the insulation to the ductwork has prevented access and the removal of the trunking lid. Please see the attached photograph.
| 02SL - Stations (LUL) | Cxxx-NCR-002008 | NCR | Water ingress into BTH - 22 January 2018 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-07-31 | 2018-05-03 08:59 | -89 | 2018-01-25 17:15 | Civil - Civil Engineering General | 6000 |  | Damaged | Repair | 3 (3-6k) | Complete | External Phenomenon - Weather or ambient condition | Completed |  | There was a lot of water ingress into BTH area and Basement area on the weekend 20-21/01/2018 with the rain, with potential damage to CMS, blockwork and other electrical equipment due to insufficient protection measures that were not taken. Proper bunds should be put in but they weren’t. Following a review on the 22/01/2018 within the rooms it was agreed a clean-up on the rooms was required especially in the SCR (BTH - Basement areas, water ingress). There was water sitting on top of the switch gear panel and within the tray located above. Please see pictures attached.
| 02SL - Stations (LUL) | Cxxx-NCR-002009 | NCR | Co-ordination of MCC panel with access and maintenance plan in Fan IV (2/777). |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-02-28 | 2019-01-14 08:58 | -45 | 2018-12-06 11:53 | Electrical - General | 5000 |  | Design | Repair | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | MCC panel relocated due to clash with ventilation ductwork, the location of the MCC was re-located where it impeded access behind AHU
| 02SL - Stations (LUL) | Cxxx-NCR-002010 | NCR | Watermist Suppression Issues |  | Crossrail | PDP | LIS - Liverpool Street Station (Central) |  | 2018-07-10 | 2018-02-20 07:10 | -140 | 2018-01-29 10:47 | Fire - Suppression | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | 1.Installation of void detection nozzle pipework configuration is not as shown on the typical detail as indicated on approved drawing Cxxx-LAO-E6-DWG-C101-50012 Rev C02. 2.The zone valve supplying room 8/411 has not been installed in the location detailed on drawing Cxxx-LAO-E6-DWG-C101-50011-Rev C02 3.Lack of co-ordination between CHT & __and the required space proofing has not been followed and this has resulted in __having to install ad hoc, this has meant extra fittings having to be used which could affect pump/system performance, CRL have not received any updated calculation report from __yet.
| 02SL - Stations (LUL) | Cxxx-NCR-002011 | NCR | GFRC - Double Curve PNZ Panel Damaged Lifting Point |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-04-30 | 2018-03-08 09:26 | -53 | 2018-01-31 10:08 | Architectural - General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The lifting points cast into the back of the double curve PNZ panel to assist with panel installation have some damaged threads inside two of the lifting points and the lifting eyes are not able to be inserted.
| 02SL - Stations (LUL) | Cxxx-NCR-002012 | NCR | __X – All Levels – Statutory Signage – Wrong Installation of FDKLS instead of FDKS |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-05-31 | 2018-11-02 15:12 | 155 | 2018-01-31 10:08 | Civil - Civil Engineering General | 4000 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Sub-contractor, __, prepared their drawing schedule (ref: Cxxx-LAO-A-DWG-C101_WS103-50178) based on document Cxxx-LAO-A-TSC-C101_WS103-50001 prepared by __ and to which CRL have given Code 1 status. The __ document was checked against the __ document and approval was given for the installation to start in Blomfield Box. (Note: Drawing pack is status B from __ as SID numbers and room ID’s information is still to be agreed by CRL) During a walk round by CRL comments were made by them that the FDKLS and FDKS signs had been incorrectly located as detailed in document G102:A1, Fire systems – passive fire protection (PP.20/22).
| 02SL - Stations (LUL) | Cxxx-NCR-002013 | NCR | GFRC - Broken AP6 Infill Strips |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-02-28 | 2018-02-14 11:23 | -14 | 2018-01-31 10:27 | Architectural - General | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper handling of material | Completed |  | 7# AP6 infill strips have been broken during the logistics of unloading the crate and hoisting it down to platform level.
| 02SL - Stations (LUL) | Cxxx-NCR-002014 | NCR | __ AHP-141 Hatches Pressure Rated Plenum |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-10-31 | 2018-10-09 13:22 | -22 | 2018-09-04 13:26 | Architectural - Doors | 2000 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | AHP-141 __ hatches in the Blomfield Box plenum above street level have failed to achieve Class A leakage as per DW140. Hatches installed in durasteel in __ plenum did not achieve a smoke seal - leakage noticed when pressure tested.
| 02SL - Stations (LUL) | Cxxx-NCR-002015 | NCR | __X - BWK - Cube Strength Failure |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-04-30 | 2018-03-09 13:33 | -52 | 2018-02-06 13:23 | Architectural - Brickworks/Blockworks | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | As discussed with __. __ Wi Mortar for Platform +2 level (89.820 level) has not achieved the full 40MPa required strength. 2 x 28 day results making 38.3MPa and 38.8MPa. __ Wi Mortar for Platform +3 (95.940) has not achieved the full 40MPa required strength. 2 x 28 day results making 24.0 and 24.5MPa. 56 day cube result making 41.1MPa.
| 02SL - Stations (LUL) | Cxxx-NCR-002016 | NCR | Installing Cable of with LV Switchroom A/B before CMS IRF |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-06-12 | 2018-04-17 13:45 | -56 | 2018-02-06 14:37 | Electrical - Cable Management | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | LV Cabling installed on CMS prior to IRF sign off
| 02SL - Stations (LUL) | Cxxx-NCR-002017 | NCR | NLL - Continuity of reinforcement in floor screed |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-05-31 | 2018-03-28 12:13 | -64 | 2018-02-13 14:40 | Architectural - Flooring | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | During construction of the reinforced concrete unbounded screed base in the Northern Line Link (AP6) tunnel continuity of reinforcement across day joints was not always provided. Refer to the attached markup 'NLL - Screed joints with discontinuous reinforcement_Rev 1.0' showing the affected locations.
| 02SL - Stations (LUL) | Cxxx-NCR-002018 | NCR | HUS 3 fixings in flameshield fire rated ductwork |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-08-07 | 2018-09-13 11:19 | 37 | 2018-02-14 16:46 | Mechanical - Mechanical Engineering General | 1000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | HUS 3 fixings are being installed and is shown in detail on flameshield fire rated ductwork drawings, these have not been tested as part of the flameshield fire rated system.
| 02SL - Stations (LUL) | Cxxx-NCR-002019 | NCR | AHU 251 & 351 MCR not approved. |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-09-01 | 2018-04-10 22:10 | -144 | 2018-02-15 16:24 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | MCR-000458 has received comments from CEG, these comments are to be addressed and approved. The AHU's are already installed on site.
| 02SL - Stations (LUL) | Cxxx-NCR-002020 | NCR | Deflection of firemain brackets |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-08-08 | 2019-10-04 14:35 | 422 | 2018-02-21 16:59 | Fire - Fire Systems & General | 2999 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The attached photographs show deflection of fire main brackets, the issues have been identified against each Photo.
| 02SL - Stations (LUL) | Cxxx-NCR-002021 | NCR | __ Control panels MCR not approved |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-10-01 | 2018-06-21 11:49 | -102 | 2018-02-23 11:49 | Mechanical - Public Health Engineering | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | __ have installed sump control panels without an approved MCR.
| 02SL - Stations (LUL) | Cxxx-NCR-002022 | NCR | __X - Damaged SWA cable installed at AP1 |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2018-03-23 | 2018-04-30 08:11 | 38 | 2018-02-23 12:25 | Electrical - Power Distribution | 2000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | Noted that an installed SWA cable B1017 supply to escalator, area was rear of lift shaft 7 at platform level has sustaianed damage to the sheath, exposing the insulation.
| 02SL - Stations (LUL) | Cxxx-NCR-002023 | NCR | FFO - Escape Stairs Handrails |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-10-24 | 2018-08-03 07:51 | -82 | 2018-02-23 17:22 | Architectural - Handrail | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | This NCR is raised concerning the following issues related to BAL-208A balustrading installed in Blomfield Box ESSII Street Level to Platform Level. 1. Photo 1 shows screws fixed to the underside of the handrail joints which hold the two tubes together. The dome-head fixing detail is should give a smooth finish with the tube however a lip has been created. 2. There is also an issue with the handrails aligning at the joints. Photo 2 shows how the galvanising has produced a thick layer which bulges at the end of the tube. 3. Photo 3 shows a build-up of galv inside the tube which causes the spigot to un-align the two tubes and therefore also creates lipping. 4. Photo 4 shows unfinished rough edges where the tube has been cut. Please give details of how this will be finished.
| 02SL - Stations (LUL) | Cxxx-NCR-002024 | NCR | Location of sump pump control panel not as drawings |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-10-01 | 2019-09-03 06:33 | 337 | 2018-03-01 13:47 | Mechanical - Public Health Engineering | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Sump pump control panels not installed as small power drawings. These were installed in a different position after being coordinated on site and exploit the existing CMS layout rather than install a large amount of new CMS.
| 02SL - Stations (LUL) | Cxxx-NCR-002025 | NCR | SWA installed on tray prior to CMS sign off |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-05-31 | 2018-04-30 14:38 | -31 | 2018-03-02 09:18 | Electrical - Cable Management | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | SWA sub main cable installed on CMS prior to Inspection and sign off from client.
| 02SL - Stations (LUL) | Cxxx-NCR-002026 | NCR | CMS not installed to a fully approved design |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-06-30 | 2018-09-12 07:38 | 74 | 2018-03-02 09:33 | Electrical - Cable Management | 1000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | CMS has not been fully installed to the latest approved design.
| 02SL - Stations (LUL) | Cxxx-NCR-002027 | NCR | singles cables installed in trunking prior to CMS inspection and sign off by client |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-05-31 | 2018-06-05 09:44 | 5 | 2018-03-02 09:39 | Electrical - Cable Management | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | singles cabling installed in trunking prior to CMS sign off
| 02SL - Stations (LUL) | Cxxx-NCR-002028 | NCR | CMS not installed to a fully approved design , FCD required |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-10-24 | 2018-10-19 09:03 | -5 | 2018-03-02 09:53 | Electrical - Cable Management | 2000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | The CMS( Comms tray) in the vent shaft has not been installed to the latest approved drawing .
| 02SL - Stations (LUL) | Cxxx-NCR-002029 | NCR | Singles cables installed prior to CMS sign off |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-05-31 | 2018-06-05 09:42 | 5 | 2018-03-02 10:10 | Electrical - Cable Management | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | LV singles cabling has been installed prior to CMS sign off
| 02SL - Stations (LUL) | Cxxx-NCR-002030 | NCR | CMS not installed to a fully approved design , FCD required |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-05-25 | 2018-06-04 08:06 | 10 | 2018-03-02 10:21 | Electrical - Cable Management | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Supervision - Other | Completed |  | CMS not installed to a fully approved design , FCD required
| 02SL - Stations (LUL) | Cxxx-NCR-002031 | NCR | Ductwork Insulated Before Being Tested |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-05-31 | 2018-04-24 10:18 | -37 | 2018-03-05 16:01 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Incomplete Works | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | In Moorgate shaft street level -1, the ductwork in the plant room was lagged due to the __ works requiring the area to be cleared. This ductwork was lagged before it has been tested, this is not in accordance with the ITP and therefore an NCR.
| 02SL - Stations (LUL) | Cxxx-NCR-002032 | NCR | TUN – EBP Surface cracking to Precast Slabs |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-10-09 | 2018-03-09 15:52 | -214 | 2018-03-08 15:24 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Following preparation work for Screeding on EBP some surface cracking was observed emanating from the lifting points of the precast slabs. Following site review by __ CRL and __ __ it is deemed that the cracks are not through cracks and were most likely caused during initial de-moulding operations and transport to site. No further action required as cracks are less than 0.3mm and do not got through the slabs.
| 02SL - Stations (LUL) | Cxxx-NCR-002033 | NCR | MSH. Potential damage to Cxxx __ dampers in Moorgate Shaft from scaffold wokrs |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-09-03 | 2018-04-12 12:43 | -144 | 2018-03-07 13:50 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | __ have erected a scaffold onto the MSH __ dampers for the secondary CMS installation. There are foot print marks etc on the dampers from the scaffold installation suggesting that the scaffold operatives where standing on the dampers for the erection of the scaffold. The dampers are not designed to support the loads of operatives or the scaffolding and may now be damaged.
| 02SL - Stations (LUL) | Cxxx-NCR-002034 | NCR | MCR not approved prior to installation of Air Shield Control and Shut off Dampers |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2018-09-05 | 2018-09-28 11:52 | 23 | 2018-03-12 11:55 | Mechanical - Heating Ventilation & Air Conditioning | 5999 |  | Supervision/Management | Use As-Is | 3 (3-6k) | Complete | Management Problem - Inadequate administrative control | Completed |  | A Crossrail Surveillance was undertaken to look at the installation of Ductwork, Lagging and Dampers. Post Site inspection it was found that the MCR for Air Shield Control and Shut off Dampers was not approved. Dampers had been installed on site with the MCR at INITIATE stage since 12/10/17. Therefore as materials have been installed without prior approval of the MCR there has been a breakdown in the ITP procedure; MCR approval is a hold point preceding site installation.
| 02SL - Stations (LUL) | Cxxx-NCR-002035 | NCR | Ductwork Layout Drawing on site does not match ASite |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2018-09-05 | 2018-06-11 07:21 | -86 | 2018-03-12 12:10 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | A Crossrail Surveillance was undertaken to look at the installation of ductwork, lagging and dampers. During the site visit it was found that the revision of drawing Cxxx-LAO-M-DWG-C101_9-50001 was P01. On checking ASite, this drawing was confirmed at revision C01 and had passed through P01 and P02. Therefore the drawing on site is outdated and there has been a breakdown in the drawing management process. Furthermore, the associated Cxxx-FCD-002185 is not approved.
| 02SL - Stations (LUL) | Cxxx-NCR-002036 | NCR | __ Ductwork Supports & Insulation Issues-PES WE-WB Platform |  | Crossrail | PDP | LIS - Liverpool Street Station (Central) |  | 2018-07-06 | 2021-04-01 08:15 | 1000 | 2018-03-14 08:07 | Mechanical - Heating Ventilation & Air Conditioning | 5999 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Management Problem - Other | Completed |  | __ Supports not installed as per the __ guidance documentation, insulation applied to incorrect installation with possible rework required. 1000 x1000 fire rated ductwork requires M16 drop rods, M12 has been installed, also not installed as per the requirements, rods are not external to insulation.
| 02SL - Stations (LUL) | Cxxx-NCR-002037 | NCR | __ insulation has commenced without flameshield bracket upgrade of ductwork being carried out. |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-06-29 | 2018-06-04 07:06 | -25 | 2018-03-14 14:13 | Mechanical - Heating Ventilation & Air Conditioning | 5999 |  | Supervision/Management | Repair | 3 (3-6k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | Excel have commenced installing firerated insulation on the top of the ductwork before the __ had uprated there brackets. __ had inspected the ductwork and approved the methodology of installing the top of the insulation before the brackets are uprated.
| 02SL - Stations (LUL) | Cxxx-NCR-002038 | NCR | Fire main bracketry |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2020-01-28 | 2020-01-14 17:26 | -14 | 2018-03-22 14:56 | Fire - Fire Systems & General | 2999 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | A Non Conformance Report is raised in relation to the Thrust calculations for the Fire main bracketry, the thrust calculations have not been issued as part of the assurance process.
| 02SL - Stations (LUL) | Cxxx-NCR-002039 | NCR | Piped services bracketry |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-06-29 | 2019-06-12 14:27 | 348 | 2018-03-22 15:30 | Mechanical - Hot & Cold Water Supplies | 2999 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | This NCR has been raised to capture the Piped services braketry not being issued for the assurance of the system.
| 02SL - Stations (LUL) | Cxxx-NCR-002040 | NCR | AP11 - GRC Base Plate Bolt Embedment |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-11-30 | 2018-11-28 14:17 | -2 | 2018-03-23 15:20 | Architectural - General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | GRC base bracket bolt embedment in AP11 is approximately 80mm which is less that the typical 130mm embedment specified on the typical design drawings
| 02SL - Stations (LUL) | Cxxx-NCR-002041 | NCR | __X- P+3 CMS trunking covered by lagging preventing lid removal/access |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2018-08-23 | 2018-10-23 15:04 | 61 | 2018-03-27 08:56 | Mechanical - Heating Ventilation & Air Conditioning | 3000 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Supervision - Supervisor does not have access to all pertinent information | Completed |  | __X P+3 area outside of lift 6, the insulation to the ductwork has been installed on/in close proximity to the multi-compartment trunking, this will prevented the removal of the trunking lid and access to the cms for cabling.
| 02SL - Stations (LUL) | Cxxx-NCR-002042 | NCR | __ Air Conditioning units |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-07-31 | 2018-11-05 12:04 | 97 | 2018-03-28 07:13 | Mechanical - Heating Ventilation & Air Conditioning | 10000 |  | Manufacturing Defect | Repair | 2 (6-60k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | Upon the initial review, the __ Air Conditioning units may have not been supplied in accordance with the approved MCR. A review will need to be held to ensure the materials within the unit comply with the MCR. Any other quality issues with the unit that may be picked up from the review will be re-worked to meet the specification and manufacturers recommendations.
| 02SL - Stations (LUL) | Cxxx-NCR-002043 | NCR | Design and Fabrication Assurance for welded fan frame support steelwork |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2020-10-14 | 2020-02-06 11:30 | -251 | 2018-03-28 11:21 | Mechanical - Heating Ventilation & Air Conditioning | 100000 |  | Documentation and Records | Rework | 1 (>60k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | During a planned surveillance at Liverpool Street Station smoke extract fan supports were inspected. These comprised of a coated base plate welded to a steel post to support the fan. The following information was requested to confirm acceptable fabrication: - Welding competency records for the __ operatives (WPQR) including associated weld procedures (WPS) and fabrication records. - Coating records (thickness and product) to confirm applied product meets the required design life based on the assigned corrosion category. - Evidence that __ drawings have been accepted by __. It was confirmed post surveillance that __ hold no welding certification, Furthermore, no evidence of __ acceptance of __ fabrication drawings was provided. Therefore fabrication and the integrity of both the welding and coating cannot be confirmed as acceptable for supporting a safety critical system.
| 02SL - Stations (LUL) | Cxxx-NCR-002044 | NCR | No UKAS Accreditation (or alternative) for __ carrying out air leakage testing |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2018-06-30 | 2018-05-15 14:38 | -46 | 2018-03-28 12:28 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | Evidence of UKAS or similar accreditation was requested from the Contractor for __ undertaking air leakage testing. It was stated that __ do not hold such accreditation and were unaware of this being a requirement. No PMs acceptance is in place for an alternative testing process whereby procedure(s), competence and equipment has been proposed.
| 02SL - Stations (LUL) | Cxxx-NCR-002045 | NCR | LEER and EER Doors |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-09-30 | 2018-12-17 10:56 | 78 | 2018-04-03 11:43 | Architectural - Doors | 40000 |  | Design | Rework | 2 (6-60k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Door to Lift LEER's and Escalator EER's are shown as opening inwards rather than outwards as required by BS EN 81-20. Doors need to be re-fitted to open outwards.
| 02SL - Stations (LUL) | Cxxx-NCR-002046 | NCR | 25% spare capacity in risers, __X |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-05-31 | 2020-04-06 13:11 | 311 | 2018-04-06 13:51 | Electrical - Cable Management | 10000 |  | Design | Rework | 2 (6-60k) | Complete | Design Problem - Other | Completed |  | Cable capacity on trays in risers are unable to meet the 25% spare capacity requirement as per specification.
| 02SL - Stations (LUL) | Cxxx-NCR-002048 | NCR | MTH Blown floor tiles due to failure of materials |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-06-15 | 2018-07-05 12:19 | 20 | 2018-04-11 15:33 | Architectural - Flooring | 2500 |  | Material | Repair | 4 (0.5-3k) | Complete | External Phenomenon - Weather or ambient condition | Completed |  | Floor tiles laid in MTH basement level became detached (Blown) from screed substrate due to freezing temperature conditions which affected the curing process of the product __ A38.
| 02SL - Stations (LUL) | Cxxx-NCR-002049 | NCR | Water damage to __ Air Release Fans Junction Boxes |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-09-11 | 2018-05-03 08:48 | -131 | 2018-04-12 13:27 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper storage of material | Completed |  | Damage to Air Release Fans Electrical Junction box, due to water ingress. See attached photos.
| 02SL - Stations (LUL) | Cxxx-NCR-002051 | NCR | Maximum tray length supports exceeded on AHU secondary containment |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-05-14 | 2018-04-18 09:58 | -26 | 2018-04-16 10:17 | Electrical - Cable Management | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Secondary CMS cable tray over the AHU is supported at a maximum of 2.2M spacing. Clause JY63 states maximum support spacings should be limited to 1.5M.
| 02SL - Stations (LUL) | Cxxx-NCR-002052 | NCR | PAVA chains 31 and 35 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-05-15 | 2018-07-16 15:29 | 62 | 2018-04-17 15:50 | Communications and Control Systems - Public Address Systems | 500 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | During the assurance review it has been established that quality check sheet that under pins the individual cables between speakers has been incorrectly populated. The test values of the loop resistance far exceed the actual and true readings, due to the fact that the cables were tested with excess coils of cable at the end positions and not at the finished/ prepped ends of the cable before termination. This coupled to the fact that the cable length formularised to provide the distance of the cable was incorrect resulted in the distance of the cable also being incorrectly recorded, and CRL were not give enough time to inspect and witness test any of the cable testing for these PAVA chains.
| 02SL - Stations (LUL) | Cxxx-NCR-002053 | NCR | UPS Outputs in ESR VII |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-10-24 | 2018-11-22 14:06 | 29 | 2018-04-18 13:12 | Electrical - LV Equipment | 2000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | As per works information JV 20 . 1304 C the floor needs to be 75mm higher that the adjacent corridors or the LV switchboards needs to be on a 100 mm plinth this is to prevent LV switchboard from flood water. The ESR VII room currently does not have the required floor level specified, current drawing shows the floor level as the same as the corridor, compared to adjacent rooms which are 100mm higher, see attached __ detail drawing.
| 02SL - Stations (LUL) | Cxxx-NCR-002054 | NCR | Moorgate CMS Street Level -1 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-05-08 | 2018-06-09 11:37 | 32 | 2018-04-24 08:37 | Electrical - General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Wiring in Moorgate CMS street level -1 began before CRL inspection and sign off.
| 02SL - Stations (LUL) | Cxxx-NCR-002055 | NCR | MTH. Leaks in the Southern Penisular precast units at Street Level |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-07-11 | 2018-05-10 12:36 | -62 | 2018-04-30 12:22 | Civil - Civil Engineering General | 2000 |  | Planning | Repair | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | 3no minor leaks have appeared / noticed WC 23rd April 2018 at the underside of the precast plank joints within the Southern Peninsular at Street Level (Moorgate Ticket Hall changing rooms). Please see attached marked up drawings and photos for exact locations and clarity.
| 02SL - Stations (LUL) | Cxxx-NCR-002056 | NCR | __X - Radio Cable CMS install, cabling prior to Inspection/sign of CMS |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2018-06-30 | 2019-09-20 13:49 | 447 | 2018-04-30 14:55 | Electrical - Cable Management | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | It has been noted that cabling of the radio system has commenced prior to inspection and sign off of installed CMS and also the IRN for this install within __ street level -1 to platform level.
| 02SL - Stations (LUL) | Cxxx-NCR-002057 | NCR | BTH - __ clash with scaffold supports on ES1 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-08-21 | 2018-12-15 09:22 | 116 | 2018-05-01 08:37 | Systems - Fire Detection systems and Mains | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | __ pipework installed on the Northern escalator of bank ES1 prevents use of scaffold support points required for A&M.
| 02SL - Stations (LUL) | Cxxx-NCR-002058 | NCR | Type D Connectors Damaged in Type 2B Cabients |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-07-31 | 2018-09-12 06:28 | 43 | 2018-05-01 11:50 | Communications and Control Systems - Crossrail Data Network | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Type D Connectors in Cabinets for SCADA connections have been damaged
| 02SL - Stations (LUL) | Cxxx-NCR-002059 | NCR | MOORGATE LIGHTNING PROTECTION AT 136 LEVEL |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-06-01 | 2018-05-25 10:38 | -7 | 2018-05-04 07:11 | Electrical - Electrical Engineering General | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Management Problem - Inadequate supervision | Completed |  | Lightning protection air termination joint plates installed at correct level, witnessed by CRL, upon subsequent final visit, it appears during the slab pour and following sealing works 2 of the joints have been damaged and 4 have been set at incorrect levels
| 02SL - Stations (LUL) | Cxxx-NCR-002060 | NCR | PLT - AP2 Manhole set out incorrectly |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-09-30 | 2018-06-22 09:08 | -100 | 2018-05-10 11:22 | Civil - Civil Engineering General | 2500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | Position of Man hole in AP2 set out to co-ordinates from Cxxx-RFI-003701, Sketch no: SK-MEP-096. However revised layouts for the floors were issued under Cxxx-RFI-004249, Sketch No. SK11259 which has resulted in a misalignment between manhole and cover of ~60mm.
| 02SL - Stations (LUL) | Cxxx-NCR-002061 | NCR | Electrical Conduit Blocking Duct Work Access Door |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-10-31 | 2018-12-04 09:32 | -331 | 2018-05-11 08:06 | Electrical - Electrical Engineering General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | In Moorgate Shaft accommodation area, the electrical conduit for the lights have been installed under the ductwork access door preventing access to them. The ceilings have now been installed and re-works will need to take place to the electrical conduit to allow access to the ductwork access doors
| 02SL - Stations (LUL) | Cxxx-NCR-002062 | NCR | BTH - BWK - POM wall |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-10-01 | 2018-06-22 12:13 | -101 | 2018-05-11 08:51 | Architectural - Brickworks/Blockworks | 20000 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Please see attached asbuilt. 3m section of Blockwork wall on ticket hall level is approximately 100mm too far towards front of house.
| 02SL - Stations (LUL) | Cxxx-NCR-002063 | NCR | Subcontractor __'s supplier documentation |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-07-26 | 2018-12-13 15:37 | 140 | 2018-05-14 10:04 | Architectural - Glazing | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | At this time of writing no offsite manufacture ITP submitted or approved for Suppliers __ __ Colt
| 02SL - Stations (LUL) | Cxxx-NCR-002064 | NCR | __X + NLL - Architectural Movement Joints |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-10-10 | 2018-10-12 08:41 | 2 | 2018-05-11 14:02 | Architectural - Brickworks/Blockworks | 750 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Further to Cxxx-FCD-002245, 2 locations of blockwork have been identified as not having a movement joint installed over a structural movement joint. Upstands and bottom of blockwork are showing evidence of cracking already.
| 02SL - Stations (LUL) | Cxxx-NCR-002065 | NCR | __- Supplier proceeding fabrication without approved MCR |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-07-11 | 2019-02-01 10:26 | 205 | 2018-05-14 10:12 | Architectural - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | MCR for PPOC triangulated cladding is not approved by CRL at this time.
| 02SL - Stations (LUL) | Cxxx-NCR-002066 | NCR | Grid line W CMS Cladding support clash |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-02-21 | 2019-03-26 12:29 | 33 | 2018-05-17 12:55 | Architectural - Finishes | 5000 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | Along Grid line W there is a clash between the supporting steel work and the CMS. The CMS was installed prior to the cladding design as it was behind on programme, the cladding design developed and install is now clashing with the CMS.
| 02SL - Stations (LUL) | Cxxx-NCR-002067 | NCR | __ fan frame calculation/installation |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2021-02-18 | 2020-02-06 11:27 | -378 | 2018-05-18 07:34 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Design | Reject | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | The FAN frame Calculations submitted on eB do not reflect the installed framework. This NCR is to capture this Non conformance
| 02SL - Stations (LUL) | Cxxx-NCR-002068 | NCR | Platform Cabinets and Totem Bases |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-11-30 | 2018-10-03 12:36 | -58 | 2018-08-28 15:20 | Architectural - Flooring | 2000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Management Problem - Other management problem | Completed |  | Required evidence not produced. (Torque Readings)
| 02SL - Stations (LUL) | Cxxx-NCR-002069 | NCR | ES6 Broken Glass |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-08-02 | 2018-10-04 12:27 | 63 | 2018-05-21 10:51 | Architectural - Glazing | 1000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | A glass was broken belonging to ES6
| 02SL - Stations (LUL) | Cxxx-NCR-002070 | NCR | ES6 Glass Installation - Defect |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-08-02 | 2018-07-11 12:02 | -22 | 2018-05-21 10:44 | Architectural - Glazing | 1000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The glass on the South elevation was installed 15mm too far North. See attachment. This has a knock on effect to inspection and handover of area to SEELE/ __
| 02SL - Stations (LUL) | Cxxx-NCR-002071 | NCR | MTH. Waterproofing on the Southern Penisular on findings of NCR 002055 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-06-18 | 2018-06-22 09:03 | 4 | 2018-05-21 11:42 | Civil - Civil Engineering General | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | Further to NCR 002055. We decided to remove the remainder of the stainless steel protection for the rest of the Southern Penisular area and visually re check and spark test to confirm that no more damage to the waterproofing layer was done during the removal of the temporary protection slab. The removal of the stainless steel plate and retesting however did reveal that further damage was caused in several areas of the waterproofing.
| 02SL - Stations (LUL) | Cxxx-NCR-002072 | NCR | Difficulties in fitting the Platform PAEE |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-08-31 | 2019-07-23 14:09 | 326 | 2018-05-25 06:48 | Architectural - General | 5000 |  | Design | Repair | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | During installation of the first PAEE frame it has become apparent that the level of design coordination achieved and tolerances available within the space proofing constraints is causing installation difficulties.
| 02SL - Stations (LUL) | Cxxx-NCR-002073 | NCR | ES6 STO system noticed issues |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-08-06 | 2018-06-24 20:35 | -43 | 2018-05-25 13:07 | Architectural - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Previous Construction - Interfacing issues | Completed |  | Two issues were flagged on inspection. 1. 20 mm packers were used behind STO helping hand bracket (Not shown on drawing). 2. Some brackets were rotated 180 degrees ( facing the same direction as other brackets, not shown on the drawing).
| 02SL - Stations (LUL) | Cxxx-NCR-002074 | NCR | __X FFO PAD BAL-208A Balustrade oversailing wall |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-09-30 | 2019-03-22 11:01 | 173 | 2018-05-30 09:23 | Architectural - Balustrade | 750 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | PAD's handrail in the Blomfield Box maintenance stairs has two issues on street level -1. On one side the handrail over sails the blockwork wall and sticks out - meaning someone could catch themselves on it (DSCF2392.JPG). The same issue occurs on the other side of the stairs and comes as a result of the concrete line being further back than anticipated (DSCF2391.JPG).
| 02SL - Stations (LUL) | Cxxx-NCR-002075 | NCR | __ - Supplier documentation |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-08-11 | 2018-11-22 10:45 | 103 | 2018-05-30 09:55 | Architectural - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | __ commencing VE triangular panels without full MCRs for all materials that make up the panel.
| 02SL - Stations (LUL) | Cxxx-NCR-002076 | NCR | Proceeding without CRL approval of subcontractor documentation |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-09-08 | 2018-12-14 16:21 | 97 | 2018-06-27 07:29 | Architectural - General | 500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Steelwork has been installed to the Moorgate shaft. __ are currently installing louvers to the east elevation onto this steelwork. This is without approval of • Offsite manufacture ITP – for __ Steelwork • MCR for steelwork for __ Steelwork - Cxxx-LAO-O4-XDS-C101-50816 is only a placeholder
| 02SL - Stations (LUL) | Cxxx-NCR-002077 | NCR | MTH (Street level) Damaged FloorTiles |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2018-09-07 | 2018-08-07 10:17 | -31 | 2018-06-27 12:59 | Civil - Civil Engineering General | 2000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Floor tiles installed at street level within Moorgate Ticket Hall have been damaged. Attached picture (ref: 7524) demonstrates the damage caused to one of these tiles.
| 02SL - Stations (LUL) | Cxxx-NCR-002078 | NCR | PLT - GAD1&2 - Foam Concrete within design strength but below target strength specified on ITP |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-12-31 | 2018-09-16 20:06 | -106 | 2018-07-03 12:36 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Other human error | Completed |  | Foam concrete for AS1 addits (GAD 1&2) has 17no. 28 day strength result between 0.7N\mm2 and 1N\mm2. This is above design requirements of 0.5N\mm2 does not achieve the target ITP strength 1N\mm2 set out in the Cxxx-LAO-O4-ITP-C101-50104.
| 02SL - Stations (LUL) | Cxxx-NCR-002079 | NCR | Installing cable prior to CMS sign off |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-08-01 | 2018-10-29 13:02 | 89 | 2018-07-04 07:50 | Electrical - Cable Management | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Installing LV cabling prior to CMS IRF sign off
| 02SL - Stations (LUL) | Cxxx-NCR-002081 | NCR | ES2 and ES3 GRC Cladding Brackets |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-09-30 | 2018-12-17 12:57 | 78 | 2018-07-06 10:40 | Architectural - General | 7000 |  | Design | Repair | 2 (6-60k) | Complete | Previous Construction - Problems based on previous construction errors | Completed |  | The GRC cladding brackets for ES2 and ES3 do not have sufficient adjustment to cope with the as-built SCL position.
| 02SL - Stations (LUL) | Cxxx-NCR-002082 | NCR | BTH + TUN, Radio Cable CMS install, cabling prior to Inspection/sign of CMS |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2019-05-31 | 2019-09-20 13:52 | 112 | 2018-07-09 09:56 | Electrical - Cable Management | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | It has been noted that cabling of the radio system has commenced prior to inspection and sign off of CMS installation within BTH and also Platforms and tunnels areas. In addition there is no specific design for the installed radio CMS, in has also been identified that the installed CMS is not adequate/fit for purpose for the cable installed. These issue was previously raised and associated NCR - Cxxx-NCR-002056 for the same issue in __X.
| 02SL - Stations (LUL) | Cxxx-NCR-002083 | NCR | MTH - Breaking out a section of Lift 1 for __ Cladding |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-09-29 | 2018-11-21 14:32 | 53 | 2018-07-17 09:40 | Civil - Structural Engineering | 3000 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | There is a design clash with the installation of the __ steel support for the lift cladding at the designed location of the concrete walls on lift 1 at Moorgate ticket hall. With reference to drawing Cxxx-LAO-A-DDD-C101_1-20321 and also the attached mark ups and photos.To overcome the problem on site the supervisor and operatives have chased out a section of the wall to make fit. This was done without prior approval from the design team. The steel work has been installed within the chased out section, however Flexcrete 851 product has not been installed on the area now with reduced concrete cover.
| 02SL - Stations (LUL) | Cxxx-NCR-002084 | NCR | BTH - AP2 high level CMS not installed to accepted design |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2018-10-15 | 2019-03-05 12:05 | 141 | 2018-07-18 09:23 | Electrical - Cable Management | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | High level CMS within the tunnel crown at AP2 has not been installed as per current agreed construction drawings. Accepted design identifies 2no. 3 compartment trunkings and 100mm tray for radio cable install to be installed at high level. 2no. trunkings have been installed without adequate spacing left to install the Radio tray.
| 02SL - Stations (LUL) | Cxxx-NCR-002085 | NCR | MSH FFO ESS1 & ESS2 PAD Handrail over sailing structure |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-11-16 | 2018-11-16 09:07 | 0 | 2018-08-22 11:34 | Architectural - Handrail | 2500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | In Moorgate Shaft ESS1 and ESS2 there are 6 locations where PAD's handrail is over sailing the structure - please see attached photos. Modifications are required to ensure the handrails are fully supported.
| 02SL - Stations (LUL) | Cxxx-NCR-002086 | NCR | Sump Pump Control Panels |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2018-11-30 | 2019-10-23 10:36 | 327 | 2018-07-24 07:04 | Mechanical - Pumps | 10000 |  | Design | Repair | 2 (6-60k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | Sump pump control panels have been assessed through the MCR process as fire code F2 (CRL-MCR-006013). The panels are therefore required to be installed within a fire compartment less than 200m3 that is also equipped with fire detection. Certain of these panels have been installed off the platform ends in areas greater than 200m3 which don't have fire detection. It should also be noted that the panel locations cause red and green lamps to be displayed to train drivers which has previously been advised as not acceptable.
| 02SL - Stations (LUL) | Cxxx-NCR-002087 | NCR | TUN - BWK - CP9 change point incorrect |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-09-30 | 2018-11-13 14:48 | 44 | 2018-07-27 08:26 | Architectural - Brickworks/Blockworks | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | See attached RFI 5964 from asite and associated sketches. 1st stage construction of wall in CP9 resulted in the change point being built 140mm closer to the track than required. This would have encroached on __ platform endwall cladding zone. Once the issue was identified (during 2nd stage of wall construction to the track edge) __ remedial was to cut back the blockwork to the required change point. Upon LU inspection, it was flagged that cutting back of blockwork had violated 60min fire rating between spaces 8/261 and 8/243.
| 02SL - Stations (LUL) | Cxxx-NCR-002088 | NCR | __X - Lining Wall out of tolerance |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-08-27 | 2018-08-03 12:32 | -24 | 2018-07-30 15:39 | Shafts - Linings | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During asbuilt of blockwork walls in __X, it was identified that lining wall on P+1.5 is locally 12090mm wide. The design width is 12600mm wide. Tolerances in this area are in the region of 175mm (1/200 out of alignment plus setting out error). The lining walls are therefore each 80mm out of tolerance.
| 02SL - Stations (LUL) | Cxxx-NCR-002089 | NCR | Fabrication ITP not being accepted prior to works commencing for Finsbury Gantry Steelwork |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-08-29 | 2018-08-13 12:34 | -16 | 2018-08-01 16:29 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Installation works for Finsbury Gantry Steelwork started before Fabrication ITP was accepted. However, Installation ITP was in place and accepted
| 02SL - Stations (LUL) | Cxxx-NCR-002090 | NCR | Cat 6a Cables exceeding 90m requirement |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-02-03 | 2019-06-24 11:59 | 141 | 2018-08-03 09:11 | Communications and Control Systems - Crossrail Data Network | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Upon completion of installation, cat 6a cameras have exceeded the 90m requirement. See below lengths of cable: CAM-0210 – Cable ID – M135-DAT-04364 – Cable length -104.3m – Failed CAM-0216 – Cable ID – M135-DAT-04363 – Cable length -101.3m – Failed
| 02SL - Stations (LUL) | Cxxx-NCR-002091 | NCR | BTH ES1 North wall PPC clading |  | Crossrail | PDP | LIS - Liverpool Street Station (Central) |  | 2019-08-31 | 2019-11-07 17:01 | 68 | 2018-08-06 10:28 | Architectural - General | 20000 |  | Damaged | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Top edge tech screw fixings to secure triple segment part perforated high level feature PPC paneling in North Face of ES1 to top hat support framework, have badly damaged the slotted holes designed for this purpose. These defects appear to compromise the performance requirements within the WI for robustness, life expectancy, regular demountability for maintenance oprurposes and blast resistance. See attached images for details.
| 02SL - Stations (LUL) | Cxxx-NCR-002092 | NCR | Fire rated duct supports |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2019-08-12 | 2021-04-01 08:17 | 598 | 2018-08-08 11:32 | Mechanical - Heating Ventilation & Air Conditioning | 5999 |  | Incorrect Installation | Use As-Is | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | CRL have recently been offered IRF packs for bracket upgrades to fire rated ductwork installed through CP9 & 10 and AP1. The packs contain no drawings or details of the new "upgraded" brackets that are being offered for inspection. The __ __ inspection pro-forma Q6 included to the IRF packs records the brackets to be in accordance with __ Table 12. Reference to this table shows the brackets as being “40x80 SC M16” with a note “Ref. Fig. 58 for support details M16 studding”. This is the only information made available for the works offered to be assured against. From site inspections it was noted that the installations are not in accord with __ figure 58, HUS fixings have been used and not the "anchors" as drawn however, we accept the current assurances of Cxxx that __ have approved the substitute fixing type. The drawn detail requires these fixings to be M12 whereas M10 have been installed, the detail also requires RSC soffit brackets whereas PFC has been used in most cases. It was also noted that fixing embedment depth varied and that many of the fixings are installed at a significant angle both which reduce the fixing's capacity. Photographs attached..
| 02SL - Stations (LUL) | Cxxx-NCR-002093 | NCR | Skirting alignment / protrusion |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-09-24 | 2018-09-21 07:21 | -3 | 2018-08-09 10:12 | Architectural - Flooring | 1000 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | The skirting which is protruding out from the design line/line of GFRC. This appears to be an error in the manufacturing of the skirting.
| 02SL - Stations (LUL) | Cxxx-NCR-002094 | NCR | Temporary Services Behind GFRC Cladding |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-03-31 | 2019-08-21 08:17 | 143 | 2018-08-09 11:34 | Architectural - General | 2000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | GRC cladding panels installed with temporary services still in the cavity behind. The temporary services cables in some instances are also running behind the cavity barriers, refer to the attached photos, which may need to be remediated when the cables are removed.
| 02SL - Stations (LUL) | Cxxx-NCR-002095 | NCR | AP8 VE Cladding |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-10-31 | 2019-02-05 09:03 | 97 | 2018-08-13 14:18 | Architectural - Glazing | 3000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The VE panels installed in AP8 at Broadgate look a bit wavy and when hit there is a drumming effect and they also deflect considerably. With reference to the Cxxx Architectural Specification Addendum Cxxx-LAO-A-RSP-C101_WS103-50001 , clause IWS-719, JK17.1217 which mentions a backing material that "shall be agreed upon to achieve flatness and structural requirements" and clause JK17.1409 which also mentions +/-2mm tolerance, with recognised metal fabrication methods, with flatness in accordance to "EN 14431 or better but is dependent on panel design and backing material selected", the installed panels do not appear to meet the requirements of the specification.
| 02SL - Stations (LUL) | Cxxx-NCR-002096 | NCR | BTH - BWK - Lintels |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-10-15 | 2018-09-21 07:27 | -24 | 2018-08-15 16:50 | Architectural - Brickworks/Blockworks | 10000 |  | Design | Rework | 2 (6-60k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | See attached drawings 25750, 25751, 25752 and 25765 from the Cxxx blockwork setting out information. See also attached drawing 63142 from the Broadgate cladding setting out information for inward opening doors. Blockwork is FFL+2500 on the blockwork drawings, and +2600 on the cladding drawings. The inward-opening doors will clash on the blockwork lintels if left where they have been built.
| 02SL - Stations (LUL) | Cxxx-NCR-002097 | NCR | TUN - Cutting of Structural Concerte in AP5 to allow for Installation of GRC Frame Member |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2018-11-23 | 2018-10-16 13:57 | -38 | 2018-08-16 12:51 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | At the intersection of AP5 with Moorgate shaft a section of concrete has been cut to allow for installation of a GRC frame member. See attached photograph (Ref:101_7987)
| 02SL - Stations (LUL) | Cxxx-NCR-002098 | NCR | MTH. Missing concrete cube results - LST014 23/3/18 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-09-14 | 2018-09-19 12:20 | 5 | 2018-08-17 07:54 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | A set of concrete cubes for pour no LST 014 - Moorgate SOR room ref with SCC Cxxx-LAO-C-LRC-C101_WS099-50242 have been misplaced between site and __ testing therefore we have no concrete cube strength conformation for this pour. Please note that a this time of construction the main civils work has been completed and there was no other concrete poured on this day. The concrete pour with the missing cubes was a total of 3m3.
| 02SL - Stations (LUL) | Cxxx-NCR-002100 | NCR | Moorgate Shaft Louvre Site inspection |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-09-21 | 2019-05-16 14:44 | 237 | 2018-08-24 17:59 | Architectural - General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Bottom central panel is not installed to correct level resulting in an alignment issue between all adjacent panels. The gap is approximately 10mm as can be seen in the photos.
| 02SL - Stations (LUL) | Cxxx-NCR-002101 | NCR | Installation of PAEE commenced before ITP approval |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-10-26 | 2018-09-11 16:27 | -45 | 2018-08-24 18:03 | Architectural - General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | The installation of the PAEEs commenced on site prior to the ITP
| 02SL - Stations (LUL) | Cxxx-NCR-002102 | NCR | Kerb Installation - Damage to Installed Units |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-10-31 | 2021-05-17 14:43 | 929 | 2018-08-20 09:26 | Architectural - General | 2500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Damage has been sustained to some of the kerb units installed
| 02SL - Stations (LUL) | Cxxx-NCR-002103 | NCR | GFRC Cladding - Minor Repairs/Making Good |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-11-30 | 2021-05-17 10:52 | 899 | 2018-08-20 09:44 | Architectural - General | 4000 |  | Damaged | Repair | 3 (3-6k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Minor damage to the GFRC cladding panels site wide requires repairing/making good
| 02SL - Stations (LUL) | Cxxx-NCR-002104 | NCR | Escalator Deck Cladding |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2019-03-14 | 2019-05-28 09:41 | 75 | 2018-08-20 14:23 | Architectural - Finishes | 2500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | ES6 Escalator Deck Cladding & Trim and Deck Light An escalator deck light on ES6 was presented for review. It was noted that exposed edges to the escalator deck cladding (at interface with deck lights, see photo 2) and angle trim (adjacent and parallel to escalator handrails, see photo 1) have not been sufficiently arrised/rounded (as required under Cxxx spec. clause JA.6511 and Cxxx spec. clause JA.6510). As such the edges are sharp. There is a risk that customers on moving escalators will cut their hands when touching the sharp edges. The sharp edges were reviewed at the location of the proposed deck light benchmark on ES6. However it is assumed that all decking and side trim that has been installed to all escalators throughout the station may contain sharp edges. Therefore all installed deck cladding should be checked by Cxxx to identify any sharp edges that requires remedial work. Prior to executing remedial works throughout (if required), Cxxx are to provide a benchmark for site remedial works for Crossrail agreement and approval. The benchmark for the deck light itself also contains sharp edges to the outside perimeter of the trim. This can be noted on the rejected benchmark for the deck light as a separate exercise to this NCR.
| 02SL - Stations (LUL) | Cxxx-NCR-002105 | NCR | energisation of submains cables with no IRN in place |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2018-11-30 | 2019-08-10 21:33 | 253 | 2018-08-22 11:29 | Electrical - Power Distribution | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Supplies to the Cxxx VCDs were energized without an IRN in place, in addition no pre energisation check list had been signed for these cables in line with CTP.
| 02SL - Stations (LUL) | Cxxx-NCR-002106 | NCR | TUN - GFRC twisted braces and temporary service behind fire break |  | Crossrail | PDP | LIS - Liverpool Street Station (Central) |  | 2019-01-29 | 2019-02-25 13:10 | 27 | 2018-08-22 11:11 | Architectural - General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | The bracing to the support framework for the GFRC to one panel in CP6 is distorted beyond repair and should be replaced, see attached photo. A temporary service air hose has penetrated the fire break and needs to be removed and made good, also in attached photo.
| 02SL - Stations (LUL) | Cxxx-NCR-002107 | NCR | TUN. Storage of site cubes |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-10-12 | 2018-09-19 10:33 | -23 | 2018-08-23 15:27 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | During a site quality walk about it has been correctly noted that the concrete cubes have not be stored correctly in line with BSEN-12390-2, Specification for Civil and Structural Works Section KF10 - Insitu Concrete or the approved site concreting ITP. Numerous faults have been found which required rectifying thus being: 1. There where several concrete cubes which where being stored out side the cube tank. The cubes where labeled with the days all exceeding 3 days since cast 2. The record of the concrete temperature on the cube tank is outside the allowable clause of 20deg+/- 2deg. (Recorded 23dag and 24 deg) 3. The monitoring of the cube tank temperatures was not consistent. 4. Many of the dates on the concrete cubes exceeded 7 days since cast therefore 7 day cube results will not be available for these cubes. 5. Calibration certificates was not available at the time of request
| 02SL - Stations (LUL) | Cxxx-NCR-002108 | NCR | Grilles and Diffusers |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2018-01-31 | 2019-02-27 08:22 | 392 | 2018-08-28 14:04 | Mechanical - Heating Ventilation & Air Conditioning | 30000 |  | Material | Repair | 2 (6-60k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | Following the recent request for inspection of a benchmark for the installation of a ceiling mounted diffuser the following items were noted as not according to the specifications. It is also noted that despite no approval of the benchmark similar non-compliant installations are proceeding. •JY46.1301 (h) The Contractor shall provide a method statement and details to the Project Manager outlining the final fixing methods and details of all grilles, diffusers and louvres prior to installation. No such information has been provided •JY46.1301 (m) Grilles and diffusers visible in rooms shall be secured by concealed fixings wherever possible. Concealed fixings are available, there is no need for through flange fixings. •JY46.1301 (o) Visible grilles and diffusers shall be secured by concealed fixings wherever possible. Units shall be capable of being easily cleaned by having faces readily accessible or by removable centre cores as indicated. Internal faces are not readily accessible and cores are not removeable. •JY46.1304 Ensure an electrical bonding terminal suitable for connection of 6 mm2 maximum conductor is provided on metal grilles, diffusers. No such stud is evident •JY46.1305 b) Diffusers constructed of extruded aluminium shall be anodized to a colour acceptable to the Project Manager. Grilles and diffusers are bare mill finish. •JY46.1305 (d) Diffusers shall be equipped with aluminium or steel opposed blade volume control dampers of black colour with concealed adjustment lever. No such dampers are fitted. •JY46.1305 (f) Diffusers’ rings or frames shall be compatible with the ceiling construction in which they are installed….Internal parts shall be removable to permit cleaning of the diffuser and provide access to the duct. Specific diffusers are available from all manufacturers to suit the __ 150 ceiling installed, these have not been used. Also internals are fixed not removable such internal cleaning is precluded •JY46.1305 ( i) Diffusers with ducted connections shall be provided with plenum boxes selected and fabricated by the diffuser manufacturer to match the output of the diffuser. Plenums are not from the diffuser manufacturer and have also been cut down. •JY46.1306 (f) All grille cores shall be capable of being removed easily from the ductwork for access to dampers. Cores are not removable
| 02SL - Stations (LUL) | Cxxx-NCR-002109 | NCR | TUN - GAD 1&2 - Non UKAS accredited lab used for 4No. foam concrete pours |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-12-29 | 2018-09-12 09:06 | -108 | 2018-08-29 16:19 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | The concrete cube testing company used by __ Ltd. for the first 4No. pours of the grout addits foam concrete infill's has been found to be no longer UKAS accredited. The company ceased to be UKAS accredited on 22nd August 2017 and cubes were tested 03-06 April 2018. The eight number cubes which were tested by the non UKAS accredited laboratory have results consistent with the 42No. subsequent tests carried out by the subcontractors UKAS accredited laboratory - see attached spread sheet.
| 02SL - Stations (LUL) | Cxxx-NCR-002110 | NCR | Scratched panels along the South elevation of ES1 -67a |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-11-23 | 2018-11-05 10:50 | -18 | 2018-09-03 09:29 | Architectural - General | 2000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | One of the benchmark plain grey PPC panels appears to have three areas which have been “ treated” in some way which can be seen as patches under the right light. It seems that remedial works to spray scratches have been progressed without formal approval of MCR. If there are damaged panels they should either be selected out before installation and inspected for Crossrail to determine if the defects can be accepted or to agree any repairs protocol prior. See attached picture of treated area.
| 02SL - Stations (LUL) | Cxxx-NCR-002111 | NCR | Damaged panels along the North elevation of ES1 -67a |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-12-20 | 2019-10-24 12:09 | 308 | 2018-09-03 09:46 | Architectural - General | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | 1. North Elevation high level perforated s/s panels are showing distortion such as a bend in the mid of panel - See attached picture (20180809) of the mid panel where a vertical “bowing/fold” visible in some of the high level panel. 2. There is a panel with a circular dent. Please confirm the reason for this. 3. Area of matt finish patchiness to r/h side of high level plain panel and mark to perforated panel below. See attached marked up photo (Scan 10082018). All three above are visible under the current lighting conditions and may not be under the permanent condition. Still a preventive measure must be taken for works ongoing.
| 02SL - Stations (LUL) | Cxxx-NCR-002113 | NCR | __X FFO - Floor Access Hatch into Plenum - Fire Rating / Pressure Rating |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-10-28 | 2018-09-23 14:58 | -35 | 2018-09-04 16:51 | Fire - Compartmentation | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | A floor access hatch (E-01-238-A02) was installed in the __ plenum which is not certified to achieve a fire or pressure rating as per the access hatch schedule.
| 02SL - Stations (LUL) | Cxxx-NCR-002114 | NCR | TUN - Incorrect Floor Level in AP10 |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2018-12-21 | 2018-11-21 09:06 | -30 | 2018-09-06 15:33 | Civil - Civil Engineering General | 6000 |  | Supervision/Management | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the tiling and door installation works within AP10 it has become apparent the floor is out of level. As a consequence part of the tiling, doors and frames have been removed see attached pictures (8117, 8117 and 8119).
| 02SL - Stations (LUL) | Cxxx-NCR-002116 | NCR | Lift 2: Shaft wall builders work hole: Clash with Cladding |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-11-30 | 2018-11-29 08:31 | -1 | 2018-09-11 09:35 | Civil - Civil Engineering General | 5000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The builders work for the services entering lift shaft 2 at Street Level -1 has been formed below the suspended ceiling rather than above it. It is not clear why it was formed in this location as it is not shown on the structural drawings, as such it can only be attributed to a setting out error.
| 02SL - Stations (LUL) | Cxxx-NCR-002117 | NCR | __X - Platform Extract Discharge - repeat failure of air pressure test |  | Crossrail | PDP | LIS - Liverpool Street Station (Central) |  | 2019-01-31 | 2019-04-30 14:14 | 89 | 2018-09-12 11:01 | Mechanical - Heating Ventilation & Air Conditioning | 5999 |  | Testing and Commissioning | Repair | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The __ Platform Extract Discharge shaft (SID number A, B, C, D/820) has failed to meet the requirements for air pressure tests, as per JY30.2202. CRL have been invited to witness a number attempts at carrying out the pressure tests since the beginning of the year, the latest attempt was carried out on Monday 10th September 2018.
| 02SL - Stations (LUL) | Cxxx-NCR-002118 | NCR | Escalator Brackets for Interface CMS ES5 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-12-31 | 2019-04-09 15:20 | 99 | 2018-09-13 10:25 | Mechanical - Escalators | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | The interface brackets designed to support the CMS for the deck lights and speakers have been installed incorrectly in the location of the scaffold standard support posts. As a result, the CMS has been installed too close to the scaffold posts obstructing the posts.
| 02SL - Stations (LUL) | Cxxx-NCR-002119 | NCR | bbx emergency lighting not installed in line with latest CO drawing |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2019-02-28 | 2019-12-12 13:45 | 287 | 2018-09-17 08:34 | Electrical - Lighting | 30000 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The emergency lighting within __ has not been installed inline with current CO drawing which shows fire rated boxes where the emergency lighting circuits pass from rooms to corridors in the same area, this was raised as an issue under EWN Cxxx-EWN-01566 Cxxx design manager has stated this will be complete after project completion which is not acceptable.
| 02SL - Stations (LUL) | Cxxx-NCR-002120 | NCR | bus duct installation |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2019-03-31 | 2019-02-27 15:01 | -32 | 2018-09-19 09:23 | Electrical - Power Distribution | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | During an IRF inspection of the BUS duct installation numerous issues were raised on the install against the manufactures requirements, main issues being brackets spacing and lack of fixings clips to the bus duct. this was inspected by the installation team on completion of install and a statement issued that the installation was in line with manufacturer's requirements which was not the case, in addition these items were not raised by Cxxx prior to this inspection.
| 02SL - Stations (LUL) | Cxxx-NCR-002121 | NCR | Cleaning of BTH ductwork system |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-11-26 | 2019-07-01 14:19 | 217 | 2018-09-21 07:51 | Mechanical - Heating Ventilation & Air Conditioning | 2000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | System hygienics have stated the Broadgate Ductwork system has been cleaned, after inspection it was found that some areas of the ductwork still contains a level of dust Photos attached.
| 02SL - Stations (LUL) | Cxxx-NCR-002122 | NCR | Damage to PES glazing on Eastbound Platform between CP8 and CP10 |  | Crossrail | PDP | LIS - Liverpool Street Station (Central) |  | 2019-03-01 | 2018-12-03 13:42 | -88 | 2018-09-21 11:13 | Architectural - Glazing | 5000 |  | Damaged | Rework | 3 (3-6k) | Complete | Personnel Error - Other human error | Completed |  | CRL FE __ witnessed glass PES screen had been damaged on the EB platform between CP8 and CP10 (east end). Damage has been notified to Cxxx who have been requested to attend site asap to review assessment of damage. Glass has shattered but remains in place. It is clear that something has been pulled along as the cordex is ripped/scratched at the same level as the initial damage for some length which is also concerning. The plyboard walkway where materials are moved is also less than 500mm from the glass door in this area.
| 02SL - Stations (LUL) | Cxxx-NCR-002123 | NCR | TUN – Installation of PES Grill Mesh without an MCR |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2019-05-31 | 2019-07-18 11:42 | 48 | 2018-09-24 08:16 | Civil - Civil Engineering General | 5000 |  | Material | Use As-Is | 3 (3-6k) | Complete | Management Problem - Other | Completed |  | The PES Grill Mesh has been installed on both east and west bound platforms prior to issuing of MCR documentation to CRL for the product.
| 02SL - Stations (LUL) | Cxxx-NCR-002124 | NCR | Proceeding works without Steelwork Documentation |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-01-14 | 2019-05-09 14:07 | 115 | 2018-09-25 11:48 | Architectural - General | 5000 |  | Documentation and Records | Use As-Is | 3 (3-6k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | __ went into steelwork fabrication with various suppliers without appropriate approved ITP and MCRs in place. Suppliers include: __, __, __, __ and __. This is a non-conformance to sections 20.8 (ITP) and 13.3.8 (MCR) of the Works Information Volume 2B – Part 20.
| 02SL - Stations (LUL) | Cxxx-NCR-002125 | NCR | __ grout cubes not stored in accordance with EN 12390-2:2009 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-01-30 | 2019-01-14 10:10 | -16 | 2018-09-26 19:12 | Structural Engineering - Grouting | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | The grout/concrete cubes on W/B platform adjacent to CP5 were found, possibly made in a timber moulds (see email from __). These have been stored incorrectly by __ on site for a long period, thereby not adhering to clauses 5.5.1 and 5.5.2 of EN 12390-2:2009.
| 02SL - Stations (LUL) | Cxxx-NCR-002126 | NCR | Smoke downstands installation without approved Benchmark in place |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-05-31 | 2019-04-17 13:18 | -44 | 2018-09-27 12:12 | Materials - Approval | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | __ have progressed with the installation without formal benchmark signoff for the smoke downstands at Platform level. The reason for the Benchmark not taking place is due to pending approval of the fixing used in the SCL. The MCR for __ Bolts for Concrete - Cxxx-LAO-O4-XDS-C101-50815 has been Code 1, but the fixing is not yet approve to be used into SCL. This has been raised in an RFI Cxxx-RFI-004491. HA rework - 20/12/18: Cxxx-RFI-004491 has been accepted. The drawings have been revised to show fixings proposed on the RFI. The Pullout test reports have been submitted within the RFI-004491. The Benchmark IRF will be issued as soon as the appropriate paperwork is ready.
| 02SL - Stations (LUL) | Cxxx-NCR-002127 | NCR | Damages to VE Cladding Finish |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-01-31 | 2020-10-20 14:42 | 628 | 2018-10-01 11:20 | Architectural - General | 3000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper handling of material | Completed |  | The Vitreous Enamel panels in the below areas are damaged. It is not clear if the damage has been caused in delivery, Handling or if this is Manufacturing issue. • BTH Damage VE panels 22a & 23a • PRM corridor damage VE panels 65a Please see attached pictures of the damages identified.
| 02SL - Stations (LUL) | Cxxx-NCR-002128 | NCR | Air Ducts and ancillary equipment storage |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2018-10-29 | 2018-11-05 12:23 | 7 | 2018-10-01 13:18 | Materials - General | 45000 |  | Supervision/Management | Reject | 2 (6-60k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Despite several NCR's on the subject air ducts and ancillary equipment including MAP smoke dampers are again stored outside and open to the elements. Specification JY30.1423 requires ductwork to be in accord with HVCA document TR/19 to PDI level 2 which under 2.14.1 the storage area is defined as "...shall be permanently clean, dry and dust free..." The required storage facilities are not being provided allowing potential deleterious effects to the incorrectly stored materials especially the 240v electric equipment fitted to the MAP dampers.
| 02SL - Stations (LUL) | Cxxx-NCR-002130 | NCR | Installation of cabling without appropriate MCR |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-01-17 | 2019-01-09 09:30 | -8 | 2018-10-03 07:10 | Electrical - LV Equipment | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other management problem | Completed |  | Installation of cabling in Northern line link without appropriate MCR
| 02SL - Stations (LUL) | Cxxx-NCR-002131 | NCR | __ Pump Motors |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-12-18 | 2018-11-29 14:16 | -19 | 2018-10-10 12:53 | Mechanical - Pumps | 2999 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | __ have supplied pumps, in 2015, with different motor connections for the BMS connections, to that which was ordered by Cxxx. __ have visited site and have accepted liability for the fault. The motors will be changed by __, with no adaptions necessary to the main pump body or the pipework connected to it. Minor wiring may be necessary.
| 02SL - Stations (LUL) | Cxxx-NCR-002132 | NCR | TUN - Delta Fabrication - BOH Screens - Works commenced prior to documentation sign off |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-01-31 | 2018-10-14 14:50 | -109 | 2018-10-10 12:41 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other management problem | Completed |  | Platform Ends Westbound West and Eastbound East BOH of house screen installation commenced prior to documentation being signed off.
| 02SL - Stations (LUL) | Cxxx-NCR-002133 | NCR | Oil leak on finished tiles BTH |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-02-24 | 2018-12-13 10:41 | -73 | 2018-12-06 09:33 | Architectural - Flooring | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | This NCR has been raised to cover the oil leak that potentially has leaked through the protection onto the tiles.
| 02SL - Stations (LUL) | Cxxx-NCR-002134 | NCR | MSH - Damaged Concrete Precast Soffits GL10.5/Z |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-01-01 | 2018-12-03 13:21 | -29 | 2018-10-17 11:21 | Architectural - Ceilings & Soffits | 1500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | As per attached from __ and location plan 22806. Damaged precast plank on MTH GL 10.5 and GLZ. PG notes 13/11/2018 - PPC have now completed repairs. Please see attached photographs. Please pass to review stage. Review on top of AAR2 hoarding will require LU interface permit through __.
| 02SL - Stations (LUL) | Cxxx-NCR-002135 | NCR | Site Wide FFO BAL-208+BAL-110+BAL-111 Mid-Handrail Heights - PAD |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-04-30 | 2019-05-20 13:28 | 20 | 2018-10-15 09:22 | Architectural - Balustrade | 15000 |  | Design | Repair | 2 (6-60k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | An investigation was conducted following comments from CRL/LU that PAD's handrail heights for the mid-rail should be 600mm from the nosing line to the top of the rail. Instead PAD have been working to the centreline of the rail which means that the rails are 24mm too high to be in compliance with BS 8300. This was queried back to the design team (__) who have responded (see attached RFI response). Their view is that the handrails are in compliance with DFT-COP and PMR which allows a range of heights from 500-750mm for this rail. Areas which are affected by this dimension are as follows: MSH - ESS1, ESS2, AP5, PRM Ramp MTH - EB and WB stairs NLL - AP10 __X - ESS1 and ESS2 BTH - AP8
| 02SL - Stations (LUL) | Cxxx-NCR-002136 | NCR | TUN: GRC Panel / Support Framework Alignment Issue at CP3a – 4a Junction with Central Concourse |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2019-01-31 | 2018-12-03 15:10 | -59 | 2018-10-16 12:25 | Civil - Civil Engineering General | 15000 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the installation of the GRC panels at CP3a – 4a junction with the central concourse it has become apparent the alignment of the panels is not as expected. This has led to the removal of installed GRC panels in the location while dimensional surveys and design model checks are undertaken.
| 02SL - Stations (LUL) | Cxxx-NCR-002137 | NCR | GFRC Cladding - Oversize Gaps Between Cladding Panels and Infill Strips |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-09-30 | 2019-08-13 10:32 | -48 | 2018-10-19 07:30 | Architectural - General | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Occasional large gaps between cladding panels and infill strips
| 02SL - Stations (LUL) | Cxxx-NCR-002138 | NCR | Totems - Incorrect Lock |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-08-01 | 2018-12-17 15:54 | -227 | 2018-10-19 07:36 | Architectural - General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Works information (PMI 1200) stipulates the totem locks should be Euro profile if it is located below 2.5m AFFL
| 02SL - Stations (LUL) | Cxxx-NCR-002139 | NCR | BTH Precast Frieze |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-08-31 | 2019-09-05 09:54 | 5 | 2018-10-19 13:46 | Architectural - General | 3000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The height of the light from the bottom of the precast changed between P06 and C01, to 185mm from bottom of precast. This change was not coordinated with the adjacent precast soffit. Resulting in the light fixture being partially obscured. Please refer to CRL observation CRL-OBS-24669 (Scope: Global) and NCR Cxxx-NCR-002154. These items supersede this NCR.
| 02SL - Stations (LUL) | Cxxx-NCR-002140 | NCR | Installation of Moorgate Trumpet Steelwork commenced before ITP and RAMS approval |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-11-23 | 2018-11-04 22:14 | -19 | 2018-10-23 15:40 | Civil - Civil Engineering General | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | The installation of the Moorgate Trumpet Steelwork commenced on site prior to the ITP and RAMS being formally approved
| 02SL - Stations (LUL) | Cxxx-NCR-002141 | NCR | Installation of exane singles cabling prior to MCR approval AP 2 corridor . |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-11-23 | 2018-11-16 11:19 | -7 | 2018-10-26 13:17 | Electrical - LV Equipment | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | The NCR covers the installation of an Exane type of singles LV cabling prior to MCR acceptance . The Cabling has been installed for emergency lighting from an emergency DB and also Fire dampers from a Non Emergency board.
| 02SL - Stations (LUL) | Cxxx-NCR-002142 | NCR | Poor Quality Adaptable Boxes |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-12-21 | 2019-07-08 11:53 | 199 | 2018-10-29 15:08 | Communications and Control Systems | 500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Not Defined | Completed |  | Adaptable boxes have been installed that do not comply to IP4X on the BMS system, boxes that have been installed by L.B Fosters have split along the sides of the box. Believed to be a bad batch of adaptable box and investigation has been launch into damaged and potentially poor quality boxes installed in and around the site.
| 02SL - Stations (LUL) | Cxxx-NCR-002143 | NCR | MGS - damaged earth connection points. |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2018-12-11 | 2019-01-28 10:03 | 48 | 2018-10-31 11:25 | Electrical - Earthing & Bonding | 2000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Earthing connection points/cables installed at street level outside of Moorgate __S substation have been damaged ( insulation has been ripped).
| 02SL - Stations (LUL) | Cxxx-NCR-002144 | NCR | Air Conditioning - Installation of Incorrect Control Cables |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-02-28 | 2019-05-28 08:56 | 89 | 2018-10-31 15:13 | Electrical - Electrical Engineering General | 10000 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | This NCR is to cover the non conformance of the installation of the incorrect control cables on the Air Conditioning system. The correct cable should be FT120.
| 02SL - Stations (LUL) | Cxxx-NCR-002145 | NCR | ___AMF lack of assurance for welding |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-02-28 | 2019-03-28 07:51 | 28 | 2018-11-02 19:41 | Structural Engineering - Welding | 7500 |  | Documentation and Records | Use As-Is | 2 (6-60k) | Complete | Management Problem - Inadequate administrative control | Completed |  | __ have had steelwork elements fabricated by a supplier called AMF engineering. The supplier can not provide assurance for the steel in accordance with the welding standard of BS EN 1011, as specified in the architectural spec. (clause JZ11.0403 Mild Steel Fabrication and JZ11.0404 Stainless Steel Fabrication). Evidence of Welders qualifications, Welding procedure and weld inspection can not be provided. AMF ering’s scope is S/S brackets to PRM corridor (65A), S/S brackets to smoke downstands (41A), S/S brackets to ES1 north decline (67A 8 no. only) and Mild Steel steelwork to Westbound stairs (2A).
| 02SL - Stations (LUL) | Cxxx-NCR-002146 | NCR | ___Undersized welds to smoke downstands |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-05-15 | 2019-04-05 12:38 | -40 | 2018-11-02 19:48 | Structural Engineering - Welding | 3000 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | 30 no. of the 48no. B-1 S/S brackets supporting the smoke downstand screens were found to have undersized leg length. The specified leg length of these fillet welds is 5mm as shown on drawings Cxxx-LAO-A-DWG-C101-50410, Cxxx-LAO-A-DWG-C101-50411, Cxxx-LAO-A-DWG-C101-50412, Cxxx-LAO-A-DWG-C101-50415, Cxxx-LAO-A-DWG-C101-50420, Cxxx-LAO-A-DWG-C101-50426.
| 02SL - Stations (LUL) | Cxxx-NCR-002147 | NCR | AP6- Drill depth into SCL |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-02-28 | 2019-04-11 12:18 | 42 | 2018-11-09 21:09 | Civil - Structural Engineering | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | In AP6 / Northern Line Link, whilst installing the baseplates for one of the PAEE helppoints , 10 no holes have been drilled into the SCL for an M20 __ fixing, with 9 of the holes exceeding the permitted drill depth of 150mm. The maximum depth of these holes drilled on site was 230mm. The theoretical depth of the secondary sprayed concrete lining is 250 mm. The boroscope investigation that was carried out into each of these holes determined that there was no evidence of masterseal encountered, confirming that the waterproofing layer has not been breached. Can Cxxx also confirm that Cxxx (__) have oversprayed the depth of the secondary lining in this area. Which would mean that the depth of the secondary SCL lining is in excess of the theoretical 250mm.
| 02SL - Stations (LUL) | Cxxx-NCR-002148 | NCR | Fire rated ductwork sign off |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2020-08-07 | 2021-04-01 08:19 | 237 | 2018-11-14 13:43 | Mechanical - Heating Ventilation & Air Conditioning | 5999 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | CRL have been requested to undertake an inspection of fire rated ductwork brackets / supports fitted to platform smoke extract at platform -1 Moorgate shaft. An IRF pack 94A entitled "bracket Upgrade" was issued with the inspection request. The flameshield inspection sheet Q6 was completed and signed of by the __ __ inspector. The sheet correctly detailed the supports for this particular run of 1200 x 1200 ducting should be as Table 12 which in turn identifies soffit fixing as figure 58. Upon inspection it was found that the necessary table 12 M16 rods were not installed nor was the figure 58 soffit fixing. This NCR is for incorrect / incomplete works being offered for CRL inspection and to cover the specialist inspector signing off works as complete and compliant without undertaking any inspection contrary to his QA procedures.
| 02SL - Stations (LUL) | Cxxx-NCR-002150 | NCR | TUN - Installation of AP9 DripTray without an ITP |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2018-12-31 | 2019-03-25 14:59 | 84 | 2018-11-15 09:52 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | The drip tray in AP9 has been installed without an ITP. The ITP is currently only a placeholder on eB, Cxxx-LAO-O4-ITP-C101-50310.
| 02SL - Stations (LUL) | Cxxx-NCR-002151 | NCR | Deviation from design intent for __ +5 mesh screen |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-03-13 | 2019-03-15 08:51 | 2 | 2018-11-15 16:44 | Archaeology - General | 3000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | NCR is raised to cover the deviation from the design intent and bad workmanship of the installation. Due to temporary nature of the structure, the Contractor proposes to use as is.
| 02SL - Stations (LUL) | Cxxx-NCR-002152 | NCR | ___Non availability of Company Compliance from Supplier |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-02-17 | 2019-04-15 13:11 | 57 | 2018-11-20 14:10 | Architectural - General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | See below MCRs for materials for which Suppliers do not hold appropriate certification from a UKAS accredited body. Generally this means a ISO 9001 certified QMS. 1. Cxxx-LAO-O4-XDS-C101-50393 - MCR for Kencar Perforated Stainless Steel 'Lozenge' Panel 2. Cxxx-LAO-O4-XDS-C101-50822 - MCR for __ PPC Cladding
| 02SL - Stations (LUL) | Cxxx-NCR-002153 | NCR | The use onsite of __ GTEC weather defence board without an approved MCR |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-04-30 | 2019-03-28 08:00 | -33 | 2018-11-21 10:49 | Architectural - Finishes | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | __ GTEC weather defence board is being installed on site for the front facade at Moorgate ticket hall without an approved MCR ( materials compliance record) being in place.The following MCR Cxxx-LAO-O4-XDS-C101-50933 has now been submitted and is working its way through the system for approval.
| 02SL - Stations (LUL) | Cxxx-NCR-002154 | NCR | Moorgate & Broadgate Ticket Hall - Luminaire Colour Temperature |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-10-02 | 2020-01-17 14:45 | 107 | 2018-11-22 15:17 | Electrical - Lighting | 10000 |  | Design | Rework | 2 (6-60k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | It has been raised that the type F5 & T luminaires installed within Broadgate Ticket Hall are the wrong colour temperature. The F5's are 5000K and the T's are 4000K, __'s specification shows the F5's as 5000K and the T's as 3000k (4000K for Moorgate Ticket Hall). This contradicts the attached RFI which states the luminaires to be 3000K. This information was based upon document Cxxx-LAO-E-RGN-C101_WS102-50001 (REV 3.2), this document is now REV 4 and this information has not been included within it.
| 02SL - Stations (LUL) | Cxxx-NCR-002155 | NCR | ductwork connections to grilles |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-11-01 | 2019-04-23 13:10 | -192 | 2018-11-21 20:21 | Mechanical - Mechanical Engineering General | 45000 |  | Design | Repair | 2 (6-60k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Following a recent inspection with Mark Tilden it was noted the duct connections to the grilles were undersized to achieve the required design.
| 02SL - Stations (LUL) | Cxxx-NCR-002156 | NCR | BTH - Unpaid Side - __ Signage - First Fix Installation |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-08-31 | 2019-10-21 09:39 | 51 | 2018-11-23 12:25 | Architectural - Signage | 1500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | __ First Fix for Signage is being installed in BTH. It was noticed on a site visit by __ Quality Team the existence of over-sized holes / redundant holes on __’s STO sub-frame (BTH North Elevation) - only visible on the reverse of the sub-frame.
| 02SL - Stations (LUL) | Cxxx-NCR-002157 | NCR | 1st Fix cladding installation inspection issues at Moorgate |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-01-31 | 2020-11-27 08:11 | 666 | 2018-11-22 10:36 | Architectural - General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | __ have installed cladding panels to the following Moorgate locations. 01a,03a, 04a,10a, 30a, 33a,65a Before cladding commenced, pre-cladding hold point inspections for each area was undertaken as per the ITPs. The inspections raised a number of design related and workmanship issues relating to co-ordination, installation, workmanship and confirmation of testing. A number of the issues raised were not adequately resolved prior to cladding installation and remain so. This may result in the need for inspection and possible rework to the area to demonstrate satisfactory closure of the issues. The __ tracker was used to log all issues identified during these inspections.
| 02SL - Stations (LUL) | Cxxx-NCR-002158 | NCR | 1st Fix cladding installation inspection issues at Broadgate |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-02-28 | 2019-08-13 14:11 | 531 | 2018-11-22 10:51 | Architectural - General | 3000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | __ have installed cladding panels to the following Broadgate locations. 20a, 21a, 22a,23a,24a,67a Before cladding commenced, pre-cladding hold point inspections for each area was undertaken as per the ITPs. The inspections raised a number of design related and workmanship issues relating to co-ordination, installation, workmanship and confirmation of testing. A number of the issues raised were not adequately resolved prior to cladding installation and remain so. This may result in the need for inspection and possible rework to the area to demonstrate satisfactory closure of the issues. The __ tracker was used to log all issues identified during these inspections.
| 02SL - Stations (LUL) | Cxxx-NCR-002159 | NCR | 1st Fix cladding installation inspection issues to PAEE and Smoke Downstands |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-02-28 | 2019-09-05 13:04 | 189 | 2018-11-22 11:13 | Architectural - General | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | __ have installed cladding panels to the following platform / tunnel locations. 41a and 42a Before cladding commenced, pre-cladding hold point inspections for each area was undertaken as per the ITPs. The inspections raised a number of design related and workmanship issues relating to co-ordination, installation, workmanship and confirmation of testing. A number of the issues raised were not adequately resolved prior to cladding installation and remain so. This may result in the need for inspection and possible rework to the area to demonstrate satisfactory closure of the issues. The __ tracker was used to log all issues identified during these inspections.
| 02SL - Stations (LUL) | Cxxx-NCR-002160 | NCR | ___Installation progressed without Approved MCR |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-03-31 | 2020-03-27 13:14 | 362 | 2018-11-22 12:57 | Architectural - General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Installation of materials being progressed without CRL formal Approval by __: Cxxx-LAO-O4-XDS-C101-50910 C12.020ban - MCR for __ Doors Cxxx-LAO-O4-XDS-C101-50933 C12.020bbh - MCR for __ Board Cxxx-LAO-O4-XDS-C101-50752 C12.020atn - MCR for Stainless Steel Metalwork - Fabrication Facilities Cxxx-LAO-O4-XDS-C101-50841 C12.020axg - MCR for __ Doors Cxxx-LAO-O4-XDS-C101-50851 C12.020axq - MCR for __ SS solid and SS perforated panels Cxxx-LAO-O4-XDS-C101-50857 C12.020axw - __ PPC Panel for ES5 Cxxx-LAO-O4-XDS-C101-50860 C12.020axz - MCR for __ Metalwork supply, Galv and Stainless Steel Cxxx-LAO-O4-XDS-C101-50873 C12.020ayt - MCR for PE Foam Backer Rod Cxxx-LAO-O4-XDS-C101-50359 C12.020qa - Materials Compliance Record for __ EPDM Membrane Cxxx-LAO-O4-XDS-C101-50859 C12.020axy - __ Metalwork supply, PPC, Galv and Stainless Cxxx-LAO-O4-XDS-C101-50822 C12.021awl - MCR for __ PPC Cladding Cxxx-LAO-O4-XDS-C101-50819 C12.020awi - MCR for __ Specialist SR3 Double & Single Doors at Platform End Walls Cxxx-LAO-O4-XDS-C101-50710 C12.020arv - MCR - __ VHB 4947F Tape Cxxx-LAO-O4-XDS-C101-50697 C12.020aei - Galvanized Z Support Angles Cxxx-LAO-O4-XDS-C101-50915 C12.020bap - Material Compliance Record for __ SW4307 Insulation Cxxx-LAO-O4-XDS-C101-50932 C12.020bbg - MCR for Application of Spray Clad Cladding Repair
| 02SL - Stations (LUL) | Cxxx-NCR-002161 | NCR | FFO: Back of House Staff Accom Ceilings - Service Layout Change |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-08-31 | 2019-08-13 11:23 | -18 | 2018-11-22 17:32 | Architectural - Ceilings & Soffits | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Site install of revised ceiling grill layout installation in staff accommodation ceilings on site prior to CRL PTR approval.
| 02SL - Stations (LUL) | Cxxx-NCR-002162 | NCR | Bi-metallic isolation has not been installed between dissimilar metals as specified |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2019-03-31 | 2019-02-17 20:48 | -42 | 2018-11-26 13:57 | Architectural - Finishes | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | During a planned surveillance to inspect the __ cladding installation it was found that the __ glazed system primary grid, that consists of stainless steel brackets fixed to the structure, with aluminium cladding rails connected, had no Bi-Metal separation between the dissimilar metal faces. Architectural Specification JH13.1401 Metalwork a) Refer to Section JZ11. JZ11.0406 Bimetallic Corrosion a) adequate measures shall be taken to prevent bimetallic corrosion between dissimilar metals. See attached photograph.
| 02SL - Stations (LUL) | Cxxx-NCR-002163 | NCR | No evidence provided of Benchmark acceptances |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2019-03-12 | 2019-08-06 16:05 | 147 | 2018-11-26 14:02 | Architectural - Finishes | 500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | During a planned surveillance to inspect the __ cladding installation in the PRM passage it found that the Contractor could not provide evidence of Benchmark acceptance in line with the specification. JH13.2105 Benchmark Requirements; The first completed length of each system installed.
| 02SL - Stations (LUL) | Cxxx-NCR-002164 | NCR | MTH - toilet area finishes SID 2/441 and 2/440 not as per drawing Cxxx-LAO-A-DDD-C101_2-68802 |  | Crossrail | PDP | LIS - Liverpool Street Station (Central) |  | 2019-06-28 | 2019-09-27 12:49 | 91 | 2018-11-28 08:55 | Mechanical - Public Health Engineering | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | The works installed in SID room numbers 2/441 and 2/440 are not as per drawing Cxxx-LAO-A-DDD-C101_2-68802.
| 02SL - Stations (LUL) | Cxxx-NCR-002165 | NCR | M135-DAT-04363, 4364 Cat 6a cables over 90 meters |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2018-08-31 | 2019-06-19 07:45 | 292 | 2018-11-29 11:15 | Communications and Control Systems - CCTV | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | When cables M135-DAT-04363, 4364 is has been found Cat 6a cables are over 90 meters. M135-DAT-04363 - 101.3m M135-DAT-04364 - 104.3m See attached fluke results
| 02SL - Stations (LUL) | Cxxx-NCR-002166 | NCR | Moorgate Trumpet Middle Section misalignment |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-05-31 | 2019-05-01 10:00 | -30 | 2018-12-07 12:10 | Architectural - General | 3000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Moorgate Trumpet Middle Section steelwork is slightly out of position on south side, by approximately 15mm. Brackets for GRC panels cannot be installed in this area, as they will be out of position.
| 02SL - Stations (LUL) | Cxxx-NCR-002167 | NCR | Cladding Installation Commenced Without Accepted Blast and Static Calculations |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2019-01-31 | 2019-01-18 14:20 | -13 | 2018-12-11 12:19 | Architectural - Finishes | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | During a planned surveillance to inspect the __ cladding installation in the PRM the Contractor presented both, Blast and Static Calculations for the PRM Passage. On review it was found that both sets of calculations were draft copies and not formally accepted. As such the installation has commenced with an incomplete design. ITP ‘Installation of Cladding Components at Passengers Reduced Mobility (PRM), North and South Corridor’ Cxxx-LAO-O4-ITP-C101-50226 (Rev 3), inspection number 1.1 Acceptance of Design is a Hold Point for all parties.
| 02SL - Stations (LUL) | Cxxx-NCR-002168 | NCR | Pressure Relief Dampers Moorgate Shaft |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-04-04 | 2019-05-01 13:14 | 27 | 2018-12-11 18:16 | Mechanical - Heating Ventilation & Air Conditioning | 2000 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Pressure Relief Dampers in Moorgate PRS Platform +4 installed with controls located in the pressure relief shaft.
| 02SL - Stations (LUL) | Cxxx-NCR-002169 | NCR | Air short circuit between grills |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-05-31 | 2019-05-31 10:23 | 0 | 2018-12-11 18:24 | Mechanical - Heating Ventilation & Air Conditioning | 1000 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Leer extract ductwork terminating in ceiling void outside lift 7 has its grille installed immediately adjacent to the intake grill for the space. The ductwork requires extending from its current location in the ceiling void outside of lift 7 to further along the corridor ceiling void.
| 02SL - Stations (LUL) | Cxxx-NCR-002170 | NCR | MSH - RC level SOR GL12 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-03-22 | 2019-02-06 09:13 | -44 | 2018-12-12 18:00 | Structural Engineering - Concrete Member | 1500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Concrete ramp and upstand around GL12 / GLZ has been cast between 50 and 100mm high.
| 02SL - Stations (LUL) | Cxxx-NCR-002171 | NCR | _____ - NO MCRs and ITPs submitted |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-05-31 | 2019-07-23 11:53 | 53 | 2018-12-13 11:23 | Architectural - General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | __ has used a contractor (Mettal Uk Limited) for components across some of their scopes. We are now told that the contractor company has been put into Liquidation. __ will not be able to supply any assurance for the works. Please find attached schedule for the components procured through __. A new Company has been opened by the same people called __. An ITP and MCR has been submitted for this: Cxxx-LAO-O4-ITP-C101-50321 Cxxx-LAO-O4-XDS-C101-50957
| 02SL - Stations (LUL) | Cxxx-NCR-002172 | NCR | Fan Room 4 BMS Containment |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-03-29 | 2019-05-14 13:41 | 46 | 2018-12-14 08:34 | Communications and Control Systems | 5000 |  | Design | Repair | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Access to remove packaged fan unit is obstructed by unistrut framing supporting electrical containment.
| 02SL - Stations (LUL) | Cxxx-NCR-002173 | NCR | The Contractor was unable to provide evidence of formal acceptance for Glazed Cladding prototype |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2019-08-31 | 2019-09-04 11:25 | 4 | 2018-12-17 10:05 | Architectural - Finishes | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Lack of procedure | Completed |  | During a planned surveillance to inspect the __ cladding installation in the PRM the Contractor was unable to provide evidence of formal acceptance for the __ glazed cladding system prototype.
| 02SL - Stations (LUL) | Cxxx-NCR-002174 | NCR | M135-DAT-06299 PSD SCADA Cat 6a Cables over 90m |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-06-27 | 2019-06-20 15:23 | -7 | 2018-12-21 11:17 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | PSD SCADA Cat 6a Cables exceed 90 meters M135-DAT-06299 - 116m
| 02SL - Stations (LUL) | Cxxx-NCR-002175 | NCR | EDNE @ Broadgate Entrance |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2020-04-01 | 2021-01-15 13:23 | 289 | 2019-01-02 15:37 | Architectural - Signage | 500 |  | Design | Reject | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Refer to Verification Report CRL-OBS-24230. As currently installed the mounting does not allow access to the locks to release the front cover of the EDNE for maintenance. The colour and finish do not match adjacent finishes. Cxxx-RFI-004258 was issued with Cxxx's proposal due to clash with beam within glazed fascia however, sketches associated with the RFI do not show sufficient detail and would require further development. Detailed design of proposal was not be submitted for "acceptance" allowing development of detail. 20.08.2019 -Update As discussed, further to Cxxx-NCR-002175 & Cxxx-RFI-004528: • The EDNE sign as installed at the Broadgate canopy entrance does not work. o The EDNE sign slightly obstructs visibility of the station identification signage frieze. The continuous backlit blue frieze would be slightly visually occluded which would look odd. o The two key holes at the bottom of the EDNE unit will be obstructed by the __ metal soffit. o Sketch Cxxx-HB-SK11548 (attached to Cxxx-RFI-004528) shows a mastic joint between the metal soffit and the black glass/EDNE zone: the mastic will partially cover the speaker holes at the bottom of the EDNE unit. Note: Mastic will be a bit challenging to install at the bottom of the EDNE sign (see attached photo) as there is a large open gap: the mastic would need some sort of backing. o There are currently gaps between the sides of the EDNE sign and the adjacent black glass. I assume that Cxxx intend to seal these gaps to prevent water ingress into the void behinf the EDNE sign. As discussed with __ (Cxxx), Cxxx are aware of the above design co-ordination issues and have been considering remedial design options in conjunction with their architectural team (__ - __) As discussed with __ we recommend: • that the EDNE sign is moved away from the black fascia so that it is hung from the __ metal soffit (as close to the metal soffit as possible), with Cxxx providing any secondary support structure as required • In elevation, the EDNE should be centered on the entrance portal opening and centered on the metal soffit. • The projecting fixing brackets at the bottom of the EDNE unit (see attached photo) should be removed • Cxxx to confirm blast load capacity for the standard top-hung fixing detail for the EDNE units. • Cxxx to confirm that the rear side of the EDNE sign is neat in appearance as it will be visible if the sign is top hung.
| 02SL - Stations (LUL) | Cxxx-NCR-002177 | NCR | MSH - Level -1 - Back of House Staff Rooms - Doors / Blockwork |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2020-05-19 | 2020-03-05 14:55 | -75 | 2020-01-20 12:27 | Architectural - Doors | 500 |  | Incomplete Works | Repair | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | CRL-OBS-26104 - __e During a general Quality Surveillance walk back of house staff rooms were viewed. Concerns raised in relation to the fixing of the door within the block work opening and the termination of finishes in relation to the frame. In many instances the finishes - wall and floor - have been interrupted at the door frame leaving areas of block work exposed. Examples of these at the Moorgate Shaft attached.
| 02SL - Stations (LUL) | Cxxx-NCR-002178 | NCR | MTH - Basement Level - PRM Corridor - VE Cladding |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2020-03-31 | 2020-02-21 14:20 | -39 | 2020-01-20 12:38 | Architectural - Finishes | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | CRL-OBS-23936 - __ CRL-OBS-25940 - __e A Quality Surveillance Inspection took place for the Cxxx Sub-contractor - __ related to internal finishes. During the inspection CRL reviewed the Vitreous Enamel Cladding - Type IWS-719 - installed along the PRM Corridor, Basement Level (Moorgate Ticket Hall) (Specification Cxxx-LAO-A-RSP-C101-WS103-50001 - Clause JK17 - 1217). Concerns were raised associated with the damage to the panels installed on site. • Damaged panels will require repair to an agreed procedure and repair benchmark; there is little evidence that this is in place as repairs have not be carried out. • Damage is clearly visible on panels with their edges exposed; there is no obvious evidence that the installed panels do not have similar damage. • Damage to the panels if left will impact on performance; rust, and therefore will not meet the requirement of the works information. Manufacture/Installation Tolerances. Panels as installed are not aligned. • Refer to Cxxx-LAO-A-RSP-C101-WS103-50001 - Clause JK17 -3221 – Workmanship. • This requires tolerances to be added to approved drawings and should also be detailed in the installation Inspection and Test Plan Cxxx-LAO-A-ZFM-C101-50155 Revision 2.0 (ITP) Activity 4.12 – Installation of VE Panels provides setting out. • The contractor to confirm the VE Panels as installed meet these requirements?
| 02SL - Stations (LUL) | Cxxx-NCR-002179 | NCR | TUN - BWK - Endwall Column Repairs |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-04-17 | 2019-02-26 15:26 | -50 | 2019-01-07 10:19 | Architectural - Brickworks/Blockworks | 1500 |  | Planning | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Due to clash between cladding posts and blockwork, small elements of blockwork at 2 platform Endwalls have to be removed to allow for torqueing of __ cladding. Removal of blockwork in some areas requires removing of concrete column portions.
| 02SL - Stations (LUL) | Cxxx-NCR-002180 | NCR | AP2 CCTV Cable Lenghts exceed 90 meters |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-02-06 | 2019-02-18 10:40 | 12 | 2019-01-09 11:45 | Communications and Control Systems - CCTV | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | AP2 CCTV Cable Lenghts exceed 90 meters: Cam-0227 (M135-DAT-04353) - 149.25m Cam-0224 (M135-DAT-04372) - 101.1m Cam-0225 (M135-DAT-04355) - 103.4m Cam-0226 (M135-DAT-04353) - 121.8m
| 02SL - Stations (LUL) | Cxxx-NCR-002181 | NCR | TUN - Back of House Platform End Screens Earthing Mesh Cut Out |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-12-30 | 2019-06-12 13:54 | -201 | 2019-01-09 12:31 | Architectural - General | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Platform Ends Westbound West and Eastbound East Mesh were cut to form location of earthing and bonding braiding to connect to post. Mesh should not have been cut due to change in design, holes formed no longer required. Metal Clips to be installed on the mesh over the locations to remove gaps.
| 02SL - Stations (LUL) | Cxxx-NCR-002182 | NCR | Access and Maintenance to Life safety Axail fans |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-08-13 | 2019-10-25 06:41 | 73 | 2019-01-10 16:55 | Mechanical - Heating Ventilation & Air Conditioning | 5999 |  | Planning | Repair | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | This NCR is raised to cover the Access and Maintenance to the __ Axail fans, the following fans require re-works to the associated ductwork system to enable the access and maintenance of the fans to be carried out: __X - FAN B51 & B52 - FAN 251 & 252 - FAN 301 & 302 MGS - FAN 351 & 352 - FAN 601 & 602 - FAN A02 & A03
| 02SL - Stations (LUL) | Cxxx-NCR-002183 | NCR | __X FFO PAD BAL-208 handrail fixed into movement joint |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-03-31 | 2019-06-17 12:33 | 78 | 2019-01-11 15:14 | Architectural - Balustrade | 1000 |  | Design | Repair | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | In Blomfield Box on Level 102 PAD's BAL-208 handrail has a wall bracket located over a movement joint with a fixing going directly into the mastic. This is an issue for the top and mid rail on both sides of the run. Please see attached photo.
| 02SL - Stations (LUL) | Cxxx-NCR-002184 | NCR | Totems - Broken Glass End Panel |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-11-30 | 2020-08-05 12:05 | 249 | 2019-01-14 10:32 | Architectural - General | 2000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | Glass end panels on 2# totems broken
| 02SL - Stations (LUL) | Cxxx-NCR-002185 | NCR | ___MTH Mastic to Glass Cladding Panels |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-04-14 | 2019-07-03 07:55 | 80 | 2019-01-14 13:31 | Architectural - Glazing | 1500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | __ Comments 14 January 2019 : For glass cladding types, Cxxx have not provided the required samples for all glass cladding. Material samples were provided, however the work information requires sample to include all seals and edge treatments. In the absence of these approved submissions, it was agreed that Cxxx would provide an on-site “mock-up” of different colour mastics (white, black and clear) for different cladding conditions (white glass, blue glass, stainless steel and the various interfaces between the differing materials). __ suggested that this would best be conducted on the cladding on the interior of the BTH Canopy. The “mock-up” for mastic colours has not been provided by Cxxx for agreement of mastic with Crossrail. This issue has been raised by comments on sub-contractor drawings and has been discussed via design meetings with the Cxxx design team at multiple meetings. It is observed that a large amount of black mastic that has been installed in the Morogate and Broadgate tickets halls without an approved sample, mockup or benchmark. This is not compliant with the requirements of the works information
| 02SL - Stations (LUL) | Cxxx-NCR-002186 | NCR | Moorgate Ticket Hall - F2b Luminaire Alignment with Cladding Panels |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-06-28 | 2021-07-15 15:10 | 748 | 2019-01-15 14:27 | Electrical - Lighting | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | Regarding the F2b luminaires within Moorgate Ticket Hall it has been raised as a non conformance that the joints between the fittings do not line up with the joints of the cladding panels.
| 02SL - Stations (LUL) | Cxxx-NCR-002187 | NCR | Broadgate Ticket Hall - F2a Luminaire Alignment with Cladding Panels |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-06-28 | 2020-01-24 17:11 | 210 | 2019-01-15 10:02 | Electrical - Lighting | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | Regarding the F2a luminaires within Broadgate Ticket Hall it has been raised as a non conformance that the joints between the fittings do not line up with the joint of the cladding panels.
| 02SL - Stations (LUL) | Cxxx-NCR-002188 | NCR | PLT Ends FFO BOH Handrails Blocking Access to Cxxx Control Panels |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-06-28 | 2019-09-16 08:58 | 80 | 2019-01-15 15:45 | Architectural - Handrail | 2000 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Regarding the BOH platform ends where Cxxx are installing handrails for public escape there is an issue where the handrails block access to Cxxx MEP control panels.
| 02SL - Stations (LUL) | Cxxx-NCR-002189 | NCR | PLT Ends FFO BOH Handrails clashing with unistrut supports within UPE |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-04-30 | 2019-08-20 10:17 | 112 | 2019-01-15 16:14 | Architectural - Handrail | 2500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | There are 5 locations on the Moorgate Eastbound platform end where the BOH handrails brackets are clashing with uni-strut within the UPE which supports the CMS at high level.
| 02SL - Stations (LUL) | Cxxx-NCR-002190 | NCR | TUN - BOHPS Gate Hinge Bolts installed incorrectly |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-06-30 | 2019-02-12 14:51 | -138 | 2019-01-16 08:57 | Architectural - Security | 1500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The bolts fixing the hinges to the posts have been installed incorrectly. Further investigation to be carried out.
| 02SL - Stations (LUL) | Cxxx-NCR-002191 | NCR | MSH - GL7 Damaged Precast |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-05-31 | 2019-04-08 17:32 | -53 | 2019-01-16 08:29 | Architectural - Ceilings & Soffits | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | Please see attached images. Small chip on precast frieze panel on GL7 MTH
| 02SL - Stations (LUL) | Cxxx-NCR-002192 | NCR | BTH - ES1 deck lights - sharp edges |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-04-26 | 2019-10-10 16:53 | 167 | 2019-01-16 08:43 | Architectural - Finishes | 5000 |  | Workmanship | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | Further to Cxxx-NCR-002104, the exposed edges to the ES1 escalator deck cladding and angle trim have not been sufficiently arrised/rounded (as required under Cxxx spec. clause JA.6511 and Cxxx spec. clause JA.6510). As such the edges are sharp. There is a risk that customers on moving escalators will cut their hands when touching the sharp edges.
| 02SL - Stations (LUL) | Cxxx-NCR-002193 | NCR | BTH - Floor gully discharge pipe through FAN IV room |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-06-30 | 2019-05-03 12:33 | -58 | 2019-01-17 11:43 | Structural Engineering - Concrete Member | 750 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 100mm timesaver pipe cast into the BTH ticket hall suspended floor slab was not installed with enough protrusion below the slab to allow a coupler to be connected, and the pipe extended to the floor.
| 02SL - Stations (LUL) | Cxxx-NCR-002194 | NCR | Lightning Protection |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-12-20 | 2019-04-01 10:56 | -263 | 2019-01-17 12:55 | Electrical - Earthing & Bonding | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | Specification states lightning protection is to be installed using copper tape, however, aluminium tape has been installed in its place.
| 02SL - Stations (LUL) | Cxxx-NCR-002195 | NCR | ___Non Compliant Backing rod used for sealant application |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-04-30 | 2019-08-05 08:42 | 97 | 2019-01-24 11:03 | Fire - Compartmentation | 1000 |  | Material | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | The Sub-contract has installed a Non-compliant backing rod in sealant application on Ticket hall levels. The MCR Cxxx-LAO-O4-XDS-C101-50873 has not been accepted by CRL and __. There has been no fire assessment on the project.
| 02SL - Stations (LUL) | Cxxx-NCR-002196 | NCR | FFO Site Wide PAD Handrails Guarding PRM Ramp and Platform Ends |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-07-31 | 2019-11-29 16:22 | 121 | 2019-02-12 15:05 | Architectural - Balustrade | 2500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | NCR raised due to lack of 'guarding' in the PRM ramp handrails and platform ends BOH handrails. Required as per BS 6180:1995 Code of practice for barriers in and about buildings. It was also noted that mid-rails should have been included where there are ramp handrails mounted to the wall - PRM ramp and BOH platform (westbound east end)
| 02SL - Stations (LUL) | Cxxx-NCR-002200 | NCR | BTH - Tickethall Precast Soffit Minor Damages |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-05-30 | 2019-09-10 10:29 | 103 | 2019-02-04 10:08 | Architectural - Ceilings & Soffits | 4000 |  | Damaged | Repair | 3 (3-6k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | Minor surface damage to the precast soffit through Broadgate Ticket Hall. Minor damages have been observed on the beamlets. Damages includes, scuffs, marks and minor indentations. This has become more evident as the permeant lighting is installed and commissioned. Damage has likely to have been occurred during the fitting of the acoustic panels, CMS installation, cable pulling and electrical items installation.
| 02SL - Stations (LUL) | Cxxx-NCR-002201 | NCR | BTH - Urban Realm Drainage Brickwork |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-04-02 | 2019-02-18 08:15 | -43 | 2019-02-01 16:57 | Civil - Drainage | 2500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Brickwork not up to standard, further to inspection by the City of London inspector.
| 02SL - Stations (LUL) | Cxxx-NCR-002202 | NCR | FFO - __ Access Hatch, E-C-776-A01 , Requires Fire Insulation 120mins |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-03-04 | 2019-05-28 13:23 | 85 | 2019-02-04 11:26 | Fire - Compartmentation | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | __ Access hatch E-C-776-A01 been installed to achieve fire performance of 120mins Integrity. This hatch requires a 120mins insulation rating as well as the 120min integrity. A __ FS120 Fire boarding ceiling that has been installed below the hatch to achieve the fire performance as per Cxxx-LAO-A-DWG-C101_WS103-50176 Rev C01. This system will be enhanced to achieve the required fire insulation, refer Cxxx-LAO-A-DWG-C101_WS103-50176__Markup E__on 2019_02_04
| 02SL - Stations (LUL) | Cxxx-NCR-002203 | NCR | non conformity of bending radius in lift motor rooms for ATS load cables |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-03-08 | 2019-10-09 12:59 | 215 | 2019-02-08 15:58 | Electrical - Power Distribution | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Insufficient information made available to the worker. | Completed |  | This NCR covers the non conformance for bending radius on Some ATS load cables In Lift motor rooms and DBs at NLTT. LIFT 2/LIFT 3 / LIFT 5/ LIFT 6 / LIFT 7 /LIFT 8 and NLTT DBs
| 02SL - Stations (LUL) | Cxxx-NCR-002204 | NCR | ___Platform end doors Part K non-compliance |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-07-31 | 2019-07-10 10:17 | -21 | 2019-02-12 11:10 | Architectural - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | The following doors supplied and delivered by __ do not meet Part K and BS 8300-2 requirements due to the glazed door required with a panic hardware which does not meet the manufacturing and testing criteria. Door W-08-262-D05 shown on Cxxx-LAO-A-DWG-C101-51119 Door E-08-261-D01 shown on Cxxx-LAO-A-DWG-C101-51120 Door W-08-261-D04 shown on Cxxx-LAO-A-DWG-C101-51117 Door W-08-262-D04 shown on Cxxx-LAO-A-DWG-C101-51118 Door E-08-262-D02 shown on Cxxx-LAO-A-DWG-C101-51116 Please find attached Cxxx comments: Cxxx: height of vision window as shown doesn't comply with BS 8300-2 & Part K. Vision window to be in the range 1150-1500mm from FFL. Sketch in green. Cxxx HB Response 27/06/2019: The vision panels on the doors noted, are set-out 1350-1700mm FFL which is within the zone of visibility for the upper vision panel outlined in Part K 10.1. W-08-262-D05 E-08-261-D01 W-08-261-D04 W-08-262-D04 E-08-262-D02
| 02SL - Stations (LUL) | Cxxx-NCR-002205 | NCR | BTH - L8 + L9 Lift frame coordination |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-07-22 | 2019-10-13 14:28 | 83 | 2019-02-22 09:33 | Mechanical - Lifts | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | __ entrance frames at top and bottoms of L8 and L9 inclined lifts in BTH do not coordinate & interface with __ glazed screens
| 02SL - Stations (LUL) | Cxxx-NCR-002206 | NCR | Ductwork External Areas-Insulation & Tape Residue |  | Crossrail | PDP | LIS - Liverpool Street Station (Central) |  | 2020-05-20 | 2019-12-05 10:31 | -167 | 2019-02-27 09:55 | Mechanical - Heating Ventilation & Air Conditioning | 2999 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | Cxxx removed insulation applied to ductwork earlier in the project expecting to replace it with 90mm __ insulation. the risk assessments completed by __ for all station areas indicated that a number of areas would not need the 90mm __. This has resulted in surplus pieces of insulation and tape residue being left in place. This issue is station wide.
| 02SL - Stations (LUL) | Cxxx-NCR-002210 | NCR | Damaged Door (Bowed) |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-06-30 | 2019-08-14 08:20 | 45 | 2019-02-28 13:40 | Architectural - Doors | 10000 |  | Damaged | Rework | 2 (6-60k) | Complete | Personnel Error - Other human error | Completed |  | Door E-A-792-D01 in Bloomfield Box has been damaged and is now bowed and does not close flush against the door frame.
| 02SL - Stations (LUL) | Cxxx-NCR-002211 | NCR | 60a___-ES 5 Escalator Cladding Stainless steel cladding |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-07-31 | 2020-01-07 16:31 | 160 | 2019-03-04 16:06 | Architectural - General | 4000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | __on has raised concerns associated with the stainless steel cladding adjacent to ESC 22/23/24 – ES 5 Escalator Cladding. During inspection cladding joints and anti-drumming were raised as concerns.
| 02SL - Stations (LUL) | Cxxx-NCR-002212 | NCR | ___Damage STO Glass panel in MTH to 1a |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-06-03 | 2019-05-09 07:53 | -25 | 2019-03-05 14:54 | Architectural - General | 3000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Damage occurred to 1no STO glazed panel on grid W to western wall of Moorgate ticket Hall. It is believed that the damage occurred in situ due to a MEWP or other heavy object making impact with the glass
| 02SL - Stations (LUL) | Cxxx-NCR-002213 | NCR | __ damaged STO Glass panels in MTH to 4a external glazing |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-06-03 | 2019-05-09 07:57 | -25 | 2019-03-05 15:19 | Architectural - General | 2500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Damaged occurred to 2no STO glass panels intended to be used for the inclined façade elevation 4a (external MTH entrance). The damage occurred whilst the panels were stored on a pallet under the front entrance. It is believed that the panels where damaged during forklift operations to clear area ready for the groundwork contractor. However they could also have been damaged by passing plant.
| 02SL - Stations (LUL) | Cxxx-NCR-002214 | NCR | __ Portland stone panels damaged in MTH to 4a |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-09-30 | 2020-12-04 12:14 | 431 | 2019-03-05 15:32 | Architectural - General | 1500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Damage occurred to 2no Portland stone panels in MTH intended to be used for the entrance façade cladding, elevation 4a. The damage occurred during the lifting operation whilst the panels where moved on a pallet. The driver dropped the pallet down as he was drawing his forks out the pallet. It resulted in hairline cracks to the stone panels.
| 02SL - Stations (LUL) | Cxxx-NCR-002215 | NCR | __ damaged STO glazed panel on PRM Corridor 13a |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-06-04 | 2019-05-24 09:11 | -11 | 2019-03-06 13:30 | Architectural - General | 2000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Damage occurred to 1no STO glazed panel on PRM Corridor 13a scope. The damage has been discovered by the night shift team when they unwrapped the pallet where all the glass for this scope has been delivered to workface. There is no evidence to help us determine when or where this damage occurred.
| 02SL - Stations (LUL) | Cxxx-NCR-002216 | NCR | Incorrect Crimping Tool used |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-04-03 | 2019-08-15 11:05 | 134 | 2019-03-06 11:49 | Electrical - LV Equipment | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Inadequate/insufficient tooling. | Completed |  | The incorrect crimping method used by __ on the BMS MCC panels. The crimp size should be matched with the same size of crimping tool and as you can see they have used a smaller tool causing the severe compression and weakening of the connection.
| 02SL - Stations (LUL) | Cxxx-NCR-002217 | NCR | GFRC Cladding - Oversize Gaps Between Infill Sti__ and Lighting Boom |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-09-30 | 2019-11-08 13:25 | 39 | 2019-03-06 12:42 | Architectural - General | 5000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Gaps between the cross passage lighting boom and the adjacent GFRC infill strip.
| 02SL - Stations (LUL) | Cxxx-NCR-002218 | NCR | Inadequate effective door width to PRM Corrdior Door / Ramp interface |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2020-05-30 | 2020-11-20 14:14 | 174 | 2019-03-11 14:57 | Architectural - Doors | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Previous Construction - Interfacing issues | Completed |  | The effective clear opening of the door does not allow for 300mm from the leading edge to a wall or obstruction (in this case the ramp). It does not comply with BS 8300
| 02SL - Stations (LUL) | Cxxx-NCR-002219 | NCR | ES5 gap width between precast and SS panels out of tolerance |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-06-30 | 2020-01-07 16:04 | 191 | 2019-03-11 15:00 | Architectural - Ceilings & Soffits | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Previous Construction - Problems based on previous construction errors | Completed |  | The gap between the Stainless Steel panels and adjacent precast above Escalators 22/23/24 is supposed to be nominally 20mm. The slot between the panels diminishes 4mm to approx. 35mm. it will become difficult to remove panels in the future.
| 02SL - Stations (LUL) | Cxxx-NCR-002220 | NCR | USN 225 - Damaged |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-08-31 | 2019-10-09 18:09 | 39 | 2019-03-08 14:43 | Architectural - Signage | 2000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | USN 225 glass ticket fascia sign is broken
| 02SL - Stations (LUL) | Cxxx-NCR-002221 | NCR | energisation of cables prior to closure of NCR raised regarding cable bending radius |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2019-10-02 | 2019-09-20 10:56 | -12 | 2019-03-11 09:08 | Electrical - Power Distribution | 10000 |  | Supervision/Management | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | NCR Cxxx-NCR-002203 was raised ??? regarding the cables not being installed in line with manufacturers recommendation or works information, since this NCR has been raised no rectification works have been carried out on the cables and the cables have now been energised and the cables are covered by fire rated enclosure.
| 02SL - Stations (LUL) | Cxxx-NCR-002222 | NCR | Broadgate Ticket Hall Canopy - stone plinth and lighting |  | Crossrail | PDP | LIS - Liverpool Street Station (Central) |  | 2020-08-31 | 2020-03-02 15:42 | -182 | 2019-03-11 14:28 | Architectural - General | 5000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | An inspection of the 8 No. installed Portland Stone panels on 08/03/19 noted the following non-conformities: - ITP Cxxx-LAO-O4-ITP-C101-50256 is code 3. - The previous sample of stonework has been lost and other samples required in specification JH12.2102 have not been provided. - The relevant __ drawings have not been accepted. - A number of the stone panels have been damaged and will need replacing. (photo 4) - Inadequate protection to installed works (including glazing above); evidence of dirt splatter on panels and glazing. (photo 3) - The joint detail between the panels is yet to be agreed; the 8mm gap is excessive. - Trim detail to close gap between stone panels and LED lighting has been poorly installed, some of it is loose.
| 02SL - Stations (LUL) | Cxxx-NCR-002223 | NCR | Broken Sto glass on South elevation of Moorgate shaft |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-06-10 | 2019-05-01 08:28 | -40 | 2019-03-12 11:05 | Architectural - Glazing | 3000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | On the South (stair side) elevation of the Moorgate shaft (__ Package 33a), during the installation of the Sto glass cladding and the left side 60mm x 60mm SHS stainless steel post, it appears that the SHS post has pressed against the glass resulting in the glass to break.
| 02SL - Stations (LUL) | Cxxx-NCR-002224 | NCR | Broken Sto glass on the West (AP6 side) elevation of Moorgate shaft |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-06-12 | 2019-05-01 08:35 | -42 | 2019-03-12 11:27 | Architectural - Glazing | 3000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | The square piece of glass for the West (AP6 side) elevation of the Moorgate shaft was stored flat on a pallet and temporarily stored in AP6 by __. It appears that another subcontractor has attempted to move this pallet as this was in the way of their works and in doing so the corner of the glass was accidentally clipped resulting it in getting broken.
| 02SL - Stations (LUL) | Cxxx-NCR-002225 | NCR | DAL lighting boom works commencing without documentation approvals |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-08-31 | 2019-08-15 09:41 | -16 | 2019-03-12 12:04 | Architectural - General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | The DAL lighting boom works has commence on site without documentation Code 1 approval. Including: Manufacturing ITP Cxxx-LAO-O4-ITP-C101-50248 (Pending CRL) MCR Cxxx-LAO-O4-XDS-C101-50812 (not submitted) Note installation ITP for this work is code 1 - Cxxx-LAO-O4-ITP-C101-50249
| 02SL - Stations (LUL) | Cxxx-NCR-002226 | NCR | PES commissioning |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2019-07-31 | 2019-07-04 09:00 | -27 | 2019-03-12 14:03 | Mechanical - Heating Ventilation & Air Conditioning | 25000 |  | Incomplete Works | Repair | 2 (6-60k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | Due to numerous incidents of non-compliance with specification JY30.1423 it was agreed that all ductwork would be cleaned so as to provide the specified level of cleanliness. The East end PES ductwork connected to smoke extract fans 351 / 352 had not be cleaned at platform level at the time of IRN and recorded as a category A punchwork (Cxxx-PWK-01537). The specialist cleaner engaged by __ to undertake this cleaning requires "head and shoulders" access into the ducts however poorly co-ordinated services negate use of the access doors fitted such additional doors are now required prior to final cleaning & witnessing as specification JY30.1415. At the __ commissioning meeting 12/3/19 __ confirmed that commissioning of fans 351 / 352 had commenced and that air balancing of the system was underway despite the outstanding category A punchwork, the additional doors not being fitted, duct cleaning to be completed and inspections outstanding.
| 02SL - Stations (LUL) | Cxxx-NCR-002227 | NCR | Commissioning proceeding without approved CTP |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2019-06-04 | 2019-05-16 15:47 | -19 | 2019-03-12 14:42 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | Works Information volume 2B s.28 requires the contractor to undertake commissioning and testing activities against an approved testing and commissioning plan. Such testing and commissioning plan for the platform smoke extract systems (Cxxx-LAO-M-STP-C101-50006) was returned to the contractor 3 April 2018 code 3 ie works not to proceed. Despite several workshops and discussions to refine the document so as to attain approval the document has yet to be re-submitted. At the commissioning meeting 12/3/19 __ confirmed that commissioning of the platform smoke extract system East end was underway without an approved plan.
| 02SL - Stations (LUL) | Cxxx-NCR-002228 | NCR | Change in resin flooring specification |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-07-31 | 2019-06-13 16:32 | -48 | 2019-03-14 10:26 | Architectural - Flooring | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Original specification for resin flooring was found to be not suitable for proposed use. AS such __ have proposed to use the Resbuild MMA Smoothscreed fR system which is an approved LU material.
| 02SL - Stations (LUL) | Cxxx-NCR-002229 | NCR | Cracking to Terrazzo Tiles |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-08-28 | 2019-09-30 12:13 | 33 | 2019-07-03 13:53 | Architectural - Flooring | 2000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Cracking to Terrazzo Flooring in CP5 (Main Concourse)
| 02SL - Stations (LUL) | Cxxx-NCR-002230 | NCR | BTH - Lift 8/9 Galvanised Portal Frame |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-06-30 | 2019-09-05 13:19 | 67 | 2019-03-20 17:20 | Civil - Structural Engineering | 2000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | During installation of landing door steel support work at the top of lift 8 and 9, the galvanised tabs at the bottom of "__" frame were cut. This was to faciliate installation of the inclined lift landing door supporting steelwork. This has removed the galvanic protection to the steelwork at 4no. discrete locations.
| 02SL - Stations (LUL) | Cxxx-NCR-002231 | NCR | __X Bronze Portland Stone Louvre Facade without design approval and Benchmark |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-06-30 | 2020-02-19 11:37 | 234 | 2019-03-20 17:28 | Architectural - Finishes | 5000 |  | Documentation and Records | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | Works are in progress for the installation of the Bronze/Portland Stone/Louvred façade at Bloomfield Box. The first installed material of each type requires a "Benchmark" for CRL's acceptance. The secondary structure/waterproofing/SR3 rated door and the bronze are installed on site with outstanding issues on comments sheet for 50a Cladding drawings (Cxxx-LAO-A-XCS-C101_WS103-50068)
| 02SL - Stations (LUL) | Cxxx-NCR-002232 | NCR | Lean bars installed within pedestrian zone in AP6 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-08-31 | 2019-06-03 17:46 | -89 | 2019-03-20 17:51 | Architectural - Finishes | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | The lean bar brackets installed in AP6 project into the Pedestrian zone set out by Cxxx. Cxxx Drawings state the edge of the lean bar to be in the same plane as the vertical edge of the of the terrazzo skirting. This is incorrect and not as per the design.
| 02SL - Stations (LUL) | Cxxx-NCR-002233 | NCR | Missed Benchmark for Stainless steel acoustic panel to Ticket Hall Beams (IWS-815) BTH and MTH |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-10-02 | 2019-09-12 09:50 | -20 | 2019-09-04 10:33 | Architectural - Ceilings & Soffits | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | Benchmark was missed for for Stainless steel acoustic panel to Ticket Hall Beams (IWS-815) BTH and MTH. The Benchmark was to demonstrate demountability of the panels.
| 02SL - Stations (LUL) | Cxxx-NCR-002234 | NCR | M135-DAT-04530 Cable Failure |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-04-22 | 2019-04-15 13:18 | -7 | 2019-03-25 12:38 | Communications and Control Systems - CCTV | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | M135-DAT-04530 Cable Failure (103.8 meters)
| 02SL - Stations (LUL) | Cxxx-NCR-002236 | NCR | BTH - lighting cable route in Gateline precast plank |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2019-05-31 | 2020-01-20 13:21 | 234 | 2019-03-28 10:15 | Electrical - Cable Management | 20000 |  | Incorrect Installation | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Other | Completed |  | Cabling for the lighting installed in BTH pre cast plank MEP recessed void located in gridline B has not utilised the CMS that was cast into the planks ( see lighting drawing attached). The cables have been routed through the pre cast planks shadow gaps, this method of installation was not advised or agreed with anyone prior to the precast CMS not being used, routing within the shadow gaps does not provide adequate mechanical protection or support and is not the accepted installation detail for these cables. this method of installation is not acceptable and needs addressing.
| 02SL - Stations (LUL) | Cxxx-NCR-002237 | NCR | __ procured materials from contractor without appropriate certificaiton |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-06-30 | 2019-10-11 08:53 | 103 | 2019-03-29 09:19 | Architectural - Finishes | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | __ procured materials from companies that do not hold appropriate certification from a United Kingdom Accreditation Service (UKAS) accredited certification body (or one that has mutual recognition with UKAS). e.g. ISO 9001 certification. The contractors noted in this non conformance is __ Limited (steelwork Fabricator) and Spray Technologies Limited (Grass Grip for paint repair)
| 02SL - Stations (LUL) | Cxxx-NCR-002238 | NCR | PAD Balustrading Architectural Issues - Moorgate Ticket Hall |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-08-16 | 2020-07-20 11:14 | 339 | 2019-04-08 16:52 | Architectural - Balustrade | 500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | There are a number of Architectural issues with the PAD installed BAL-112 glazed balustrades across the station. Cxxx-NCR-002198 has been cancelled and the associated issues split into the 3 station areas. Cxxx-NCR-002238 - PAD Balustrading Architectural Issues - Moorgate Ticket Hall (this NCR) Cxxx-NCR-002239 - PAD Balustrading Architectural Issues - PRM Corridor Cxxx-NCR-002240 - PAD Balustrading Architectural Issues - AP5 Staircase These NCR’s also cover issues raised within CRL-OBS-27320 and CRL-OBS-27792 which all relate to Architectural issues with the balustrades. Cxxx-NCR-002429 - captures missing benchmarks for the PAD balustrades BAL-112 and CRL-OBS-27230 photo 11 also relates to a missing benchmark. Cxxx-NCR-002549 - captures all design related issues for the balustrades including CRL-OBS-27341 on security. This NCR covers - Moorgate Ticket Hall: 1. Quality issues with supporting baseplates identified in CRL-OBS-27320, CRL-OBS-27792 and CRL-OBS-30904. - During installation or transportation of the materials there has been damage done to the exposed finished surface of the baseplates. - The large amount of welding required to hold the base plates together has distorted the finished surface so that there are noticeable bumps/warping. - The gaps between installed baseplates are inconsistent - Termination of not all finished satisfactorily - Some panels not fully adhered to structural baseplate - Finish / polishing of overcladding plates not all finished satisfactorily - Some baseplates appear out of tolerance with visible gaps - Some areas of __ resin poured low and required “topping up” 2. Glass quality issues identified in the attached spreadsheet - Missing Kite Marks - Glass panels of incorrect thickness - Manifestation patterns/provisions incorrect/misaligned - Glazing specification incorrect (2xtoughened panes) not as per WI requirement Note: This design item is addressed under design NCR Cxxx-NCR-002549 3. Installation concerns resulting from design change to 2 toughened glass panes and resin bonded base - Glass MCR not accepted ahead of installation – Address under Cxxx-NCR-002549 for design - Installation quality risk – use of accredited __ installer - Potential for warranty from manufacturer/installer due to reliance on bonded base - Need to ensure a high level of installation checking is completed - __ pour heights not achieved in single pour - Reduced glass embedment depths Note: there are also missing hard/soft body impact test results, these have been raised as part of the quality pack review. Recording as non-conforming to the WI requirements but to be addressed as part of the quality pack.
| 02SL - Stations (LUL) | Cxxx-NCR-002239 | NCR | PAD Balustrading Architectural Issues - MTH PRM Corridor |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-08-15 | 2020-07-20 11:22 | 340 | 2019-04-08 16:59 | Architectural - Balustrade | 500 |  | Manufacturing Defect | Reject | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | There are a number of Architectural issues with the PAD installed BAL-112 glazed balustrades across the station. Cxxx-NCR-002198 has been cancelled and the associated issues split into the 3 station areas. Cxxx-NCR-002238 - PAD Balustrading Architectural Issues - Moorgate Ticket Hall Cxxx-NCR-002239 - PAD Balustrading Architectural Issues - PRM Corridor (this NCR) Cxxx-NCR-002240 - PAD Balustrading Architectural Issues - AP5 Staircase These NCR’s also cover issues raised within CRL-OBS-27320 and CRL-OBS-27792 which all relate to Architectural issues with the balustrades. Cxxx-NCR-002429 - captures missing benchmarks for the PAD balustrades BAL-112 and CRL-OBS-27230 photo 11 also relates to a missing benchmark. Cxxx-NCR-002549 - captures all design related issues for the balustrades including CRL-OBS-27341 on security. This includes the design risk assessment. This NCR covers - Moorgate Ticket Hall - PRM Corridor: 1. Quality issues with supporting baseplates identified in CRL-OBS-27320, CRL-OBS-27792 and CRL-OBS-30309 (linked from Cxxx-NCR-002553). - During installation or transportation of the materials there has been damage done to the exposed finished surface of the baseplates. - The large amount of welding required to hold the base plates together has distorted the finished surface so that there are noticeable bumps/warping. - The gaps between installed baseplates are inconsistent - Termination of not all finished satisfactorily - Some panels not fully adhered to structural baseplate - Finish / polishing of overcladding plates not all finished satisfactorily - Some baseplates appear out of tolerance with visible gaps - Some areas of __ resin poured low and required “topping up” 2. Glass quality issues identified in the attached spreadsheet - Missing Kite Marks - Glass panels of incorrect thickness - Manifestation patterns/provisions incorrect/misaligned - Glazing specification incorrect (2xtoughened panes) not as per WI requirement Note: This design item is addressed under design NCR Cxxx-NCR-002549 3. Installation concerns resulting from design change to 2 toughened glass panes and resin bonded base - Glass MCR not accepted ahead of installation – Address under Cxxx-NCR-002549 for design - Installation quality risk – use of accredited __ installer - Potential for warranty from manufacturer/installer due to reliance on bonded base - Need to ensure a high level of installation checking is completed - __ pour heights not achieved in single pour - Reduced glass embedment depths Note: there are also missing hard/soft body impact test results, these have been raised as part of the quality pack review. Recording as non-conforming to the WI requirements but to be addressed as part of the quality pack. Cxxx-NCR-002511 and Cxxx-NCR-002512 relate to this PRM balustrade, the issues in these NCR’s are: - Reduced glazing panel embedment depths in __ base resin Note: this is captured and addressed in Cxxx-NCR-002549 - __ resin pours topped up, captured as above in this NCR - Cleaning and cladding panel replacement due to resin leak Note: this is captured and covered by the NCR’s themselves
| 02SL - Stations (LUL) | Cxxx-NCR-002241 | NCR | Lifts - Co axial cable resistances |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-07-11 | 2019-10-18 11:56 | 99 | 2019-04-02 11:23 | Mechanical - Lifts | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | As per the attached, __ have installed 50 Ohm cables for connecting lift cameras instead of specified 75 Ohm. Issue has been noted on L5 and L1 as minimum at Liverpool Street.
| 02SL - Stations (LUL) | Cxxx-NCR-002242 | NCR | M135-DAT-00511 Cable Failure |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-05-01 | 2019-05-03 15:45 | 2 | 2019-04-03 12:27 | Communications and Control Systems - Radio | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | M135-DAT-00511 is over the 90 meter limit for cat6a and is 134.9 meters long. See attached fluke result
| 02SL - Stations (LUL) | Cxxx-NCR-002246 | NCR | CCTV installation in MTH Entrance – Lack of Design Coordination (CRL-OBS-27230) |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-08-31 | 2019-07-16 12:30 | -46 | 2019-05-03 09:18 | Architectural - Security | 2000 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Raised by __on on Observation: CRL-OBS-27230 CCTVs have been installed in the Portland stone band on the Moorgate Ticket Hal Façade. This not compliant with the architectural design, so either the design has not been co-ordinated with the CCTV design or the cameras have not been installed as per the CCTV design.
| 02SL - Stations (LUL) | Cxxx-NCR-002250 | NCR | P+T CMS - centre concourse advertising supplies conduit installation |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2019-11-15 | 2019-11-27 11:25 | 12 | 2019-04-05 11:06 | Electrical - Cable Management | 2000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | CMS previously installed from Platform-1 invert to platform level within the centre concourse has been extended to the supply FCUs for the TFL halo advertising signs ( conduits installed behind now fitted GRC panels), at 3 locations between CP7 and CP9 these have not been installed in line with the requirements of the M+W specifications. Conduit and __ junction have not been installed with the use of a BESA box. Excessive lengths __ have been used, __ should only be used for final connection to equipment and length kept to a minimum. Furthermore the conduits installed to the 3no. HALO FCUs have obstructed the additional conduits that have been previously installed for provision of future use, preventing their usage.
| 02SL - Stations (LUL) | Cxxx-NCR-002252 | NCR | Cat 6a Cable Failures |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-05-04 | 2019-05-09 07:57 | 5 | 2019-04-09 09:08 | Communications and Control Systems - Telephony | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The following Cat6a cables are over the 90 meter requirement. See attached Test results 90 meters M135-DAT-04513 – 126.3 meters M135-DAT-00453- 126.5 meters M135-DAT-04374 – 126.3 meters
| 02SL - Stations (LUL) | Cxxx-NCR-002253 | NCR | MShaft - Crack in concrete construction joint wall Streel Level -1 corridor |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-06-19 | 2019-09-16 09:35 | 89 | 2019-04-24 10:46 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | The infill wall to the north elevation of the Street level -1 has been poured. The concrete has not adhered to the adjacent concrete resulting in a visible crack in the wall.
| 02SL - Stations (LUL) | Cxxx-NCR-002254 | NCR | CAM-237 Installed on Temporary Bracket |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-05-13 | 2019-07-03 16:41 | 51 | 2019-04-15 13:17 | Communications and Control Systems - CCTV | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | CAM-237 has been installed on temporary brackets in the final position to allow for commissioning of the CCTV systems whilst waiting for the lighting boom installation.
| 02SL - Stations (LUL) | Cxxx-NCR-002255 | NCR | M135-TEL-00524, 525 , 535, 537, 526 cat 6a cable failure |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-05-02 | 2019-05-10 10:06 | 8 | 2019-04-15 15:07 | Communications and Control Systems - Telephony | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Cat 6a cables exceed 90 meters. See attached distances below. M135-TEL-00524 – 120.4 meters M135-TEL-00525 – 127.9 meters M135-TEL-00526 – 127.9 meters
| 02SL - Stations (LUL) | Cxxx-NCR-002260 | NCR | Incorrect FAN Motors |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-07-31 | 2019-06-07 09:42 | -54 | 2019-04-17 08:03 | Mechanical - Heating Ventilation & Air Conditioning | 45000 |  | Manufacturing Defect | Repair | 2 (6-60k) | Complete | Material/Preservation Problems - Other | Completed |  | Incorrect 6 pole motors have been supplied from __s which will need to be changed to the correct 4 pole Motors as per quotation & order. The current fans installed do not meet the duty required for the system to operate. Fans affected: FAN 601 & 602 FAN 351 & 352 FAN 301 & 302
| 02SL - Stations (LUL) | Cxxx-NCR-002261 | NCR | No Ceiling Installed around CAM-195 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-06-02 | 2019-07-03 16:48 | 31 | 2019-04-23 11:22 | Communications and Control Systems | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | __ ceiling yet to be installed around CAM-195. Camera is installed in it permanent position with it permanent bracket. Howerver, when the ceiling is installed adjustment will have to be made.
| 02SL - Stations (LUL) | Cxxx-NCR-002262 | NCR | M135-TEL-00477 over 90 meters |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-05-21 | 2019-05-09 07:47 | -12 | 2019-04-23 15:42 | Communications and Control Systems - Telephony | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | When tested M135-TEL-00477 was identified as over 90 meters. M135-TEL-00477 - 101.3 meters
| 02SL - Stations (LUL) | Cxxx-NCR-002264 | NCR | CAM-0243 - Ceiling not installed |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-05-23 | 2019-07-03 16:46 | 41 | 2019-04-25 14:00 | Communications and Control Systems - Telephony | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | CAM-243 - This camera is in an area that will have the ceiling fitted later that will mean the camera will need to be moved
| 02SL - Stations (LUL) | Cxxx-NCR-002266 | NCR | Labelling of electiral accessories |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2019-09-08 | 2019-12-02 15:21 | 85 | 2019-04-29 09:27 | Electrical - General | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | Electrical accessories, fused connection units/isolators and lighting junction boxes installed site wide have not been labelled in line with the requirements of the M&W specifications. JY74 requires accessories to show circuit reference and to indicate equipment served on connection units/equipment functions. Jy 82 labelling for electrical accessories requires fused connection units and isolators labelling to indicate function, size of fuse fitted and circuit reference. in addition voltage warning labels are to be fitted to junction/terminal boxes. currently these accessories have had permanent labels fitted indicating their circuit reference details only. Additional labelling is required to be installed to meet the specifications.
| 02SL - Stations (LUL) | Cxxx-NCR-002276 | NCR | robust labels on electrical equipment |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2019-10-31 | 2020-10-14 12:40 | 349 | 2019-05-01 09:20 | Electrical - General | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Management Problem - Other | Completed |  | Labels installed on site are not as per works information and also items identified in PMI Cxxx-pmi-01828 have not been captured, the labels installed on Distribution boards and field equipment use the architectural location number where the SID numbers should be used.
| 02SL - Stations (LUL) | Cxxx-NCR-002277 | NCR | Cables M135-TEL-00535, 537 over 90 meters |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-05-29 | 2019-05-03 15:06 | -26 | 2019-05-01 10:27 | Communications and Control Systems - Telephony | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The following cables have been tested at distances above the 90 meter limit for cat6a. See attached test results. M135-TEL-00535 - 108.0 meter M135-TEL-00537 - 103.8 meter
| 02SL - Stations (LUL) | Cxxx-NCR-002278 | NCR | M135-TEL-00480, 481 Over 90 meters |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-07-17 | 2019-05-03 14:57 | -75 | 2019-05-01 13:47 | Communications and Control Systems - Telephony | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The following cable has been testing at a distance over 90 meters. See attached test results: M135-TEL-00480 - 105.5 meters M135-TEL-00481 - 104.5 meters
| 02SL - Stations (LUL) | Cxxx-NCR-002279 | NCR | M135-TEL-00398 cable over 90 meters |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-08-14 | 2019-05-02 14:45 | -104 | 2019-05-01 14:22 | Communications and Control Systems - Telephony | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The following cat 6a cable is over 90 meters. See attached test results: M135-TEL-00398 - 122.8 meters
| 02SL - Stations (LUL) | Cxxx-NCR-002280 | NCR | BTH - GL9 Column Damages |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-05-30 | 2019-09-05 13:23 | 98 | 2019-05-02 16:30 | Architectural - Finishes | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | During the install of the column skirtings by the sub-contractor. It has been noted at the location of the stainless skirting band install, damages have occurred to the GL 9 precast column. Damage includes 2no. distinct chips. This has occurred at the location of the Eastern fixing points.
| 02SL - Stations (LUL) | Cxxx-NCR-002281 | NCR | BTH Stainless steel panel in POMS heat marks |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-07-31 | 2019-11-07 18:23 | 99 | 2019-05-03 11:05 | Architectural - Finishes | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | A stainless steel wall panel between the POMS on the east elevation of the ticket hall has visible heat marks. (see attached photo)
| 02SL - Stations (LUL) | Cxxx-NCR-002282 | NCR | TEST |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-08-08 | 2019-08-13 16:17 | 5 | 2019-08-08 09:55 | Communications and Control Systems - CCTV | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Not Defined | Completed |  | TEST
| 02SL - Stations (LUL) | Cxxx-NCR-002283 | NCR | Over length Cables |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-05-10 | 2019-05-08 14:19 | -2 | 2019-05-07 10:20 | Communications and Control Systems - Telephony | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | M135-TEL-00535 (108.0m) M135-TEL-00537 (103.8m)
| 02SL - Stations (LUL) | Cxxx-NCR-002284 | NCR | ___Proposed material without ISO9001 Cert |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-08-05 | 2019-06-12 08:29 | -54 | 2019-05-07 12:23 | Architectural - General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Due to longer leadtimes of the __ Backer Rod, a Ceramic backer rod is proposed by __ from an alternate supplier. This backer rod is the same used on the FIRAS certification of __ Doors installed on the Site. Once the backer Rod was bought from the supplier, it was found out that they do not have an ISO9001 Certification. The material is Fire compliant and an MCR will be issued for CRL acceptance.
| 02SL - Stations (LUL) | Cxxx-NCR-002285 | NCR | ___Material Procured without MCR and ISO9001 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-08-05 | 2019-06-12 21:41 | -54 | 2019-05-07 13:28 | Architectural - General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other management problem | Completed |  | The Below orders have been procured by __ from __ without any MCR in place. These are not structural elements and are only architectural PPC Pressed metal or minor support for architectural Flashings. It has been found out the supplier does not have a ISO9001 certificate. Mill sheets for the materials have been supplied and will be submitted on the referenced MCR. Supplier Area installed __ Limited 01a / PPC flashings - Light box __ Limited 67a / PPC Equipment Top Hats __ Limited 06b / PPC Light Box
| 02SL - Stations (LUL) | Cxxx-NCR-002286 | NCR | BTH - Cracks in screed plantroom corridor 3/237 CIR-PL |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-08-31 | 2019-09-10 15:36 | 10 | 2019-05-07 15:12 | Architectural - Flooring | 3000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | The screed in the corridor to the BTH plant room has surface cracks.
| 02SL - Stations (LUL) | Cxxx-NCR-002287 | NCR | Over length cables |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-05-08 | 2019-05-09 08:00 | 1 | 2019-05-08 14:09 | Communications and Control Systems - CCTV | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | M135-DAT-04373 109.9M
| 02SL - Stations (LUL) | Cxxx-NCR-002288 | NCR | Over length cables |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-05-08 | 2019-05-09 07:51 | 1 | 2019-05-08 14:16 | Communications and Control Systems - CCTV | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | M135-DAT-04375 126.3M
| 02SL - Stations (LUL) | Cxxx-NCR-002290 | NCR | ___33a_Glazing surface penetrations Lift moorgate shaft PL+1 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-12-31 | 2020-06-17 17:23 | 169 | 2019-05-09 07:13 | Architectural - General | 10000 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The Cladding was designed with the penetration for the Lift CMS at the head detail. Please refer to attached drawing. The CMS has been installed on site approx 150mm to the right from centre of the designed position. This impacts the already manufactured STO panel and the CMS clashes by 50mm.
| 02SL - Stations (LUL) | Cxxx-NCR-002292 | NCR | Over length cables |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-05-09 | 2019-05-09 09:00 | 0 | 2019-05-09 08:32 | Communications and Control Systems - CCTV | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | M135-DAT-04374 108.7M M135-DAT-04401 113.2M
| 02SL - Stations (LUL) | Cxxx-NCR-002293 | NCR | Over length cables |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-05-09 | 2019-05-10 06:40 | 1 | 2019-05-09 14:46 | Communications and Control Systems - CCTV | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | MI35-DAT-04513 126.3M M135-TEL-00453 126.5M
| 02SL - Stations (LUL) | Cxxx-NCR-002295 | NCR | Over length cables |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-05-10 | 2019-05-10 15:19 | 0 | 2019-05-10 12:26 | Communications and Control Systems - Telephony | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The following cable has been tested at a distance over 90 meters. M135-TEL-00398 122.8M
| 02SL - Stations (LUL) | Cxxx-NCR-002296 | NCR | MTH - Stainless Steel panels to OSD column defects |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-08-31 | 2020-02-07 16:17 | 160 | 2019-05-13 08:18 | Architectural - Walls | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Defects / issues noted on OSD Stainless Steelwork Cladding EWS-723. - The gap with between the corner pieces is not a constant size - The panels installed are dirty and stained - Panels are installed out of tolerance and gaps need to be filled - The joints are too large and do not meet the works information - The panels are not flush - From a distance there is a rippling effect on the face of the stainless steel
| 02SL - Stations (LUL) | Cxxx-NCR-002299 | NCR | Cxxx-LAO-E-NOX-C101-50176 Cable drum tests |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-05-13 | 2019-08-13 09:55 | 92 | 2019-05-13 10:21 | Communications and Control Systems - Radio | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | Cxxx-LAO-E-NOX-C101-50176 Appendix 09 of the IRN folder that relates to Cable drum tests “none or not all” of the drum associated with this IRN file are available or have been tested prior to installation.
| 02SL - Stations (LUL) | Cxxx-NCR-002300 | NCR | P&T - Escalator Barrel 3 - RSS Hinged S/S Cladding Panels - Issues Identified at Benchmark Inspection |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-12-31 | 2020-01-13 15:04 | 13 | 2019-05-14 09:26 | Architectural - General | 10000 |  | Design | Repair | 2 (6-60k) | Complete | Design Problem - Inadequate or defective design | Completed |  | A Benchmark Inspection was carried out on 29th April 2019 with CRL. The issues below have been identified: - On ES3 the Superlux has now been installed (Note) - The Stainless Steel Panels do not match the curvature of the in-fills - The butt joints are not chamfered or neat - The Panels are heavy now the Superlux is in place - This should be co-ordinated so that the fuse spur is not located next to the stop button - The brush is the panels should be horizontal but this does not look correct - The Edges of the panels seem to have marks
| 02SL - Stations (LUL) | Cxxx-NCR-002301 | NCR | __X Entrance Door Push Bar Heights |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-10-31 | 2019-10-14 11:51 | -17 | 2019-05-15 08:39 | Architectural - Doors | 1500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | The pushbars installed on the __ entrance door is installed at different heights. Refer to the photo attached. pushbars both detailed at 1010 from FFL on drawings 50232 and 50233. Drawing 50234 shows them at different levels.
| 02SL - Stations (LUL) | Cxxx-NCR-002302 | NCR | BMS CRL asset IDs do not match software IDs |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-08-22 | 2020-05-14 16:10 | 266 | 2019-05-15 12:42 | Mechanical - Mechanical Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Verification Problems - Inspector not familiar with inspection methods | Completed |  | CRL asset ID information labels have been installed on site. The IDs used on the labels do not match the IDs on the __ BMS software. This is applicable to all site areas relating to BMS works. ID schedules should have been agreed / locked down between parties.
| 02SL - Stations (LUL) | Cxxx-NCR-002303 | NCR | Over length cables |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-05-16 | 2019-05-16 14:45 | 0 | 2019-05-16 07:38 | Communications and Control Systems - Telephony | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | M135-TEL-00380 96.3M
| 02SL - Stations (LUL) | Cxxx-NCR-002304 | NCR | Over length cable |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-05-16 | 2019-05-16 14:49 | 0 | 2019-05-16 07:50 | Communications and Control Systems - Telephony | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | M135-tel-00477 101.3m
| 02SL - Stations (LUL) | Cxxx-NCR-002305 | NCR | GFRC Cladding - Connection of Stainless Steel Support to Galvanised Primary Steel |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-10-31 | 2019-11-25 10:19 | 25 | 2019-05-16 11:16 | Architectural - General | 2000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Bracketry connection of stainless steel GFRC steel support to galvanised primary steel is currently achieved using designed galvanised bolt and washer fixings. There is a low risk of bimetallic corrosion in the area due to no presence of water (a factor which must be present for this to occur), however due to the design life of the structure being over the 5 years of a temporary structure using this connection cannot be assured. A physical barrier between the stainless steel and galvanised steel is therefore required.
| 02SL - Stations (LUL) | Cxxx-NCR-002306 | NCR | Blofmield Box Staircase pressurisation grilles |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2020-02-20 | 2019-09-30 12:06 | -143 | 2019-05-16 14:35 | Mechanical - Heating Ventilation & Air Conditioning | 2999 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | The current installed grilles were ordered to the latest __ equipment datasheets and Crossrail M&S specification available at the time. Upon review it was agreed that the grilles form part of a life safety system and must be fixed blade - Not adjustable.
| 02SL - Stations (LUL) | Cxxx-NCR-002307 | NCR | BTH - Escalator decking to match cladding |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2020-08-10 | 2021-03-05 14:34 | 207 | 2019-05-20 07:13 | Architectural - Finishes | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | After a site walk round with CRL, LU and __, solutions were agreed. A mastic bead would be applied where the escalator decking interfaced with stainless steel cladding panels. Where the interface is between escalator decking and glazed glass panels the agreed solution is an approved rubber gasket. This is being captured in a CCM to be sent over to CRL. In the interim samples of the mastic and gasket have been offered up to and been accepted on site by CRL. Photos of both have been uploaded. The gaskets are being ordered and should be on site by the week commencing Monday 20th July.
| 02SL - Stations (LUL) | Cxxx-NCR-002308 | NCR | M135-DAT-04348, 04350, 04351, 04535 cat 6a cable failure |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-05-22 | 2019-05-22 08:23 | 0 | 2019-05-20 15:12 | Communications and Control Systems - CCTV | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The following Cat 6a Cables have been identified as the over 120 meters see below numbers and length with test results attached: M135-DAT-04348 169.8 meter M135-DAT-04350 151.8 meter M135-DAT-04351 160.9 meter M135-DAT-04535 156.9 meter
| 02SL - Stations (LUL) | Cxxx-NCR-002309 | NCR | M135-DAT-04349, 04360 Cat 6a Cable failure |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-05-22 | 2019-05-22 08:26 | 0 | 2019-05-20 15:53 | Communications and Control Systems - CCTV | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The following Cables have been identified between 90 - 120 meters long when tested. See below cable numbers and length with attached test results. -M135-DAT-04349 96.1 meter -M135-DAT-04360 101.5 meter
| 02SL - Stations (LUL) | Cxxx-NCR-002312 | NCR | P&T - End Walls - __ __ Doors Package 04a - Installation / Interface Issues |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-10-24 | 2019-10-31 16:00 | 7 | 2019-05-22 16:16 | Architectural - Doors | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Cxxx-PMI-03350 - Drawings forming part of this Package re-coded to allow for red lines to be progressed. Outstanding comments to be addressed during this phase and reflected in final “As builts”. Works have commenced and progressed on site without an accepted F2 design or an offer of a completed benchmark for works installed (__ Package 40a) - CRL-OBS-27826 and associated Cxxx-NCR (progressing without an approved design in place ref – JA.3102). No portion of the works shall commence without acceptance of the required submittals by the Project Manager. CRL have raised concerns associated with the design and installation on drawings that have not been addressed in the as installed design. The Platform End Glass/Doors and Telephone Cabinet and Equipment have been installed on site. Refer to attached photographs in CRL-OBS-27826 and outstanding comments as per comment log Cxxx-LAO-A-XCS-C101-50488 Rev C01 associated with Observation. Quality Surveillance: Inspection Notes – Work in Progress – Platform End Walls: - Final lighting – not functional. - Top trim and interface with GFRC missing. - Mastic not installed (TSC-202). - Dirty. - Pushbar and closer not installed on door (cannot check functionality). - Threshold detail – threshold plate not installed. Refer to photographs – reference WI drawings – Cxxx-LAO-A-DWG-C101-50216 C01 Photo 1. Interface with PES – A hole in the floor finishes (not acceptable). Photo 8/13. Missing floor finishes adjacent to steel support frame visible between door frame. Photo 3. Visible screw fixings – type of screw not acceptable – samples of alternatives to be provided (this will be a comment on __ Cxxx-LAO-N2-LRG-C101-50003 Rev 1739.0 Revision 1.0). Photo 4/5. Gap between where PES terminates and Platform End Wall starts. Photo 7. Damage to door Photo 11. Smashed panel – could be a result of unfinished glazing – no s/s profile. Photo 10. Telephone enclosure – door/aperture in cladding relationship, cut out shapes and location of lock. Photo 6. Joints in glazing - mis-alignment of door architrave with joints. Photo 12. Open joints at interfaces and where bulkhead glass meets GFRC and PES. Photo 2. Unfinished finishes at door/interfaces with GFRC/PES
| 02SL - Stations (LUL) | Cxxx-NCR-002313 | NCR | MSH - Lift 2 MAP Panel Clash with __ Cladding |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-10-31 | 2019-09-26 14:34 | -35 | 2019-05-22 09:24 | Mechanical - Lifts | 1500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Please see attached images and drawings. Lift 2 at 107 level Moorgate Shaft (PRM corridor, __ package 13a) has a clash between __ MAP panel and __ cladding door. Door cannot be moved back to sit flush with rest of cladding line, and currently sits 17mm proud of adjacent cladding.
| 02SL - Stations (LUL) | Cxxx-NCR-002314 | NCR | __X Ductwork access Doors ( Required for Future Cleaning Requirements ) |  | Crossrail | PDP | LIS - Liverpool Street Station (Central) |  | 2019-09-25 | 2019-09-12 06:27 | -13 | 2019-05-22 10:03 | Mechanical - Heating Ventilation & Air Conditioning | 2500 |  | Incomplete Works | Repair | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | The document attached has been produced inline with document CRL1-XRL-Z-RGN-CR001-50523 which I believe you are aware of and have reviewed, I have looked at all areas of __ to ensure that the ductwork access doors are adequate for future cleaning requirements by the IM. The list attached indicate where I believe more/larger access doors are required, I have used the relevant standards as detailed in document CRL1-XRL-Z-RGN-CR001-50523 to produce the list and we would request that we discuss the contents this week to agree a way forward.
| 02SL - Stations (LUL) | Cxxx-NCR-002315 | NCR | M135-TEL-00524, 00525 Cables over 90 meters |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-06-19 | 2019-06-05 06:52 | -14 | 2019-05-22 14:56 | Communications and Control Systems - Telephony | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Other | Completed |  | Cables have been identified as over the 120+ limit by during testing, see below lengths and cable number with test results attached
| 02SL - Stations (LUL) | Cxxx-NCR-002316 | NCR | No evidence provided of First Fix Benchmark acceptances for 1a and 3a - Kaice scope -MTH |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-11-30 | 2019-11-29 10:56 | -1 | 2019-09-13 09:34 | Architectural - Finishes | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Sub Contractor __, could not provide evidence of first fix Benchmark acceptance in line with submitted ITP.
| 02SL - Stations (LUL) | Cxxx-NCR-002317 | NCR | __ 04A External Facades - No evidence of Benchmark acceptances |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-10-31 | 2020-11-04 17:18 | 370 | 2019-09-13 09:36 | Architectural - Finishes | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | The Sub Contractor, __, could not provide evidence of Benchmark acceptance in line with the specification. JH13.2105 Benchmark Requirements
| 02SL - Stations (LUL) | Cxxx-NCR-002319 | NCR | P&T – End Walls / Screens - __ Package 40a – Visible Fixings (CRL-OBS-27921) |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-09-07 | 2019-10-14 14:45 | 37 | 2019-05-30 12:45 | Architectural - General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | __ fixing drawings have been submitted for acceptance. However, works have commenced on site and sample/details of fixings were not provided. During a site observation the fixings to the Platform End Screens were reviewed along with fixings. Concerns have been raised verbally. Observation CRL-OBS-27921 has been raised to identify an area that requires re-consideration. Refer to attached photographs (1 and 3) and attached comment log (Cxxx-LAO-A-XCS-C101-50488 Rev C01). Refer to Architectural Specification - Cxxx-LAO-A-RSP-C101_WS103-50001 - Cxxx Section - JH11.2101 – Samples - g) All visible fixings (where visible fixings form part of the design intent).
| 02SL - Stations (LUL) | Cxxx-NCR-002320 | NCR | Installation of insulation matts without approved NCR. |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2020-02-04 | 2020-06-16 14:15 | 133 | 2019-05-30 13:57 | Mechanical - Heating Ventilation & Air Conditioning | 5999 |  | Material | Rework | 3 (3-6k) | Complete | Management Problem - Inadequate administrative control | Completed |  | The valve mats have been installed prior to the MCR signed off, the works information procedure is that all materials must be approved prior to installation thus this Non conformance report.
| 02SL - Stations (LUL) | Cxxx-NCR-002321 | NCR | Moorgate Shaft Riser Volume Control |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2020-08-10 | 2019-11-08 11:15 | -276 | 2019-05-30 14:05 | Mechanical - Heating Ventilation & Air Conditioning | 2999 |  | Incomplete Works | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Moorgate shaft lobby pressurisation on Platform level +2, Platform level +1, Platform level +0 system cannot fit volume control dampers onto the branches thus creating a non conformance inline with Cxxx specification JY30.1404.
| 02SL - Stations (LUL) | Cxxx-NCR-002322 | NCR | Damage to chiller coils |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2020-03-05 | 2019-06-26 10:20 | -253 | 2019-05-30 14:13 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Site works near to the chiller have caused damage to the coils. Previous NCR had been raised and chiller coil guard had since been installed, additional damage through the chiller protection has been done thus this NCR
| 02SL - Stations (LUL) | Cxxx-NCR-002323 | NCR | __ 30a LVR 115_No evidence provided of Benchmark acceptances |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-10-31 | 2019-12-12 18:10 | 42 | 2019-06-28 15:50 | Architectural - General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Contractor could not provide evidence of Benchmark acceptance in line with the specification and ITP. JH13.2105 Benchmark Requirements; The first completed length of each system installed.
| 02SL - Stations (LUL) | Cxxx-NCR-002324 | NCR | M135-DAT-04405 Cable over 90 meters |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-06-05 | 2019-06-03 16:25 | -2 | 2019-06-03 13:04 | Communications and Control Systems - CCTV | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The following Cat 6a Cable has been identified as the over 90 meters see below number and length with test results attached: M135-DAT-04405- 92.4 meters
| 02SL - Stations (LUL) | Cxxx-NCR-002325 | NCR | M135-TEL-00400 over 90 meters |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-06-05 | 2019-06-03 16:28 | -2 | 2019-06-03 13:45 | Communications and Control Systems - Telephony | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The following Cat 6a Cables have been identified as the over 120 meters see below numbers and length with test results attached: M135-DAT-00400 93.5 meter
| 02SL - Stations (LUL) | Cxxx-NCR-002326 | NCR | BTH – ES1 – __ Package 67a – Stainless Steel Cladding IWS-717 (CRL-OBS-27956) |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-10-31 | 2019-11-04 11:24 | 4 | 2019-06-03 14:51 | Architectural - Finishes | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | ESC1 Stainless Steel Cladding (IWS-717 – __ Package 67a) has been installed without approved drawings. Outstanding comments have been captured on Comment Log – Cxxx-LAO-XCS-C101_WS099-50092 Revision 2.0. These comments to be addressed on site – (refer to document relationships and pdf of comment log attached to this Observation) and Cxxx-PMC-03550.
| 02SL - Stations (LUL) | Cxxx-NCR-002327 | NCR | MTH – Level -1 - PRM Corridor - Ceiling/Equipment Installation (CRL-OBS-27775) |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-07-31 | 2019-06-26 11:50 | -35 | 2019-06-05 16:24 | Architectural - Ceilings & Soffits | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | The ceiling was not constructed in accordance with approved drawings stated below. The lack of co-ordination between architectural/services drawings has resulted in a number of queries / comments as listed below in PRM corridor. __ to review and close out as below. - The layout for ceiling mounted services is a bit haphazard and not ideal visually: the equipment should have been arranged so that the components are symmetrical around the centre of each ceiling section. - It was agreed that for __ ceilings that MEP equipment would be fixed to the narrow “semi-fixed” ceiling panels and that the larger alternating panels would be fully demountable to allow for better access to ceiling level services and regular inspection of the concrete structure above. - The majority of MEP equipment on the PRM corridor is fixed to the larger panels. Cxxx need to demonstrate if the larger panels can be demounted without requiring removal or re-commissioning of the ceiling mounted equipment so that access and maintenance is maintained for services and structures. VAP-10C Tag Sheet - CLG-718 / PT-185
| 02SL - Stations (LUL) | Cxxx-NCR-002329 | NCR | __X - Hydrant enclosure lock rusted (CRL-OBS-27780) |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-12-21 | 2019-10-24 14:06 | -58 | 2019-10-22 08:25 | Architectural - Finishes | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | The Lock to the hydrant enclosure on the Façade at Broad Street Avenue is exhibiting signs of rust.
| 02SL - Stations (LUL) | Cxxx-NCR-002330 | NCR | __X incomplete works- After Architectural Cladding has been Completed |  | Crossrail | PDP | LIS - Liverpool Street Station (Central) |  | 2019-07-03 | 2019-11-27 10:58 | 147 | 2019-06-05 08:56 | Fire - Compartmentation | 5000 |  | Incomplete Works | Rework | 3 (3-6k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | __X Entrance area-Station & tunnel firemain pipework and PH Vent pipe are sleeved and the sleeves have not been firestopped. CRL raised observations 27075-21.3.2019 before the cladding commenced and 27744 10.5.2019 after cladding had been installed which greatly hindered access to complete the works correctly. Cxxx have ignored the observations and the firestopping because of its location could be missed, incomplete compartmentation is a contravention and this work needs to be completed before handover to the LU/RFL.
| 02SL - Stations (LUL) | Cxxx-NCR-002331 | NCR | __ louvered Doors Moorgate |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-07-05 | 2020-02-06 13:12 | 216 | 2019-06-07 15:05 | Architectural - Doors | 1000 |  | Material | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The Fixings used to secure the framework to the concrete structure (Sleeve Anchor HEX Bolts) are a none approved product supplied by __ Doors. To ensure that they reached the required strength, pull test would be taken to demonstrate the fixings reached the required limit.
| 02SL - Stations (LUL) | Cxxx-NCR-002332 | NCR | On site testing |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-08-20 | 2019-08-15 10:06 | -5 | 2019-07-23 15:28 | Architectural - Doors | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | No on site water test carried out on __ louvre doors and panels as detailed in ITP.
| 02SL - Stations (LUL) | Cxxx-NCR-002333 | NCR | BTH - Entry lighting gaps between strip lights and stainless steel |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2020-05-01 | 2020-12-22 15:08 | 235 | 2019-07-03 15:47 | Architectural - Finishes | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The interface between the stainless steel and strip lighting at BTH entrance has gaps. This gap is present on both sides of the lights.
| 02SL - Stations (LUL) | Cxxx-NCR-002335 | NCR | Sign off sheet for the final inspection of the completed works for the waterlining ,ES6 ( __ package 24a) North elevation is missing |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-09-30 | 2019-06-20 15:52 | -102 | 2019-06-07 13:29 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | For ES6 (__ Package 24a) North Elevation in Broadgate we are missing the final inspection sign off for the water lining that was installed . The final inspection of the completed works is a hold point requirement under section 3.11 of ITP Cxxx-LAO-04-ITP C101-50219. However we have records ( as per the attacahed) of inspections such as the first fix install for the above works as carried out by Stephen Tucker of __.
| 02SL - Stations (LUL) | Cxxx-NCR-002336 | NCR | Moorgate Watermist System-No Electrical/Fire/Controls Design Approved ( Works Commenced Nov 18 ) |  | Crossrail | PDP | LIS - Liverpool Street Station (Central) |  | 2019-12-24 | 2020-01-30 20:55 | 37 | 2019-06-07 09:28 | Fire - Fire Systems & General | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | CRL have issued the following EWNs regarding the lack of an approved design for the electrical/fire & controls wiring systems for the Moorgate Watermist System, EWN 01599-June 2018 EWN 01700-Nov 2018 EWN 01765-May 2019 EWN 01599 was issued to record that no design was in place even though the mechanical installation was 90% complete. EWN 01700 was issued to record that Cxxx commenced CMS & wiring of associated systems with out an approved design. EWN 01765 was issued to record that CRL had organised meetings In May 2019 to discuss and ensure that Cxxx had a design ready for approval, Cxxx assured CRL that the design would be available but the last meeting held on the 23.5.2019 Cxxx did not attend. As of todays date 7.6.2019 Cxxx have not got an approved design and the elec/fire & controls wiring has progressed without an approved design.
| 02SL - Stations (LUL) | Cxxx-NCR-002337 | NCR | Over length cables |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-06-10 | 2019-06-12 12:06 | 2 | 2019-06-10 08:25 | Communications and Control Systems - CCTV | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | M135-DAT-04429 (147.6 M) M135-DAT-04425 (128.6M) M135-DAT-04424 (126.0M)
| 02SL - Stations (LUL) | Cxxx-NCR-002338 | NCR | Site Wide - __ Signage - All Different Types of Signage - Installation proceeded without approved Benchmarks |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2020-03-31 | 2021-05-28 11:21 | 423 | 2019-06-12 14:05 | Architectural - Signage | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | Installation of W&W Signage proceeded without approved Benchmarks for scopes such as: - Totems Signs - Suspended Signs - Fascia Signs & Poster Cases - Curved Glass and General Wall Signs - Projecting Signs On a Weekly CRL Site Inspection the comment below was raised for the Curved Wall Signs on the Platforms (CRL-OBS-28077): - Alignment between top and bottom signage units is not acceptable. The step in alignment far exceeds the 2mm tolerance allowance. This issue has been observed on several platform signs. Cxxx-NCR-002245 was raised previously (CRL-OBS-27230) however not progressed to the next stage.
| 02SL - Stations (LUL) | Cxxx-NCR-002339 | NCR | Non complaint use of flexible Cable |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2020-03-18 | 2020-02-21 15:39 | -26 | 2019-06-12 12:20 | Electrical - Electrical Engineering General | 10000 |  | Incorrect Installation | Rework | 2 (6-60k) | Complete | Design Problem - Other | Completed |  | Cable installed to emergency light fittings within Moorgate and Broadgate Ticket Halls without approved MCR. Subsequent return of MCR is rejected for use for emergency light fittings.
| 02SL - Stations (LUL) | Cxxx-NCR-002340 | NCR | P&T - AP1/CH7 - __ Signage - PHP VE Signs - Incorrect Installation |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-10-10 | 2020-03-11 13:39 | 153 | 2019-06-12 14:14 | Architectural - Signage | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The installed sign above the PHP at Platform Level, AP1/CH7 is not compliant with the standard heights agreed upon with Cxxx (via Cxxx-FCD-02692 - 1600 mm AFFL to bottom of sign).
| 02SL - Stations (LUL) | Cxxx-NCR-002341 | NCR | AP6 Lean Bars- Aluminium Finish |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-11-01 | 2019-08-13 10:49 | -80 | 2019-06-12 16:56 | Architectural - Finishes | 500 |  | Material | Reject | 4 (0.5-3k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | AP6 (Northern Line Link Tunnel) has 5 no lean bars. The design of the lean bars was for the seat panel to be a natural bright anodised aluminium with the aluminium end caps having a matt nylon powder coat. (RAL 9011). The full seat panel has been coated instead of only the end caps.
| 02SL - Stations (LUL) | Cxxx-NCR-002342 | NCR | __X - Broadgate External Facade - __ Package 50a - Several Issues (CRL-OBS-27964) |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2020-01-15 | 2020-02-19 11:53 | 35 | 2019-07-23 08:28 | Architectural - General | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | The Blomfield Box (__ Package 50a) has been constructed without "accepted" drawings in place. Cxxx-PMC-03550 has been raised allowing drawings to be progressed to Code 01 on the understanding that all outstanding issues will be addressed during the "red-line" stage to assist programme. Comment logs associated with this package are attached to the Observation and are to be addressed in order to close. Site Inspections have yet to be arranged to review installation, workmanship and performance.
| 02SL - Stations (LUL) | Cxxx-NCR-002344 | NCR | Ductwork Identification |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2020-03-27 | 2020-03-20 15:36 | -7 | 2019-06-21 06:55 | Mechanical - Heating Ventilation & Air Conditioning | 2000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not trained for the work being performed | Completed |  | After a walk down of various ductwork systems it was highlighted that the identification i.e. arrows were on the wrong ductwork systems.
| 02SL - Stations (LUL) | Cxxx-NCR-002346 | NCR | BTH – ES1 and ES6 – Misalignment of __ panels installation (CRL-OBS-27230) |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2020-05-31 | 2020-04-03 15:50 | -58 | 2019-08-14 15:11 | Architectural - Finishes | 10000 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | Inspection carried out by __ raised concerns associated with the stainless steel cladding as detailed below Photo 1: Broadgate Ticket Hall - Escalator Deck - Cladding Interface At the junction between the blue glass, stainless steel and escalator deck there there is an open gap through which object can be pushed into the cladding void. The design should prevent objects from being pushed into the cladding/escalator void so as to avoid a fire hazard in the void. Photo 2: Broadgate Ticket Hall Canopy - Internal Cladding There is a large gap at the of joints between stainless steel cladding where the s/s meets the blue glass above. As mentioned for Photo 1, the design should prevent objects from being pushed into the void. Photos 3, 4, 5, 6, 7 & 10: Moorgte and Broadgate ticket halls - Escalator Deck - Cladding Interface -There is a gap between the escalator deck and wall cladding. This allows dust, debris and object to fall into the cladding/escalator void. As mentioned for Photo 1, the design should prevent objects from being pushed into the void. -the gap between the deck and the cladding demonstrates that the cladding is passing below the deck line. This is a design issue that is evident on escalators ES1, ES6 & ES6 (Upper escalators from both Moorgate and Broadgate tickets halls) and occurs for interface between decking with glass, stainless steel & perforated vitreous enamel cladding. Cxxx are required to demonstrate that each cladding type can be demounted without fully demounting the escalator deck. -additionally, on the above photos, the gap between the escalator deck and the cladding is visibly tapered, in some cases the taper is from 0mm to approx. 10mm. This appears to be because cladding panels are not meeting the max. allowed tolerance in cladding alignment of 2mm within and between panels. For all of the issue noted above, for photos 1-7, an NCR should be raised with a proposal on how to rectify the issues identified.
| 02SL - Stations (LUL) | Cxxx-NCR-002347 | NCR | BTH – ES6 – Gaps between STO Panels and S/S Panels (CRL-OBS-27230) |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-09-01 | 2019-08-29 09:16 | -3 | 2019-07-03 21:52 | Architectural - Finishes | 3000 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Information not detailed | Completed |  | The Joint Gap in between the Stainless steel panel is larger than design intent. There are voids in the interface with the joints and escalators.
| 02SL - Stations (LUL) | Cxxx-NCR-002348 | NCR | MTH - Waterproofing of Station Entrance Facade (CRL-OBS-26107, CRL-OBS-27283 & Cxxx-NCR-002176) |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2020-09-25 | 2020-11-20 16:39 | 56 | 2019-09-13 09:22 | Architectural - Finishes | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | CRL-OBS-27283 Works have commenced on the Moorgate Ticket Hall and specifically the façade of the building. Waterproofing is being carried out as part of the façade package that seals the building at roof/façade interface. Drawings for this area are not approved and concerns have been raised previously via mark-ups of drawings. These include but are not limited to the following: - Coping - EPDM lapping detail - does not seem to be properly installed between the Sto and Portland Stone panel. - Suitability of mastic as a waterproofing sealant - longevity. - Suitability of bolts fixing the coping into concrete - weatherproofing? - MTH High-walk - coping fixed into place but no evidence of a waterproofing membrane - this is linked to the station fascia and will provide a route for water ingress. The waterproofing installed does not meet the sub-contractor detail. Witness points were not offered during installation and the works have now been covered. (0594/1 - 5). During a Quality Surveillance site walk we observed the installation of the glazed rain screen cladding for the Moorgate Ticket Hall. The façade design is made up of number of components or systems each with a differing performance requirement: EWS-115, EWS-220 and EWS -910. The water proofing behind the cladding has not been installed using a single water proofing system – sheet membrane and liquid applied systems have both been installed. In some areas there is no evidence of waterproofing being in place (around Bostwick Gate floor/jamb and head details) and how this has been co-ordinated with adjacent finishes/types of façade (Tag sheet references noted above). If water does penetrate the façade in some areas this will require an outlet again, this is not evident in what has been installed on site. CRL-OBS-26107 Fire separation is also to be provided between the station and OSD/Adjacent Buildings. There is no evidence that this has been considered based on what can be seen on site.
| 02SL - Stations (LUL) | Cxxx-NCR-002350 | NCR | MTH - Entrance Interface Matwell / __ (CRL-OBS-27290) - __ Package |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2020-05-31 | 2020-09-04 15:34 | 96 | 2019-09-13 09:58 | Architectural - Flooring | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The Bostwick Gates have been installed at Moorgate Ticket Hall- between Grid lines 7-8 Drawings have not been accepted by CRL and state that additional information/detail is required to conclude a review. The door guide at the interface with the matwell is damaged and raises concerns with performance and durability that must be address. Benchmark for this gate is outstanding.
| 02SL - Stations (LUL) | Cxxx-NCR-002351 | NCR | MTH - Entrance Matwell/Cladding Interface/__ housing screed infills |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-04-30 | 2020-11-24 12:25 | 574 | 2019-10-03 14:58 | Architectural - Flooring | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Incorrect Skirting layout interface in the MTH South Matwell. Cxxx to provide proposal to address issues (captured on Cxxx-XRL-A-MRC-C101_WS099-50001 -Item 4.9)
| 02SL - Stations (LUL) | Cxxx-NCR-002352 | NCR | __X - Emergency Staircases - Pre-cast stairs and landings - Reduced rise dimension (VAP 450 - Photo 11) |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-10-31 | 2019-10-21 16:02 | -10 | 2019-07-01 14:03 | Civil - Civil Engineering General | 5000 |  | Design | Repair | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | PCC stairs cast and installed to design and specification, no issue In-situ slab cast to design and specification, no issue The in-situ landing slab effectively dictates the rise of the first step in each flight, and has been noted as out of tolerance to the stair BS.
| 02SL - Stations (LUL) | Cxxx-NCR-002353 | NCR | __X - Back Entrance - Louvres - Several Issues (VAP 473 - Photos 5, 6, 7, 8) |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2020-01-10 | 2020-01-07 16:49 | -3 | 2019-10-25 16:19 | Architectural - Walls | 500 |  | Incomplete Works | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Please find attached comments raised on VAP 473 for the Louvre Elevation. Photo 1: General view of door with the louvres cut for key and handle access Photo 2: Access to insert key is limited. The top louvre should be cut back in line with those below to allow easier and safe key insertion. The aperture should be boxed out to close off the sharp edges of the louvres. At present it is not possible to grip the handle without brushing the edges of the louvres. Photo 3: There is long movement on the handle which hits the bottom louvre. This allows fingers to be trapped. The aperture should be increased to allow safe and easy use of the handle. Photo 5: The jamb flashing/closer is to be fitted and the louvres below completed. Photo 6: How will the opening above the door be closed off? Will there be an insect mesh behind the open louvres? What security/fire rating is required? The door is to SR 3 construction. Photo 7: Internal view of door head and louvres over. Refer to comment on Photo 8. Photo 8: Is the louvre installation completed? Has it been installed to the correct details? What function does the steel plate perform? The flashing at the head is bent.
| 02SL - Stations (LUL) | Cxxx-NCR-002355 | NCR | BTH - AP8 Hanger Support |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2020-06-30 | 2020-06-05 08:05 | -25 | 2019-06-28 11:42 | Civil - Structural Engineering | 3000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other management problem | Completed |  | Following install of AP8 hanger beam, it is apparent that there are a number of items that do not meet specification. 1) Inspection and Test Plan - Not Code 1 2) Unclear/ Missing drawings to fixing arrangement/details 3) It appears there are missing fixings - slotted holes are present with no fixings installed 4) Fixings installed at an angle, such that the bolt does not make contact with fixing plate/washers
| 02SL - Stations (LUL) | Cxxx-NCR-002356 | NCR | BTH - Damage to lift 8 portal frame support steelwork |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-07-26 | 2019-09-16 09:31 | 52 | 2019-06-28 11:52 | Civil - Structural Engineering | 2500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Following fixing of Lift 8 portal frame, it was apparent the supporting steelwork bolting sleeve (RSS) did not line up with the lift portal base plate (__). It was requested by the subcontractor to drill the RSS frame to fit the bolts and actioned. In the process of drilling the sleeve stiffening supports were damaged and reduced the structural integrity and durability of the section.
| 02SL - Stations (LUL) | Cxxx-NCR-002357 | NCR | BTH - Entrance Matwell (CRL-OBS-28112) - __ Package |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2020-12-31 | 2021-03-26 15:06 | 85 | 2020-02-21 15:05 | Architectural - Flooring | 3000 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Details: Following a CRL Inspection of BTH Matwell System the below issues have been identified as not in line with the Architectural Specification Clauses JM40.1224 and JM40.1225. 1 – Works have progressed without drawings been submitted for CRL Acceptance. 2 – There was no opportunity for CRL to witness the water test of the substrate demonstrating the screed is laid to falls and water falls to the drainage points. 3 – Drawings (such as Cxxx-LAO-A-DDD-C101_Z-25864 C02) should have been updated/taking into consideration to incorporate the removal of the flood barrier. 4 – No evidence of MCR being submitted for the matwell stainless steel support frame, aluminium ridged sections and waterproof to screed. 5 – Strategy for de-mountability of the matwell system for cleaning to be demonstrated. Concerns were also raised by LUL Premises with regards to the support framing being laid in two directions making it more difficult and time consuming to maintain and clean the matwell and the drainage as well as the fact of some of the drainage gullies being located under the aluminium ridged sections and the presence of a lip that may prevent all water to drain to the gully (VAP 599 – Photo 31 and Photo 33). The unsupported trellidor track (VAP 599 – Photo 32) was also mentioned as a concern. 6 – Concerns were raised for the integration of the matwell drainage system along with details for interfaces with other adjacent elements of work including the cladding, the skirtings, the inclined lift floor plate, the trellidor and the PHP.
| 02SL - Stations (LUL) | Cxxx-NCR-002358 | NCR | M135-TEL-00524 & M135-TEL-00525 CAT 6A CABLE FAILURE |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-07-01 | 2019-07-05 10:44 | 4 | 2019-07-01 12:06 | Communications and Control Systems - Telephony | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | CAT6a CABLES EXCEED 90 METERS, DETAILS ADDED BELOW. M135-TEL-00524 - 120.4 METERS M135-TEL-00525 - 127.9 METERS
| 02SL - Stations (LUL) | Cxxx-NCR-002359 | NCR | TUN - BWK - Doorways unaligned |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-07-29 | 2019-09-16 09:24 | 49 | 2019-07-01 16:30 | Architectural - Brickworks/Blockworks | 2500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Translation from F1 to F2 design (__ to __) means that door installation E-08-262-D02 was built incorrect location.
| 02SL - Stations (LUL) | Cxxx-NCR-002360 | NCR | MSH – Louvres – __ Package 30a & __ Package – Several Issues (CRL-OBS-28170) |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-12-20 | 2019-12-12 19:30 | -8 | 2019-07-04 08:52 | Architectural - Finishes | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following on from CRL review of __ Package 30a for the Moorgate Louvres. Observation CRL-OBS-28170 raised and linked to outstanding comment log along with site inspection notes. NCR raised to allow closing of comments and review of works as completed on site. (__ comments, CRL) __ Package: Photo 1: Moorgate Façade Works information and Cxxx architectural design (drawing Cxxx-LAO-A-DDD-C101_Z-24101) shows louvres as being frameless, and with no intermediate edge trim to louvre bays. Each separate louvre bay has been installed with edge trim. This is not compliant with the works information and as a comparison, the __ louvered façade is much larger and does not contain intermediate framing/trim between louvre bays. Photo 2: Moorfields Façade Similar to Photo 1, the individual louvre bays are articulated with a perimeter frame/trim. This was not in the works information or the Cxxx architectural design (except for the __ louvres on the right-hand side of the façade). Photos 3 & 4: Moorfields Façade a) Louvres are fixed by a surface mounted perimeter fixing plate. This is not compliant with the Cxxx architectural design (drawing Cxxx-LAO-A-DDD-C101_Z-24100). b) There are two fixing holes provided for each fixing location on the surface mounted perimeter fixing detail for the __ louvres: i) For each paired holes, the “outside” hole is positioned very closely to the edge of the metal leaving very little metal left to provide structural strength for the fixing. ii) For the most part, only one hole has been used at each fixing location, however at some locations two fixings have been used. Cxxx to confirm if only one fixing is required to achieve the design and supplier criteria. c) There is a metal cladding panel covering the joint between the Crossrail concrete and the adjacent building. This was a detail that has not been discussed with Crossrail architecture. Cxxx to confirm that this has been agreed upon with Crossrail, CoL town planning, the OSD and the adjoining property. d) Generally, Cxxx architectural drawings shows a requirement for an EPDM lapped with louvres and concrete (e.g. drawing Cxxx-LAO-A-DDD-C101_Z24119). This has not been included on any of the installed louvres. Photo 5: Moorfields Façade Bottom “cill” flashing is bent. Bottom of Intermediate trim is visibly bent. Photos 6, 7 & 8: Trim to Louvres Outer perimeter and intermediate side trims are both poorly aligned and have for the most part been bent/deformed. Photo 9, 10, 11 & 12: Fixings to __ Louvres a) Outer perimeter fixing detail contains what appears to be plastic shims, Cxxx to confirm if this detail been approved and demonstrated to provide the design and performance criteria. Cxxx to provide an MCR for the shimming material. b) On Photo 10, surface mounted screw fixings were not shown on __ drawing (Cxxx-LAO-A-DWG-C101-50300) or Cxxx architectural drawings (Cxxx-LAO-A-DD-C101_Z-24119). c) On photo 10 the bottom cill flashing between the two louvre banks is steeped due to the inconsistent amount that the flashing projects from the façade line. d) On photo 10, the alignment of the trim/frame between the four louvre banks is poor. e) On Photo 11, fixing holes are on outside holes with very little metal left over between the hole and the outer edge of the metal fixing plate. f) Size of fixings used appear to be inconsistent. On photo 12, the head of the fixings do not fully cover the countersunk hole, whereas on Photo 11 they do. Photo 13: Moorfields – Cladding to demise with neighbouring property a) As stated for photos 3 & 4 above there is a cladding panel installed in between Crossrail and the adjoining property. b) There are numerous in the concrete façade. Is Cxxx going to fill these? Photo 17: Moorgate – Louvre blades misaligned The louvre blades are very misaligned in the lower right louvre bank. This is not acceptable. Photo 19: Moorfields – Surface Mounted Conduit Surface mounted conduit for security cameras creates two issues: a) Pre-OSD completion, the cables are somewhat vulnerable as the mounting height is not very high. Is this acceptable for a security critical system? b) Post-OSD completion, the conduit will be covered by third party OSD cladding. If the cables/cameras require maintenance or replacement, LU will need to remove the OSD’s cladding: this does not seem practical if the requirement can be designed out. If the requirement can’t be designed out, Cxxx to confirm that this is included in the developer agreement. Photo 21: High Level Louvres High level louvres were not made available to Crossrail for inspection prior to striking of scaffolding. Interface with __ Package – __ Package: Photo 14 & 15: Moorgate – __ Louvres – Header detail The trim at the top of the louver appears to have been added in because the louvres have both been made to correct opening height of the opening in the concrete structure. Photo 16: Moorgate – __ Louvres – Bottom detail Bottom flashing detail does not appear on Cxxx drawing Cxxx-LAO-A-DDD-C101-_Z-24101. Cxxx to confirm if the bottom flashing has been approved as a design by Crossrail and has it been co-ordinated with the urban realm finishes and finishes levels to provide the required level of waterproofing to the building envelope. Photo 18: Moorgate – __ Louvres – Sealant and Staining a) Louvre frame is stained and grimy and the paint finish to the louvre has been damaged b) Hole in concrete: is the Cxxx proposal to fill this hole or to leave it as is? Photo 20: Moorgate – __ Louvres – Door hardware Door to __ transformer secured by padlock. Cxxx to confirm if this is compliant with the security requirements.
| 02SL - Stations (LUL) | Cxxx-NCR-002361 | NCR | __X – Broad Street Avenue Louvred Façade – __ Levolux – Several Issues (CRL-OBS-28024) |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-11-20 | 2020-01-21 14:10 | 62 | 2019-07-23 11:12 | Architectural - Finishes | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Information not detailed | Completed |  | Observations CRL-OBS-27778, CRL-OBS-27779 and CRL-OBS-27780 have been raised and associated NCR’s have been raised: Cxxx-NCR-002328 __ louvered escape door – EWS-720 (CRL-OBS-27778, 27779) Cxxx-NCR-002329 __ – Hydrant enclosure lock rusted (CRL-OBS-27780) Following on from CRL review of __ Levolux Package for the __ Louvred Façade in Broad Street Avenue CRL-OBS-28024 was raised to link the outstanding comment log and site inspection notes. NCR raised to allow closing of comments and review of works as completed on site. CRL-OBS-28024 A Quality Surveillance carried out for the installation of the Louvred Façade on Broad Street Avenue (Blomfield Box). The intention of the surveillance was to assess progress of outstanding design/installation issues in order to progress Certification Packages. Comments are as follows: Photos 1 – __ louvered escape door • The detail around the door hardware is still incomplete and a design (drawing) has yet to be submitted and/or approved. • The door hardware has not been fully installed and the door was un-operable • The left hand angle (on photo 3) is fixed only to the louvres by rivets and is not robust enough. This has been discussed with __ (Cxxx) and he has noted that a Cxxx remedial detail is forthcoming • For the right hand side angle trim, strengthening is required. • It was agreed that rivets will be colour matched to the louvres Photo 2 - __ bi-folding louvered maintenance doors (Broad St. Avenue Facade) • At the top of the door o Top louvre blade on the left leaf is misaligned o Top louvre blade on the right leaf is misaligned and the trim has been bent inwards. This trim needs to be replaced o It appears that some impact damage has occurred at the top of the doors Photo 3 - __ bi-folding louvered maintenance doors (Broad St. Avenue Facade) • Rivet fixings are inconsistently set- out and spaced. As discussed with __, new angles are to be installed and fixed with consistent setting-out and spacings with colour matched rivets. • Rivet fixing of angle trim to face of louvres is not a robust enough solution (this was commented on design drawings). It has been agreed that the trim will also be fixed on the sides: the louvres have fixing holes at the ends that allow for side fixing. Photo 4 – __ Hydrant Enclosure (Broad St. Avenue Facade) • There is a gap that allows rubbish to be pushed into the void at the top of the hydrant enclosure. It was agreed with __ (Cxxx), that the gap will be closed by using a trimmed louvre blade. • The enclosure is dirty and stained. It needs to be cleaned and re-visited to ensure that it has not been damaged and requires replacements • The lock is rusted and requires replacement. Photo 5 and 6 – comments associated with setting out of the equipment and lighting on the façade have yet to be responded to by Cxxx yet the services installed. This to be reviewed. This is not a full review but an update on “outstanding” design issues. Façade yet to be offered as a complete piece of work for “acceptance”.
| 02SL - Stations (LUL) | Cxxx-NCR-002362 | NCR | P&T – PAEE’s – __ Package 42a – Several Issues (CRL-OBS-28275) |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-11-05 | 2019-10-14 15:27 | -22 | 2019-07-08 13:39 | Architectural - Finishes | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following on from the acceptance of the Benchmark for the Fire Hydrant Cabinet Cxxx-LAO-A-ZFM-C101-50186 (Eastbound and Westbound Platforms only), CRL carried out a Quality Surveillance of other as installed cabinets to provide comment as part of the final inspection. A marked-up drawing was produced (attached) for 7 of the 10 Platform Cabinets that are associated with CRL-OBS-28275. As agreed with the __ Package Manager on site, the comments on the attached marked up drawing are to be addressed on site. 3no. PAEE’s have been installed outside of tolerances on the Platforms and Tunnels – East and Westbound Platforms. On review of LM01a, LM01b and LM01f it became apparent that the cabinets have been installed incorrectly and in the worst case 55 mm closer to the SCL than the requirement on the Works Information. This will mean that these cabinets are adjusted in position or that site specific details are required to address the installation. The extent of the issue cannot be assessed until the remainder of the cabinets become available for inspection. There are 4no. PAEEs where the top detail results in a larger gap. The head angle has been removed and sent as a template so a "C" shape channel can be made to close the gap.
| 02SL - Stations (LUL) | Cxxx-NCR-002364 | NCR | BTH - damaged water heater in 2/411 Cleaners Store |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-09-12 | 2019-08-30 09:03 | -13 | 2019-07-04 13:47 | Mechanical - Hot & Cold Water Supplies | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | Water heater in cleaners store has a dent in the front panel.
| 02SL - Stations (LUL) | Cxxx-NCR-002365 | NCR | FINS - Removal of CoL asset |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-12-18 | 2019-12-18 12:37 | 0 | 2019-07-04 15:21 | Civil - Demolition/Site Clearance | 2500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | During the removal of the foundations in Finsbury Circus, it is apparent that the brick gate post has been removed without agreement. This is a City of London asset, and was planned to be retained as a per Schedule 5. See attached mark up.
| 02SL - Stations (LUL) | Cxxx-NCR-002366 | NCR | Resin Floor company Resbuild no ISO 9001 certification |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-08-02 | 2019-08-16 09:23 | 14 | 2019-07-05 09:01 | Architectural - Flooring | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | A resin flooring system was installed BTH basement, MShatf and Platform and tunnels back of house areas. The supplier (RESBUILD) for the product used does not have ISO 9001 certification. The system was selected due to the product already having LU -APR approval. it was procured and installed without first checking certification.
| 02SL - Stations (LUL) | Cxxx-NCR-002367 | NCR | BTH - Mattwell floor hatch at canopy entrance incorect size |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-08-02 | 2019-11-01 13:12 | 91 | 2019-07-05 13:08 | Architectural - Flooring | 1500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Cover and frame have been fabricated to the size of the opening, and hence have nothing to support them.
| 02SL - Stations (LUL) | Cxxx-NCR-002368 | NCR | Asset removal and damaged cable |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2019-08-02 | 2019-09-20 11:55 | 49 | 2019-07-05 15:50 | Communications and Control Systems - Radio | 3000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Directional antenna 136 has been removed and feeder FD259 has had the connector removed/cut off. at the bottom of escalator no.1 right hand side where incline lift finishes.
| 02SL - Stations (LUL) | Cxxx-NCR-002370 | NCR | No Benchmark for platform seating benches |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-12-31 | 2020-01-14 15:06 | 14 | 2019-07-10 10:47 | Architectural - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | The following platform benches / seats with TAG ref FX-501, FX-504, FX-506, FX-509 have not been completed.
| 02SL - Stations (LUL) | Cxxx-NCR-002371 | NCR | MTH GLAP alignment issue |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2020-02-29 | 2020-01-14 16:31 | -46 | 2020-01-10 14:50 | Architectural - General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | GLAP and gate line gap exceeds 100mm, exceeding allowed dimension in Moorgate ticket hall.
| 02SL - Stations (LUL) | Cxxx-NCR-002372 | NCR | __ -24A Missing __ M10 pull test on South elevation and head wall |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-08-31 | 2019-08-29 11:14 | -2 | 2019-07-16 13:53 | Architectural - General | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other management problem | Completed |  | FX143 __ FAZII 10/10 A4 Art.no.501403 for the installation of the Sto brackets to the concrete has not been Pull tested on the ES6 south elevation and east elevation head wall
| 02SL - Stations (LUL) | Cxxx-NCR-002373 | NCR | ___Material Procured without MCR and ISO9001 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-09-30 | 2019-10-04 13:50 | 4 | 2019-07-17 09:37 | Architectural - General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | The stainless steel Fly mesh has been procured by Kacier from a supplier (FLYDOR) who does not hold UKAS accreditation or ISO9001. The material has been used at the top of the ES1 to close the gap between precast and PPC panels.
| 02SL - Stations (LUL) | Cxxx-NCR-002374 | NCR | Spare Core to be terminated to Earth |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-08-15 | 2020-02-11 14:36 | 180 | 2019-07-18 08:34 | Communications and Control Systems - General | 5000 |  | Incomplete Works | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | During routine inspections of the BMS CE and MCC panels, it was found that there are a number of spare cables and cores that have not been properly terminated and put to earth as required by the specification. The cables have just been left in either the internal panel or external trunking. This is the case in multiple panels, and will need to be addressed and resolved sitewide.
| 02SL - Stations (LUL) | Cxxx-NCR-002375 | NCR | MSH - Staircase S-0.5 water ingress |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-10-26 | 2019-09-02 08:44 | -54 | 2019-07-18 15:46 | Structural Engineering - Concrete Member | 2000 |  | System Defect | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | As per attached photographs - evidence of leak between street level beam and GL2 750 wall.
| 02SL - Stations (LUL) | Cxxx-NCR-002376 | NCR | Escalator 3, MG Platform, Air Flow issue . |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2020-06-03 | 2020-09-22 13:09 | 111 | 2020-04-16 13:34 | Fire - Detection | 500 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 2 months after testing & witnessing a correctly functioning bank of Escalators, bank 3, __'s 18,19, &20, contractor realised they there were spurious indications of Air Flow faults noticed while commissioning the site. This is in spite of the fact that operationally it functions as it should and is backed up by the theoretical and actual calculations used in the commissioning process.
| 02SL - Stations (LUL) | Cxxx-NCR-002377 | NCR | Platform end walls floor level issue (step) |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-12-31 | 2020-01-21 10:20 | 21 | 2019-07-30 12:30 | Architectural - Flooring | 1000 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | There is a ~25mm step between platform tiling and the BOH screed at Eastbound West end and Westbound East end.
| 02SL - Stations (LUL) | Cxxx-NCR-002378 | NCR | Door Ironmongery |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-09-24 | 2019-11-21 15:43 | 58 | 2019-07-23 15:36 | Architectural - Doors | 15000 |  | Manufacturing Defect | Repair | 2 (6-60k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Reported that some doors that have been fit by __ with a D-Handle (to pull the door closed) the D-Handle position on the door does not allow enough room for a person's hand (Between the handle and door frame) and therefore the hand could get injured closing the door.
| 02SL - Stations (LUL) | Cxxx-NCR-002379 | NCR | 50a __ Bronze Facade |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-10-31 | 2020-01-14 14:12 | 75 | 2019-07-23 08:31 | Architectural - General | 1000 |  | Design | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | The rainscreen system installed on the __ 50a façade has been installed with Sealant details. There is noticeable staining on the panels and potential permanent damage to the Bronze material. See attached concerns raised by CRL (__e)
| 02SL - Stations (LUL) | Cxxx-NCR-002380 | NCR | DOO Camera 3 Camera Housing Glass Cracked |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-08-05 | 2019-09-04 12:20 | 30 | 2019-07-23 08:48 | Communications and Control Systems - Driver only Operation CCTV | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | DOO Camera 3 Camera Housing glass was cracked after being moved.
| 02SL - Stations (LUL) | Cxxx-NCR-002381 | NCR | Moorgate Box / AP5 Entrance - Bent GRC Support Pins |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-12-20 | 2019-12-06 16:16 | -14 | 2019-07-23 14:16 | Architectural - General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The GRC support pins for the cladding in Moorgate Box / AP5 Entrance have been bent out of the design position to allow the panels to be installed correctly.
| 02SL - Stations (LUL) | Cxxx-NCR-002382 | NCR | __X - Surface course arround TW lids |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-10-31 | 2019-11-12 08:36 | 12 | 2019-07-25 15:35 | Civil - Wearing Course | 6000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | 5no. TW lids on Blomfield Street opposite the entrance to CRL structure are low causing a puddle after rain.
| 02SL - Stations (LUL) | Cxxx-NCR-002383 | NCR | P&T - AP6 - Ceiling/Cladding/Services Co-ordination - Site amendments to accommodate mis-installed services |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-12-27 | 2020-06-17 17:20 | 173 | 2019-07-30 16:30 | Architectural - Finishes | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | An area of the GFRC Cladding in AP6 (refer to photographs) has been modified on site to suit the “as installed” services arrangement. Works were completed without consultation or the agreement of the Project Manager. This represents a non-compliance with the Works Information as follows: Architectural Specification (Cxxx-LAO-A-RSP-C101_WS103-50001 Revision 41.0) Section JH - GFRC PANEL CLADDING JH40.1502 - General Requirements n) On site drilling or cutting of GFRC panels shall not be permitted. JH40.3701 – General d) The Contractor shall not cut, drill or otherwise alter any work without review and acceptance by the Project Manager.
| 02SL - Stations (LUL) | Cxxx-NCR-002384 | NCR | MSH - 887 - 8 Moorfields __ DB |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-11-09 | 2019-10-01 12:40 | -39 | 2019-08-01 16:00 | Electrical - Power Distribution | 6500 |  | Design | Rework | 2 (6-60k) | Complete | Design Problem - Other | Completed |  | New Distribution board has been installed in 8 Moorfields. Due to larger load, the panel is larger than the existing head. This panel therefore obscures the existing display cabinet for the building owner
| 02SL - Stations (LUL) | Cxxx-NCR-002385 | NCR | MSH PAD FFO - AP5 BAL-112 Broken Glazing |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-11-04 | 2020-01-28 19:15 | 85 | 2019-08-06 08:15 | Architectural - Balustrade | 1500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | 2 no. glazing panels of the balustrade were damaged during scaffolding activity
| 02SL - Stations (LUL) | Cxxx-NCR-002386 | NCR | Moorgate Ticket Hall - Facade Glazing - (__ Package 4a) - Glass Colour (as installed). |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2019-09-30 | 2019-09-04 17:21 | -26 | 2019-08-08 10:55 | Architectural - Finishes | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | Following on from site inspection - 29.07.2019 - JB/JD/JR/JLA/RG - concerns were raised associated with the colour match of the blue __ installed as part of the Southern Façade. Works Information requires sampling to ensure that a consistent colour is achieved for architectural finishes in this instance the glazed external façade. On site colour differences are evident between __ and Kitemark glass and again in the __ Application. As installed CRL do not believe that the Works Information has been met as per the following: Architectural Specification - Section JA –General Requirements (Cxxx-LAO-A-RSP-C101_WS103-50001 Revision 41.0) Clause JA.4008 - Post Contract Samples: a) Post contract award samples provided during the Detailed Design shall be checked against the pre-contract samples, where applicable, and the Specification to ensure that quality and type have been maintained. Architectural Specification Section JH11 – Glazed Curtain Walling Systems. Clause JH11.2104 - Prototype Requirements: Prototypes of the following shall be provided, in accordance with Section JA.4000: A full height and 3 bays width of Type EWS-115 to indicate all finishes and the glazing interfaces. Architectural Specification Section JH11 – Glazed Curtain Walling Systems. Clause JH11.2105 – Benchmark Requirements: Quality benchmarks of the following shall be provided, in location(s) to be agreed with the Project Manager, in accordance with Section JA.4000: The first completed structural bay of each type of system.
| 02SL - Stations (LUL) | Cxxx-NCR-002387 | NCR | ESC - ES6 - Handrail Screw Damage |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-11-16 | 2020-02-26 09:45 | 102 | 2019-08-08 14:10 | Mechanical - Escalators | 10000 |  | Damaged | Repair | 2 (6-60k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | 3rd party damage by 2x screw on escalator 12 LHS handrail.
| 02SL - Stations (LUL) | Cxxx-NCR-002388 | NCR | Cladding Colour Contrast levels |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-10-31 | 2020-02-21 17:06 | 113 | 2019-08-09 09:19 | Architectural - General | 2000 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | The colour contrast levels on the Column skirtings do not have enough difference in LRV Readings. The difference in LRV levels between flooring and column surface is approx. 22 points and therefore non-compliant.
| 02SL - Stations (LUL) | Cxxx-NCR-002389 | NCR | Commissioning proceeding ahead of IRN |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2020-04-30 | 2021-01-25 08:32 | 270 | 2019-08-09 13:11 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - No evidence of program review from Contractor's Quality Manager or Management | Completed |  | CTP ref. Cxxx-LAO-M-STP-C101-50006 for Platform Smoke Extract Systems contains at 1.8 for "receipt of IRN from PES sub-contractor", this is a hold point prior to running fans. The current IRN received bears no mention of the required leakage testing of the PES structure. Tests were conducted August 2018 but the results are not included to any IRN or uploaded to EB moreover the document doesn't appear to demonstrate that leakage is within limits or that the correct criteria has been used.
| 02SL - Stations (LUL) | Cxxx-NCR-002391 | NCR | Cover panels on GRC/Wall mounted bench interface |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2025-12-31 | 2020-02-28 11:18 | -2133 | 2019-08-09 15:10 | Architectural - Finishes | 500 |  | Material | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Cover panels on GRC/Wall mounted bench interface bottom section has some play, to be resolved to no movement.
| 02SL - Stations (LUL) | Cxxx-NCR-002392 | NCR | BTH - AP8 AP door misaligned holes |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-11-30 | 2020-01-15 13:30 | 46 | 2019-08-13 13:14 | Civil - Structural Engineering | 3000 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | It is apparent that during the installation of the door supporting steelwork in AP8 AP doors, the central supporting door column, does not align with supporting door beam. Supporting door beam to be drilled in-situ and repaired using approved metaflux repair paste. Please note the beam is fully fixed and the beam is cast in, preventing re-fabrication.
| 02SL - Stations (LUL) | Cxxx-NCR-002393 | NCR | MTH PRM Corridor Signage height |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-11-14 | 2020-08-05 11:55 | 265 | 2019-08-16 06:42 | Architectural - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | LU Standard 1-371 A3 Cl. 3.5.1 requires that the headroom measured to the underside of a permanent sign in ticket hall should not be less than 2.4m for a local obstacle protruding downwards. The signage on PRM corridor in Moorgate ticket hall street level -1 is 2.3m above FFL and does not comply to the LU standard. See attached Markup of the sign on the CRL inspection on site.
| 02SL - Stations (LUL) | Cxxx-NCR-002394 | NCR | Overclad Door Skirting colour LU Complaince |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-12-31 | 2020-07-09 12:04 | 191 | 2019-08-16 12:58 | Architectural - General | 2500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | It is observed that a different skirting (SS) has been used in some areas of the paid side of the BTH: doors and before the ramp. Although the LRV are compliant, it must be noted that using different type of skirting (and LRV) within the same wall can cause confusion about the extent of the room and the perception of the wall (perceived recesses). This is not in accordance with LU Standard 1-351 Station Décor design: 3.1.1 Station décor planning shall be undertaken in order that the Underground customer is presented with a calm, orderly, consistent, predictable, welcoming and attractive environment.
| 02SL - Stations (LUL) | Cxxx-NCR-002395 | NCR | BTH - Lift 8 Ladder/Equipment Coordination |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2020-06-30 | 2020-06-23 15:18 | -7 | 2019-08-16 15:04 | Mechanical - Lifts | 3000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | During the coordination and install of the ladder in the top pit of lift 8, it is apparent that the ladder cannot be fitted due to the __ electrical cabinets being installed in the space proofed zone of the ladder. The install does not appear to follow the approved __ drawing, attached. It is apparent that the cabinets will need to be relocated and terminations re-wired to allow the ladder to be installed.
| 02SL - Stations (LUL) | Cxxx-NCR-002396 | NCR | BTH - L+E - Escalator 1 + 6 Newel Ends |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2020-01-17 | 2020-07-22 16:42 | 187 | 2019-08-20 07:13 | Mechanical - Escalators | 10000 |  | Design | Rework | 2 (6-60k) | Complete | Design Problem - Inadequate or defective design | Completed |  | __ have installed of incorrect widths of newel ends on Escalators 13 (Escalator bank 6) and Escalator 15 (escalator bank 1) where they align with the inclined lifts at Broadgate Ticket Hall
| 02SL - Stations (LUL) | Cxxx-NCR-002397 | NCR | BTH - L+E - Landing frame sides uncoordinated design |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2020-01-17 | 2020-06-12 13:55 | 147 | 2019-08-20 09:48 | Mechanical - Lifts | 1000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Uncoordinated design between __ and __ has resulted in side angles for supporting of lift landing frame not aligning with cladding.
| 02SL - Stations (LUL) | Cxxx-NCR-002398 | NCR | P&T – AP5 Staircase – Dimensional consistency check for goings and risers (CRL-OBS-28812) |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2020-02-01 | 2020-03-09 09:29 | 37 | 2019-10-04 13:09 | Architectural - Flooring | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A dimensional consistency check for goings and risers on AP5 Staircase (Moorgate Shaft) was done by CRL Architects. The flatness of the stair treads was found consistent for level of each stair going (checked with a spirit level at two points for each stair channel on both the terrazzo and metal nosing portions of the goings). The spirit level indicated that the surfaces were consistently level on the goings. With regards to consistency in going dimensions there is a variation in the size of the goings which have been designed to be 300mm in length – The shortest going length found is approx. 295mm and the longest going length found is approx. 312mm. These variations in going size are outside the tolerances outlined in the specification (Design Length -5mm and Design Length +12mm). With regards to consistency in riser heights there is a variation in the height of the risers which have been designed to be 180mm in height – The highest riser height found is approx. 185mm and the lowest riser height found is approx. 177mm. These variations in riser heights are outside the tolerances outlined in the specification (Design Height +5mm and Design Height -3mm). The variations in stair riser heights should be reduced as far as possible as small variations have been widely observed to cause trip hazards. The risk is heightened in locations subject to a high numbers of users (which this stair will be). These measurements were made with a tape measure and scale. The stairs should be fully surveyed by Cxxx (every step @ 600mm for going dimensions and riser heights) to verify the full scope of non-conformance so that the appropriate remedial works (if any) can be sensibly proposed by Cxxx for CRL acceptance.
| 02SL - Stations (LUL) | Cxxx-NCR-002400 | NCR | P&T - ES2 and 3 - Escalator interface with advertising |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2020-10-31 | 2021-02-08 13:09 | 100 | 2020-01-10 13:34 | Architectural - Finishes | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Escalator deck level was out of tolerance varying from 0mm to 25mm. - Generally.Cladding Escalator Deck Interface, however this has resulted in the advertising ribbon and infill panels above being affected.
| 02SL - Stations (LUL) | Cxxx-NCR-002401 | NCR | ITP Checksheet |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-12-31 | 2020-04-07 21:43 | 98 | 2019-08-29 07:09 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Robert Stevens ITP- Cxxx-LAO-O4-ITP-C101-50149 Specifies that the pull out test of fixing be to 8kn, however this was submitted prior to details for the works requiring 5kn.
| 02SL - Stations (LUL) | Cxxx-NCR-002402 | NCR | No Sample submitted for __ Gate |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-11-30 | 2020-03-13 16:13 | 104 | 2019-08-30 08:37 | Architectural - General | 1000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | There has been no sample submitted for the __ Gate as per specification.
| 02SL - Stations (LUL) | Cxxx-NCR-002403 | NCR | BTH - SL Entrance Uplighter Damaged |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2020-02-29 | 2020-01-10 09:56 | -50 | 2019-09-02 08:28 | Architectural - Finishes | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | During a site inspection on 3rd September 2019, it is apparent 1no. uplighter to the South of the BTH glazed canopy has been damaged. The glass lens of the light has been cracked and will require replacing.
| 02SL - Stations (LUL) | Cxxx-NCR-002404 | NCR | BTH - ES1 Floor Infill Support Steelwork |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-11-30 | 2019-11-04 09:56 | -26 | 2019-09-02 08:42 | Civil - Structural Engineering | 2000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | It is apparent that the support steelwork has not been constructed as per the approved drawing at the base of ES1 to the South. Cxxx-LAO-S-DWG-C101-50112. The steelwork horizontal sway strut was designed to transfer the load through the structural top hat. The strut however has been constructed to fix to the non-structural waterproofing liner sheet. See attached picture.
| 02SL - Stations (LUL) | Cxxx-NCR-002406 | NCR | MShaft - Paint damage to Fan Room door 2/784 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-11-14 | 2020-06-24 09:47 | 223 | 2019-09-03 08:09 | Architectural - Doors | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Localised areas of paint has been removed on the door frame - back to bare metal. It is believed that this came off during the removal of protection tape.
| 02SL - Stations (LUL) | Cxxx-NCR-002407 | NCR | Cladding Installation Commenced Without Accepted Blast Calculations |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2019-11-24 | 2020-02-07 09:53 | 75 | 2019-09-03 14:11 | Architectural - Glazing | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | As part of a Quality Surveillance a design review was undertaken. On checking eB it was found that the Blast Calculations for the ‘External Glazed Cladding’ Cxxx-LAO-A-XCL-C101-50056 and 50057 were placeholders. As such the installation has commenced with an incomplete design. ITP ‘Installation of External Cladding Components’ *50073 (Rev 2), inspection number 1.1 Acceptance of Design is a Hold Point for all parties.
| 02SL - Stations (LUL) | Cxxx-NCR-002409 | NCR | PLT - Leak through AP1 Wraparound’ |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2020-01-31 | 2019-12-03 13:57 | -59 | 2019-09-04 14:02 | Civil - Civil Engineering General | 3000 |  | Material | Repair | 4 (0.5-3k) | Complete | Previous Construction - Other | Completed |  | There is water ingress through at construction joint at VD1 wraparound The leak is in __ Platform +0.5, Room 7/826, CIR-PL
| 02SL - Stations (LUL) | Cxxx-NCR-002410 | NCR | CMS Installation in __ incline lift pit BGTH at street level , Non Segregation . |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2020-02-04 | 2019-12-11 11:39 | -55 | 2019-09-06 10:46 | Mechanical - Lifts | 10000 |  | Incorrect Installation | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Other | Completed |  | The CMS has been installed without segregation . There is a project requirement to have segregation between small power , comms and FA systems . At present they are installed and mixed in a one compartment trunking .
| 02SL - Stations (LUL) | Cxxx-NCR-002411 | NCR | TUN - L+E - Damaged Handrail E18 ES2 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2020-08-15 | 2020-09-17 15:49 | 33 | 2019-09-06 11:56 | Mechanical - Escalators | 2500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Personnel Error - Other human error | Completed |  | Please see attached photographs. Dilapidation survey on handover of ES2 to __ has uncovered handrail damage to E18 RHS handrail.
| 02SL - Stations (LUL) | Cxxx-NCR-002413 | NCR | VCD's not installed |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2020-10-14 | 2019-10-25 06:49 | -355 | 2019-09-11 13:09 | Mechanical - Heating Ventilation & Air Conditioning | 2999 |  | Incomplete Works | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | 4No essential VCD's shown on the design drawings and required for satisfactory commissioning of __ staircase pressurisation system have not been installed. Lack of these dampers continues to directly delay commissioning of this system. The retrospective installation will also create the need to retest the ductwork for leakage.
| 02SL - Stations (LUL) | Cxxx-NCR-002414 | NCR | __X - SL -1 Leak in Crane Room |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-10-31 | 2019-09-27 10:05 | -34 | 2019-09-12 08:24 | Civil - Civil Engineering General | 2500 |  | Material | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Water ingress through construction joint in shaft wall in the Moorgate SL-1 Crane Room
| 02SL - Stations (LUL) | Cxxx-NCR-002415 | NCR | ITP Documentation |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-10-14 | 2019-11-01 13:09 | 18 | 2019-09-16 07:51 | Architectural - Flooring | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Inspection points not adequate | Completed |  | Flooring ITP for installation of sand and cement screed Cxxx-LAO-O4-ITP-C101-50193 references benchmark for screed to be carried out. This was not carried out as works progressed, but checklists and visual inspections have been signed off by CRL on installation of the sand and cement screeding as well as drop hammer tests on the screed, which have all be recorded and captured in the QA packs and also signed off by both CRL and __.
| 02SL - Stations (LUL) | Cxxx-NCR-002416 | NCR | Conduit installation not in line with SPEC JY60.3209a Pulling boxes to be every 6 meters. |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-10-14 | 2019-11-08 11:28 | 25 | 2019-09-16 14:44 | Electrical - Cable Management | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | The conduit installed along the length of the northern line link has Pulling boxes at intervals of 12m. SPEC JY60.3209a has a maximum distance of 6m. The run is straight the entire length and the data cable installed was an easy push through the installed conduits.
| 02SL - Stations (LUL) | Cxxx-NCR-002417 | NCR | Watermist Electrical IRN |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2020-05-19 | 2019-10-15 14:30 | -217 | 2019-09-17 08:36 | Electrical - Electrical Engineering General | 5000 |  | Supervision/Management | Rework | 3 (3-6k) | Complete | Management Problem - Other | Completed |  | The fire suppression watermist system plant and equipment within the plantroom has been wired by various parties. Wiring includes power supplies to pumps, controls wiring from sensors and equipment and alarm wiring. These works were installed to no approved design (subject of another NCR), no inspections of CMS, wiring or panels have been undertaken by the contractor or any works offered to CRL hence no 2.1 IRN yet 2.2 commissioning has proceeded.
| 02SL - Stations (LUL) | Cxxx-NCR-002418 | NCR | No MCR for installed control panels |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2020-02-18 | 2020-02-21 16:09 | 3 | 2019-09-17 08:45 | Fire - Suppression | 2999 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - No evidence of program review from Contractor's Quality Manager or Management | Completed |  | Control panels for the water mist suppression system were submitted under CRL-MCR-005062, subsequently approved. The installation including the control panels have not been offered for any inspection or 2.1 IRN acceptance (see NCR 002417). The control panels installed, wired and offered at 2.3 commissioning are not those within the above MCR. It has since transpired that no MCR has been issued for the installed control panels.
| 02SL - Stations (LUL) | Cxxx-NCR-002419 | NCR | __X, MGS - Power Factor Correction units not installed |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2019-10-18 | 2020-10-07 12:04 | 355 | 2019-09-20 08:38 | Electrical - Switchgear | 1000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | PFC units have not been installed at 4no. Main LVAC switch boards at MGS and __ as detailed within JY71 M&W specifications. we are aware that the contractor is currently undertaking a power quality study and are planning to install these PFC unit, but as yet no equipment has been proposed or procured.
| 02SL - Stations (LUL) | Cxxx-NCR-002420 | NCR | Terrazzo Flooring |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-10-31 | 2019-12-19 11:26 | 49 | 2019-09-20 15:46 | Architectural - Flooring | 3000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During CRL and __ inspection of the terrazzo flooring it was noted that the structural movement joint (at the end of AP5 passage towards to base off AP5 staircase) showed cracking along the grout lines and also a drop in the tiles levels either side of the MJ resulting in a difference floor level on the tiles.
| 02SL - Stations (LUL) | Cxxx-NCR-002421 | NCR | Terrazzo Flooring Interface with Lift 2 Architrave in AP6 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2020-05-29 | 2020-07-10 15:04 | 42 | 2019-09-27 14:40 | Architectural - Flooring | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | AP6 / Lift 2 the floor tiles and architrave interface at floor level joint detail is poor and a gap can be seen.
| 02SL - Stations (LUL) | Cxxx-NCR-002426 | NCR | No evidence provided of Prototype acceptance for Glazed Entrance Canopy |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2019-11-22 | 2019-11-25 19:40 | 3 | 2019-09-23 12:41 | Architectural - Glazing | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | A surveillance was carried out on Glazing Compliance. On checking documentation submitted it was discovered that there was no evidence of Prototype acceptance for Glazed Entrance Canopy
| 02SL - Stations (LUL) | Cxxx-NCR-002427 | NCR | No evidence provided of Benchmarks acceptance for Glazed Entrance Canopy |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2019-11-22 | 2020-10-05 13:53 | 318 | 2019-09-23 12:46 | Architectural - Glazing | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | A surveillance was carried out on Glazing Compliance. On checking documentation submitted it was discovered that there was no evidence of Benchmarks acceptance for Glazed Entrance Canopy
| 02SL - Stations (LUL) | Cxxx-NCR-002428 | NCR | No evidence provided of Prototype acceptance for Glazed Balustrade |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2019-11-30 | 2019-10-14 09:51 | -47 | 2019-09-23 12:55 | Architectural - Balustrade | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | A Quality surveillance was carried out on Glazing Compliance. On checking documentation submitted it was discovered that there was no evidence of Prototype acceptance for Glazed Balustrade
| 02SL - Stations (LUL) | Cxxx-NCR-002429 | NCR | No evidence provided of Benchmarks acceptance for Glazed Balustrade |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2019-07-12 | 2020-07-10 14:03 | 364 | 2019-09-23 13:02 | Architectural - Balustrade | 500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | A Quality Surveillance was carried out on Glazing Compliance. On checking documentation submitted it was discovered that there was no evidence of Benchmarks acceptance for Glazed Balustrade
| 02SL - Stations (LUL) | Cxxx-NCR-002430 | NCR | No accepted test results provided for the Glazed Entrance Canopy. |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2020-07-31 | 2020-05-21 11:40 | -71 | 2019-09-23 13:10 | Architectural - Glazing | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | A Quality Surveillance was carried out on Glazing Compliance. On checking documentation submitted it was discovered that there was no evidence of accepted test results provided for the Glazed Entrance Canopy.
| 02SL - Stations (LUL) | Cxxx-NCR-002431 | NCR | Moorgate shaft Illuminated Escape signage at St-1 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-10-30 | 2020-06-25 14:53 | 239 | 2019-09-25 15:02 | Architectural - Signage | 1000 |  | Design | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | The illuminated disabled emergency exit signage installed per __ signage layout plan Cxxx-LAO-A-DDA-C101_Z-27350 rev.C02 on top of the door reference W-02-631-003. However this should be W-02-138-D01. 2 actions; 1) Signage onsite to be relocated from W-02-631-003 to W-02-138-D01 (as per attached markup) 2) __ Signage plan design (Cxxx-LAO-A-DDA-C101_Z-27350 rev.C02 )to be updated to reflect correct requirements Note: * W-02-631-003 which is exit to stair case area and no facility for disable persons rescue * illuminated wheelchair emergency exit signage at street -1 to Moorgate shaft need to install to top of the door reference W-02-138-D01 as this door exit to lift 3 lobby
| 02SL - Stations (LUL) | Cxxx-NCR-002432 | NCR | P&T - Glass Type not as per spec to PAEE Help Point Surround |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2020-03-31 | 2020-06-25 14:59 | 86 | 2019-09-25 15:25 | Architectural - Glazing | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The glass type to the Help Point surround of the PAEE enclosures is not as per spec. TYPE FX-801 HYDRANT CABINET ENCLOSURE TYPE 1. The installed glass to the help point surround is single glazed toughened fully bonded to the stainless steel tray in accordance with the drawings. This contradicts the spec clause noted below.
| 02SL - Stations (LUL) | Cxxx-NCR-002433 | NCR | MTH and BTH - Glass Type not as per spec to PAEE Help Point Surround |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2020-03-31 | 2020-03-27 16:25 | -4 | 2019-09-25 15:51 | Architectural - Glazing | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | All glass type to the Help Point surround of the PAEE enclosures is not as per spec. TYPE FX-815 (Similar to FX-802 (Cxxx) HYDRANT CABINET ENCLOSURE TYPE 2) The installed glass to the help point surround is single glazed fully bonded to the stainless steel tray in accordance with the drawings. This contradicts the spec clause noted below.
| 02SL - Stations (LUL) | Cxxx-NCR-002434 | NCR | __ locks not europrofile |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-01-31 | 2020-04-17 14:51 | 442 | 2019-09-26 09:43 | Architectural - Doors | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | 4 no. __ gates to BTH canopy, AP8 and MTH do not have europrofile locks installed. The 3 __ doors have thumb turn locks installed and the __ Canopy door did not have the lock installed at the time of the security audit 19/09/19.
| 02SL - Stations (LUL) | Cxxx-NCR-002436 | NCR | AP5/AP6 Cladding OBS-27791 & OBS-27792 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2020-04-30 | 2020-04-30 13:29 | 0 | 2019-09-27 15:52 | Architectural - General | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | CRL-OBS-27792 Benchmark inspection for remedial works associated with BAL-122 and stainless steel plates forming balustrade base. Area now completed and adjacent finishes installed. (Refer to separate Observation for comments on alignment with interfacing packages CRL-OBS-27791). 1. Termination of stainless steel over-cladding with corner of base plate is untidy and not polished. 2. Panel to left is not properly adhered to the stainless steel base plate of the balustrade. Reconsider method of adhesion. 3. Material fitted behind the two cladding sheets does not terminated correctly – should maintain the same profile as the over cladding panels – this forms a hole that would need to be filled? 4. Edges to sheets forming cladding should be polished. 5. Alignment with balustrade acceptable. (interfacing materials and setting out not reviewed) CRL-OBS-27791 Quality surveillance carried out on installation (__ Package 23a - IWS-715 and IWS-816 - no tag sheet reference for stainless steel skirting) with particular attention paid to alignment of different cladding systems. Refer to sketch and photos. Generally: Misalignment between all elements forming this elevation Skirting • No specification/tag sheet for the stainless steel skirting. • Profile and interface with stairs leaves gaps – consider re-templating along with the interface detail with the stair – provide intent detail and tolerances. • Fixings missing • Mis-aligned with the steel flat forming part of the __ Glazing above. • Mis-aligned with the steel balustrade baseplate/over-cladding. Sto Cladding/Stainless Steel Flat (above skirting). • 10mm gap/5mm flat/5mm gap to skirting as per other areas not achieved. • S/S flat lengths do not correspond with adjacent elements – sometimes short/others too long and then no parallel with adjacent panels. • Vertically mis-aligned with adjacent panels – confirm tolerances in plan. Handrail • The termination details and relationship of the balustrade to the last stair differs between GFRC mounted/central and handrail mounted on the glazing - this should be addressed to provide a consistent detail/termination point (on plan). Flooring: • Stair nosings – final tile is a different colour to adjacent tiles – is this intentional? • Tile colour to be confirmed – outstanding action – provide accepted samples. Comment to be addressed to facilitate CRL acceptance.
| 02SL - Stations (LUL) | Cxxx-NCR-002437 | NCR | MSH - L+E - Architrave install out of tolerance |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2020-08-28 | 2020-07-30 13:24 | -29 | 2019-10-01 12:45 | Mechanical - Lifts | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Based on Crossrail observation CRL-OBS-27704, the following have been noted as non-conformances on front-of-house lift architraves: MTH - Lift 1 - 114 level - architrave gaps too large - presenting finger trap. MTH - Lift 1 - 109 level - architrave leg lengths incorrect. Design does not match that proposed under Option 4 of HB sketch Cxxx-HB-SK11329.
| 02SL - Stations (LUL) | Cxxx-NCR-002438 | NCR | PLT - Leak Through AP1 Construction Joint |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-11-26 | 2019-10-23 07:33 | -34 | 2019-10-01 15:39 | Civil - Civil Engineering General | 5000 |  | Material | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | There is water ingress through at construction joint at AP1 and platform level
| 02SL - Stations (LUL) | Cxxx-NCR-002439 | NCR | wateringress to moorgate accommodation area , electrical room 2-700-DBA-01 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-11-03 | 2019-12-12 13:13 | 39 | 2019-10-06 14:00 | Civil - Civil Engineering General | 10000 |  | Damaged | Rework | 2 (6-60k) | Complete | External Phenomenon - Other | Completed |  | On the 19th October __ were required to carry out an emergency isolation of the DB-2-700DBA-01 which is situated in electrical room within Accommodation block . This was due to the fact that there was a substantial intake of water from outside after a heavy rain storm . There has been substantial water damage to the Electrical DB and associated electrical equipment including CMS trunking and tray . . Water damage to be repaired correctly and then repair work can be carried out to the electrical DB Potential re-work scope -: 1. replace the distribution board . 2. replace Trunking and tray work CMS 3. Replace electrical spur , conduit and wiring . 4.re-test all outgoing circuits from DB . See attached layout showing location and also the DB schedule showing all field circuits associated .
| 02SL - Stations (LUL) | Cxxx-NCR-002441 | NCR | P&T - Benchmark and testing to platform screed |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-12-05 | 2019-11-01 16:06 | -34 | 2019-10-10 12:52 | Architectural - Flooring | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | Missing evidence of benchmark and testing requirements for the screed to eastbound and westbound platforms. Ref: Cxxx-LAO-C-CER-C101-50238. Despite numerous CRL and VAP inspections of the screed undertaken during the laying of the screed, no formal benchmark approval was provided as required by spec JM10.1205. Evidence for testing requirements is not provided for Adhesion test, slip resistance, abrasion, surface permeability as required under JM10.2202. Note. Drop hammer testing was completed and provided.
| 02SL - Stations (LUL) | Cxxx-NCR-002443 | NCR | BTH - Glass Canopy - Non-security fixings |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-11-11 | 2020-03-11 13:51 | 121 | 2019-10-14 14:09 | Architectural - Security | 2000 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The fixings to the entrance of Broadgate Canopy has exposed 'allen key' bolts on all fixing elements external to the station. As per Cxxx-LAO-A-RSP-C101_WS103-50001, CAN-104 item h) Fixingsl concealed for the purpose of security and resistance to vanadlism. At present this is not the case. This relates to the external entrance to the canopy at BTH. The fixings external, except the glass fixings are to be replaced. Mark up provided within the attached email.
| 02SL - Stations (LUL) | Cxxx-NCR-002445 | NCR | __ - BTH Area Scope 20a_21a_22a_23a - No evidence provided of First Fix Benchmark acceptances |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-11-19 | 2019-10-23 09:06 | -27 | 2019-10-22 07:29 | Architectural - General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Inspection points not adequate | Completed |  | Sub contractor __, could not provide evidence of the first fix benchmark acceptance in line with submitted ITP, for the following scope on Broadgate Ticket Hall area: 20a, 21a, 22a, 23a.
| 02SL - Stations (LUL) | Cxxx-NCR-002447 | NCR | Floor Tiling (Skirting Detail) to left and right hand sides of escalators E13/E15 at the start of AP2 at interface with S/S Cladding. |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-11-22 | 2020-09-17 14:08 | 300 | 2019-10-25 09:03 | Architectural - Flooring | 2000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Incorrect Skirting detail at interface with wall cladding
| 02SL - Stations (LUL) | Cxxx-NCR-002448 | NCR | BTH - Glass Canopy - Trelidor Gate |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-11-26 | 2021-02-23 15:24 | 455 | 2019-10-29 15:37 | Architectural - Security | 1000 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Following installation of the trelidor gate, it is apparent that the installation was installed without the following documentation: 1) Code 1/4 status drawings 2) Inspection and Test Plan 3) Risk Assessment and Method Statement 4) MCR 5) SR3 design statement inc. test data
| 02SL - Stations (LUL) | Cxxx-NCR-002449 | NCR | BTH Poster Frame Bracketry |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-02-24 | 2020-05-28 16:40 | 459 | 2019-11-04 17:02 | Civil - Civil Engineering General | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Interfacing problems | Completed |  | During the installation of the 2 no. poster frames in BTH it has become apparent that LBS have drilled into __'s galvanised bracketry. This has caused concerns regarding warranty to the steel structure. Furthermore it is apparent that the bracketry is not suitable for poster frames.
| 02SL - Stations (LUL) | Cxxx-NCR-002450 | NCR | Movement Joint within Terrazzo Flooring in BTH |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2020-09-25 | 2021-07-16 11:04 | 294 | 2019-12-16 13:44 | Architectural - Flooring | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Visual inspection carried out by __ and CRL to terrazzo flooring after removal of floor protection in BTH identified that the veymac rubber infill had de-bonded from the metal support frame. This is the same situation that has occurred in the platforms and tunnels.
| 02SL - Stations (LUL) | Cxxx-NCR-002452 | NCR | BTH - Matwell Tile Infill |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2020-01-23 | 2020-01-22 16:24 | -1 | 2019-10-31 14:18 | Archaeology - General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | Following installation of the tiling at the BTH trelidor gate, it is apparent that the tiling infill has not been installed as per drawing Cxxx-LAO-A-DDD-C101_1-44310, nor the specification reference DRS-574. The installed tiling is grey, however the documentation state the tiles should be black.
| 02SL - Stations (LUL) | Cxxx-NCR-002453 | NCR | __ - 67A No evidence provided of First Fix Benchmark acceptances |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-11-29 | 2020-01-07 16:44 | 39 | 2019-11-01 12:26 | Architectural - General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | Sub Contractor __, could not provide evidence of first fix Benchmark acceptance in line with submitted ITP.
| 02SL - Stations (LUL) | Cxxx-NCR-002454 | NCR | BTH - Lift 9 Bottom Landing Internal Cladding |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-12-02 | 2021-03-18 16:28 | 472 | 2019-11-04 10:51 | Archaeology - General | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Further to the incorrect installation of the lift 9 guide rails, despite assurances by the __ that this issue was resolved, the lift car has had to be lowered down the slope to meet FFL. As a result the lift door set has clashed with the internal cladding. To facilitate lift installation the cladding has been removed. However, additional cladding will require fabricating with approximately 15mm less projection into the shaft.
| 02SL - Stations (LUL) | Cxxx-NCR-002455 | NCR | ___Metal & Glass Cladding Demountibility interface |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2020-03-31 | 2020-04-30 16:04 | 30 | 2019-11-04 12:20 | Architectural - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The Spec calls for Architectural Specification - JA.5202 - Clause CO iii - independent removal of elements without progressive dismantling of adjacent elements. The cladding details and joints are currently designed to perform for blast and do not allow for an independent removal in all situations and a sequenced removal of materials is required.
| 02SL - Stations (LUL) | Cxxx-NCR-002457 | NCR | Over length cable RHP-00038 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-11-30 | 2020-01-13 09:20 | 44 | 2019-11-07 09:47 | Communications and Control Systems - Telephony | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | LIS-06-RHP-00038 / M135-TEL-00529 LENGTH: 97.8 Meters
| 02SL - Stations (LUL) | Cxxx-NCR-002458 | NCR | Over length cables RHP-00037 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-11-29 | 2019-12-19 11:04 | 20 | 2019-11-07 10:28 | Communications and Control Systems - Telephony | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Contamination | Completed |  | LIS-06-__-00037 / M135-TEL-00528 RHP-00037
| 02SL - Stations (LUL) | Cxxx-NCR-002461 | NCR | Additional Quality Check Sheets Fire Alarm IRN's |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2020-01-08 | 2021-01-18 12:08 | 376 | 2020-05-29 14:08 | Fire - Fire Systems & General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Information not detailed | Completed |  | Additional QCS to be included in the Fire Alarm IRN's subsequent to IRN completion.
| 02SL - Stations (LUL) | Cxxx-NCR-002462 | NCR | Water meters not installed |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2019-02-08 | 2020-01-14 07:30 | 340 | 2019-11-14 08:26 | Mechanical - Hot & Cold Water Supplies | 103000 |  | Supervision/Management | Use As-Is | 1 (>60k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | The WI requires leak detection be included to water supplies to accord with __EAM requirements. The satisfy this requirement the contractor chose a method requiring 2No water meters be fitted to each supply as shown on various __ F1 & __ F2 drawings. The contractor has subsequently chosen not to install 1No of these meters and instead has put forward an alternative proposal as a field change under Cxxx-FCD-002871. As the proposal satisfies the WI requirement it has been accepted however there is significant cost and time associated with the change which is solely incurred as a result of the contractors default thus costs will be disallowed, to include deletion of 3No BMS points @£10k each, add 3No BMS software points @£6k each, re-writing, issue & approval BMS des ops and test scripts @£20k, __ design time including revisions & reissue to 6No drawings £35k.
| 02SL - Stations (LUL) | Cxxx-NCR-002463 | NCR | SCS damper control |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2020-04-14 | 2020-11-04 16:27 | 204 | 2020-01-23 12:35 | Fire - Fire Systems & General | 250000 |  | Design | Repair | 1 (>60k) | Complete | Design Problem - Inadequate or defective design | Completed |  | During recent commissioning and witnessing of the smoke control systems OPE extract and staircase pressurisation systems the following matters became apparent, 1) Damper controllers not in accord with the requirements of BS EN 12101 - 8 2) Faults reporting to the fire alarm system contrary to the requirements of CRL1-XRL-M-RGN-CR001-50061 issued under PMI 01729 3) Dampers controlled utilizing intermediate control system as opposed to directly from PLC as per minimum requirement within CRL1-XRL-M-RSP-CR001-50110 issued under PMI 980 4) System includes single points of failure and duplication of function that could be designed out as required by CRL1-XRL-M-RGN-CR001-50047 issued under PMI 1471, this also requires a RAM analysis to demonstrate ALARP, this has not been undertaken and the system includes components that are not certificated for such a RAMS demonstration. 5) Controls wiring has been routed through the fire alarm CMS contrary to BS 5839
| 02SL - Stations (LUL) | Cxxx-NCR-002464 | NCR | 02a West bound staircase position changed in plan |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2020-03-31 | 2020-11-09 10:46 | 223 | 2019-11-18 11:19 | Architectural - General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The position of the West bound stair first landing flight from the bottom case at MTH -1 level 109300 FFL has moved average 84mm in plan towards Grid Z further East. Please see attached markup. The above impacts and changes the vertical setting out position of the hand rail from the stair nosings and the handrail is 50mm higher than the design position. The permenant hand rail is not yet installed, but the penetration holes in the glass have already been made and the glass is installed in position. The correct position of the rail as per applied concession (Document Cxxx-LAO-A-QAP-C101-50005 Rev 1.0) is bottom rail @ 624mm above pitch, top rail @ 924mm above pitch. If the handrail were to be installed in the position designated by glass holes/brackets - the left/right hand side mid rails and top rails would be approx. 50mm higher than installed mid rail. (bottom rail @ 674mm above pitch, top rail @ 974mm above pitch).
| 02SL - Stations (LUL) | Cxxx-NCR-002465 | NCR | __ Isolators |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2020-09-25 | 2020-09-16 10:18 | -9 | 2019-11-19 15:32 | Communications and Control Systems - General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Isolators for Fans 601 & 602 are installed too low.
| 02SL - Stations (LUL) | Cxxx-NCR-002466 | NCR | __ MCR for __ Doors Not Approved prior to install |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2020-03-20 | 2020-06-09 08:27 | 81 | 2019-11-21 11:46 | Architectural - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | Please see linked referenced __ Door MCR which is not Code 1 prior to installation works on site. Please note that this issue was raised in Cxxx-NCR-002160. This NCR is raised in order to close Cxxx-NCR-002160.
| 02SL - Stations (LUL) | Cxxx-NCR-002467 | NCR | AP10 Staircase Tolerances NLL |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-12-23 | 2020-03-06 15:19 | 74 | 2019-11-25 16:42 | Architectural - Flooring | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following detailed survey of AP10 staircase areas found that fall outside the required specification requirements / tolerances.
| 02SL - Stations (LUL) | Cxxx-NCR-002468 | NCR | MTH SL-1 Leak through ceiling in SR (Switch Room) XI-B [Room no. 2/701] |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2019-12-27 | 2019-12-02 22:04 | -25 | 2019-11-29 12:06 | Civil - Civil Engineering General | 1500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Water ingress through ceiling in switch room above
| 02SL - Stations (LUL) | Cxxx-NCR-002470 | NCR | MTH___ scope 01a_Damaged STO panels |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2020-05-28 | 2020-04-03 15:43 | -55 | 2019-11-28 08:46 | Architectural - General | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Insufficient quantity of material to do the job | Completed |  | Damaged has been found on two number STO panels along GL W on MTH, __ scope 01a. The cause for damaged cannot be determined.
| 02SL - Stations (LUL) | Cxxx-NCR-002471 | NCR | __ LED drivers |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2020-09-04 | 2021-04-07 13:15 | 215 | 2019-11-29 14:18 | Electrical - Electrical Engineering General | 10000 |  | Material | Rework | 2 (6-60k) | Complete | Management Problem - Not Defined | Completed |  | Materials Compliance Approval for the __ LED drivers have been stipulated as F2. The location of these drivers are on the platform and tunnels which exceed the maximum 200m3 volume allowance stated within the F2 compliance.
| 02SL - Stations (LUL) | Cxxx-NCR-002472 | NCR | ___30a_ Deviation from design intend |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2020-05-01 | 2020-06-03 17:24 | 33 | 2019-12-09 13:09 | Architectural - General | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The Louvre of the Moorgate Shaft Keat's Place elevation above the Double Door has been manufactured shorter and installed to the survey of the Duct. At the time of the survey, the door was not installed and once the door is now installed, there is a 281mm gap above the Double Door.
| 02SL - Stations (LUL) | Cxxx-NCR-002473 | NCR | Platform tunnel end lighting |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2020-08-17 | 2020-08-12 08:37 | -5 | 2020-07-20 14:44 | Electrical - Lighting | 7000 |  | Design | Rework | 2 (6-60k) | Complete | Design Problem - Inadequate or defective design | Completed |  | lighting not installed in Tunnel ends as there appears to be large spaces with no lighting
| 02SL - Stations (LUL) | Cxxx-NCR-002474 | NCR | Platform tunnel end lighting |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2020-01-30 | 2020-02-19 11:16 | 20 | 2019-12-06 13:28 | Electrical - Lighting | 20000 |  | Design | Rework | 2 (6-60k) | Complete | Management Problem - Inadequate administrative control | Completed |  | This NCR contains non conformance of lighting at Tunnel ends . CHT drawing Cxxx-LAO-DWG-C101_9-50011 C01 is not updated to the last __ drawing Cxxx-LAO-E-DDA-C101_8-10631 CHT drawing Cxxx-LAO-DWG-C101_9-50019 C01 is not updated to the last __ drawing Cxxx-LAO-E-DDA-C101_8-10639 Due to this fact there are light fittings missing from the interface between Cxxx and Cxxx. west end, west bound misses 5 lights . East end misses 2 lights , one on each platform.
| 02SL - Stations (LUL) | Cxxx-NCR-002475 | NCR | Doors (Delamination) |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2020-06-30 | 2020-06-18 16:38 | -12 | 2019-12-10 14:49 | Architectural - Doors | 1000 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | It has been reported that Door W-02-776-D03 the outer skin (Left Hand Leaf) has delaminated.
| 02SL - Stations (LUL) | Cxxx-NCR-002476 | NCR | BTH AP8 __ Redesign of cladding on LU side for EDNE area |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2020-08-24 | 2020-11-24 18:02 | 92 | 2019-12-10 16:57 | Architectural - Ceilings & Soffits | 500 |  | Planning | Repair | 4 (0.5-3k) | Complete | Previous Construction - Improper As Built | Completed |  | Redesign of cladding on LU side of AP8 door caused by MEP lack of Co-ordination
| 02SL - Stations (LUL) | Cxxx-NCR-002477 | NCR | Doors |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2020-03-27 | 2020-06-26 08:44 | 91 | 2019-12-11 14:15 | Architectural - Doors | 500 |  | Incomplete Works | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Reported that Doors W-08-407-D01 and W-08-408-D01 (All four leafs) have had 4 x no Pre-drill holes for door closure fixings, but the closers have been fitted internally. This leaves 4 holes (per door) showing on the FOH side of the door.
| 02SL - Stations (LUL) | Cxxx-NCR-002478 | NCR | Incorrect or Missing Fire Door Labels (Site Wide) |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2020-05-29 | 2020-08-31 20:53 | 94 | 2019-12-12 12:00 | Architectural - Doors | 3000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Reported that some doors do not meet the required specification requirements (JL20) for fire door labelling.
| 02SL - Stations (LUL) | Cxxx-NCR-002479 | NCR | Smoke Control System Operational Reliability during C&E Testing |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2020-05-29 | 2020-10-27 08:22 | 151 | 2019-12-12 14:45 | Fire - Fire Systems & General | 500000 |  | System Defect | Repair | 1 (>60k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | The Smoke Control System is provided to meet the requirements of __ design document Cxxx-LAO-M-RGN-C101-50020 – Control of HVAC Services in a Fire Alarm – Cxxx Design Proposal. This has been issued at revision 5.0 incorporating comments from numerous workshops with the F2 designers CRL , CEG and Cxxx and has a Code 1 status. This design document outlines the system architecture and explains the reasoning for its specification. This is based upon deploying LUL approved __ec Fire panels to control dampers by incorporating addressable I/O relays installed on their device loops. Damper controls to these __ec Panels are derived from the existing __ PLC’s which also control the fans. The current works have been constructed to meet the requirements of this approved design. During the testing of the OPE system, it has been observed that the system does not operate reliably. Upon further investigation, the monitored control relay which initiates the damper command has been recorded as un-stable, accounting for the system reliability issues. The OPE being driven in ‘safe’ mode using a FAS ‘alarm’ state i.e. the interface relay being permanently closed (fire state), also introduces alarm reporting complications into the FAS. FAS’s normally recognise a permanently closed contact as an alarm state. To complicate matters, the SCS DCP’s currently only report a general alarm to the FAS.
| 02SL - Stations (LUL) | Cxxx-NCR-002480 | NCR | Louvre blanking panel |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2020-09-23 | 2020-09-04 08:03 | -19 | 2019-12-12 15:24 | Mechanical - Mechanical Engineering General | 5999 |  | Design | Repair | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | During commissioning of __ chillers it became apparent that the air discharged from the Northerly chiller was being drawn back through the louvre adjacent to the discharge, this warmed air reducing performance and capacity of the machine. To prevent this the louvre adjacent to the chiller discharge requires blanking, - specification Cxxx-LAO-A-RSP-C101_WS103-50001 Revision 41.0 – Section JL13 – Clause 1205 (f) refers.
| 02SL - Stations (LUL) | Cxxx-NCR-002482 | NCR | Blomfield Box - Broad Street Elevation - Facade at Street Level - Roller Shutter* |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2020-01-12 | 2020-06-25 15:35 | 165 | 2019-12-15 14:48 | Architectural - Doors | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | During Verification Inspection a number of queries/concerns were raised associated with the installation of the Roller Shutter at street level behind the Louvred Façade (Grid Line 9) - Refer to photographs attached. Issues associated with roller shutter - installation and interfaces with adjacent finishes/threshold plate/waterproofing - function given damage to rails on as installed. The Contractor is requested to share details of design as detailed above, arrange for re-inspection and at the same time demonstrate operation of the roller shutter to close this NCR.
| 02SL - Stations (LUL) | Cxxx-NCR-002483 | NCR | BTH - Lift 8 - drilling of fixings into structural steelwork |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2020-06-30 | 2020-05-22 08:37 | -39 | 2019-12-16 16:19 | Mechanical - Lifts | 1000 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Further to inspection of the lift 8 pit, it is apparent that the lift subcontractor has drilled fixings into the supporting structure for the portal. The unknown fixing has damaged the galvanised coating, of the 110 year design life structure. See attached pictures.
| 02SL - Stations (LUL) | Cxxx-NCR-002484 | NCR | MTH - Ground Floor Level - GL9 Paid Side - Damaged __ Ceiling Tile CLG-212 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2020-06-19 | 2020-03-10 12:14 | -101 | 2020-02-20 17:28 | Architectural - Ceilings & Soffits | 1500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Personnel Error - Other human error | Completed |  | Refer attached plan markup and photo. Stainless Steel Ceiling panel CLG-212 to be refabricated and installed due to unknown damage
| 02SL - Stations (LUL) | Cxxx-NCR-002485 | NCR | “P&T – AP7 within CP5/CP6 – Floor tile cracks” |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2020-03-06 | 2020-03-13 15:25 | 7 | 2019-12-17 11:12 | Architectural - Flooring | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Cracking observed in terrazzo tiles along AP7 within CP5/CP6. Attached Report CRL-OBS-29269 shows drawing location of cracking and also photographic evidence.
| 02SL - Stations (LUL) | Cxxx-NCR-002486 | NCR | SY Cable On AHUs |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2020-08-21 | 2020-08-13 16:06 | -8 | 2019-12-17 13:50 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | SY cable to be replaced within AHU’s 201, 301, 251, 252 and 351. These were delivered from __ with SY cable pre-wired to the fan motors. SY cable is not allowed on LUL sites and so this needs to be replaced.
| 02SL - Stations (LUL) | Cxxx-NCR-002487 | NCR | AHU High Pressure DP Switches |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2020-01-14 | 2020-06-04 10:32 | 142 | 2019-12-17 13:57 | Communications and Control Systems - General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | DP switches – Recently raised instruction to __ to provide 8 of DP switches, (PA-DPS-85) has not been adhered to. The devices bought are incorrect and do not have an approved MCR. HBS have fitted these to ensure that the units operate over the Christmas break. The correct devices need to be provided and HBS will now need to re-fit the devices.
| 02SL - Stations (LUL) | Cxxx-NCR-002488 | NCR | Mechanical Plant Isolators |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2020-10-22 | 2020-10-23 08:52 | 1 | 2020-07-23 11:51 | Communications and Control Systems - General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Information not detailed | Completed |  | Isolators – We have found isolators that have had their internals uprated. However, the equipment label does not now match the rating. For example, W/04 has detailed on __ equipment schedule an 80A __ Isolator but the internal is rated for 100A. The fan is able to achieve 97Amps. We need a full survey of the isolators to ensure that the equipment schedule matches the field equipment, and if the field equipment has been modified then this needs to be fully reflected on site and within the documentation.
| 02SL - Stations (LUL) | Cxxx-NCR-002489 | NCR | IP 54 Rating of Water Mist Panel |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2020-09-24 | 2020-03-06 13:32 | -202 | 2019-12-19 13:39 | Fire - Fire Systems & General | 2999 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | The current installed water mist control panels are rated to IP 51. The panels therefore do not comply with the following materials and workmanship specifications which state an IP54 rated panel is required in this application: CRL1-XRL-M-RSP-CR001-50082 – JY71 LV Switch Gear and Distribution boards Part JY71.3201 ‘General’ – Part P) which states: p) Control or Instrumentation sections of the FBA (Factory Built Assemblies) shall be manufactured to a minimum IP 54. CRL1-XRL-M-RSP-CR001-50083 - JY72 Contractors and Starters Part JY72.1306 ‘Assembly Construction’ – Section H) which states: h) Degree of protection to BS EN 60529: ii) IP 54 for all units installed in plantroom and pump rooms
| 02SL - Stations (LUL) | Cxxx-NCR-002490 | NCR | MTH – __ Tiling – Paid Side – 7. Movement joint sticking up – Occurred on 1 occasion |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2020-05-24 | 2020-03-18 17:53 | -67 | 2020-01-25 11:19 | Architectural - Flooring | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Movement joint to be repaired to within acceptable tolerance. Location shown on attachment
| 02SL - Stations (LUL) | Cxxx-NCR-002492 | NCR | MTH – __ Tiling – Unpaid and Paid Side – 15. Movement joint needed – Occurred on 3 occasions |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2020-05-15 | 2020-02-24 09:54 | -81 | 2020-01-16 17:41 | Architectural - Flooring | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Movement joints have been installed as per spec and approved drawing
| 02SL - Stations (LUL) | Cxxx-NCR-002494 | NCR | __X Life safety fan room temperature |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2020-09-24 | 2020-12-22 11:45 | 89 | 2020-01-06 10:39 | Mechanical - Mechanical Engineering General | 5000 |  | Design | Repair | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | __ fan room containing platform extract fans also contains life safety SCS panels, ATS and fan inverters. None of the ductwork within the room is insulated such in platform smoke extract operation there is approx. 38m2 of sheet metal potentially radiating circa 270 degrees Centigrade heat into a small room circa 150m3. It is understood that the TAAS can operate at 69 degrees Centigrade inverters can operate at 59 degrees Centigrade , the PLC's within the panel 44 degrees centigrade and other panel components at 39 degrees Centigrade. There currently appears to be inadequate temperature control to ensure safe operating temperatures of the electrical equipment are not exceeded for the prescribed emergency operation period.
| 02SL - Stations (LUL) | Cxxx-NCR-002495 | NCR | Chiller modification |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2020-02-29 | 2020-01-24 15:42 | -36 | 2020-01-06 11:45 | Mechanical - Heating Ventilation & Air Conditioning | 3000 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | MGS chiller No 2 has been retro-fitted with a new controller. No reason for this change has been advised or the need made known such CRL approval can be given, the machine is therefore no loonger as approved. In addition the machine has not been modified to accept the new controller but rather a fly lead of presumably ULV is fed through the open aperture now vacant from the previous controller which provides an opening through which a hand can reach non-shrouded 400v terminals such the machine cannot be energised. __ AP office have been requested to padlock off the MCC switch powering the machine.
| 02SL - Stations (LUL) | Cxxx-NCR-002497 | NCR | Chilled water system water quality |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2021-04-23 | 2020-04-07 10:11 | -381 | 2020-01-06 12:50 | Mechanical - Mechanical Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | It is understood that the water quality of both __ and MGS chilled water system significantly deteriorated with a rise in Iron content and dissolved solids. No reports have been received by CRL or notification of intended remedial works although it is understood that certain flushing has been undertaken this has not been agreed, notified or witnessed.
| 02SL - Stations (LUL) | Cxxx-NCR-002498 | NCR | MGS SER access to MSFD |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2020-02-03 | 2020-05-29 10:44 | 116 | 2020-01-06 13:43 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Design | Reject | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Maintenance access to the SER extract MSFD at platform level is from the narrow corridor. A luminaire has been installed that prevents the necessary narrow tower / MEWP from going high enough to access the damper. it was agreed with Andy Smith that the luminaire would be relocated however in the intervening 15 months this has yet to happen.
| 02SL - Stations (LUL) | Cxxx-NCR-002499 | NCR | Frost [protection to small bore pipework |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2020-03-31 | 2020-08-10 09:34 | 132 | 2020-01-06 13:52 | Mechanical - Mechanical Engineering General | 2000 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The designs for the chilled water systems include for electric trace heating to provide frost protection to main pipework within areas susceptible to frost / external conditions. These areas also contain small bore (8mm diameter) pipes of static water connecting main pipes to pressure sensors, these pipes have not been fitted with trace heating or any other form of frost protection and are therefore susceptible to the freezing contemplated by the design.
| 02SL - Stations (LUL) | Cxxx-NCR-002500 | NCR | MGS segregation of pressurisation air inlet |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2020-05-30 | 2020-07-27 16:28 | 58 | 2020-01-06 14:06 | Mechanical - Heating Ventilation & Air Conditioning | 30000 |  | Incomplete Works | Repair | 2 (6-60k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | MGS pressurisation system draws air from a louvre at street +1 which is hard ducted to the floor slab at that level. The air then passes through a builderswork shaft to a duct connection to the underside of the slab at street level. BS EN 12101 - 6 requires at 11.8.2.7 that any such shafts are used soley for air distribution. The shaft as curerently complete encompasses the passage of other services that need to be segregated as __ email 2 February 2019 and nothing has been put forward for approval to the contrary. It is also noted that the slab at street +1 needs to be imperforate which is currently not the case.
| 02SL - Stations (LUL) | Cxxx-NCR-002503 | NCR | TUN - Lift 7 CMS not mounted on __ |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2020-08-10 | 2020-07-22 09:48 | -19 | 2020-01-09 16:57 | Mechanical - Lifts | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | At the top of lift 7, it is apparent that the CMS has not been mounted on unistrut, contrary to CRL and LU specification. See attached pictures.
| 02SL - Stations (LUL) | Cxxx-NCR-002504 | NCR | Insulation to ductwork in running tunnels |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2020-07-31 | 2020-09-03 14:25 | 34 | 2020-01-13 10:38 | Mechanical - Mechanical Engineering General | 25000 |  | Design | Repair | 2 (6-60k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | Ventilation and smoke control system ductwork located in the running tunnels at the West end of the station complex has been insulated in line with the requirements of the fire engineers requirements in the associated fire risk assessment. On review of the performance requirements from this area it has come to light that the standard ductwork insulation system installed is not considered to be robust enough for the tunnel environment and forces imposed on it from train piston effect forces.
| 02SL - Stations (LUL) | Cxxx-NCR-002505 | NCR | BTH - Precast Soffit Minor Damage |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2020-02-13 | 2020-08-05 12:24 | 174 | 2020-01-16 07:59 | Architectural - Ceilings & Soffits | 6000 |  | Damaged | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | During the drilling of the wholes through the precast concrete beamlets for the rewiring of the lights, a small section of damage occurred to one of the beamlets. The damage consisted of a 1no. chipped edge on the south side of the memorial glass. Please see attached picture of the damage.
| 02SL - Stations (LUL) | Cxxx-NCR-002508 | NCR | 14a____Installation progressed without approved MCR |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2020-04-30 | 2020-04-30 16:02 | 0 | 2020-01-28 10:43 | Architectural - General | 500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Installation of materials being progressed without CRL approval: Cxxx-LAO-O4-XDS-C101-51129 - MCR for toughened glass for use in Signage
| 02SL - Stations (LUL) | Cxxx-NCR-002509 | NCR | ___Glass specification for SIP/SOP, MAP and MTH glass cabinets |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2020-02-29 | 2020-02-20 10:06 | -9 | 2020-01-28 11:56 | Architectural - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The Glass for the SIP/SOP, MAP and MTH glass cabinets are not laminate as per specification. The specification asks for the cladding glass to be a laminate glass due to breakage characteristics in blast. The SIP/SOPs are tagged with spec Lift Directory Signs SGN-112 on the Cxxx design intent drawings. The specification shows the below on the SGN-112: JN15.1213- Directional/ way finding sign to be in accordance with the relevant LU/ TfL standards and Cxxx Wayfinding and Signage reports, comprising; a) Signage incorporated as part of hinged / demountable glass facing access panel: i) Material: Low iron clear laminated (minimum PVB inter-layer of 0.76mm thickness) glass with a toughened outer pane and heat strengthened inner pane. The MAP panels refer to the spec IWS-817 which is the As IWS-816 with integrated glass door panels. JH13.1218- Type IWS-817 Internal Glazed Cladding System shall be as Type IWS-816 but shall incorporate glazed door module within panel make up. b) Doors: i) Glazed laminated glass to identical finish as Type IWS-816.
| 02SL - Stations (LUL) | Cxxx-NCR-002511 | NCR | Moorgate PRM Corridor - __ leak, damage to 60a & Cladding Panels |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2020-07-31 | 2020-07-17 16:01 | -14 | 2020-01-29 11:21 | Architectural - General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | __ leaked through a mastic joint in the balustrade base. The leak has stained a number of cladding panels on the northern elevation of ES5
| 02SL - Stations (LUL) | Cxxx-NCR-002512 | NCR | MTH – PRM Corridor – PAD Balustrade BAL-112 – Pour grade __ embedment achieved in east end of balustrade |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2020-06-26 | 2020-07-17 16:11 | 21 | 2020-01-29 12:22 | Architectural - Balustrade | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Leakage of __ in the east end of the channel means full embedment depth has not been fully achieved in a short section of the balustrade base
| 02SL - Stations (LUL) | Cxxx-NCR-002513 | NCR | __X - Sequence of work in Z/791 MRS Riser (Waterproofing) |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2020-11-30 | 2020-09-18 13:06 | -73 | 2020-02-05 11:24 | Structural Engineering - Surface Treatment | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Information not detailed | Completed |  | Cladding works complete before structural waterproofing works
| 02SL - Stations (LUL) | Cxxx-NCR-002514 | NCR | BTH - Lift 9 - Cables tied incorrectly |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2020-05-04 | 2020-07-22 09:50 | 79 | 2020-02-05 13:33 | Mechanical - Lifts | 2000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Further to inspection of lift 9 CMS, it is apparent that the cables have been secured to the cable ties using plastic cable ties. This is in contrary to Clause 29.4.2 of the lifts works information "Specification for SMVT lift and SMVT Inclined Lifts". See attached Photos
| 02SL - Stations (LUL) | Cxxx-NCR-002515 | NCR | BTH - Lift 9 - Drilling into Galvanised Structure |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2020-06-30 | 2020-05-22 08:38 | -39 | 2020-02-05 14:04 | Mechanical - Lifts | 1500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other management problem | Completed |  | Following inspection of the lift 9 pit, it is apparent that the supporting structural steelwork for the portal has been drilled by the lift contractor. This had already been communicated prior as unsatisfactory under Cxxx-NCR-2483. This requirement to drill the galvanised structure was not communicated to the Tier 1 or the contractor prior to the works commencing.
| 02SL - Stations (LUL) | Cxxx-NCR-002516 | NCR | BTH - Canopy Bonding |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2020-04-27 | 2020-04-01 10:48 | -26 | 2020-02-07 10:36 | Electrical - Earthing & Bonding | 8000 |  | Incorrect Installation | Rework | 2 (6-60k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Bonding not installed as per contract specification and __-__-RFI-00622, RFI3304 __ response 10-Oct-2016
| 02SL - Stations (LUL) | Cxxx-NCR-002517 | NCR | Duct Probe |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2021-01-04 | 2020-12-24 12:59 | -11 | 2020-02-07 13:41 | Fire - Detection | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - NCR excessive closure due to design issue | Completed |  | To monitor air flow within the Stair Pressurisation inlet ductwork, a probe is inserted. It is currently a Fireclass DPK6 device as described within the A__ F2 design. These are connected to the fire system loops and are currently operating fault-free on the system. Duct Probes are installed for both the Moorgate and Blomfield Box systems. During smoke testing, it became apparent that the probe did not detect the presence of the smoke as expected. It appears that airflow within the duct at the point of installation is of such low volume that the probe is unable to detect it. Our current belief is that either:- • An unsuitable detector has been specified to meet the required functionality. • The probe requires re-positioning such that it is exposed to sufficient airflow to operate. Consequently, this NCR is raised to record the symptoms we are witnessing, and request A__ provide a workable replacement solution. Should an alternative detection device be required, a MCR covering the product must be supplied.
| 02SL - Stations (LUL) | Cxxx-NCR-002518 | NCR | BTH - Lift 8/9 Switches |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2020-03-09 | 2021-03-02 12:27 | 358 | 2020-02-10 08:12 | Architectural - Finishes | 6000 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | Further to site inspection of Lift 8/9, it is apparent the stop switches have been installed without the appropriate pre-construction documentation, i.e. drawings. Furthermore, contrary to JX10.1408 H, all visible fixings are to be accepted by the Project Manager, as the location of the switches are visible through the inclined lift glass. See attached photos.
| 02SL - Stations (LUL) | Cxxx-NCR-002519 | NCR | BTH AP8 Ramp gradient |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2020-04-07 | 2020-03-17 09:56 | -21 | 2020-02-11 12:20 | Architectural - Flooring | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The AP8 ramp installation differs from the works information with it being shallower than the 1:20 gradient. The works information didn’t show the tile colour differentiation between landings and ramps required for DDA BS 8300 design criteria. Under Cxxx-PMC -03616 the Employer issued an initial DDA assessment, in the form of the DDA report Cxxx-ATK-A-RGN-CRG02-50133 Rev 2 with perceived non-compliances, this PMC also states that that a further site assessment is to be completed by the Contractor. The Contractor has completed a further assessment on site and wishes to communicate the findings to the Employer in the form of the attached report __ Report Cxxx-LAO-S-RGN-C101-50016.
| 02SL - Stations (LUL) | Cxxx-NCR-002520 | NCR | SIP/SOP Signage - Incorrect Graphics and Wording in Three Locations |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2020-05-04 | 2020-08-18 12:56 | 106 | 2020-02-17 11:37 | Architectural - Signage | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | USN 113 and USN 441 - Wording on SIP/SOP doesn't replicate the text on the __ equipment behind. USN 266 - Incorrect graphics on the lift directory
| 02SL - Stations (LUL) | Cxxx-NCR-002521 | NCR | Fire Alarm System Interface Boxes - Installation Quality |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2020-05-16 | 2020-08-19 06:55 | 95 | 2020-02-17 15:27 | Fire - Detection | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Previous Construction - Problems based on previous construction errors | Completed |  | Upon sample Crossrail inspection of Fire Alarm Interface Boxes, it was found that the quality of the installations was below the required standard in the majority of those inspected. Significant termination and general installation issues were observed, resulting in a lack of confidence in the overall works.
| 02SL - Stations (LUL) | Cxxx-NCR-002522 | NCR | Lift 7 Ladder :: Clear Depth Impeded by Light Fittings |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2020-10-30 | 2021-04-30 14:01 | 182 | 2020-02-18 13:00 | Electrical - Lighting | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The ladder has been removed from the shaft. A new means of access will be agreed but the issue of "no clear depth" has been eliminated by the removal of the ladder. Review has been completed with __, __ and CRL representatives and an Access Statement and Risk Assessment has been produced and accepted by all parties Cxxx-LAO-E1-RGN-C101-50168. This will be included in the __ O&M for L7.
| 02SL - Stations (LUL) | Cxxx-NCR-002523 | NCR | __ 00A - __ Doors - No evidence of Benchmark acceptance |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2020-03-17 | 2020-04-28 10:29 | 42 | 2020-02-18 16:25 | Architectural - General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | The subcontractor, __, could not provide evidence of Benchmark acceptance in line with specification. JH13.2015 Benchmark Requirements.
| 02SL - Stations (LUL) | Cxxx-NCR-002524 | NCR | MTH 06A SOR - No evidence of benchmark acceptance for __ Curtain Walling System |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2020-03-20 | 2020-02-25 11:38 | -24 | 2020-02-21 09:37 | Architectural - General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The subcontractor, __, could not provide evidence of Benchmark acceptance in line with specification. JH13.2015 Benchmark Requirements.
| 02SL - Stations (LUL) | Cxxx-NCR-002525 | NCR | Excessive Door Opening Forces |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2021-04-16 | 2021-04-01 07:27 | -15 | 2020-06-03 12:11 | Architectural - Doors | 20000 |  | Design | Repair | 2 (6-60k) | Complete | Design Problem - Other | Completed |  | In the Staff Accommodation area at Moorgate, level Street -1, a number of doors have been observed as non-compliant with the opening forces requirements as stated in BS8300 and LU standards. Those doors have been initially identified in EWN 1818 and in more detail on PTR Cxxx-RFI-004801. All other BoH and maintenance areas should record forces of up to 110N maximum. During SPA testing forces in excess of 110N have been recorded as a number of doors have been observed to be slamming
| 02SL - Stations (LUL) | Cxxx-NCR-002527 | NCR | __X Stair pressurisation - door issues |  | Crossrail | PDP | LIS - Liverpool Street Station (Central) |  | 2021-03-26 | 2021-05-14 14:56 | 49 | 2020-02-26 14:58 | Mechanical - Mechanical Engineering General | 5999 |  | Testing and Commissioning | Repair | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | Following demonstration of the __ stair pressurisation system a number of doors within the __ shaft are either slamming or not closing, under stair pressurisation operation. 3 Doors Not Closing are: E-02-731-D01 (CER room) E-02-776-D01 (Fan room) E-03-131-D01 (LCC room) 4 doors which are slamming are: E-02-762-D01 (Fan room) E-02-731-D01 (Battery room) E-01-237-D01 (CIR room) E-03-236-D01 (CIR-PL) None of these doors are on the means of escape.
| 02SL - Stations (LUL) | Cxxx-NCR-002528 | NCR | BTH - Lift 8 Bottom Landing Internal Cladding |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2020-03-27 | 2021-03-18 16:35 | 356 | 2020-02-28 12:21 | Architectural - General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Information not detailed | Completed |  | Further to the incorrect installation of the lift 8 portal guide rails. As a result the lift door set has clashed with the internal cladding. To facilitate lift installation the cladding has been removed. However, additional replacement cladding will require fabricating with approximately 15mm less projection into the shaft.
| 02SL - Stations (LUL) | Cxxx-NCR-002529 | NCR | Broadgate UPS Insufficient Cooling Design |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2020-12-08 | 2020-07-13 07:10 | -148 | 2020-03-03 09:40 | Mechanical - Heating Ventilation & Air Conditioning | 20000 |  | Design | Repair | 2 (6-60k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | During the BMS commission of the VRF system within Broadgate Ticket hall, it was noticed that the units IDU105A & IDU 105B were not providing the cooling capacity required for the room and the temperature was exceeding the set point. The design of the original cooling capacity of the room required was 0.3KW, the units provided on the smallest selection was 2.0KW, yet the heat within the room was still exceeding the set point. __ issued an EWN and an RFI to the consultant to verify the cooling requirements of the room. Upon investigation it has been identified that the cooling design for this room was substantially undersized. Please find attached the RFI response from the consultant.
| 02SL - Stations (LUL) | Cxxx-NCR-002531 | NCR | Fan flexes |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2020-10-30 | 2021-01-13 08:13 | 75 | 2020-03-16 12:27 | Mechanical - Heating Ventilation & Air Conditioning | 2000 |  | Material | Repair | 4 (0.5-3k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | Axial fans installed to life safety systems (Platform extract, stair pressurisation / air release) are supplied by FlaktWoods and fitted with flexible connections the contractor advises are also supplied by __. The flexes are devoid of markings or labelling to identify manufacturer or type or temperature rating; appear to be a woven glass cloth with a sealing polymer possibly silicone facing to one side. The cloth flexes are sewn into a tube which is fitted over circular spigots fitted to fan and adjoining duct and secured with worm drive clips. On the suction side of the fans the flex is drawn into the airway of the duct causing it to be pulled taught over the end of the steel spigots at anywhere up to 90 degrees. Air movement and vibration cause the flex to rub against the end of the spigot abrading the cloth. This process causes the flexes to fail in a relatively short period of time. Attached pictures from pressurisation fan 251 with around 500 hours run time (inlet pressure circa -250Pa). Pictures from air release fan B51 with around 50 hours run time (inlet pressure circa -1100Pa). As can be seen even at low pressures the flexes wear through albeit over a longer period.
| 02SL - Stations (LUL) | Cxxx-NCR-002532 | NCR | double escape door operation |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2020-08-31 | 2020-12-16 15:51 | 107 | 2020-03-12 15:39 | Architectural - Doors | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | A number of double doorsets have been supplied as SR3 security rated and are also required to operate as public and/or staff escape doors. These doorsets have been fitted with astragals in order to provide security compliance and as a result can currently only be fully opened by opening the astragal-fitted leaf before the non-astragal side can be opened. This operation is in contravention of BS EN 1125 (2008) and TfL guidance G0102 A1 and as such, represents a non-compliance to the works requirements. BS EN 1125 (2008) Section 4.1.2 “…panic exit device shall be designed to release a door at all times from the inside in less than 1 s and that it is operated by hand or body pressure in one continuous movement in the direction of exit and/or in an arc downwards.” TfL guidance G0102 A1 “Rebated double doors shall not be installed on means of escape access / escape routes (Public / Non-public).” Doors affected by this issue are as follows: __X twin double bronze-clad final exist escape doors – E-01-631-D03 (individual doors form part of and are set into this larger door). Moorgate shaft stainless steel final exit escape double doorset – W-01-631-D01 AP5 twin double stainless steel escape doorsets – W-08-240-D01 & 02 Platform end screen double escape doorset – E-08-261-D01 Note that other similar doorsets do currently operate successfully from either leaf: Moorgate shaft stainless steel final exit escape doors – W-01-632-D01 AP1 twin double escape doorsets – E-08-201-D01 & 02 and E-09-236-D03 & 04
| 02SL - Stations (LUL) | Cxxx-NCR-002533 | NCR | Tunnel fire main trace heating |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2020-05-29 | 2020-08-21 11:35 | 84 | 2020-03-16 11:07 | Electrical - LV Equipment | 2999 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The WI requires the tunnel fire main trace heating to be monitored for fault by SCADA and as such is included to the SCADA I/O. The WI also requires the station fire main trace heating to be monitored for fault by the fire alarm system (also see RFI 4184), the BMS also monitors this fault. At __ the trace heating controller that provides the fault signal is wired to the trace heating tape to both the station and tunnel fire mains. This means there is no differentiation of fault as to which system is affected. It also means that a fault to the station main is reported to SCADA and conversely a tunnel fire main fault is reported to the station fire alarm and BMS. The __ drawing (Cxxx-LAO-C-LRC-C101-50324) shows 2No separate trace heating circuits (TH 105 and TH 108), only one has been installed. At present the system is not as per the approved __ drawing and is incapable of complying with the WI
| 02SL - Stations (LUL) | Cxxx-NCR-002534 | NCR | ___Installation progressed without Approved MCR for 3M VHB 4947F Tape |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2020-05-29 | 2020-04-17 10:44 | -42 | 2020-03-16 13:50 | Architectural - General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Installation of materials being progressed without CRL formal Approval by __: Cxxx-LAO-O4-XDS-C101-50710 C12.020arv - MCR - 3M VHB 4947F Tape
| 02SL - Stations (LUL) | Cxxx-NCR-002535 | NCR | ___Installation progressed without Approved MCR for __ EPDM Membrane |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2020-04-13 | 2020-06-25 15:04 | 73 | 2020-03-16 14:07 | Architectural - General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | Installation of materials being progressed without CRL formal Approval by __: Cxxx-LAO-O4-XDS-C101-50359 - Materials Compliance Record for __ EPDM Membrane
| 02SL - Stations (LUL) | Cxxx-NCR-002536 | NCR | Lighting Design |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2020-12-22 | 2020-04-07 12:09 | -259 | 2020-03-17 09:35 | Electrical - Cable Management | 10000 |  | Design | Rework | 2 (6-60k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Emergency / non emergency lighting Design does not meet the requirements of S-1 066 A2 as required within the specification.
| 02SL - Stations (LUL) | Cxxx-NCR-002542 | NCR | FFO_AP8 LU Interface Ceilng CLG-211__relocate Step in ceiling to avoid service |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2020-04-15 | 2020-08-27 17:05 | 134 | 2020-03-18 15:25 | Architectural - Ceilings & Soffits | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | AP8 LU Interface Ceiling CLG-211 design as per __ Drawing Cxxx-LAO-A-DWG-C101_Z-50042 rev C01 is not feasible due to clash with pipe drain valve. Refer attached sketch and photo
| 02SL - Stations (LUL) | Cxxx-NCR-002543 | NCR | Damaged Escalator Handrail |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2020-08-22 | 2020-07-29 08:48 | -24 | 2020-04-24 13:05 | Mechanical - Escalators | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Other human error | Completed |  | Escalator handrail on esc 10 have been damaged
| 02SL - Stations (LUL) | Cxxx-NCR-002544 | NCR | __-31a-Securiclad SR4 panels installed damaged |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2020-05-31 | 2020-07-07 12:17 | 37 | 2020-03-25 11:50 | Architectural - General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Moorgate Shaft - Keats Place Elevation, Securiclad panels has been installed with visible damage as shown in the photos attached to this NCR.
| 02SL - Stations (LUL) | Cxxx-NCR-002545 | NCR | AP5-AP6 Signage |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2020-07-17 | 2020-09-17 13:49 | 62 | 2020-03-26 13:05 | Architectural - Signage | 500 |  | Incomplete Works | Repair | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | Refer to CRL-OBS-31209. • Sign 404: o Note S/S box was installed above sign. This was done as a solution to the unsightly gap between the sign and the GFRC ceiling. Note CRL was not consulted nor approved this remedial solution. o Note also the top of the sign sits above the lighting boom. This still appears very uncoordinated and Cxxx should review and propose an overall integrated design for CRL review. • Signs above doors 402 and 403 installed, although gaps are visible below and above signs. Cxxx to review and propose solution for CRL review. • Sign 304: large gap between sign and GFRC. This appears incomplete. Cxxx to review.
| 02SL - Stations (LUL) | Cxxx-NCR-002546 | NCR | FFO_ Horizontal Fire compound Locations installed at increase spans without reinforcment |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2020-11-30 | 2021-01-18 10:57 | 49 | 2020-08-25 17:34 | Fire - Compartmentation | 5000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | Below listed Horizontal Compound locations have been identified as outside non reinforced __ Compound size limitations. __ have reviewed these locations and advised while the locations are outside size limitations they do not believe this will affect the fire performance of the compound. However __ can not guarantee the load bearing performance of the horizontal / floor compounds. Refer attached; *email correspondence with __ Fire *email correspondence with __ *Photos of each location *__ records of each location LOCATIONS: *Moorgate, Plat level +3, Tablet Obsv # 2240 *Moorgate, Plat +4, Tablet Obsv #614 *__X, Plat level +2 , Tablet Obsv # 1635 *__X St +1, Tablet Obsv # 526 *__X St + 2, Tablet Obsv # 471 *BTH, Tablet Obsv #436 *__X plat level, Obsv # 610
| 02SL - Stations (LUL) | Cxxx-NCR-002547 | NCR | AP5/AP6 Stainless steel cladding over BAL112 balustrade base (OBS CRL-OBS-27792) |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2020-08-21 | 2020-07-14 10:55 | -38 | 2020-04-23 10:10 | Architectural - Balustrade | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | This NCR was raised to separate issues raised in Cxxx-NCR-002436. It was originally raised to cover CRL-OBS-27792 on the glazed balustrade bases. During a review and alignment of NCR's in readiness for progression to closure this observation was moved to be addressed in 3 area NCR's as follows: Cxxx-NCR-002238 – Installation and Architectural – Moorgate Ticket Hall Balustrades Cxxx-NCR-002239 - Installation and Architectural – Moorgate PRM Corridor Balustrade Cxxx-NCR-002240 - Installation and Architectural – Moorgate AP5 Stair Balustrade This NCR has now been revised to only address CRL-OBS-27791 which relates to the interfacing packages surrounding the glazed balustrade on the staircase in AP5. OBS text as follows: Moorgate Ticket Hall - AP5 Stair - Balustrade/Cladding Installation Quality surveillance carried out on installation (__ Package 23a - IWS-715 and IWS-816 - no tag sheet reference for stainless steel skirting) with particular attention paid to alignment of different cladding systems. Refer to sketch and photos. Generally: Misalignment between all elements forming this elevation Skirting • No specification/tag sheet for the stainless steel skirting. • Profile and interface with stairs leaves gaps – consider re-templating along with the interface detail with the stair – provide intent detail and tolerances. • Fixings missing • Mis-aligned with the steel flat forming part of the Sto Glazing above. • Mis-aligned with the steel balustrade baseplate/over-cladding. Sto Cladding/Stainless Steel Flat (above skirting). • 10mm gap/5mm flat/5mm gap to skirting as per other areas not achieved. • S/S flat lengths do not correspond with adjacent elements – sometimes short/others too long and then no parallel with adjacent panels. • Vertically mis-aligned with adjacent panels – confirm tolerances in plan. Handrail • The termination details and relationship of the balustrade to the last stair differs between GFRC mounted/central and handrail mounted on the glazing - this should be addressed to provide a consistent detail/termination point (on plan). Flooring: • Stair nosings – final tile is a different colour to adjacent tiles – is this intentional? • Tile colour to be confirmed – outstanding action – provide accepted samples. Comment to be addressed to facilitate CRL acceptance.
| 02SL - Stations (LUL) | Cxxx-NCR-002548 | NCR | AP5 Stairs - Stainless Steel Handrail |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2020-07-30 | 2020-07-14 10:29 | -16 | 2020-04-28 07:33 | Architectural - Balustrade | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | The termination details and relationship of the balustrade to the last stair differs between GFRC mounted/central and handrail mounted on the glazing - this should be addressed to provide a consistent detail/termination point (on plan).
| 02SL - Stations (LUL) | Cxxx-NCR-002549 | NCR | MTH, PRM, AP5 - PAD BAL-112 Balustrades design deviates from WI and security (incorporating CRL-OBS-27341) |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2020-07-31 | 2020-07-09 16:20 | -22 | 2020-04-28 08:01 | Architectural - Balustrade | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | PAD Glazed Balustrades – BAL-112 - Design deviation from the WI The WI design for glazed balustrades uses a clamped base solution. The Cxxx subcontractor design for glazed balustrades in Moorgate Ticket Hall, at Moorgate PRM corridor and for the Moorgate AP5 staircase uses a resin fixed solution and additionally changes the glass type used. The changes were not formally communicated and agreed with the Crossrail team ahead of commencing fabrication and construction. The changes raise several concerns over assurance of the revised design. Particularly ensuring the performance requirements are met both in the design and during installation. To enable a suitable split of items for closeout issues have been split into separate NCR’s as follows: Cxxx-NCR-002549 - Design issues / design change Cxxx-NCR-002429 – No benchmarks provided Cxxx-NCR-002238 – Installation and Architectural – Moorgate Ticket Hall Balustrades Cxxx-NCR-002239 - Installation and Architectural – Moorgate PRM Corridor Balustrade Cxxx-NCR-002240 - Installation and Architectural – Moorgate AP5 Stair Balustrade The following items are to be addressed in this NCR to enable the design changes to be accepted: 1. Design drawings clearly showing the installed arrangement - Correct drawings issued for review and accepted by Crossrail 2. Static and blast calculations cover all locations / arrangements - The handrail fixed to the glass is included in the designs 3. Change to __ resin fixed glass 4. Change in glass type to 2 no. toughened panes with structural interlayer - MCR - Demonstration of alignment of the materials used with the design calculations 5. Omission of the chamfer on the top edges of the baseplates 6. Blast calculations have been reviewed and confirmed adequate 7. Access and maintenance strategy / Operation and maintenance manuals - Provision of information on glass replacement - Input from a reputable glazing supplier/installer if possible - Confirmation of acceptance by London Underground 8. Specification clause non-compliances and records assuring the deviations - JL32.1210 a) i) – interlayer and glass types - JL32.1210 b) – clamped base brackets - JL32.1210 b) iii) – 5mm chamfer to inside top face of clamp brackets - JL32.1210 b) vii) – fixing penetrations for glass retention in blast CRL-OBS-21341 - OBS text as follows “During a site walk with __, it was observed that the glazed balustrades (BAL-112) was being installed adjacent to escalator void (ESC 22/23/24). Concerns raised are as follows: The design as installed is a move away from the Cxxx WI (based on Cxxx's F1 design). An adhered as opposed to clamped solution is being installed although bolts have been maintained in the design (part of the clamping system). • Depth of the clamped glass. • Glass selection – not as per the WI – although this could be feasible additional detail should be provided. • Blast Calculations – provide confirmation that these have been accepted. The current installation is a move away from the WI and calculations supporting the design have yet to be “accepted” by CRL. WO CRL-REV-00210661 is currently with CRL for review. This detail has also been installed for the PRM lift at level -1 and at NLL Lobby at Level -5.” The issues raised in the OBS have been captured in the Design Deviation description above apart from reduction in the depth of clamped glass. 9 - Depth of clamped glass not in line with design requirement in document Cxxx-LAO-A-XCL-C101_WS099-50019. The design change to a resin bonded base also has items to address at installation stage, particularly around method and quality. This will be addressed in the area NCR’s listed at the start of this NCR including – installation method, achieving required quality, __/CRL/manufacturer witnessing, installer competency.
| 02SL - Stations (LUL) | Cxxx-NCR-002550 | NCR | MSH - Cxxx radio cables installed in firefighting shaft |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2020-08-31 | 2020-07-28 10:25 | -34 | 2020-04-28 12:19 | Communications and Control Systems - Radio | 3000 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Additional Cxxx radio cables have been installed at Platform Level in Moorgate shaft (space 8/081 CIR-S). This area is considered a fire fighting lobby and part of the protected shaft where standards dictate that only services serving the shaft are permitted. All other non-essential services should be routed elsewhere of be enclosed in fire rated construction. This area was subject to a detailed review and assessment in 2019 where other affected services were assessed, headroom and refuge requirements agreed and the necessary compartmentation introduced, refer Cxxx-RFI-004359. At the time the Cxxx design in the area showed a single cable to the antenna in the lift lobby of space SID 7/048. This is shown on Cxxx drawing Cxxx-SMN-R3-DDA-C101_7-90003 Rev C02 (cable FD013 to antenna ANT-006). The Cxxx design was based on this arrangement and services passing through the congested lobby area along with associated fire separation aligned with this, as detailed in Cxxx-RFI-004359. Subsequent Cxxx radio system design changes have introduced further cables in this area that are not considered in the design and are now not compliant with fire standards requiring having only services in the lobby that serve the lobby. it is understood these additional cables were introduced by Cxxx when it was identified their existing design did not perform as expected during testing.
| 02SL - Stations (LUL) | Cxxx-NCR-002553 | NCR | PRM Corridor Balustrade - S/S Channels |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2020-07-31 | 2020-07-24 09:18 | -7 | 2020-05-15 10:43 | Architectural - Balustrade | 500 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | When witnessing the __ pour on 27/01/2020, refer to CRL-OBS-30309, it was noticed that some S/S channels appear out of tolerance with visible gaps in the joints. This creates an unsightly situation. Refer to attached photos.
| 02SL - Stations (LUL) | Cxxx-NCR-002554 | NCR | AP2 - Lift Fascia/Equipment and interfaces with adjacent finishes. |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2020-08-14 | 2020-09-15 15:58 | 32 | 2020-05-18 13:37 | Architectural - Finishes | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During a CRL Inspection of __ Package 13 and 15a - CRL-OBS-29886 was completed for the areas as identified in this Observation and the mark-up attached to this PTR. A number of comments were made that required action to be agreed and addressed however, these have yet to be captured on a PTR. Refer to associated mark-up and photographs. 1. Glass Cladding/Cabinet co-ordination and existence of gaps beyond tolerances of architectural specification. 2. Missing trim to top of cladding. 3. (Left) gaps between __ Cladding (__) GFRC and Skirting (__) proposal to be put forward to address. 4. Cabinets to have shroud to prevent items/keys dropping behind cladding. 5. MAP Door panel clashes with adjacent skirting preventing opening of door fully - to be addressed. 6. Internal finishes of MAP panel leave gaps to floor and behind cladding - to be addressed. 7. Lift fascia/portal generally installed out of tolerance.
| 02SL - Stations (LUL) | Cxxx-NCR-002555 | NCR | MFD 1308 Damper A&M |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2021-02-23 | 2020-08-06 15:18 | -201 | 2020-05-19 13:53 | Mechanical - Heating Ventilation & Air Conditioning | 2999 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Platform Level +4 Moorgate shaft, motorised fire damper 1308 cannot be accessed safely to carry out A&M tasks due to the surrounding services.
| 02SL - Stations (LUL) | Cxxx-NCR-002556 | NCR | TUN - Piston effect ductwork bracketry installed without approved design |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2020-07-22 | 2021-01-11 09:36 | 173 | 2020-05-27 06:49 | Mechanical - Mechanical Engineering General | 2999 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Additional bracketry to transfer piston effect loads to ductwork in the running tunnels was designed by __. __ produced detail drawings based on the __ design intent but the drawings were not issued to eB and accepted ahead of installation of the brackets.
| 02SL - Stations (LUL) | Cxxx-NCR-002557 | NCR | P&T AP2 - door floor motor box |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2020-07-31 | 2020-08-27 15:59 | 27 | 2020-05-27 11:15 | Architectural - Flooring | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Floor mounted motor boxes for powered smoke doors in passage AP2 were been fitted on site. A checker plate finish on the FFL is not acceptable. The floor mounted motor box needs to be dropped to allow terrazzo floor finishes to be installed over the cover. A sketch detailing the arrangement was produced, but the proposal was not formally issued under and FCD. Remedial works include breaking back screed and re-installing the box at a lower level. A terrazzo infill tray to be installed. __s will need to confirm that an extender piece to connect the spindle on the motor to the door hinge can be provided. Note: this issue was raised on CRL observation CRL-OBS-0029576.
| 02SL - Stations (LUL) | Cxxx-NCR-002558 | NCR | BTH - Clash between signs and lift (8&9) portal cladding |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2020-12-13 | 2021-03-18 16:45 | 95 | 2020-05-27 11:58 | Architectural - Signage | 2000 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Clash between signs and lift (8&9) portal cladding, see attached sketchs
| 02SL - Stations (LUL) | Cxxx-NCR-002559 | NCR | AP9 Terrazzo Joint mis-aligned damaged |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2020-08-28 | 2020-09-24 15:11 | 27 | 2020-05-27 14:58 | Architectural - Flooring | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | The structural movement joint has been laid in two parts. One section (the shorter) appears to be working reasonably well. The second, longer section is not working properly. Something seems to be preventing the joint from operating correctly; likely an installation problem. Note that a similar problem was identified and closed in NCR 2420. These issues were noted in CRL observation CRL-OBS-29673
| 02SL - Stations (LUL) | Cxxx-NCR-002560 | NCR | Number of Hinges on __ Doorsets |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2020-11-24 | 2021-01-11 10:46 | 48 | 2020-06-02 22:12 | Architectural - Doors | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | Doorsets manufactured and supplied By __ (__) do not comply with JP21.1211 @Hinges@ section of the Architectural Specification and in particular point i) which states: 3No. butt hinges shall be provided to each leaf, unless the height of the door is over 2040mm when 4No. butt hinges shall be provided. The majority of __ doors have been supplied with 2No hinges per leaf.
| 02SL - Stations (LUL) | Cxxx-NCR-002562 | NCR | __X/Moorgate shaft - missing emergency lighting |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2020-08-31 | 2021-01-12 10:20 | 134 | 2020-06-05 13:49 | Electrical - Lighting | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Emergency lighting fitting has not been supplied and fitted to the entrance of Blomfield Box ,Moorgate Shaft escape routes and Moorgate Ticket Hall. The cladding to Blomfield Box has been completed without the light fitting in place.
| 02SL - Stations (LUL) | Cxxx-NCR-002563 | NCR | Moorgate Shaft Accommodation Heater Clash SSO Mess Room |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2020-09-24 | 2020-11-05 09:57 | 42 | 2020-07-22 13:41 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | This NCR Is to capture the heater clash with the draw within Moorgate Shaft Accommodation SSO Mess Room
| 02SL - Stations (LUL) | Cxxx-NCR-002564 | NCR | lighting design calculations for escalator skirt lighting |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2020-07-07 | 2020-06-30 10:29 | -7 | 2020-06-09 13:43 | Electrical - Lighting | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | PMI Cxxx-PMI-02092 issued on the 22nd may 2020 requesting the below. to supply evidence of the Contractor’s electrical design and supporting calculations that demonstrate that a compliant solution has been implemented for each bank of escalators. This should include both the escalator skirt lighting circuit design, inrush currents, protective devices and all cabling. The Contractor is requested to provide this information within one week of receipt of this instruction to date there has been no formal response to this PMI and no evidence provided
| 02SL - Stations (LUL) | Cxxx-NCR-002565 | NCR | MTH - Clash with Poster Frame and Ticket Machine |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2020-09-30 | 2021-01-22 11:33 | 114 | 2020-06-09 15:27 | Archaeology - General | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A clash between the poster frame and ticket machine exists (adjacent to the SOR). Both the poster case and the ticket machine are able to be opened, but the poster case cannot be opened to 90°.
| 02SL - Stations (LUL) | Cxxx-NCR-002567 | NCR | Moorgate Shaft - Platform Level +4 - Smoke Extract Fan Room temperatures |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2021-04-22 | 2020-10-21 12:46 | -183 | 2020-07-16 07:16 | Mechanical - Mechanical Engineering General | 5000 |  | Design | Repair | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | MGS fan room containing platform smoke extract fans also contains the fan inverters. None of the ductwork is insulated despite potential for surfaces to reach circa 270 degrees Centigrade. The control equipment within the room are at risk of shutting down due to elevated temperatures when in operation.
| 02SL - Stations (LUL) | Cxxx-NCR-002568 | NCR | Moorgate Shaft - Platform Level +1 Future Plant Room - Room temperatures |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2021-04-28 | 2020-09-29 08:39 | -211 | 2020-07-22 09:30 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | This non conformance was raised by the contractor over the potential heat radiation from the life safety ductwork within the Moorgate shaft Platform level +1 future plant room heating up the local vicinity and potentially causing the DC cabinet to over heat and fail in operation.
| 02SL - Stations (LUL) | Cxxx-NCR-002569 | NCR | Moorgate Shaft - Street Level +1 Fan A02 & A03 - Room Temperatures |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2020-12-16 | 2021-02-09 15:28 | 55 | 2020-07-16 07:20 | Mechanical - Heating Ventilation & Air Conditioning | 2999 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | MGS fan room containing air release fans also contains fan inverters. None of the ductwork is insulated despite potential for surfaces to reach elevated temperatures. The control equipment within the room are at risk of shutting down due to elevated temperatures when in operation.
| 02SL - Stations (LUL) | Cxxx-NCR-002570 | NCR | Blomfield Box - Street Level +2 Fan B51 & B52 - Room Temperatures |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2021-04-22 | 2020-11-04 16:24 | -169 | 2020-07-16 07:26 | Mechanical - Heating Ventilation & Air Conditioning | 12000 |  | Design | Repair | 2 (6-60k) | Complete | Design Problem - Not Defined | Completed |  | __ fan room containing air release fans also contains fan inverters. None of the ductwork is insulated despite potential for surfaces to reach elevated temperatures. The control equipment within the room are at risk of shutting down due to elevated temperatures when in operation.
| 02SL - Stations (LUL) | Cxxx-NCR-002571 | NCR | BTH Canopy Poster Frames |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2021-07-31 | 2021-11-10 12:07 | 102 | 2020-07-01 13:54 | Architectural - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The poster frames installed within the Broadgate Ticket Hall canopy at street level on the upstands are designed to heights that are non-compliant with the Works Information and LU standard 1-313, which both describe the maximum top of the standard TfL poster frame at 2.080mm above FFL.
| 02SL - Stations (LUL) | Cxxx-NCR-002572 | NCR | Fire Panel Config Schedule Beacon References |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2020-07-29 | 2020-07-01 13:53 | -28 | 2020-07-01 09:34 | Fire - Fire Systems & General | 500 |  | Software | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The description of the Fire Alarm Beacons on the Fire Panel printout the “Config Schedule” does not describe Beacons with their correct manufacturer’s model reference. The Fire Panel printout “Alarm System Configuration Data” (the “Config Schedule”) is produced via software, supplied with the Fire Panel, direct from the manufacturer, and cannot be modified by the site team. __ have installed “__ Wall Sounder Beacon Red Case Red LEDs (CHQ-WSB2/RL)” onto “__ Wall Mounting Base YBO—R/3 (RED) at Liverpool Street Station. The sounders within these Beacon units have been disabled and do not emit an audible warning when in use. The sole purpose of the CHQ-WSB2 in this installation is to act as a visual warning only. All Design Drawings, Schematics, the L-Class designation and the Asset Data within the AIMS Database refer to the installed units as Beacons. The software automatically recognises devices connected to the system and allocates a “Device Description” from the “signature” signal received from each individual device. However as stated by __, the Beacon Manufacturer, “If a Control Panel has not implemented the CHQ-WSB then it will be recognised as a YBO-BSB”. In the Config Schedule printout the Beacons are allocated the inaccurate Device Description “Sounder/Beacon Base (YBO-BSB)”.
| 02SL - Stations (LUL) | Cxxx-NCR-002573 | NCR | BTH - CoL Totem Damaged Glass |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2020-10-31 | 2020-08-27 17:30 | -65 | 2020-07-03 11:39 | Civil - Street Furniture | 25000 |  | Damaged | Reject | 2 (6-60k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Further to installation of the City of London totem at the entrance to BTH, the following issues have been noted: 1) Broken map panel 2) Totem 25mm out of verticality 3) 1no. holding down nut not installed 4) Signage facing the wrong way 5) Replace temporary upper vitreous panels 6) Roundel damaged 7) Gaps around base trim 8) Panels not flush around installation 9) Gaskets damaged, pinched or not in alignment 10) Cracked edges and delamination around corners of signs 11) Varying/tapering gaps around panels 12) Rust appearing to stainless steel panels 13) Scuffs and damage to all stainless trims 14) No CE marking evident on the glass 15) At point of wiring, earth connection fell out of junction box 16) “Cellotape” introduced to wiring connection 17) Armouring stripped from cable at time of installation
| 02SL - Stations (LUL) | Cxxx-NCR-002575 | NCR | SCS SAT for MGS OPE |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2020-08-05 | 2020-09-09 13:03 | 35 | 2020-07-08 09:12 | Electrical - General | 500 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The SCS SAT for MGS OPE will be conducted on Fri 10 July 2020. The SAT document is currently coded 2 and has minor comments. The responses to the comments are to be reviewed in conjunction with CRL on the 8th July. If the responses are approved the test will be conducted with the revised SAT and the document will be submitted for approval via the usual channel. If the comments are not approved, the SAT will proceed as planned using the existing SAT document and additional tests shall be performed at a later to cover the additional scope.
| 02SL - Stations (LUL) | Cxxx-NCR-002576 | NCR | MTH - CoL Sign adhesive |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2022-11-11 | 2022-11-15 10:36 | 4 | 2020-07-10 15:09 | Architectural - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Further to installation on September 2019, it has been found that inspection by 07/07/2020 CRL achitecture representative that the adhesive is not suitable. It has been agreed with City of London deem the installation acceptable. Cxxx raise this NCR to allow for the ADM mechanism. It has been agreed that CRL are to transfer the installation
| 02SL - Stations (LUL) | Cxxx-NCR-002578 | NCR | Heater in female locker room 2/318 Moorgate ST-1 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2020-10-07 | 2020-10-22 10:06 | 15 | 2020-08-17 08:08 | Architectural - General | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | Female Locker room 2/318 - Headroom under electric heater-risk of hitting head on heater. __ have issued Cxxx-HB-SK11829 to resolve issue which is acceptable by __ .
| 02SL - Stations (LUL) | Cxxx-NCR-002579 | NCR | Signage Lower than 2300mm AFFL |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2020-12-23 | 2020-12-22 15:43 | -1 | 2020-08-21 07:38 | Architectural - Signage | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | USN 437 in CP9/10 and USN 340 in AP10, when it is installed, do not achieve a minimum of 2300mm to the underside of the sign
| 02SL - Stations (LUL) | Cxxx-NCR-002580 | NCR | CP5 SCL Leak Causing Damage to Lighting Boom, GRC and Tiling Finsihed Works |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2020-12-18 | 2021-02-26 12:45 | 70 | 2020-08-26 07:31 | Civil - Civil Engineering General | 4000 |  | Damaged | Rework | 3 (3-6k) | Complete | External Phenomenon - Other | Completed |  | SCL in CP5 is leaking causing damage to Cxxx assets including but not limited to; DAL Lighting Boom, GRC Cladding, Terrazzo Floor Tilling. Assets are to be repaired or replaced to previous client signed off condition. For clarification this is not an NCR for Cxxx works. Works to be performed in conjunction with Cxxx-PMI-02131 - TUN: Leak within CP5 and CP7 and costed to this.
| 02SL - Stations (LUL) | Cxxx-NCR-002581 | NCR | ___14a_AP5_Level_Sip-Sop_(__ Internal Cabinet door opening wrong Side) |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2020-11-03 | 2020-10-27 12:58 | -7 | 2020-09-08 16:21 | Architectural - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Miss-alignment between the internal communication box and SIP/SOP __ Panel doors. The hinge to the cladding cannot be amended to the left had side to correspond to the SIP/SOP as this is adjacent to the Lift Portal.
| 02SL - Stations (LUL) | Cxxx-NCR-002582 | NCR | BTH - AP8/LU Interface Structural Movement Joint Installation |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2020-10-16 | 2020-10-14 08:52 | -2 | 2020-09-18 11:41 | Architectural - Flooring | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | 2 no. structural movement joints were installed in the Broadgate Ticket Hall AP8/LU interface area
| 02SL - Stations (LUL) | Cxxx-NCR-002583 | NCR | Advertising Screens Interface on the Escalators- End Detail |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2020-11-10 | 2021-01-21 14:15 | 72 | 2020-09-21 16:00 | Architectural - Walls | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | As per the attached communications end alignment of GRC, design rational end stainless panels and RSS barrel cladding doesn't form continuous line.
| 02SL - Stations (LUL) | Cxxx-NCR-002584 | NCR | EI Doors - __x - 120 Mins FR |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2021-03-31 | 2021-03-29 08:55 | -2 | 2021-01-25 20:31 | Architectural - Doors | 20000 |  | Design | Use As-Is | 2 (6-60k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The two large EI Doors, E-01-781-D01 and E-01-782-D01, both at __x Street level double doors to Transformer rooms, have not passed the test criteria for 120 mins fire rating. Further assessments have been undertaken by Cxxx (__/__ Fire/__ Ind.) and the certification has not been achieved
| 02SL - Stations (LUL) | Cxxx-NCR-002586 | NCR | BTH - Blocked drainage pipe, back of wall drainage, basement level |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2021-03-07 | 2020-11-18 09:52 | -109 | 2020-10-08 13:03 | Civil - Drainage | 4000 |  | Damaged | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the final CCTV of BTH basement cast-in drainage, a partial grout blockage was noted. Several attempts to clear with high pressure jetting was unsuccessful. Access is restricted due to back of wall drainage detail (detail 1 on drg 30003) and the length of pipe + no. of bends from the basement sump. A final, and partially successful attempt was made to clear the blockage (grout was removed) using a grinding chain, however the grinding head/chain was irrecoverably lost in the pipe. Please can you review the location of the blockage, anticipated flow, and advise if the basement back of wall drainage system can be deemed functional with only 9 out of 10 of the back of wall outlets functioning as designed. Breaking down through the structure at this location to effect a repair on the pipe would involve cutting out a large area of the base slab reinforcement, with very limited options for repairing the structure.
| 02SL - Stations (LUL) | Cxxx-NCR-002587 | NCR | GEN - Formal certification/assessment of BSB SC series VCD's in fire rated ductwork |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2021-03-26 | 2021-03-16 16:23 | -10 | 2020-10-14 10:02 | Fire - Compartmentation | 20000 |  | Documentation and Records | Use As-Is | 2 (6-60k) | Complete | Subcontractor Problems - Insufficient surveillance of subcontractors | Completed |  | Further to Cxxx-NCR-001991, related PTR Cxxx-RFI-004512 and the closeout of the original issue via __ report Cxxx-LAO-E1-RGN-C101-50109 it has been identified that the agreed closeout did not include formal certification or assessment from a UKAS accredited test house for the as installed arrangement in __ fire rated ductwork.
| 02SL - Stations (LUL) | Cxxx-NCR-002588 | NCR | GEN - Formal certification/assessment of __ MB120 VCD's in fire rated ductwork |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2021-03-26 | 2021-03-04 10:04 | -22 | 2020-10-14 10:10 | Fire - Compartmentation | 5000 |  | Documentation and Records | Use As-Is | 3 (3-6k) | Complete | Subcontractor Problems - Insufficient surveillance of subcontractors | Completed |  | __ MB120 type VCD's have been installed in fire rated ductwork for balancing the system. This VCD type while taking the majority of it's construction from other tested and certified damper products from the same manufacturer (__ ) does not itself have formal fire certification/assessment evidence for the as installed arrangement inline, in __ ductwork.
| 02SL - Stations (LUL) | Cxxx-NCR-002589 | NCR | TUN - Swap SIP And SOP Panels at Lift 7 Entrance Layout (PMI 1588) |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2021-03-15 | 2021-03-04 16:52 | -11 | 2020-10-22 12:43 | Mechanical - Lifts | 5000 |  | Incomplete Works | Use As-Is | 3 (3-6k) | Complete | Management Problem - Other management problem | Completed |  | The Contactor was instructed under Cxxx-PMI-01588 to implement the response issued under FCD-002059 to swap the Staff Interface Panel (SIP) to platform level and Staff Operations Panel (SOP) to AP2 level in connection with Lift 7. This was not enacted upon and therefore will result in rework and update to the fire strategy
| 02SL - Stations (LUL) | Cxxx-NCR-002591 | NCR | __ door W-01-072-D01( Hold open double door) too low. |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2020-12-24 | 2021-01-14 15:15 | 21 | 2020-11-06 10:16 | Architectural - Doors | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Previously raised as Cxxx-NCR-002585 on the wrong template (C501). This is now raised on the Cxxx template to enable closure of issue through the NCR process. __ door W-01-072-D01( Hold open double door) has been install too low.
| 02SL - Stations (LUL) | Cxxx-NCR-002592 | NCR | Camera 164 cable length fail at 94.9m |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2020-12-10 | 2020-12-10 10:06 | 0 | 2020-11-12 12:44 | Communications and Control Systems - CCTV | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The Fluke test on the cable for Camera 0164 located in the POM room in the Moorgate Ticket Hall back of house area tests the cable at 94.9m, the camera is in its design location
| 02SL - Stations (LUL) | Cxxx-NCR-002593 | NCR | Incorrect values for pull tests on __ ITPs |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2020-12-14 | 2021-04-28 06:46 | 135 | 2020-11-16 17:02 | Architectural - Finishes | 500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Upon review of QA packs it was identified that the referenced ITP did not specify location specific pull test values. In this case the ITP (Cxxx-LAO-04-ITP-C101-50312) reference was greater than required. __ have tested to the lower value, therefore not meeting the standard stated in the ITP. The lower value meets the design requirements and the non conformance lies within the pre start documentation and record.
| 02SL - Stations (LUL) | Cxxx-NCR-002594 | NCR | Camera 336 M135-DAT-04424 cable length fail at 155.3m |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2020-12-17 | 2020-12-10 10:07 | -7 | 2020-11-19 07:39 | Communications and Control Systems - CCTV | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The cable distance for camera 336 at platform level is 155.3m
| 02SL - Stations (LUL) | Cxxx-NCR-002596 | NCR | Camera 336 M135-DAT-04424 cable length fail at 155.3m |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2021-04-30 | 2021-03-05 14:00 | -56 | 2020-11-24 14:23 | Communications and Control Systems - CCTV | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Distance from Rack to camera exeeds the 90m rule
| 02SL - Stations (LUL) | Cxxx-NCR-002597 | NCR | Omission of vision panel to Doors E-02-762-D01 (FCR) and E-03-761-D01 (MCC) |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2021-09-09 | 2021-08-25 08:06 | -15 | 2021-08-12 12:03 | Architectural - Doors | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The Cxxx design door schedules list doors E-02-762-D01 (FCR) and E-03-761-D01 (MCC) as requiring vision panels. The doors have been detailed, manufactured and installed without vision panels.
| 02SL - Stations (LUL) | Cxxx-NCR-002601 | NCR | MTH - Lack of approved documentation for LU interface Floor Infill |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2021-01-29 | 2021-05-10 14:35 | 101 | 2020-12-07 16:44 | Architectural - Flooring | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Information not detailed | Completed |  | Infill flooring to the LU interface on the westbound of metropolitan line commenced without approved documentation. No formal agreement on design through (FCD) - FCD was submitted prior, but works did not wait for formal CRL approval. No approval of MCRs (Tiles, Grout) - materials were detailed on the submitted FCD. but MCRs were not submitted before commencing.
| 02SL - Stations (LUL) | Cxxx-NCR-002602 | NCR | MTH - Matwell ITP Clarification |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2021-03-31 | 2021-02-24 12:25 | -35 | 2021-01-15 14:19 | Architectural - Flooring | 500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | The permanent Matwell installed in MTH is drained. The ITP references a temporary (undrained) Matwell however the product is covered by MCR (Cxxx-LAO-O4-XDS-C101-50814) and the drainage has been inspected by CRL (Cxxx-XRL-O4-RGN-C101-50018) and all aspects of the installation have been covered by the QA pack (Cxxx-LAO-C-LRC-C101_WS099-50558). Cast-in drainage is covered by the SCC for the civils works (Cxxx-LAO-C-CER-C101_WS099-50046)
| 02SL - Stations (LUL) | Cxxx-NCR-002603 | NCR | Grout tests to AP doors cladding steel work |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2021-01-11 | 2021-04-21 16:11 | 100 | 2020-12-14 16:05 | Structural Engineering - Grouting | 500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Not Defined | Completed |  | Section 3.4 of ITP Cxxx-LAO-04-ITP-C101-50312 states for grouting of baseplates at each installation 4No cubes will be taken in accordance with BS EN 12350 with a minimum 40N required. Grout install and testing to be completed by __ as per the __ method/ITP. The deliverable of this section of the ITP is noted as a grout cube report. A grout cube report has not been produced for this specific area, instead reports have been produced for the batch of grout used, which does not specifically reference the area covered under the ITP.
| 02SL - Stations (LUL) | Cxxx-NCR-002604 | NCR | ___01A Scope Elevation W_Glass Clad Doors |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2021-02-01 | 2021-04-16 08:31 | 74 | 2021-01-04 09:08 | Architectural - General | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The 4no Glass clad doors on elevation W, __ scope 01A, required a specific opening sequence. If for whatever reason this sequence is not follow the glass will break.
| 02SL - Stations (LUL) | Cxxx-NCR-002605 | NCR | MTH - SL-1 - Floor plate to balustrade base |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2021-04-06 | 2021-05-28 16:22 | 52 | 2021-01-06 10:18 | Architectural - Flooring | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The baseplate for the glazed balustrade does not correspond to the finished floor level. A floor plate will need to be introduced over the baseplate to accommodate the difference in levels
| 02SL - Stations (LUL) | Cxxx-NCR-002606 | NCR | MTH - SL-1 - Balustrade glazing |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2021-03-31 | 2021-03-31 10:15 | 0 | 2021-01-13 09:13 | Architectural - Glazing | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The laminated glazing installed for the balustrade base is made from toughened/toughened glass. This differs from the toughened/heat strengthened glazing prescribed in the specification The clamped/bolted channel + toughened/toughened glazing system has been assessed by RSS engineers (Cxxx-LAO-C-XCL-C101_WS099-50068). Similarly, the __ + toughened/toughened system has been assessed by PADs engineers (Cxxx-LAO-A-XCL-C101_WS099-50021). The Risk Assessment (Cxxx-LAO-O4-RGN-C101-50195) doesn’t address the interactions between the channel and the glazing – this is done by our subcontractors. The risk assessment addressed the differences between __ or bolted system ¦ toughened/toughened or toughened/heat strengthened system ¦ chamfer or no chamfer. Deviation from the WI and all associated implications with regard to the glazing composition has been comprehensively checked in all in the aforementioned Risk Assessment and Cxxx-NCR-002549
| 02SL - Stations (LUL) | Cxxx-NCR-002607 | NCR | AP10 - Floor & Wall Tiling - Inspections |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2021-02-16 | 2021-01-28 14:24 | -19 | 2021-01-19 17:33 | Architectural - Flooring | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Inspection points not adequate | Completed |  | CRL inspection of the screed/render in AP10 upper lobby not carried out NCR also reference for CRL inspection of AP10 lower wall tiling and skirting
| 02SL - Stations (LUL) | Cxxx-NCR-002608 | NCR | Labelling of Assets In Locations Not Identified in the Labelling Convention |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2021-03-31 | 2021-02-15 11:02 | -44 | 2021-01-21 17:08 | Information Management - Asset Information | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Further to a query from __ , and RFI 4856, regarding the position for C&D Isolators' labels it was identified that where the asset was not fixed to a structural wall, the label was subsequently attached to the asset, or as close to the asset as possible, and not to a nearby wall. With several isolators in one room identifying the specific isolator by means of a label on a wall some distance from the asset would create confusion, as to which isolator each label corresponded to, so the label was attached to, or adjacent to, the asset to avoid this confusion. The guidance from the Asset Naming and labelling Convention document {CRL1-XRL-Z3-ADDSD-CR001-50413} for labelling of L746155 – Isolator; "……... the Asset Tag Label shall be placed on a permanent structure next to the item ......." . As it is not feasible to comply with the Guidance under the circumstances described above insofar as an asset label cannot be “…placed on a permanent structure next to the item….” as the asset is not affixed to a permanent structure and also there is no ”…. structure next to the item….” . This situation is repeated throughout the project and affects multiple asset types including Isolators, actuators, fire damper (label should be on the item and it is on the actuator), control & indicating equipment, water heaters, pump controls, inverters, control panels, dali (50% of cases), auto transfer switches, condensers, interface units (50%), and water tanks, where achieving the stated convention was not feasible or the convention did not apply..
| 02SL - Stations (LUL) | Cxxx-NCR-002610 | NCR | Finishing floor paint to street +5 |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2021-05-28 | 2021-06-25 14:38 | 28 | 2021-02-01 14:40 | Architectural - Flooring | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | __X at street +5 level, The paint to floor screed at the locations of a fall from roof rain water discharge to floor gully seems to be bubbling, attached photos of the inspection of the area
| 02SL - Stations (LUL) | Cxxx-NCR-002611 | NCR | __ Light Fittings K1 / KS Communication Fault With DALI Lighting Control System |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2021-11-08 | 2021-05-20 09:47 | -172 | 2021-02-01 16:55 | Electrical - Electrical Engineering General | 40000 |  | Design | Rework | 2 (6-60k) | Complete | Material/Preservation Problems - Other | Completed |  | __ __, Luminaire type K1/KS fails to communicate LAMP Failure with the DALI lighting control system This is contrary to CRL1-XRL-M-RSP-CR001-50044 JV 40 EMERGENCY LIGHTING , JV40.1301 w Mitigation measure to be agreed with CEG
| 02SL - Stations (LUL) | Cxxx-NCR-002612 | NCR | MTH - In-situ Skirting |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2021-02-05 | 2021-04-23 16:24 | 77 | 2021-02-03 22:01 | Architectural - Flooring | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | The project specification does not specifically identify areas of in-situ skirting
| 02SL - Stations (LUL) | Cxxx-NCR-002613 | NCR | Short Circuit Isolation Failure |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2021-03-19 | 2021-05-18 13:54 | 60 | 2021-02-09 08:56 | Fire - Detection | 2999 |  | Testing and Commissioning | Repair | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | During Over & Back testing of 28/01/2021 an LU requested test was performed at Blomfield Box Street Level -1 whereby two manual call points, (P09/L25/D48) & (P09/L25/D57) were short circuited thereby simulating a short circuit isolation. Under this condition, some loop devices connected in between the two manual call points remained active and therefore considered a failed test.
| 02SL - Stations (LUL) | Cxxx-NCR-002614 | NCR | BTH - Lift 8 Primer Leakage onto Lift Equipment |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2021-05-13 | 2021-05-06 14:38 | -7 | 2021-02-10 09:29 | Mechanical - Lifts | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Other human error | Completed |  | While prepping for the screeding of the floor hatch above lift motor room, some primer leaked through into the motor room below and onto various pieces of lift equipment.
| 02SL - Stations (LUL) | Cxxx-NCR-002615 | NCR | Contractor Commenced works without an accepted ITP relevant to works undertaken |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2021-05-31 | 2021-04-30 11:53 | -31 | 2021-02-15 13:33 | Architectural - Flooring | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | During a planned surveillance it was found that the Inspection and Test Plan for the installation of Eastern and Western Ticket Mat wells Cxxx-LAO-O4-ITP-C101_WS099-50078 Rev 3.0 Code1 was not relevant to the installation. The only reference on the ITP is for a temporary Mat well installation.
| 02SL - Stations (LUL) | Cxxx-NCR-002616 | NCR | MTH – Finishes Street Level & PRM Corridor - Benchmark and Quality Records |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2021-05-31 | 2021-05-11 13:16 | -20 | 2021-03-11 15:49 | Architectural - Flooring | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Following submittal of QA pack Cxxx-LAO-C-LRC-C101_WS099_1-50001 Rev 1.0 it was determined that no benchmark evidence was referenced and the pack did not contain evidence of inspection of the first area of installed tiles and grout.
| 02SL - Stations (LUL) | Cxxx-NCR-002617 | NCR | AP5-AP6 Emergency Exit Signage |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2022-02-14 | 2021-09-07 12:36 | -160 | 2021-03-16 10:25 | Architectural - Signage | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Emergency escape signage provided on USN 402 at the bottom of AP5-AP6 staircase is not visible enough from AP5 and the emergency escape signage provided on USN 304 at the top of AP5-AP6 staircase is incorrect because it directs able bodied persons in the same direction as persons with reduced mobility.
| 02SL - Stations (LUL) | Cxxx-NCR-002618 | NCR | SEELE_Portland Stone on Broadgate Glass Canopy_Missing Benchmark |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2021-04-13 | 2021-03-21 21:39 | -23 | 2021-03-16 11:24 | Architectural - General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | Works are in progress for the installation of the Portland Stone Cladding at the Broadgate Glass Canopy. The first installed material of each type requires a Benchmark for CRL acceptance.
| 02SL - Stations (LUL) | Cxxx-NCR-002619 | NCR | AP2 __ Cabinet Doors – Opening Sequence |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2021-05-14 | 2021-06-23 11:35 | 40 | 2021-03-16 14:23 | Architectural - General | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The 3no stainless steel __ cabinet doors in AP2 require a specific opening sequence.
| 02SL - Stations (LUL) | Cxxx-NCR-002620 | NCR | AP2 __ Cabinet - Anti Drumming |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2021-04-23 | 2021-04-29 10:48 | 6 | 2021-03-18 14:31 | Architectural - General | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | AP2 __ cabinet design does not include anti drumming insulation
| 02SL - Stations (LUL) | Cxxx-NCR-002621 | NCR | AP2 - Door Functionality |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2021-11-30 | 2021-12-17 12:08 | 17 | 2021-04-09 13:50 | Architectural - Doors | 20000 |  | Testing and Commissioning | Repair | 2 (6-60k) | Complete | Design Problem - Other | Completed |  | The bespoke set of AP2 doors fails to meet some of the specified criteria.
| 02SL - Stations (LUL) | Cxxx-NCR-002622 | NCR | Blomfield Box - Amended Gate Operation |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2021-06-30 | 2021-06-23 15:31 | -7 | 2021-04-20 10:05 | Architectural - Security | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | __X maintenance gate E-01-241-D01 - locking does not comply with emergency exit strategy. The gate was instructed under PMI Cxxx-PMI-00535 and the Works Information requires SR3 rating or SR2 minimum. The gate is on a secondary escape route from adjacent plant rooms, it opens inwards and has a padlock, key and bolt operation to meet SR3 requirements. These locking features on the gate however do not comply with Emergency Fire escape routes strategy from adjacent Plant rooms. In achieving the emergency exit requirements it will reduce the security capability.
| 02SL - Stations (LUL) | Cxxx-NCR-002623 | NCR | Proof Load testing has not been carried out as required in Architectural Specification |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2021-05-17 | 2021-04-29 07:34 | -18 | 2021-04-22 09:54 | Architectural - Finishes | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | During a planned Surveillance on Architectural Assurance Packs, it was found that no evidence was found for proof load testing for Key Clamp handrails and gates as required in Cxxx Liverpool Street Architectural Specification Cxxx-LAO-A-RSP-C101_WS103-50001 JL32. It was also found that the requirement was not referenced in Installation of Key-clamp Handrails and Gates in Moorgate Shaft’ Cxxx-LAO-O4-ITP-C101_WS099-50095 Rev 1
| 02SL - Stations (LUL) | Cxxx-NCR-002624 | NCR | Contractor has not followed their Document and Data Control Procedure for the checking of Red Line Drawings. |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2021-05-07 | 2021-04-27 13:03 | -10 | 2021-04-22 10:16 | Architectural - Finishes | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other management problem | Completed |  | During a planned surveillance of Architectural assurance records, the Contractor was requested to provide CVs for Checkers as shown on decal stamps, to confirm their competency’s for checking Red Line drawings. On reviewing both CVs, it was found that neither had the relevant competencies to comply with ‘Cxxx–Document and Data Control Procedure’ Cxxx-LAO-O4-GPD-C101-50005 Rev 9.0